## Descriptions
AGC 150 Modbus descriptions
Software version
The information contained in these tables (Revision J) is applicable to software version 1.0.9.0 of the AGC 150.
Row | Hyperlink index
13 | Modbus function codes
24 | Discrete output coil
32 | Discrete input contact
41 | Output holding register
52 | Input register
Back to index | Modbus function codes
| Function code | Description
| 01 | Read a single or multiple discrete output coils.
| 02 | Read a single or multiple discrete input contacts.
| 03 | Read a single or multiple output holding registers.
| 04 | Read a single or multiple input registers.
| 05 | Write a value to a single discrete output coil.
| 06 | Write a value to a single output holding register.
| 15 | Write a value to multiple consecutive discrete output coils.
| 16 | Write a value to multiple consecutive output holding registers.
Back to index | Discrete output coil
| Function code | Effect
| 01 | Read
| 05 or 15 | Write
| Function group | Description
| Command flag | Activate a command in the controller. Read: The controller always returns 0 (false). Write: The controller executes the command if you write 1 (true).
Back to index | Discrete input contact
| Function code | Effect
| 02 | Read
| Function group | Description
| Digital input | Read the state of a digital input on the controller. The controller returns 0 (false) when the digital input is inactive. The controller returns 1 (true) when the digital input is active.
| Digital output | Read the state of a digital output on the controller. The controller returns 0 (false) when the digital output is inactive. The controller returns 1 (true) when the digital output is active.
| Status flag | Read whether a status flag is activated. The controller returns 0 (false) when the status flag is not activated. The controller returns 1 (true) when the status flag is activated.
Back to index | Output holding register
| Function code | Effect
| 03 | Read
| 06 or 16 | Write
| Function group | Description
| Control command | Activate a command in the controller. Read: The controller always returns 0 (false) from the bits. Write: The controller executes the command if you write 1 (true) to the address bit.
| Control time command | Read and write the time and date values of the controller. Read: The controller returns the value of the associated function. Write: The controller changes the value of the associated function if a valid value is entered.
| Weather area | Weather data.
| Write area 1 (PLC/external system to ASC) | Part of the DEIF Open protocol. A PLC or external system writes data here for the ASC to use.
Back to index | Input register
| Function code | Effect
| 04 | Read
| Function group | Description
| AC alarm | Read one bit to see whether the AC alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| AC measurement | Read the operating value of the associated AC measurement.
| Alarm | Read one bit to see whether the alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| APPL version | Read the controller application version.
| Control command state | Read the state of all the bits in the control command address.
| Counter | Read the counter value.
| DAVR alarm | Read one bit to see whether the digital AVR alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| DAVR measurement | Read the operating value of the associated digital AVR measurement.
| DC measurement | Read the operating value of the associated measurement.
| EIC alarm | Read one bit to see whether the alarm from engine communication is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| EIC measurement | Read the operating value of the associated engine communication measurement.
| EIC measurements validity | Read one bit to see whether the measurement from engine communication is valid. The controller returns 0 (false) when the mesaurement is not valid. The controller returns 1 (true) when the measurement is valid.
| EIC measurements value | Read the operating value of the associated engine communication measurement. Note: The offsets can be different for EIC measurement and EIC measurements value.
| EIC state | Read one bit to see whether the engine communication state is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| M-Logic state | Read one bit to see whether the M-Logic virtual event or flip-flop is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| Modbus configurable area | Read the value of the function assigned to the address using the Modbus configurator. Additional information about the assigned address should be completed by the user. Modbus addresses 0 to 499 are available for configurable Modbus.
| Modes | Read one bit to see whether the mode is activated. The controller returns 0 (false) when the mode is not activated. The controller returns 1 (true) when the mode is activated.
| Plant logic state | Read one bit to see whether the plant state is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| PM AC measurement | Read the operating value of the associated Power Management measurements and settings.
| PM alarm | Read one bit to see whether the Power Management alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| PM Plant logic state | Read one bit to see whether the Power Management state is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| Profibus configurable area | Read the value of the function assigned to the address using the Modbus configurator. Additional information about the assigned address should be completed by the user. Modbus addresses 0 to 62 are available for configurable Profibus.
| PV monitoring area | The ASC Modbus master can poll key data from the inverter(s) and place it in the designated Modbus slave area for a monitoring system to read. PV monitoring can be used with unicast and broadcast topologies. The number of nodes determines the number of inverters the ASC should poll data from. A maximum of 42 nodes can be monitored. The ASC expects that the ModbusIDs of the inverters are consecutive in order starting from the selected ModbusID and forward. 70 registers are reserved for each inverter. The Modbus addresses are only for the first inverter. Registers for the following inverters are consecutive.
| Relay state | Read one bit to see the relay state. The controller returns 0 (false) when the relay is de-energised. The controller returns 1 (true) when the relay is energised.

## Discrete output coil (01;05;15)
Discrete output coil (01;05;15)
Function group | Modbus address | PLC address | Modbus function code | Controller function name | BTB | MAINS | DG
Command flag | 0 | 1 | 01; 05; 15 | Remote start |  |  | X
Command flag | 1 | 2 | 01; 05; 15 | Remote GB ON |  |  | X
Command flag | 1 | 2 | 01; 05; 15 | Remote TB ON |  | X
Command flag | 1 | 2 | 01; 05; 15 | Remote BTB ON | X
Command flag | 2 | 3 | 01; 05; 15 | Remote GB OFF |  |  | X
Command flag | 2 | 3 | 01; 05; 15 | Remote TB OFF |  | X
Command flag | 2 | 3 | 01; 05; 15 | Remote BTB OFF | X
Command flag | 3 | 4 | 01; 05; 15 | Remote stop |  |  | X
Command flag | 4 | 5 | 01; 05; 15 | Alarm inhibit 1 | X | X | X
Command flag | 5 | 6 | 01; 05; 15 | Alarm inhibit 2 | X | X | X
Command flag | 6 | 7 | 01; 05; 15 | Alarm inhibit 3 | X | X | X
Command flag | 7 | 8 | 01; 05; 15 | Reset GOV/AVR regulation output to offset |  |  | X
Command flag | 9 | 10 | 01; 05; 15 | Alarm ack. | X | X | X
Command flag | 10 | 11 | 01; 05; 15 | Nominal setting 1 | X | X | X
Command flag | 11 | 12 | 01; 05; 15 | Nominal setting 2 | X | X | X
Command flag | 12 | 13 | 01; 05; 15 | Nominal setting 3 | X | X | X
Command flag | 13 | 14 | 01; 05; 15 | Nominal setting 4 | X | X | X
Command flag | 14 | 15 | 01; 05; 15 | Start+sync. (semi) |  |  | X
Command flag | 15 | 16 | 01; 05; 15 | Deload/stop (semi) |  |  | X
Command flag | 16 | 17 | 01; 05; 15 | Island |  | X | X
Command flag | 17 | 18 | 01; 05; 15 | Automatic mains failure (AMF) |  | X | X
Command flag | 18 | 19 | 01; 05; 15 | Peak shaving |  | X | X
Command flag | 19 | 20 | 01; 05; 15 | Fixed power |  | X | X
Command flag | 20 | 21 | 01; 05; 15 | Mains power export (MPE) |  | X | X
Command flag | 21 | 22 | 01; 05; 15 | Load takeover (LTO) |  | X | X
Command flag | 24 | 25 | 01; 05; 15 | MB ON |  | X | X
Command flag | 25 | 26 | 01; 05; 15 | MB OFF |  | X | X
Command flag | 26 | 27 | 01; 05; 15 | Auto start/stop |  | X | X
Command flag | 27 | 28 | 01; 05; 15 | Manual mode |  |  | X
Command flag | 28 | 29 | 01; 05; 15 | Semi-auto mode | X | X | X
Command flag | 29 | 30 | 01; 05; 15 | Auto mode | X | X | X
Command flag | 30 | 31 | 01; 05; 15 | Test mode |  | X | X
Command flag | 31 | 32 | 01; 05; 15 | External frequency control |  |  | X
Command flag | 32 | 33 | 01; 05; 15 | External voltage control |  |  | X
Command flag | 33 | 34 | 01; 05; 15 | External power control |  | X | X
Command flag | 34 | 35 | 01; 05; 15 | External reactive power control |  |  | X
Command flag | 35 | 36 | 01; 05; 15 | External power factor control |  |  | X
Command flag | 36 | 37 | 01; 05; 15 | Capacitive PF |  |  | X
Command flag | 37 | 38 | 01; 05; 15 | Base load |  |  | X
Command flag | 38 | 39 | 01; 05; 15 | 1. priority |  |  | X
Command flag | 40 | 41 | 01; 05; 15 | Application 1 | X | X | X
Command flag | 41 | 42 | 01; 05; 15 | Application 2 | X | X | X
Command flag | 42 | 43 | 01; 05; 15 | Application 3 | X | X | X
Command flag | 43 | 44 | 01; 05; 15 | Application 4 | X | X | X
Command flag | 44 | 45 | 01; 05; 15 | Battery test |  |  | X
Command flag | 46 | 47 | 01; 05; 15 | Synchronise clock to 4:00 a.m. | X | X | X
Command flag | 48 | 49 | 01; 05; 15 | Virtual event 1 | X | X | X
Command flag | 49 | 50 | 01; 05; 15 | Virtual event 2 | X | X | X
Command flag | 50 | 51 | 01; 05; 15 | Virtual event 3 | X | X | X
Command flag | 51 | 52 | 01; 05; 15 | Virtual event 4 | X | X | X
Command flag | 52 | 53 | 01; 05; 15 | Virtual event 5 | X | X | X
Command flag | 53 | 54 | 01; 05; 15 | Virtual event 6 | X | X | X
Command flag | 54 | 55 | 01; 05; 15 | Virtual event 7 | X | X | X
Command flag | 55 | 56 | 01; 05; 15 | Virtual event 8 | X | X | X
Command flag | 56 | 57 | 01; 05; 15 | Virtual event 9 | X | X | X
Command flag | 57 | 58 | 01; 05; 15 | Virtual event 10 | X | X | X
Command flag | 58 | 59 | 01; 05; 15 | Virtual event 11 | X | X | X
Command flag | 59 | 60 | 01; 05; 15 | Virtual event 12 | X | X | X
Command flag | 60 | 61 | 01; 05; 15 | Virtual event 13 | X | X | X
Command flag | 61 | 62 | 01; 05; 15 | Virtual event 14 | X | X | X
Command flag | 62 | 63 | 01; 05; 15 | Virtual event 15 | X | X | X
Command flag | 63 | 64 | 01; 05; 15 | Virtual event 16 | X | X | X
Command flag | 64 | 65 | 01; 05; 15 | Virtual event 17 | X | X | X
Command flag | 65 | 66 | 01; 05; 15 | Virtual event 18 | X | X | X
Command flag | 66 | 67 | 01; 05; 15 | Virtual event 19 | X | X | X
Command flag | 67 | 68 | 01; 05; 15 | Virtual event 20 | X | X | X
Command flag | 68 | 69 | 01; 05; 15 | Virtual event 21 | X | X | X
Command flag | 69 | 70 | 01; 05; 15 | Virtual event 22 | X | X | X
Command flag | 70 | 71 | 01; 05; 15 | Virtual event 23 | X | X | X
Command flag | 71 | 72 | 01; 05; 15 | Virtual event 24 | X | X | X
Command flag | 72 | 73 | 01; 05; 15 | Virtual event 25 | X | X | X
Command flag | 73 | 74 | 01; 05; 15 | Virtual event 26 | X | X | X
Command flag | 74 | 75 | 01; 05; 15 | Virtual event 27 | X | X | X
Command flag | 75 | 76 | 01; 05; 15 | Virtual event 28 | X | X | X
Command flag | 76 | 77 | 01; 05; 15 | Virtual event 29 | X | X | X
Command flag | 77 | 78 | 01; 05; 15 | Virtual event 30 | X | X | X
Command flag | 78 | 79 | 01; 05; 15 | Virtual event 31 | X | X | X
Command flag | 79 | 80 | 01; 05; 15 | Virtual event 32 | X | X | X
Command flag | 121 | 122 | 01; 05; 15 | Clear log | X | X | X
Command flag | 122 | 123 | 01; 05; 15 | Clear Parameter edits | X | X | X
Command flag | 123 | 124 | 01; 05; 15 | Enable external frequency control |  |  | X
Command flag | 124 | 125 | 01; 05; 15 | Disable external frequency control |  |  | X
Command flag | 125 | 126 | 01; 05; 15 | Enable external voltage control |  |  | X
Command flag | 126 | 127 | 01; 05; 15 | Disable external voltage control |  |  | X
Command flag | 127 | 128 | 01; 05; 15 | Enable external power control |  | X | X
Command flag | 128 | 129 | 01; 05; 15 | Disable external power control |  | X | X
Command flag | 129 | 130 | 01; 05; 15 | Enable external VAr control |  |  | X
Command flag | 130 | 131 | 01; 05; 15 | Disable external VAr control |  |  | X
Command flag | 131 | 132 | 01; 05; 15 | Enable external CosPhi control |  |  | X
Command flag | 132 | 133 | 01; 05; 15 | Disable external CosPhi control |  |  | X
Command flag | 133 | 134 | 01; 05; 15 | Enable PM base load |  |  | X
Command flag | 134 | 135 | 01; 05; 15 | Disable PM base load |  |  | X
Command flag | 135 | 136 | 01; 05; 15 | Reset horn | X | X | X
Command flag | 137 | 138 | 01; 05; 15 | DVC 310/D510C: Reset Alarms |  |  | X
Command flag | 142 | 143 | 01; 05; 15 | Virtual event 33 | X | X | X
Command flag | 143 | 144 | 01; 05; 15 | Virtual event 34 | X | X | X
Command flag | 144 | 145 | 01; 05; 15 | Virtual event 35 | X | X | X
Command flag | 145 | 146 | 01; 05; 15 | Virtual event 36 | X | X | X
Command flag | 146 | 147 | 01; 05; 15 | Virtual event 37 | X | X | X
Command flag | 147 | 148 | 01; 05; 15 | Virtual event 38 | X | X | X
Command flag | 148 | 149 | 01; 05; 15 | Virtual event 39 | X | X | X
Command flag | 149 | 150 | 01; 05; 15 | Virtual event 40 | X | X | X
Command flag | 150 | 151 | 01; 05; 15 | Virtual event 41 | X | X | X
Command flag | 151 | 152 | 01; 05; 15 | Virtual event 42 | X | X | X
Command flag | 152 | 153 | 01; 05; 15 | Virtual event 43 | X | X | X
Command flag | 153 | 154 | 01; 05; 15 | Virtual event 44 | X | X | X
Command flag | 154 | 155 | 01; 05; 15 | Virtual event 45 | X | X | X
Command flag | 155 | 156 | 01; 05; 15 | Virtual event 46 | X | X | X
Command flag | 156 | 157 | 01; 05; 15 | Virtual event 47 | X | X | X
Command flag | 157 | 158 | 01; 05; 15 | Virtual event 48 | X | X | X
Command flag | 158 | 159 | 01; 05; 15 | Virtual event 49 | X | X | X
Command flag | 159 | 160 | 01; 05; 15 | Virtual event 50 | X | X | X
Command flag | 160 | 161 | 01; 05; 15 | Virtual event 51 | X | X | X
Command flag | 161 | 162 | 01; 05; 15 | Virtual event 52 | X | X | X
Command flag | 162 | 163 | 01; 05; 15 | Virtual event 53 | X | X | X
Command flag | 163 | 164 | 01; 05; 15 | Virtual event 54 | X | X | X
Command flag | 164 | 165 | 01; 05; 15 | Virtual event 55 | X | X | X
Command flag | 165 | 166 | 01; 05; 15 | Virtual event 56 | X | X | X
Command flag | 166 | 167 | 01; 05; 15 | Virtual event 57 | X | X | X
Command flag | 167 | 168 | 01; 05; 15 | Virtual event 58 | X | X | X
Command flag | 168 | 169 | 01; 05; 15 | Virtual event 59 | X | X | X
Command flag | 169 | 170 | 01; 05; 15 | Virtual event 60 | X | X | X
Command flag | 170 | 171 | 01; 05; 15 | Virtual event 61 | X | X | X
Command flag | 171 | 172 | 01; 05; 15 | Virtual event 62 | X | X | X
Command flag | 172 | 173 | 01; 05; 15 | Virtual event 63 | X | X | X
Command flag | 173 | 174 | 01; 05; 15 | Virtual event 64 | X | X | X
Command flag | 174 | 175 | 01; 05; 15 | Virtual event 65 | X | X | X
Command flag | 175 | 176 | 01; 05; 15 | Virtual event 66 | X | X | X
Command flag | 176 | 177 | 01; 05; 15 | Virtual event 67 | X | X | X
Command flag | 177 | 178 | 01; 05; 15 | Virtual event 68 | X | X | X
Command flag | 178 | 179 | 01; 05; 15 | Virtual event 69 | X | X | X
Command flag | 179 | 180 | 01; 05; 15 | Virtual event 70 | X | X | X
Command flag | 180 | 181 | 01; 05; 15 | Virtual event 71 | X | X | X
Command flag | 181 | 182 | 01; 05; 15 | Virtual event 72 | X | X | X
Command flag | 182 | 183 | 01; 05; 15 | Virtual event 73 | X | X | X
Command flag | 183 | 184 | 01; 05; 15 | Virtual event 74 | X | X | X
Command flag | 184 | 185 | 01; 05; 15 | Virtual event 75 | X | X | X
Command flag | 185 | 186 | 01; 05; 15 | Virtual event 76 | X | X | X
Command flag | 186 | 187 | 01; 05; 15 | Virtual event 77 | X | X | X
Command flag | 187 | 188 | 01; 05; 15 | Virtual event 78 | X | X | X
Command flag | 188 | 189 | 01; 05; 15 | Virtual event 79 | X | X | X
Command flag | 189 | 190 | 01; 05; 15 | Virtual event 80 | X | X | X
Command flag | 190 | 191 | 01; 05; 15 | Virtual event 81 | X | X | X
Command flag | 191 | 192 | 01; 05; 15 | Virtual event 82 | X | X | X
Command flag | 192 | 193 | 01; 05; 15 | Virtual event 83 | X | X | X
Command flag | 193 | 194 | 01; 05; 15 | Virtual event 84 | X | X | X
Command flag | 194 | 195 | 01; 05; 15 | Virtual event 85 | X | X | X
Command flag | 195 | 196 | 01; 05; 15 | Virtual event 86 | X | X | X
Command flag | 196 | 197 | 01; 05; 15 | Virtual event 87 | X | X | X
Command flag | 197 | 198 | 01; 05; 15 | Virtual event 88 | X | X | X
Command flag | 198 | 199 | 01; 05; 15 | Virtual event 89 | X | X | X
Command flag | 199 | 200 | 01; 05; 15 | Virtual event 90 | X | X | X
Command flag | 200 | 201 | 01; 05; 15 | Virtual event 91 | X | X | X
Command flag | 201 | 202 | 01; 05; 15 | Virtual event 92 | X | X | X
Command flag | 202 | 203 | 01; 05; 15 | Virtual event 93 | X | X | X
Command flag | 203 | 204 | 01; 05; 15 | Virtual event 94 | X | X | X
Command flag | 204 | 205 | 01; 05; 15 | Virtual event 95 | X | X | X
Command flag | 205 | 206 | 01; 05; 15 | Virtual event 96 | X | X | X
Command flag | 206 | 207 | 01; 05; 15 | Set flipflop 01 | X | X | X
Command flag | 207 | 208 | 01; 05; 15 | Set flipflop 02 | X | X | X
Command flag | 208 | 209 | 01; 05; 15 | Set flipflop 03 | X | X | X
Command flag | 209 | 210 | 01; 05; 15 | Set flipflop 04 | X | X | X
Command flag | 210 | 211 | 01; 05; 15 | Set flipflop 05 | X | X | X
Command flag | 211 | 212 | 01; 05; 15 | Set flipflop 06 | X | X | X
Command flag | 212 | 213 | 01; 05; 15 | Set flipflop 07 | X | X | X
Command flag | 213 | 214 | 01; 05; 15 | Set flipflop 08 | X | X | X
Command flag | 214 | 215 | 01; 05; 15 | Set flipflop 09 | X | X | X
Command flag | 215 | 216 | 01; 05; 15 | Set flipflop 10 | X | X | X
Command flag | 216 | 217 | 01; 05; 15 | Set flipflop 11 | X | X | X
Command flag | 217 | 218 | 01; 05; 15 | Set flipflop 12 | X | X | X
Command flag | 218 | 219 | 01; 05; 15 | Set flipflop 13 | X | X | X
Command flag | 219 | 220 | 01; 05; 15 | Set flipflop 14 | X | X | X
Command flag | 220 | 221 | 01; 05; 15 | Set flipflop 15 | X | X | X
Command flag | 221 | 222 | 01; 05; 15 | Set flipflop 16 | X | X | X
Command flag | 222 | 223 | 01; 05; 15 | Reset flipflop 01 | X | X | X
Command flag | 223 | 224 | 01; 05; 15 | Reset flipflop 02 | X | X | X
Command flag | 224 | 225 | 01; 05; 15 | Reset flipflop 03 | X | X | X
Command flag | 225 | 226 | 01; 05; 15 | Reset flipflop 04 | X | X | X
Command flag | 226 | 227 | 01; 05; 15 | Reset flipflop 05 | X | X | X
Command flag | 227 | 228 | 01; 05; 15 | Reset flipflop 06 | X | X | X
Command flag | 228 | 229 | 01; 05; 15 | Reset flipflop 07 | X | X | X
Command flag | 229 | 230 | 01; 05; 15 | Reset flipflop 08 | X | X | X
Command flag | 230 | 231 | 01; 05; 15 | Reset flipflop 09 | X | X | X
Command flag | 231 | 232 | 01; 05; 15 | Reset flipflop 10 | X | X | X
Command flag | 232 | 233 | 01; 05; 15 | Reset flipflop 11 | X | X | X
Command flag | 233 | 234 | 01; 05; 15 | Reset flipflop 12 | X | X | X
Command flag | 234 | 235 | 01; 05; 15 | Reset flipflop 13 | X | X | X
Command flag | 235 | 236 | 01; 05; 15 | Reset flipflop 14 | X | X | X
Command flag | 236 | 237 | 01; 05; 15 | Reset flipflop 15 | X | X | X
Command flag | 237 | 238 | 01; 05; 15 | Reset flipflop 16 | X | X | X
Command flag | 238 | 239 | 01; 05; 15 | Toggle flipflop 01 | X | X | X
Command flag | 239 | 240 | 01; 05; 15 | Toggle flipflop 02 | X | X | X
Command flag | 240 | 241 | 01; 05; 15 | Toggle flipflop 03 | X | X | X
Command flag | 241 | 242 | 01; 05; 15 | Toggle flipflop 04 | X | X | X
Command flag | 242 | 243 | 01; 05; 15 | Toggle flipflop 05 | X | X | X
Command flag | 243 | 244 | 01; 05; 15 | Toggle flipflop 06 | X | X | X
Command flag | 244 | 245 | 01; 05; 15 | Toggle flipflop 07 | X | X | X
Command flag | 245 | 246 | 01; 05; 15 | Toggle flipflop 08 | X | X | X
Command flag | 246 | 247 | 01; 05; 15 | Toggle flipflop 09 | X | X | X
Command flag | 247 | 248 | 01; 05; 15 | Toggle flipflop 10 | X | X | X
Command flag | 248 | 249 | 01; 05; 15 | Toggle flipflop 11 | X | X | X
Command flag | 249 | 250 | 01; 05; 15 | Toggle flipflop 12 | X | X | X
Command flag | 250 | 251 | 01; 05; 15 | Toggle flipflop 13 | X | X | X
Command flag | 251 | 252 | 01; 05; 15 | Toggle flipflop 14 | X | X | X
Command flag | 252 | 253 | 01; 05; 15 | Toggle flipflop 15 | X | X | X
Command flag | 253 | 254 | 01; 05; 15 | Toggle flipflop 16 | X | X | X
Command flag | 274 | 275 | 01; 05; 15 | Easy connect add genset | X | X | X
Command flag | 275 | 276 | 01; 05; 15 | Easy connect remove genset | X | X | X
Command flag | 276 | 277 | 01; 05; 15 | Select yes on display for easy connect | X | X | X
Command flag | 277 | 278 | 01; 05; 15 | Select no on display for easy connect | X | X | X
Command flag | 284 | 285 | 01; 05; 15 | DVC 550/D550: Reset faults | X | X | X
Command flag | 285 | 286 | 01; 05; 15 | Remote PVB On | X | X | X
Command flag | 286 | 287 | 01; 05; 15 | Remote PVB Off | X | X | X
Command flag | 287 | 288 | 01; 05; 15 | PV semi start | X | X | X
Command flag | 288 | 289 | 01; 05; 15 | PV semi stop | X | X | X
Command flag | 289 | 290 | 01; 05; 15 | Controls PV auto start/stop | X | X | X
Command flag | 290 | 291 | 01; 05; 15 | Set if PV auto start/stop should be controlled from Modbus | X | X | X
Note on A4: More information about each function group is available in the description sheet.
Note on D4: 01 - Read single or multiple 05 - Write single 15 - Write multiple
Note on E4: The controller function name shows the name of the parameter in the Utility Software. Some functions might contain additional information.
Note on F4: Indicates if the address is available in the BUS TIE breaker controller.
Note on G4: Indicates if the address is available in the MAINS controller.
Note on H4: Indicates if the address is available in the GENSET controller.

## Discrete input contact (02)
Discrete input contact (02)
Function group | Modbus address | PLC address | Modbus function code | Controller function name | BTB | MAINS | DG
Digital input | 22500 | 122501 | 2 | Digital input 39 | X | X | X
Digital input | 22501 | 122502 | 2 | Digital input 40 | X | X | X
Digital input | 22502 | 122503 | 2 | Digital input 41 | X | X | X
Digital input | 22503 | 122504 | 2 | Digital input 42 | X | X | X
Digital input | 22504 | 122505 | 2 | Digital input 43 | X | X | X
Digital input | 22505 | 122506 | 2 | Digital input 44 | X | X | X
Digital input | 22506 | 122507 | 2 | Digital input 45 | X | X | X
Digital input | 22507 | 122508 | 2 | Digital input 46 | X | X | X
Digital input | 22513 | 122514 | 2 | Emergency stop input 4 | X | X | X
Digital input | 22512 | 122513 | 2 | Dplus input 7 |  |  | X
Digital input | 22593 | 122594 | 2 | Binary in 20 | X | X | X
Digital input | 22592 | 122593 | 2 | Binary in 21 | X | X | X
Digital input | 22591 | 122592 | 2 | Binary in 22 | X | X | X
Digital input | 22590 | 122591 | 2 | Binary in 23 | X | X | X
Digital input | 22594 | 122595 | 2 | CIO 116 no. 1. Input 10 | X | X | X
Digital input | 22595 | 122596 | 2 | CIO 116 no. 1. Input 11 | X | X | X
Digital input | 22596 | 122597 | 2 | CIO 116 no. 1. Input 12 | X | X | X
Digital input | 22597 | 122598 | 2 | CIO 116 no. 1. Input 13 | X | X | X
Digital input | 22598 | 122599 | 2 | CIO 116 no. 1. Input 14 | X | X | X
Digital input | 22599 | 122600 | 2 | CIO 116 no. 1. Input 15 | X | X | X
Digital input | 22600 | 122601 | 2 | CIO 116 no. 1. Input 16 | X | X | X
Digital input | 22601 | 122602 | 2 | CIO 116 no. 1. Input 17 | X | X | X
Digital input | 22602 | 122603 | 2 | CIO 116 no. 1. Input 19 | X | X | X
Digital input | 22603 | 122604 | 2 | CIO 116 no. 1. Input 20 | X | X | X
Digital input | 22604 | 122605 | 2 | CIO 116 no. 1. Input 21 | X | X | X
Digital input | 22605 | 122606 | 2 | CIO 116 no. 1. Input 22 | X | X | X
Digital input | 22606 | 122607 | 2 | CIO 116 no. 1. Input 23 | X | X | X
Digital input | 22607 | 122608 | 2 | CIO 116 no. 1. Input 24 | X | X | X
Digital input | 22608 | 122609 | 2 | CIO 116 no. 1. Input 25 | X | X | X
Digital input | 22609 | 122610 | 2 | CIO 116 no. 1. Input 26 | X | X | X
Digital input | 22610 | 122611 | 2 | CIO 116 no. 2. Input 10 | X | X | X
Digital input | 22611 | 122612 | 2 | CIO 116 no. 2. Input 11 | X | X | X
Digital input | 22612 | 122613 | 2 | CIO 116 no. 2. Input 12 | X | X | X
Digital input | 22613 | 122614 | 2 | CIO 116 no. 2. Input 13 | X | X | X
Digital input | 22614 | 122615 | 2 | CIO 116 no. 2. Input 14 | X | X | X
Digital input | 22615 | 122616 | 2 | CIO 116 no. 2. Input 15 | X | X | X
Digital input | 22616 | 122617 | 2 | CIO 116 no. 2. Input 16 | X | X | X
Digital input | 22617 | 122618 | 2 | CIO 116 no. 2. Input 17 | X | X | X
Digital input | 22618 | 122619 | 2 | CIO 116 no. 2. Input 19 | X | X | X
Digital input | 22619 | 122620 | 2 | CIO 116 no. 2. Input 20 | X | X | X
Digital input | 22620 | 122621 | 2 | CIO 116 no. 2. Input 21 | X | X | X
Digital input | 22621 | 122622 | 2 | CIO 116 no. 2. Input 22 | X | X | X
Digital input | 22622 | 122623 | 2 | CIO 116 no. 2. Input 23 | X | X | X
Digital input | 22623 | 122624 | 2 | CIO 116 no. 2. Input 24 | X | X | X
Digital input | 22624 | 122625 | 2 | CIO 116 no. 2. Input 25 | X | X | X
Digital input | 22625 | 122626 | 2 | CIO 116 no. 2. Input 26 | X | X | X
Digital input | 22626 | 122627 | 2 | CIO 116 no. 3. Input 10 | X | X | X
Digital input | 22627 | 122628 | 2 | CIO 116 no. 3. Input 11 | X | X | X
Digital input | 22628 | 122629 | 2 | CIO 116 no. 3. Input 12 | X | X | X
Digital input | 22629 | 122630 | 2 | CIO 116 no. 3. Input 13 | X | X | X
Digital input | 22630 | 122631 | 2 | CIO 116 no. 3. Input 14 | X | X | X
Digital input | 22631 | 122632 | 2 | CIO 116 no. 3. Input 15 | X | X | X
Digital input | 22632 | 122633 | 2 | CIO 116 no. 3. Input 16 | X | X | X
Digital input | 22633 | 122634 | 2 | CIO 116 no. 3. Input 17 | X | X | X
Digital input | 22634 | 122635 | 2 | CIO 116 no. 3. Input 19 | X | X | X
Digital input | 22635 | 122636 | 2 | CIO 116 no. 3. Input 20 | X | X | X
Digital input | 22636 | 122637 | 2 | CIO 116 no. 3. Input 21 | X | X | X
Digital input | 22637 | 122638 | 2 | CIO 116 no. 3. Input 22 | X | X | X
Digital input | 22638 | 122639 | 2 | CIO 116 no. 3. Input 23 | X | X | X
Digital input | 22639 | 122640 | 2 | CIO 116 no. 3. Input 24 | X | X | X
Digital input | 22640 | 122641 | 2 | CIO 116 no. 3. Input 25 | X | X | X
Digital input | 22641 | 122642 | 2 | CIO 116 no. 3. Input 26 | X | X | X
Digital output | 23001 | 123002 | 2 | Relay 5 | X | X | X
Digital output | 23002 | 123003 | 2 | Relay 6 | X | X | X
Digital output | 23003 | 123004 | 2 | Relay 9 | X | X | X
Digital output | 23004 | 123005 | 2 | Relay 10 | X | X | X
Digital output | 23005 | 123006 | 2 | Relay 11 | X | X | X
Digital output | 23006 | 123007 | 2 | Relay 12 | X | X | X
Digital output | 23007 | 123008 | 2 | Relay 13 | X | X | X
Digital output | 23008 | 123009 | 2 | Relay 14 | X | X | X
Digital output | 23009 | 123010 | 2 | Relay 15 | X | X | X
Digital output | 23010 | 123011 | 2 | Relay 16 | X | X | X
Digital output | 23011 | 123012 | 2 | Relay 17 | X | X | X
Digital output | 23012 | 123013 | 2 | Relay 18 | X | X | X
Digital output | 23056 | 123057 | 2 | CIO 208 no. 1. Output 9 | X | X | X
Digital output | 23057 | 123058 | 2 | CIO 208 no. 1. Output 11 | X | X | X
Digital output | 23058 | 123059 | 2 | CIO 208 no. 1. Output 13 | X | X | X
Digital output | 23059 | 123060 | 2 | CIO 208 no. 1. Output 15 | X | X | X
Digital output | 23060 | 123061 | 2 | CIO 208 no. 1. Output 18 | X | X | X
Digital output | 23061 | 123062 | 2 | CIO 208 no. 1. Output 21 | X | X | X
Digital output | 23062 | 123063 | 2 | CIO 208 no. 1. Output 24 | X | X | X
Digital output | 23063 | 123064 | 2 | CIO 208 no. 1. Output 27 | X | X | X
Digital output | 23064 | 123065 | 2 | CIO 208 no. 2. Output 9 | X | X | X
Digital output | 23065 | 123066 | 2 | CIO 208 no. 2. Output 11 | X | X | X
Digital output | 23066 | 123067 | 2 | CIO 208 no. 2. Output 13 | X | X | X
Digital output | 23067 | 123068 | 2 | CIO 208 no. 2. Output 15 | X | X | X
Digital output | 23068 | 123069 | 2 | CIO 208 no. 2. Output 18 | X | X | X
Digital output | 23069 | 123070 | 2 | CIO 208 no. 2. Output 21 | X | X | X
Digital output | 23070 | 123071 | 2 | CIO 208 no. 2. Output 24 | X | X | X
Digital output | 23071 | 123072 | 2 | CIO 208 no. 2. Output 27 | X | X | X
Digital output | 23072 | 123073 | 2 | CIO 208 no. 3. Output 9 | X | X | X
Digital output | 23073 | 123074 | 2 | CIO 208 no. 3. Output 11 | X | X | X
Digital output | 23074 | 123075 | 2 | CIO 208 no. 3. Output 13 | X | X | X
Digital output | 23075 | 123076 | 2 | CIO 208 no. 3. Output 15 | X | X | X
Digital output | 23076 | 123077 | 2 | CIO 208 no. 3. Output 18 | X | X | X
Digital output | 23077 | 123078 | 2 | CIO 208 no. 3. Output 21 | X | X | X
Digital output | 23078 | 123079 | 2 | CIO 208 no. 3. Output 24 | X | X | X
Digital output | 23079 | 123080 | 2 | CIO 208 no. 3. Output 27 | X | X | X
Digital output | 23080 | 123081 | 2 | CIO 116 no. 1 conf. status out | X | X | X
Digital output | 23081 | 123082 | 2 | CIO 116 no. 2 conf. status out | X | X | X
Digital output | 23082 | 123083 | 2 | CIO 116 no. 3 conf. status out | X | X | X
Digital output | 23083 | 123084 | 2 | CIO 208 no. 1 conf. status out | X | X | X
Digital output | 23084 | 123085 | 2 | CIO 208 no. 2 conf. status out | X | X | X
Digital output | 23085 | 123086 | 2 | CIO 208 no. 3 conf. status out | X | X | X
Digital output | 23086 | 123087 | 2 | CIO 308 no. 1 conf. status out | X | X | X
Digital output | 23087 | 123088 | 2 | CIO 308 no. 2 conf. status out | X | X | X
Digital output | 23088 | 123089 | 2 | CIO 308 no. 3 conf. status out | X | X | X
Status flag | 0 | 100001 | 2 | GB position ON |  |  | X
Status flag | 0 | 100001 | 2 | TB position ON |  | X
Status flag | 0 | 100001 | 2 | BTB position ON | X
Status flag | 1 | 100002 | 2 | MB position ON |  | X | X
Status flag | 3 | 100004 | 2 | Running |  |  | X
Status flag | 4 | 100005 | 2 | Generator voltage/frequency OK |  |  | X
Status flag | 4 | 100005 | 2 | Busbar voltage/frequency OK |  | X
Status flag | 4 | 100005 | 2 | Busbar B voltage/frequency OK | X
Status flag | 5 | 100006 | 2 | Mains failure (Single DG) |  |  | X
Status flag | 5 | 100006 | 2 | Mains failure |  | X
Status flag | 6 | 100007 | 2 | Block mode |  |  | X
Status flag | 7 | 100008 | 2 | Manual mode |  |  | X
Status flag | 8 | 100009 | 2 | Semi-auto mode | X | X | X
Status flag | 9 | 100010 | 2 | Auto mode | X | X | X
Status flag | 10 | 100011 | 2 | Test mode |  | X | X
Status flag | 13 | 100014 | 2 | Island |  | X | X
Status flag | 14 | 100015 | 2 | Automatic mains failure (AMF) |  | X | X
Status flag | 15 | 100016 | 2 | Peak shaving |  | X | X
Status flag | 16 | 100017 | 2 | Fixed power |  | X | X
Status flag | 17 | 100018 | 2 | Mains power export (MPE) |  | X | X
Status flag | 18 | 100019 | 2 | Load takeover (LTO) |  | X | X
Status flag | 19 | 100020 | 2 | Power management |  |  | X
Status flag | 20 | 100021 | 2 | Any alarm on PMS ID1 | X | X | X
Status flag | 21 | 100022 | 2 | Any alarm on PMS ID2 | X | X | X
Status flag | 22 | 100023 | 2 | Any alarm on PMS ID3 | X | X | X
Status flag | 23 | 100024 | 2 | Any alarm on PMS ID4 | X | X | X
Status flag | 24 | 100025 | 2 | Any alarm on PMS ID5 | X | X | X
Status flag | 25 | 100026 | 2 | Any alarm on PMS ID6 | X | X | X
Status flag | 26 | 100027 | 2 | Any alarm on PMS ID7 | X | X | X
Status flag | 27 | 100028 | 2 | Any alarm on PMS ID8 | X | X | X
Status flag | 28 | 100029 | 2 | Any alarm mains (Mains Command Unit) | X | X | X
Status flag | 29 | 100030 | 2 | Battery test |  |  | X
Status flag | 31 | 100032 | 2 | Ready auto-start DG1 | X | X | X
Status flag | 32 | 100033 | 2 | Ready auto-start DG2 | X | X | X
Status flag | 33 | 100034 | 2 | Ready auto-start DG3 | X | X | X
Status flag | 34 | 100035 | 2 | Ready auto-start DG4 | X | X | X
Status flag | 35 | 100036 | 2 | Ready auto-start DG5 | X | X | X
Status flag | 36 | 100037 | 2 | Ready auto-start DG6 | X | X | X
Status flag | 37 | 100038 | 2 | Ready auto-start DG7 | X | X | X
Status flag | 38 | 100039 | 2 | Ready auto-start DG8 | X | X | X
Status flag | 53 | 100054 | 2 | Mains sync. inhibit |  | X | X
Status flag | 54 | 100055 | 2 | Any mains sync. inhibit | X | X | X
Note on A4: More information about each function group is available in the description sheet.
Note on D4: 02 - Read single or multiple
Note on E4: The controller function name shows the name of the parameter in the Utility Software. Some functions might contain additional information.
Note on F4: Indicates if the address is available in the BUS TIE breaker controller.
Note on G4: Indicates if the address is available in the MAINS controller.
Note on H4: Indicates if the address is available in the GENSET controller.

## Holding register (03;06;16)
Holding register (03;06;16)
Function group | Modbus address | Bit | PLC address | Modbus function code | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | BTB | MAINS | DG
Control time command | 58000 |  | 458001 | 03; 06; 16 | Year (2003-2099) | INT16s | AB | 0 |  | X | X | X
Control time command | 58001 |  | 458002 | 03; 06; 16 | Month (1-12) | INT16s | AB | 0 |  | X | X | X
Control time command | 58002 |  | 458003 | 03; 06; 16 | Date (1-31) | INT16s | AB | 0 |  | X | X | X
Control time command | 58003 |  | 458004 | 03; 06; 16 | Day (1-7, Monday - Sunday) | INT16s | AB | 0 |  | X | X | X
Control time command | 58004 |  | 458005 | 03; 06; 16 | Hour (0-23) | INT16s | AB | 0 |  | X | X | X
Control time command | 58005 |  | 458006 | 03; 06; 16 | Min (0-59) | INT16s | AB | 0 |  | X | X | X
Control time command | 58006 |  | 458007 | 03; 06; 16 | Sec (0-59) | INT16s | AB | 0 |  | X | X | X
Control command | 0 |  | 400001 | 03; 06; 16 | Power regulator setpoint - 0...100% of nominal power. Activated in menu 7501 | INT16s | AB | 0 |  |  | X | X
Control command | 1 |  | 400002 | 03; 06; 16 | cosPhi regulator setpoint - 60...100 stated as cosPhi value/100. The value 100 means cosPhi = 1.00 Activated in menu 7504 | INT16s | AB | 0 |  |  |  | X
Control command | 2 |  | 400003 | 03; 06; 16 | Reactive power regulator setpoint - +/-100% of nominal power. A negative value means capacitive reactive power, and a positive value means inductive reactive power. Activated in menu 7505 | INT16s | AB | 0 |  |  |  | X
Control command | 3 |  | 400004 | 03; 06; 16 | Frequency regulator setpoint - +/-100% corresponding to +/10.0% of nominal frequency. Activated in menu 7502 | INT16s | AB | 0 |  |  |  | X
Control command | 4 |  | 400005 | 03; 06; 16 | Voltage regulator setpoint - +/-100% corresponding to +/10.0% of nominal voltage. Activated in menu 7503 | INT16s | AB | 0 |  |  |  | X
Control command | 5 | 0 | 400006 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X
Control command | 5 | 1 | 400006 | 03; 06; 16 | Remote start | BOOL | [5 empty] | X
Control command | 5 | 2 | 400006 | 03; 06; 16 | Remote GB ON | BOOL | [5 empty] | X
Control command | 5 | 2 | 400006 | 03; 06; 16 | Remote TB ON | BOOL |  |  |  |  | X
Control command | 5 | 2 | 400006 | 03; 06; 16 | Remote BTB ON | BOOL |  |  |  | X
Control command | 5 | 3 | 400006 | 03; 06; 16 | Remote GB OFF | BOOL | [5 empty] | X
Control command | 5 | 3 | 400006 | 03; 06; 16 | Remote TB OFF | BOOL |  |  |  |  | X
Control command | 5 | 3 | 400006 | 03; 06; 16 | Remote BTB OFF | BOOL |  |  |  | X
Control command | 5 | 4 | 400006 | 03; 06; 16 | Remote stop | BOOL | [5 empty] | X
Control command | 5 | 5 | 400006 | 03; 06; 16 | Reset GOV/AVR regulation output to offset | BOOL | [5 empty] | X
Control command | 5 | 6 | 400006 | 03; 06; 16 | Start+sync. (semi) | BOOL | [5 empty] | X
Control command | 5 | 7 | 400006 | 03; 06; 16 | Alarm inhibit 1 | BOOL |  |  |  | X | X | X
Control command | 5 | 8 | 400006 | 03; 06; 16 | Alarm inhibit 2 | BOOL |  |  |  | X | X | X
Control command | 5 | 9 | 400006 | 03; 06; 16 | Alarm inhibit 3 | BOOL |  |  |  | X | X | X
Control command | 5 | 10 | 400006 | 03; 06; 16 | Alarm ack. | BOOL |  |  |  | X | X | X
Control command | 5 | 11 | 400006 | 03; 06; 16 | Nominal setting 1 | BOOL |  |  |  | X | X | X
Control command | 5 | 12 | 400006 | 03; 06; 16 | Nominal setting 2 | BOOL |  |  |  | X | X | X
Control command | 5 | 13 | 400006 | 03; 06; 16 | Nominal setting 3 | BOOL |  |  |  | X | X | X
Control command | 5 | 14 | 400006 | 03; 06; 16 | Nominal setting 4 | BOOL |  |  |  | X | X | X
Control command | 5 | 15 | 400006 | 03; 06; 16 | Deload/stop (semi) | BOOL | [5 empty] | X
Control command | 6 | 0 | 400007 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X
Control command | 6 | 1 | 400007 | 03; 06; 16 | Island | BOOL |  |  |  |  | X | X
Control command | 6 | 2 | 400007 | 03; 06; 16 | Automatic mains failure (AMF) | BOOL |  |  |  |  | X | X
Control command | 6 | 3 | 400007 | 03; 06; 16 | Peak shaving | BOOL |  |  |  |  | X | X
Control command | 6 | 4 | 400007 | 03; 06; 16 | Fixed power | BOOL |  |  |  |  | X | X
Control command | 6 | 5 | 400007 | 03; 06; 16 | Mains power export (MPE) | BOOL |  |  |  |  | X | X
Control command | 6 | 6 | 400007 | 03; 06; 16 | Load takeover (LTO) | BOOL |  |  |  |  | X | X
Control command | 6 | 9 | 400007 | 03; 06; 16 | MB ON (Single DG) | BOOL | [5 empty] | X
Control command | 6 | 9 | 400007 | 03; 06; 16 | MB ON | BOOL |  |  |  |  | X
Control command | 6 | 10 | 400007 | 03; 06; 16 | MB OFF (Single DG) | BOOL | [5 empty] | X
Control command | 6 | 10 | 400007 | 03; 06; 16 | MB OFF | BOOL |  |  |  |  | X
Control command | 6 | 11 | 400007 | 03; 06; 16 | Auto start/stop | BOOL |  |  |  |  | X | X
Control command | 6 | 12 | 400007 | 03; 06; 16 | Manual mode | BOOL | [5 empty] | X
Control command | 6 | 13 | 400007 | 03; 06; 16 | Auto mode | BOOL |  |  |  | X | X | X
Control command | 6 | 14 | 400007 | 03; 06; 16 | Semi-Auto mode | BOOL |  |  |  | X | X | X
Control command | 6 | 15 | 400007 | 03; 06; 16 | Test mode | BOOL |  |  |  |  | X | X
Control command | 7 | 0 | 400008 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X
Control command | 7 | 1 | 400008 | 03; 06; 16 | External frequency control | BOOL | [5 empty] | X
Control command | 7 | 2 | 400008 | 03; 06; 16 | External voltage control | BOOL | [5 empty] | X
Control command | 7 | 3 | 400008 | 03; 06; 16 | External power control | BOOL |  |  |  |  | X | X
Control command | 7 | 4 | 400008 | 03; 06; 16 | External reactive power control | BOOL | [5 empty] | X
Control command | 7 | 5 | 400008 | 03; 06; 16 | External power factor control | BOOL | [5 empty] | X
Control command | 7 | 6 | 400008 | 03; 06; 16 | Capacitive PF | BOOL | [5 empty] | X
Control command | 7 | 7 | 400008 | 03; 06; 16 | Base load | BOOL | [5 empty] | X
Control command | 7 | 8 | 400008 | 03; 06; 16 | 1. priority | BOOL | [5 empty] | X
Control command | 7 | 9 | 400008 | 03; 06; 16 | Application 1 | BOOL |  |  |  | X | X | X
Control command | 7 | 10 | 400008 | 03; 06; 16 | Application 2 | BOOL |  |  |  | X | X | X
Control command | 7 | 11 | 400008 | 03; 06; 16 | Application 3 | BOOL |  |  |  | X | X | X
Control command | 7 | 12 | 400008 | 03; 06; 16 | Application 4 | BOOL |  |  |  | X | X | X
Control command | 7 | 13 | 400008 | 03; 06; 16 | Battery test | BOOL | [5 empty] | X
Control command | 7 | 15 | 400008 | 03; 06; 16 | Synchronise clock to 4:00 a.m. | BOOL |  |  |  | X | X | X
Control command | 8 | 0 | 400009 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X
Control command | 8 | 1 | 400009 | 03; 06; 16 | Virtual event 1 | BOOL |  |  |  | X | X | X
Control command | 8 | 2 | 400009 | 03; 06; 16 | Virtual event 2 | BOOL |  |  |  | X | X | X
Control command | 8 | 3 | 400009 | 03; 06; 16 | Virtual event 3 | BOOL |  |  |  | X | X | X
Control command | 8 | 4 | 400009 | 03; 06; 16 | Virtual event 4 | BOOL |  |  |  | X | X | X
Control command | 8 | 5 | 400009 | 03; 06; 16 | Virtual event 5 | BOOL |  |  |  | X | X | X
Control command | 8 | 6 | 400009 | 03; 06; 16 | Virtual event 6 | BOOL |  |  |  | X | X | X
Control command | 8 | 7 | 400009 | 03; 06; 16 | Virtual event 7 | BOOL |  |  |  | X | X | X
Control command | 8 | 8 | 400009 | 03; 06; 16 | Virtual event 8 | BOOL |  |  |  | X | X | X
Control command | 8 | 9 | 400009 | 03; 06; 16 | Virtual event 9 | BOOL |  |  |  | X | X | X
Control command | 8 | 10 | 400009 | 03; 06; 16 | Virtual event 10 | BOOL |  |  |  | X | X | X
Control command | 8 | 11 | 400009 | 03; 06; 16 | Virtual event 11 | BOOL |  |  |  | X | X | X
Control command | 8 | 12 | 400009 | 03; 06; 16 | Virtual event 12 | BOOL |  |  |  | X | X | X
Control command | 8 | 13 | 400009 | 03; 06; 16 | Virtual event 13 | BOOL |  |  |  | X | X | X
Control command | 8 | 14 | 400009 | 03; 06; 16 | Virtual event 14 | BOOL |  |  |  | X | X | X
Control command | 8 | 15 | 400009 | 03; 06; 16 | Virtual event 15 | BOOL |  |  |  | X | X | X
Control command | 9 | 0 | 400010 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X
Control command | 9 | 1 | 400010 | 03; 06; 16 | Virtual event 16 | BOOL |  |  |  | X | X | X
Control command | 9 | 2 | 400010 | 03; 06; 16 | Virtual event 17 | BOOL |  |  |  | X | X | X
Control command | 9 | 3 | 400010 | 03; 06; 16 | Virtual event 18 | BOOL |  |  |  | X | X | X
Control command | 9 | 4 | 400010 | 03; 06; 16 | Virtual event 19 | BOOL |  |  |  | X | X | X
Control command | 9 | 5 | 400010 | 03; 06; 16 | Virtual event 20 | BOOL |  |  |  | X | X | X
Control command | 9 | 6 | 400010 | 03; 06; 16 | Virtual event 21 | BOOL |  |  |  | X | X | X
Control command | 9 | 7 | 400010 | 03; 06; 16 | Virtual event 22 | BOOL |  |  |  | X | X | X
Control command | 9 | 8 | 400010 | 03; 06; 16 | Virtual event 23 | BOOL |  |  |  | X | X | X
Control command | 9 | 9 | 400010 | 03; 06; 16 | Virtual event 24 | BOOL |  |  |  | X | X | X
Control command | 9 | 10 | 400010 | 03; 06; 16 | Virtual event 25 | BOOL |  |  |  | X | X | X
Control command | 9 | 11 | 400010 | 03; 06; 16 | Virtual event 26 | BOOL |  |  |  | X | X | X
Control command | 9 | 12 | 400010 | 03; 06; 16 | Virtual event 27 | BOOL |  |  |  | X | X | X
Control command | 9 | 13 | 400010 | 03; 06; 16 | Virtual event 28 | BOOL |  |  |  | X | X | X
Control command | 9 | 14 | 400010 | 03; 06; 16 | Virtual event 29 | BOOL |  |  |  | X | X | X
Control command | 9 | 15 | 400010 | 03; 06; 16 | Virtual event 30 | BOOL |  |  |  | X | X | X
Control command | 10 | 0 | 400011 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X
Control command | 10 | 1 | 400011 | 03; 06; 16 | Virtual event 31 | BOOL |  |  |  | X | X | X
Control command | 10 | 2 | 400011 | 03; 06; 16 | Virtual event 32 | BOOL |  |  |  | X | X | X
Control command | 10 | 4 | 400011 | 03; 06; 16 | Clear log | BOOL |  |  |  | X | X | X
Control command | 10 | 5 | 400011 | 03; 06; 16 | Clear Parameter edits | BOOL |  |  |  | X | X | X
Control command | 13 | 0 | 400014 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X
Control command | 13 | 1 | 400014 | 03; 06; 16 | Enable external frequency control | BOOL | [5 empty] | X
Control command | 13 | 2 | 400014 | 03; 06; 16 | Disable external frequency control | BOOL | [5 empty] | X
Control command | 13 | 3 | 400014 | 03; 06; 16 | Enable external voltage control | BOOL | [5 empty] | X
Control command | 13 | 4 | 400014 | 03; 06; 16 | Disable external voltage control | BOOL | [5 empty] | X
Control command | 13 | 5 | 400014 | 03; 06; 16 | Enable external power control | BOOL |  |  |  |  | X | X
Control command | 13 | 6 | 400014 | 03; 06; 16 | Disable external power control | BOOL |  |  |  |  | X | X
Control command | 13 | 7 | 400014 | 03; 06; 16 | Enable external VAr control | BOOL | [5 empty] | X
Control command | 13 | 8 | 400014 | 03; 06; 16 | Disable external VAr control | BOOL | [5 empty] | X
Control command | 13 | 9 | 400014 | 03; 06; 16 | Enable external CosPhi control | BOOL | [5 empty] | X
Control command | 13 | 10 | 400014 | 03; 06; 16 | Disable external CosPhi control | BOOL | [5 empty] | X
Control command | 13 | 11 | 400014 | 03; 06; 16 | Enable PM base load | BOOL | [5 empty] | X
Control command | 13 | 12 | 400014 | 03; 06; 16 | Disable PM base load | BOOL | [5 empty] | X
Control command | 13 | 13 | 400014 | 03; 06; 16 | Reset horn | BOOL |  |  |  | X | X | X
Write area 1 (PLC/external system to ASC) | 46100 |  | 446101 | 03; 06; 16 | Available PV power. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_P_available will be used by logics. | INT32s | ABCD | 0 | kW* |  |  | X
Write area 1 (PLC/external system to ASC) | 46102 |  | 446103 | 03; 06; 16 | Active PV power. | INT32s | ABCD | 0 | kW* |  |  | X
Write area 1 (PLC/external system to ASC) | 46110 |  | 446111 | 03; 06; 16 | Available PV apparent power. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_S_available will be used by logics. | INT32s | ABCD | 0 | kVA* |  |  | X
Write area 1 (PLC/external system to ASC) | 46112 |  | 446113 | 03; 06; 16 | Spinning reserve in diesel system | INT32s | ABCD | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46114 |  | 446115 | 03; 06; 16 | Current operation mode of the PV plant: 200: Ready for operation | INT32s | ABCD | 0 |  |  |  | X
Write area 1 (PLC/external system to ASC) | 46116 |  | 446117 | 03; 06; 16 | Watch dog will increment continuously. To be used for PV/DEIF communication supervision on DEIF side. | INT32s | ABCD | 0 |  |  |  | X
Write area 1 (PLC/external system to ASC) | 46120 |  | 446121 | 03; 06; 16 | To raise warning and shutdown alarms on DEIF side 100: Warning. 200: Shutdown. 300: Warning & Shutdown. | INT32s | ABCD | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46122 |  | 446123 | 03; 06; 16 | Reactive PV power | INT32s | ABCD | 0 | kvar* |  |  | X
Write area 1 (PLC/external system to ASC) | 46124 |  | 446125 | 03; 06; 16 | Apparent PV power | INT32s | ABCD | 0 | kVA* |  |  | X
Write area 1 (PLC/external system to ASC) | 46126 |  | 446127 | 03; 06; 16 | Reset gensets fuel trip counters from PV side: 100: reset fuel trip counters | INT32s | ABCD | 0 |  |  |  | X
Write area 1 (PLC/external system to ASC) | 46128 |  | 446129 | 03; 06; 16 | Available PV reactive power in Q1. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_Q_available_Q1 will be used by logics. | INT32s | ABCD | 0 | kVAr* |  |  | X
Write area 1 (PLC/external system to ASC) | 46130 |  | 446131 | 03; 06; 16 | Plane of array irradiation sensor 1 | INT16s | AB | 0 | W/m2 |  |  | X
Write area 1 (PLC/external system to ASC) | 46131 |  | 446132 | 03; 06; 16 | Plane of array irradiation sensor 2 | INT16s | AB | 0 | W/m2 |  |  | X
Write area 1 (PLC/external system to ASC) | 46132 |  | 446133 | 03; 06; 16 | Plane of array irradiation sensor 3 | INT16s | AB | 0 | W/m2 |  |  | X
Write area 1 (PLC/external system to ASC) | 46133 |  | 446134 | 03; 06; 16 | Back of module temperature sensor 1 | INT16s | AB | 0 | Deg C |  |  | X
Write area 1 (PLC/external system to ASC) | 46134 |  | 446135 | 03; 06; 16 | Back of module temperature sensor 2 | INT16s | AB | 0 | Deg C |  |  | X
Write area 1 (PLC/external system to ASC) | 46135 |  | 446136 | 03; 06; 16 | Back of module temperature sensor 3 | INT16s | AB | 0 | Deg C |  |  | X
Write area 1 (PLC/external system to ASC) | 46136 |  | 446137 | 03; 06; 16 | Global horizontal irradiation [W/m2] | INT16s | AB | 0 | W/m2 |  |  | X
Write area 1 (PLC/external system to ASC) | 46137 |  | 446138 | 03; 06; 16 | Ambient temperature [C] | INT16s | AB | 0 | Deg C |  |  | X
Write area 1 (PLC/external system to ASC) | 46138 |  | 446139 | 03; 06; 16 | Relative humidity [%] | INT16s | AB | 0 | % |  |  | X
Write area 1 (PLC/external system to ASC) | 46139 |  | 446140 | 03; 06; 16 | Barometric pressure [hPa] | INT16s | AB | 0 | hPa |  |  | X
Write area 1 (PLC/external system to ASC) | 46140 |  | 446141 | 03; 06; 16 | Wind speed [m/s] | INT16s | AB | 0 | m/s |  |  | X
Write area 1 (PLC/external system to ASC) | 46141 |  | 446142 | 03; 06; 16 | Wind direction [deg] | INT16s | AB | 0 | deg |  |  | X
Write area 1 (PLC/external system to ASC) | 46142 |  | 446143 | 03; 06; 16 | Rain fall [mm] | INT16s | AB | 0 | mm |  |  | X
Write area 1 (PLC/external system to ASC) | 46143 |  | 446144 | 03; 06; 16 | Snow depth [mm] | INT16s | AB | 0 | mm |  |  | X
Write area 1 (PLC/external system to ASC) | 46144 |  | 446145 | 03; 06; 16 | Available PV reactive power in Q2. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_Q_available_Q2 will be used by logics. | INT32s | ABCD | 0 |  |  |  | X
Write area 1 (PLC/external system to ASC) | 46146 |  | 446147 | 03; 06; 16 | Available PV reactive power [kVAr*] in Q3. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_Q_available_Q3 will be used by logics. | INT32s | ABCD | 0 |  |  |  | X
Write area 1 (PLC/external system to ASC) | 46148 |  | 446149 | 03; 06; 16 | Available PV reactive power [kVAr*] in Q4. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_Q_available_Q4 will be used by logics. | INT32s | ABCD | 0 |  |  |  | X
Write area 1 (PLC/external system to ASC) | 46150 |  | 446151 | 03; 06; 16 | Active power of genset 1. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46151 |  | 446152 | 03; 06; 16 | Active power of genset 2. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46152 |  | 446153 | 03; 06; 16 | Active power of genset 3. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46153 |  | 446154 | 03; 06; 16 | Active power of genset 4. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46154 |  | 446155 | 03; 06; 16 | Active power of genset 5. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46155 |  | 446156 | 03; 06; 16 | Active power of genset 6. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46156 |  | 446157 | 03; 06; 16 | Active power of genset 7. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46157 |  | 446158 | 03; 06; 16 | Active power of genset 8. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46158 |  | 446159 | 03; 06; 16 | Active power of genset 9. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46159 |  | 446160 | 03; 06; 16 | Active power of genset 10. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46160 |  | 446161 | 03; 06; 16 | Active power of genset 11. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46161 |  | 446162 | 03; 06; 16 | Active power of genset 12. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46162 |  | 446163 | 03; 06; 16 | Active power of genset 13. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46163 |  | 446164 | 03; 06; 16 | Active power of genset 14. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46164 |  | 446165 | 03; 06; 16 | Active power of genset 15. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46165 |  | 446166 | 03; 06; 16 | Active power of genset 16. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46166 |  | 446167 | 03; 06; 16 | Reactive power of genset 1. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46167 |  | 446168 | 03; 06; 16 | Reactive power of genset 2. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46168 |  | 446169 | 03; 06; 16 | Reactive power of genset 3. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46169 |  | 446170 | 03; 06; 16 | Reactive power of genset 4. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46170 |  | 446171 | 03; 06; 16 | Reactive power of genset 5. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46171 |  | 446172 | 03; 06; 16 | Reactive power of genset 6. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46172 |  | 446173 | 03; 06; 16 | Reactive power of genset 7. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46173 |  | 446174 | 03; 06; 16 | Reactive power of genset 8. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46174 |  | 446175 | 03; 06; 16 | Reactive power of genset 9. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46175 |  | 446176 | 03; 06; 16 | Reactive power of genset 10. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46176 |  | 446177 | 03; 06; 16 | Reactive power of genset 11. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46177 |  | 446178 | 03; 06; 16 | Reactive power of genset 12. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46178 |  | 446179 | 03; 06; 16 | Reactive power of genset 13. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46179 |  | 446180 | 03; 06; 16 | Reactive power of genset 14. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46180 |  | 446181 | 03; 06; 16 | Reactive power of genset 15. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46181 |  | 446182 | 03; 06; 16 | Reactive power of genset 16. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46182 |  | 446183 | 03; 06; 16 | Active mains power. | INT16s | AB | 0 | kW |  |  | X
Write area 1 (PLC/external system to ASC) | 46183 |  | 446184 | 03; 06; 16 | Reactive mains power. | INT16s | AB | 0 | kvar |  |  | X
Write area 1 (PLC/external system to ASC) | 46184 |  | 446185 | 03; 06; 16 | GB closed feedback bitwise from genset 01..16 | INT16s | AB | 0 |  |  |  | X
Write area 1 (PLC/external system to ASC) | 46185 |  | 446186 | 03; 06; 16 | MB closed feedback bitwise from genset 01..16 | INT16s | AB | 0 |  |  |  | X
Write area 1 (PLC/external system to ASC) | 46186 |  | 446187 | 03; 06; 16 | MB open feedback bitwise from genset 01..16 | INT16s | AB | 0 |  |  |  | X
Weather area | 46432 |  | 446433 | 03; 06; 16 | Plane of array irradiation sensor 1 | INT16s | AB | 0 | W/m2 |  |  | X
Weather area | 46433 |  | 446434 | 03; 06; 16 | Plane of array irradiation sensor 2 | INT16s | AB | 0 | W/m2 |  |  | X
Weather area | 46434 |  | 446435 | 03; 06; 16 | Plane of array irradiation sensor 3 | INT16s | AB | 0 | W/m2 |  |  | X
Weather area | 46435 |  | 446436 | 03; 06; 16 | Global horizontal irradiation | INT16s | AB | 0 | W/m2 |  |  | X
Weather area | 46436 |  | 446437 | 03; 06; 16 | Back of module temperature sensor 1 | INT16s | AB | 0 | Deg C |  |  | X
Weather area | 46437 |  | 446438 | 03; 06; 16 | Back of module temperature sensor 2 | INT16s | AB | 0 | Deg C |  |  | X
Weather area | 46438 |  | 446439 | 03; 06; 16 | Back of module temperature sensor 3 | INT16s | AB | 0 | Deg C |  |  | X
Weather area | 46439 |  | 446440 | 03; 06; 16 | Back of module temperature sensor - global | INT16s | AB | 0 | Deg C |  |  | X
Note on A4: More information about each function group is available in the description sheet.
Note on C4: Bit location of the function in the associated Modbus address.
Note on E4: 03 - Read single or multiple 06 - Write single 16 - Write multiple
Note on F4: The controller function name shows the name of the parameter in the Utility Software. Some functions might contain additional information.
Note on H4: AB - Most significant byte first ABCD - Most significant byte first and most significant word first
Note on I4: Example: Scaling = 1 Read Data = 266 Actual value = 26,6
Note on J4: Unit of the associated function
Note on K4: Indicates if the address is available in the BUS TIE breaker controller.
Note on L4: Indicates if the address is available in the MAINS controller.
Note on M4: Indicates if the address is available in the GENSET controller.

## Input register (04)
Input register (04)
Function group | Modbus address | Bit | PLC address | Modbus function code | Channel | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | BTB | MAINS | DG
Plant logic state | 1018 | 8 | 301019 | 4 | 6220 | BB Hz/V OK, timer expired | BOOL |  |  |  | X | X
APPL version | 500 |  | 300501 | 4 |  | Application version | INT16s | AB | 0 |  | X | X | X
AC measurement | 501 |  | 300502 | 4 |  | Generator voltage L1-L2 | INT16s | AB | 0 | V |  |  | X
AC measurement | 501 |  | 300502 | 4 |  | Mains voltage L1-L2 | INT16s | AB | 0 | V |  | X
AC measurement | 501 |  | 300502 | 4 |  | Bus A voltage L1-L2 | INT16s | AB | 0 | V | X
AC measurement | 502 |  | 300503 | 4 |  | Generator voltage L2-L3 | INT16s | AB | 0 | V |  |  | X
AC measurement | 502 |  | 300503 | 4 |  | Mains voltage L2-L3 | INT16s | AB | 0 | V |  | X
AC measurement | 502 |  | 300503 | 4 |  | Bus A voltage L2-L3 | INT16s | AB | 0 | V | X
AC measurement | 503 |  | 300504 | 4 |  | Generator voltage L3-L1 | INT16s | AB | 0 | V |  |  | X
AC measurement | 503 |  | 300504 | 4 |  | Mains voltage L3-L1 | INT16s | AB | 0 | V |  | X
AC measurement | 503 |  | 300504 | 4 |  | Bus A voltage L3-L1 | INT16s | AB | 0 | V | X
AC measurement | 504 |  | 300505 | 4 |  | Generator voltage L1-N | INT16s | AB | 0 | V |  |  | X
AC measurement | 504 |  | 300505 | 4 |  | Mains voltage L1-N | INT16s | AB | 0 | V |  | X
AC measurement | 504 |  | 300505 | 4 |  | Bus A voltage L1-N | INT16s | AB | 0 | V | X
AC measurement | 505 |  | 300506 | 4 |  | Generator voltage L2-N | INT16s | AB | 0 | V |  |  | X
AC measurement | 505 |  | 300506 | 4 |  | Mains voltage L2-N | INT16s | AB | 0 | V |  | X
AC measurement | 505 |  | 300506 | 4 |  | Bus A voltage L2-N | INT16s | AB | 0 | V | X
AC measurement | 506 |  | 300507 | 4 |  | Generator voltage L3-N | INT16s | AB | 0 | V |  |  | X
AC measurement | 506 |  | 300507 | 4 |  | Mains voltage L3-N | INT16s | AB | 0 | V |  | X
AC measurement | 506 |  | 300507 | 4 |  | Bus A voltage L3-N | INT16s | AB | 0 | V | X
AC measurement | 507 |  | 300508 | 4 |  | Generator frequency L1 | INT16s | AB | 2 | Hz |  |  | X
AC measurement | 507 |  | 300508 | 4 |  | Mains frequency L1 | INT16s | AB | 2 | Hz |  | X
AC measurement | 507 |  | 300508 | 4 |  | Bus A frequency L1 | INT16s | AB | 2 | Hz | X
AC measurement | 508 |  | 300509 | 4 |  | Generator frequency L2 | INT16s | AB | 2 | Hz |  |  | X
AC measurement | 508 |  | 300509 | 4 |  | Mains frequency L2 | INT16s | AB | 2 | Hz |  | X
AC measurement | 508 |  | 300509 | 4 |  | Bus A frequency L2 | INT16s | AB | 2 | Hz | X
AC measurement | 509 |  | 300510 | 4 |  | Generator frequency L3 | INT16s | AB | 2 | Hz |  |  | X
AC measurement | 509 |  | 300510 | 4 |  | Mains frequency L3 | INT16s | AB | 2 | Hz |  | X
AC measurement | 509 |  | 300510 | 4 |  | Bus A frequency L3 | INT16s | AB | 2 | Hz | X
AC measurement | 510 |  | 300511 | 4 |  | Generator voltage phase angle L1-L2 | INT16s | AB | 1 | Deg |  |  | X
AC measurement | 510 |  | 300511 | 4 |  | Mains voltage phase angle L1-L2 | INT16s | AB | 1 | Deg |  | X
AC measurement | 510 |  | 300511 | 4 |  | Bus A voltage phase angle L1-L2 | INT16s | AB | 1 | Deg | X
AC measurement | 511 |  | 300512 | 4 |  | Generator voltage phase angle L2-L3 | INT16s | AB | 1 | Deg |  |  | X
AC measurement | 511 |  | 300512 | 4 |  | Mains voltage phase angle L2-L3 | INT16s | AB | 1 | Deg |  | X
AC measurement | 511 |  | 300512 | 4 |  | Bus A voltage phase angle L2-L3 | INT16s | AB | 1 | Deg | X
AC measurement | 512 |  | 300513 | 4 |  | Generator voltage phase angle L3-L1 | INT16s | AB | 1 | Deg |  |  | X
AC measurement | 512 |  | 300513 | 4 |  | Mains voltage phase angle L3-L1 | INT16s | AB | 1 | Deg |  | X
AC measurement | 512 |  | 300513 | 4 |  | Bus A voltage phase angle L3-L1 | INT16s | AB | 1 | Deg | X
AC measurement | 513 |  | 300514 | 4 |  | Generator current L1 | INT16s | AB | 0 | A |  |  | X
AC measurement | 513 |  | 300514 | 4 |  | Mains current L1 | INT16s | AB | 0 | A |  | X
AC measurement | 513 |  | 300514 | 4 |  | Bus A current L1 | INT16s | AB | 0 | A | X
AC measurement | 514 |  | 300515 | 4 |  | Generator current L2 | INT16s | AB | 0 | A |  |  | X
AC measurement | 514 |  | 300515 | 4 |  | Mains current L2 | INT16s | AB | 0 | A |  | X
AC measurement | 514 |  | 300515 | 4 |  | Bus A current L2 | INT16s | AB | 0 | A | X
AC measurement | 515 |  | 300516 | 4 |  | Generator current L3 | INT16s | AB | 0 | A |  |  | X
AC measurement | 515 |  | 300516 | 4 |  | Mains current L3 | INT16s | AB | 0 | A |  | X
AC measurement | 515 |  | 300516 | 4 |  | Bus A current L3 | INT16s | AB | 0 | A | X
AC measurement | 516 |  | 300517 | 4 |  | Generator power L1 | INT16s | AB | 0 | kW |  |  | X
AC measurement | 516 |  | 300517 | 4 |  | Mains power L1 | INT16s | AB | 0 | kW |  | X
AC measurement | 516 |  | 300517 | 4 |  | Bus A power L1 | INT16s | AB | 0 | kW | X
AC measurement | 517 |  | 300518 | 4 |  | Generator power L2 | INT16s | AB | 0 | kW |  |  | X
AC measurement | 517 |  | 300518 | 4 |  | Mains power L2 | INT16s | AB | 0 | kW |  | X
AC measurement | 517 |  | 300518 | 4 |  | Bus A power L2 | INT16s | AB | 0 | kW | X
AC measurement | 518 |  | 300519 | 4 |  | Generator power L3 | INT16s | AB | 0 | kW |  |  | X
AC measurement | 518 |  | 300519 | 4 |  | Mains power L3 | INT16s | AB | 0 | kW |  | X
AC measurement | 518 |  | 300519 | 4 |  | Bus A power L3 | INT16s | AB | 0 | kW | X
AC measurement | 519 |  | 300520 | 4 |  | Generator power | INT16s | AB | 0 | kW |  |  | X
AC measurement | 519 |  | 300520 | 4 |  | Mains power | INT16s | AB | 0 | kW |  | X
AC measurement | 519 |  | 300520 | 4 |  | Bus A power | INT16s | AB | 0 | kW | X
AC measurement | 520 |  | 300521 | 4 |  | Mains reactive power L1 | INT16s | AB | 0 | kVAr |  | X
AC measurement | 520 |  | 300521 | 4 |  | Generator reactive power L1 | INT16s | AB | 0 | kVAr |  |  | X
AC measurement | 520 |  | 300521 | 4 |  | Bus A reactive power L1 | INT16s | AB | 0 | kVAr | X
AC measurement | 521 |  | 300522 | 4 |  | Generator reactive power L2 | INT16s | AB | 0 | kVAr |  |  | X
AC measurement | 521 |  | 300522 | 4 |  | Mains reactive power L2 | INT16s | AB | 0 | kVAr |  | X
AC measurement | 521 |  | 300522 | 4 |  | Bus A reactive power L2 | INT16s | AB | 0 | kVAr | X
AC measurement | 522 |  | 300523 | 4 |  | Generator reactive power L3 | INT16s | AB | 0 | kVAr |  |  | X
AC measurement | 522 |  | 300523 | 4 |  | Mains reactive power L3 | INT16s | AB | 0 | kVAr |  | X
AC measurement | 522 |  | 300523 | 4 |  | Bus A reactive power L3 | INT16s | AB | 0 | kVAr | X
AC measurement | 523 |  | 300524 | 4 |  | Generator reactive power | INT16s | AB | 0 | kVAr |  |  | X
AC measurement | 523 |  | 300524 | 4 |  | Mains reactive power | INT16s | AB | 0 | kVAr |  | X
AC measurement | 523 |  | 300524 | 4 |  | Bus A reactive power | INT16s | AB | 0 | kVAr | X
AC measurement | 524 |  | 300525 | 4 |  | Generator apparent power L1 | INT16s | AB | 0 | kVA |  |  | X
AC measurement | 524 |  | 300525 | 4 |  | Mains apparent power L1 | INT16s | AB | 0 | kVA |  | X
AC measurement | 524 |  | 300525 | 4 |  | Bus A apparent power L1 | INT16s | AB | 0 | kVA | X
AC measurement | 525 |  | 300526 | 4 |  | Generator apparent power L2 | INT16s | AB | 0 | kVA |  |  | X
AC measurement | 525 |  | 300526 | 4 |  | Mains apparent power L2 | INT16s | AB | 0 | kVA |  | X
AC measurement | 525 |  | 300526 | 4 |  | Bus A apparent power L2 | INT16s | AB | 0 | kVA | X
AC measurement | 526 |  | 300527 | 4 |  | Mains apparent power L3 | INT16s | AB | 0 | kVA |  | X
AC measurement | 526 |  | 300527 | 4 |  | Generator apparent power L3 | INT16s | AB | 0 | kVA |  |  | X
AC measurement | 526 |  | 300527 | 4 |  | Bus A apparent power L3 | INT16s | AB | 0 | kVA | X
AC measurement | 527 |  | 300528 | 4 |  | Generator apparent power | INT16s | AB | 0 | kVA |  |  | X
AC measurement | 527 |  | 300528 | 4 |  | Mains apparent power | INT16s | AB | 0 | kVA |  | X
AC measurement | 527 |  | 300528 | 4 |  | Bus A apparent power | INT16s | AB | 0 | kVA | X
Counter | 528 |  | 300529 | 4 |  | Generator Export reactive energy counter, total | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 528 |  | 300529 | 4 |  | Mains Export reactive energy counter, total | INT32s | ABCD | 0 | kVArh |  | X
Counter | 528 |  | 300529 | 4 |  | Bus A Export reactive energy counter, total | INT32s | ABCD | 0 | kVArh | X
Counter | 530 |  | 300531 | 4 |  | Generator Export, active energy counter, day | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 530 |  | 300531 | 4 |  | Mains Export, active energy counter, day | INT32s | ABCD | 0 | kWh |  | X
Counter | 530 |  | 300531 | 4 |  | Bus A Export, active energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 532 |  | 300533 | 4 |  | Generator Export, active energy counter, week | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 532 |  | 300533 | 4 |  | Mains Export, active energy counter, week | INT32s | ABCD | 0 | kWh |  | X
Counter | 532 |  | 300533 | 4 |  | Bus A Export, active energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 534 |  | 300535 | 4 |  | Generator Export, active energy counter, month | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 534 |  | 300535 | 4 |  | Mains Export, active energy counter, month | INT32s | ABCD | 0 | kWh |  | X
Counter | 534 |  | 300535 | 4 |  | Bus A Export, active energy counter, month | INT32s | ABCD | 0 | kWh | X
Counter | 536 |  | 300537 | 4 |  | Generator Export, active energy counter, total | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 536 |  | 300537 | 4 |  | Mains Export, active energy counter, total | INT32s | ABCD | 0 | kWh |  | X
Counter | 536 |  | 300537 | 4 |  | Bus A Export, active energy counter, total | INT32s | ABCD | 0 | kWh | X
AC measurement | 538 |  | 300539 | 4 |  | Generator PF | INT16s | AB | 2 | PF |  |  | X
AC measurement | 538 |  | 300539 | 4 |  | Mains PF | INT16s | AB | 2 | PF |  | X
AC measurement | 538 |  | 300539 | 4 |  | Bus A PF | INT16s | AB | 2 | PF | X
AC measurement | 539 |  | 300540 | 4 |  | Bus B voltage L1-L2 | INT16s | AB | 0 | V | X | X | X
AC measurement | 540 |  | 300541 | 4 |  | Bus B voltage L2-L3 | INT16s | AB | 0 | V | X | X | X
AC measurement | 541 |  | 300542 | 4 |  | Bus B voltage L3-L1 | INT16s | AB | 0 | V | X | X | X
AC measurement | 542 |  | 300543 | 4 |  | Bus B voltage L1-N | INT16s | AB | 0 | V | X | X | X
AC measurement | 543 |  | 300544 | 4 |  | Bus B voltage L2-N | INT16s | AB | 0 | V | X | X | X
AC measurement | 544 |  | 300545 | 4 |  | Bus B voltage L3-N | INT16s | AB | 0 | V | X | X | X
AC measurement | 545 |  | 300546 | 4 |  | Bus B frequency L1 | INT16s | AB | 2 | Hz | X | X | X
AC measurement | 546 |  | 300547 | 4 |  | Bus B frequency L2 | INT16s | AB | 2 | Hz | X | X | X
AC measurement | 547 |  | 300548 | 4 |  | Bus B frequency L3 | INT16s | AB | 2 | Hz | X | X | X
AC measurement | 548 |  | 300549 | 4 |  | Bus B voltage phase angle L1-L2 | INT16s | AB | 1 | Deg | X | X | X
AC measurement | 549 |  | 300550 | 4 |  | Bus B voltage phase angle L2-L3 | INT16s | AB | 1 | Deg | X | X | X
AC measurement | 550 |  | 300551 | 4 |  | Bus B voltage phase angle L3-L1 | INT16s | AB | 1 | Deg | X | X | X
AC measurement | 551 |  | 300552 | 4 |  | U BB L1 - U GEN L1 phase angle | INT16s | AB | 1 | Deg |  |  | X
AC measurement | 551 |  | 300552 | 4 |  | U BB L1 - U Mains L1 phase angle | INT16s | AB | 1 | Deg |  | X
AC measurement | 551 |  | 300552 | 4 |  | U BB A L1 - U BB B L1 phase angle | INT16s | AB | 1 | Deg | X
AC measurement | 552 |  | 300553 | 4 |  | U BB L2 - U GEN L2 phase angle | INT16s | AB | 1 | Deg |  |  | X
AC measurement | 552 |  | 300553 | 4 |  | U BB L2 - U Mains L2 phase angle | INT16s | AB | 1 | Deg |  | X
AC measurement | 552 |  | 300553 | 4 |  | U BB A L2 - U BB B L2 phase angle | INT16s | AB | 1 | Deg | X
AC measurement | 553 |  | 300554 | 4 |  | U BB L3 - U GEN L3 phase angle | INT16s | AB | 1 | Deg |  |  | X
AC measurement | 553 |  | 300554 | 4 |  | U BB L3 - U Mains L3 phase angle | INT16s | AB | 1 | Deg |  | X
AC measurement | 553 |  | 300554 | 4 |  | U BB A L3 - U BB B L3 phase angle | INT16s | AB | 1 | Deg | X
Counter | 554 |  | 300555 | 4 |  | Absolute running hours | INT32s | ABCD | 0 |  |  |  | X
Counter | 556 |  | 300557 | 4 |  | Relative running hours | INT32s | ABCD | 0 |  |  |  | X
Counter | 558 |  | 300559 | 4 |  | No. of alarms | INT16s | AB | 0 |  | X | X | X
Counter | 559 |  | 300560 | 4 |  | No. of unacknowledged alarms | INT16s | AB | 0 |  | X | X | X
Counter | 560 |  | 300561 | 4 |  | No. of active acknowledged alarms | INT16s | AB | 0 |  | X | X | X
Counter | 561 |  | 300562 | 4 |  | Running minute counter, shutdown override | INT16s | AB | 0 |  |  |  | X
Counter | 562 |  | 300563 | 4 |  | Running hour counter, shutdown override | INT16s | AB | 0 |  |  |  | X
Counter | 563 |  | 300564 | 4 |  | No. of GB operations | INT16s | AB | 0 |  |  |  | X
Counter | 563 |  | 300564 | 4 |  | No. Of TB operations | INT16s | AB | 0 |  |  | X
Counter | 563 |  | 300564 | 4 |  | No. of BTB operations | INT16s | AB | 0 |  | X
Counter | 564 |  | 300565 | 4 |  | No. of MB operations | INT16s | AB | 0 |  |  | X | X
Counter | 566 |  | 300567 | 4 |  | Start attempts | INT16s | AB | 0 |  |  |  | X
DC measurement | 567 |  | 300568 | 4 |  | DC supply term. 1-2 | INT16s | AB | 1 | V | X | X | X
Counter | 569 |  | 300570 | 4 |  | Service timer 1 running hours | INT16s | AB | 0 |  |  |  | X
Counter | 570 |  | 300571 | 4 |  | Service timer 1 running days | INT16s | AB | 0 |  |  |  | X
Counter | 571 |  | 300572 | 4 |  | Service timer 2 running hours | INT16s | AB | 0 |  |  |  | X
Counter | 572 |  | 300573 | 4 |  | Service timer 2 running days | INT16s | AB | 0 |  |  |  | X
AC measurement | 573 |  | 300574 | 4 |  | Cos-phi | INT16s | AB | 2 | cosPhi | X | X | X
AC measurement | 574 |  | 300575 | 4 |  | Cos-phi Inductive/Capacitive 0=Inductive, 1=Capacitive | INT16s | AB | 0 |  | X | X | X
DC measurement | 576 |  | 300577 | 4 |  | RPM (revolutions per minute) | INT16s | AB | 0 | rpm |  |  | X
Counter | 577 |  | 300578 | 4 |  | Running hours load profile | INT32s | ABCD | 0 |  |  |  | X
DC measurement | 583 |  | 300584 | 4 |  | Multi-input 20 | INT16s | AB | 0 |  | X | X | X
DC measurement | 584 |  | 300585 | 4 |  | Multi-input 21 | INT16s | AB | 0 |  | X | X | X
DC measurement | 585 |  | 300586 | 4 |  | Multi-input 22 | INT16s | AB | 0 |  | X | X | X
DC measurement | 587 |  | 300588 | 4 |  | Multi-input 23 | INT16s | AB | 0 |  | X | X | X
AC measurement | 591 |  | 300592 | 4 |  | Busbar power, Multi-input 21 | INT16s | AB | 0 | kW |  | X
AC measurement | 591 |  | 300592 | 4 |  | Bus A power, Multi-input 21 | INT16s | AB | 0 | kW | X
AC measurement | 592 |  | 300593 | 4 |  | Mains power, Multi-input 20 | INT16s | AB | 0 | kW |  | X | X
EIC measurement | 593 |  | 300594 | 4 |  | Engine Speed | INT16s | AB | 0 | rpm |  |  | X
EIC measurement | 594 |  | 300595 | 4 |  | Engine Coolant Temperature | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 595 |  | 300596 | 4 |  | Engine Oil Pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 596 |  | 300597 | 4 |  | Number of Actual Faults | INT16s | AB | 0 |  |  |  | X
EIC measurement | 597 |  | 300598 | 4 |  | Engine Oil Temperature | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 598 |  | 300599 | 4 |  | Fuel temperature | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 599 |  | 300600 | 4 |  | Intake manifold #1 pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 600 |  | 300601 | 4 |  | Air inlet temperature | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 601 |  | 300602 | 4 |  | Coolant level | INT16s | AB | 1 | perc |  |  | X
EIC measurement | 602 |  | 300603 | 4 |  | Fuel rate | INT16s | AB | 1 | L/h |  |  | X
EIC measurement | 603 |  | 300604 | 4 |  | Charge air pressure | INT16s | AB | 0 | bar/psi |  |  | X
EIC measurement | 604 |  | 300605 | 4 |  | Intake manifold #1 temperature | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 605 |  | 300606 | 4 |  | Drivers demand engine - percent torque | INT16s | AB | 0 | perc |  |  | X
EIC measurement | 606 |  | 300607 | 4 |  | Actual engine - percent torque | INT16s | AB | 0 | perc |  |  | X
EIC measurement | 607 |  | 300608 | 4 |  | Accelerator pedal position | INT16s | AB | 0 | perc |  |  | X
EIC measurement | 608 |  | 300609 | 4 |  | Percent load at current speed | INT16s | AB | 0 | perc |  |  | X
EIC measurement | 609 |  | 300610 | 4 |  | Air inlet pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 610 |  | 300611 | 4 |  | Exhaust gas temperature | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 611 |  | 300612 | 4 |  | Engine hours | INT16s | AB | 0 | h |  |  | X
EIC measurement | 612 |  | 300613 | 4 |  | Engine oil filter differential pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 613 |  | 300614 | 4 |  | Keyswitch battery potential | INT16s | AB | 1 | V |  |  | X
EIC measurement | 614 |  | 300615 | 4 |  | Fuel delivery pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 615 |  | 300616 | 4 |  | Engine oil level | INT16s | AB | 1 | perc |  |  | X
EIC measurement | 616 |  | 300617 | 4 |  | Crankcase pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 617 |  | 300618 | 4 |  | Coolant pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 618 |  | 300619 | 4 |  | Water in fuel (1 = Yes, 0 = No) | INT16s | AB | 0 | 2 bits |  |  | X
EIC measurement | 619 |  | 300620 | 4 |  | Blowby flow | INT16s | AB | 0 |  |  |  | X
EIC measurement | 620 |  | 300621 | 4 |  | Fuel rail pressure | INT16s | AB | 0 | bar/psi |  |  | X
EIC measurement | 621 |  | 300622 | 4 |  | Timing rail pressure | INT16s | AB | 0 | bar/psi |  |  | X
EIC measurement | 622 |  | 300623 | 4 |  | Aftercooler water inlet temperature | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 623 |  | 300624 | 4 |  | Turbo oil temperature | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 624 |  | 300625 | 4 |  | Particulate trap inlet pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 625 |  | 300626 | 4 |  | Air filter differential pressure | INT16s | AB | 3 | bar/psi |  |  | X
EIC measurement | 626 |  | 300627 | 4 |  | Coolant filter differential pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 627 |  | 300628 | 4 |  | Atmospheric pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 628 |  | 300629 | 4 |  | Ambient air temperature | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 629 |  | 300630 | 4 |  | Exhaust temperature - right | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 630 |  | 300631 | 4 |  | Exhaust temperature - left | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 631 |  | 300632 | 4 |  | Winding 1 temperature | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 632 |  | 300633 | 4 |  | Winding 2 temperature | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 633 |  | 300634 | 4 |  | Winding 3 temperature | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 634 |  | 300635 | 4 |  | Auxiliary_Analog_Info | INT16s | AB | 0 |  |  |  | X
EIC measurement | 635 |  | 300636 | 4 |  | Auxiliary_Analog_Info | INT16s | AB | 0 |  |  |  | X
EIC measurement | 636 |  | 300637 | 4 |  | Engine turbocharger 1 compressor outlet temperature | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 637 |  | 300638 | 4 |  | Engine intercooler temperature | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 638 |  | 300639 | 4 |  | Engine trip fuel | INT16s | AB | 0 | L |  |  | X
EIC measurement | 639 |  | 300640 | 4 |  | Engine total fuel used | INT16s | AB | 1 | kL |  |  | X
EIC measurement | 640 |  | 300641 | 4 |  | Trip fuel, gaseous | INT16s | AB | 0 | kg |  |  | X
EIC measurement | 641 |  | 300642 | 4 |  | Total fuel used, gaseous | INT16s | AB | 1 | ton |  |  | X
Control command state | 642 |  | 300643 | 4 |  | Control command address 0 | INT16s | AB | 0 |  | X | X | X
Control command state | 643 |  | 300644 | 4 |  | Control command address 1 | INT16s | AB | 0 |  | X | X | X
Control command state | 644 |  | 300645 | 4 |  | Control command address 2 | INT16s | AB | 0 |  | X | X | X
Control command state | 645 |  | 300646 | 4 |  | Control command address 3 | INT16s | AB | 0 |  | X | X | X
Control command state | 646 |  | 300647 | 4 |  | Control command address 4 | INT16s | AB | 0 |  | X | X | X
Control command state | 647 |  | 300648 | 4 |  | Control command address 5 | INT16s | AB | 0 |  | X | X | X
Control command state | 648 |  | 300649 | 4 |  | Control command address 6 | INT16s | AB | 0 |  | X | X | X
Control command state | 649 |  | 300650 | 4 |  | Control command address 7 | INT16s | AB | 0 |  | X | X | X
Control command state | 650 |  | 300651 | 4 |  | Control command address 8 | INT16s | AB | 0 |  | X | X | X
Control command state | 651 |  | 300652 | 4 |  | Control command address 9 | INT16s | AB | 0 |  | X | X | X
Control command state | 652 |  | 300653 | 4 |  | Control command address 10 | INT16s | AB | 0 |  | X | X | X
Control command state | 653 |  | 300654 | 4 |  | Control command address 11 | INT16s | AB | 0 |  | X | X | X
Control command state | 654 |  | 300655 | 4 |  | Control command address 12 | INT16s | AB | 0 |  | X | X | X
Control command state | 655 |  | 300656 | 4 |  | Control command address 13 | INT16s | AB | 0 |  | X | X | X
DC measurement | 660 |  | 300661 | 4 |  | CIO 308 no. 1. Input 8 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 661 |  | 300662 | 4 |  | CIO 308 no. 1. Input 11 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 662 |  | 300663 | 4 |  | CIO 308 no. 1. Input 14 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 663 |  | 300664 | 4 |  | CIO 308 no. 1. Input 17 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 664 |  | 300665 | 4 |  | CIO 308 no. 1. Input 20 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 665 |  | 300666 | 4 |  | CIO 308 no. 1. Input 23 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 666 |  | 300667 | 4 |  | CIO 308 no. 1. Input 26 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 667 |  | 300668 | 4 |  | CIO 308 no. 1. Input 29 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 668 |  | 300669 | 4 |  | CIO 308 no. 2. Input 8 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 669 |  | 300670 | 4 |  | CIO 308 no. 2. Input 11 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 670 |  | 300671 | 4 |  | CIO 308 no. 2. Input 14 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 671 |  | 300672 | 4 |  | CIO 308 no. 2. Input 17 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 672 |  | 300673 | 4 |  | CIO 308 no. 2. Input 20 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 673 |  | 300674 | 4 |  | CIO 308 no. 2. Input 23 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 674 |  | 300675 | 4 |  | CIO 308 no. 2. Input 26 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 675 |  | 300676 | 4 |  | CIO 308 no. 2. Input 29 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 676 |  | 300677 | 4 |  | CIO 308 no. 3. Input 8 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 677 |  | 300678 | 4 |  | CIO 308 no. 3. Input 11 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 678 |  | 300679 | 4 |  | CIO 308 no. 3. Input 14 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 679 |  | 300680 | 4 |  | CIO 308 no. 3. Input 17 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 680 |  | 300681 | 4 |  | CIO 308 no. 3. Input 20 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 681 |  | 300682 | 4 |  | CIO 308 no. 3. Input 23 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 682 |  | 300683 | 4 |  | CIO 308 no. 3. Input 26 [Config] | INT16s | AB | 0 |  | X | X | X
DC measurement | 683 |  | 300684 | 4 |  | CIO 308 no. 3. Input 29 [Config] | INT16s | AB | 0 |  | X | X | X
AC measurement | 689 |  | 300690 | 4 |  | Power derate value | INT16s | AB | 1 | perc |  |  | X
Plant logic state | 690 |  | 300691 | 4 |  | Power derate function active: 0: No derate. 1: P derate 1. 2: P derate 2. 3: Pderate3. 4: EIC derate | INT16s | AB | 0 |  |  |  | X
Alarm | 691 |  | 300692 | 4 |  | M-Logic extended timer alarm 1 value | INT16s | AB | 0 | min/day/hrs | X | X | X
Alarm | 692 |  | 300693 | 4 |  | M-Logic extended timer alarm 2 value | INT16s | AB | 0 | min/day/hrs | X | X | X
Alarm | 693 |  | 300694 | 4 |  | M-Logic extended timer alarm 3 value | INT16s | AB | 0 | min/day/hrs | X | X | X
Alarm | 694 |  | 300695 | 4 |  | M-Logic extended timer alarm 4 value | INT16s | AB | 0 | min/day/hrs | X | X | X
EIC measurement | 696 |  | 300697 | 4 |  | Lowest Cylinder Exhaust temperature | INT16s | AB | 0 |  |  |  | X
EIC measurement | 697 |  | 300698 | 4 |  | Highest Cylinder Exhaust temperature | INT16s | AB | 0 |  |  |  | X
EIC measurement | 698 |  | 300699 | 4 |  | Average Cylinder Exhaust temperature | INT16s | AB | 0 |  |  |  | X
EIC measurement | 699 |  | 300700 | 4 |  | Cylinder Exhaust temperature: Max or Min most deviated from Average | INT16s | AB | 0 |  |  |  | X
AC measurement | 700 |  | 300701 | 4 |  | Actual nominal power (Includes derate etc.) | INT16s | AB | 0 |  | X | X | X
Plant logic state | 701 |  | 300702 | 4 |  | Mains power transducer used OR Mains power 4th CT used | INT16s | AB | 0 |  |  | X | X
Counter | 702 |  | 300703 | 4 |  | Fan A running hours | INT32s | ABCD | 0 |  |  |  | X
Counter | 704 |  | 300705 | 4 |  | Fan B running hours | INT32s | ABCD | 0 |  |  |  | X
Counter | 706 |  | 300707 | 4 |  | Fan C running hours | INT32s | ABCD | 0 |  |  |  | X
Counter | 708 |  | 300709 | 4 |  | Fan D running hours | INT32s | ABCD | 0 |  |  |  | X
Counter | 790 |  | 300791 | 4 |  | Generator Export reactive energy counter, month | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 790 |  | 300791 | 4 |  | Mains Export reactive energy counter, month | INT32s | ABCD | 0 | kWh |  | X
Counter | 790 |  | 300791 | 4 |  | Bus A Export reactive energy counter, month | INT32s | ABCD | 0 | kWh | X
Counter | 792 |  | 300793 | 4 |  | Generator Export reactive energy counter, week | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 792 |  | 300793 | 4 |  | Mains Export reactive energy counter, week | INT32s | ABCD | 0 | kWh |  | X
Counter | 792 |  | 300793 | 4 |  | Bus A Export reactive energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 794 |  | 300795 | 4 |  | Generator Export reactive energy counter, day | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 794 |  | 300795 | 4 |  | Mains Export reactive energy counter, day | INT32s | ABCD | 0 | kWh |  | X
Counter | 794 |  | 300795 | 4 |  | Bus A Export reactive energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 796 |  | 300797 | 4 |  | Generator Import active energy counter, total | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 796 |  | 300797 | 4 |  | Mains Import active energy counter, total | INT32s | ABCD | 0 | kWh |  | X
Counter | 796 |  | 300797 | 4 |  | Bus A Import active energy counter, total | INT32s | ABCD | 0 | kWh | X
Counter | 798 |  | 300799 | 4 |  | Generator Import active energy counter, month | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 798 |  | 300799 | 4 |  | Mains Import active energy counter, month | INT32s | ABCD | 0 | kWh |  | X
Counter | 798 |  | 300799 | 4 |  | Bus A Import active energy counter, month | INT32s | ABCD | 0 | kWh | X
Counter | 800 |  | 300801 | 4 |  | Generator Import active energy counter, week | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 800 |  | 300801 | 4 |  | Mains Import active energy counter, week | INT32s | ABCD | 0 | kWh |  | X
Counter | 800 |  | 300801 | 4 |  | Bus A Import active energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 802 |  | 300803 | 4 |  | Generator Import active energy counter, day | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 802 |  | 300803 | 4 |  | Mains Import active energy counter, day | INT32s | ABCD | 0 | kWh |  | X
Counter | 802 |  | 300803 | 4 |  | Bus A Import active energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 804 |  | 300805 | 4 |  | Generator Import reactive energy counter, total | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 804 |  | 300805 | 4 |  | Mains Import reactive energy counter, total | INT32s | ABCD | 0 | kWh |  | X
Counter | 804 |  | 300805 | 4 |  | Bus A Import reactive energy counter, total | INT32s | ABCD | 0 | kWh | X
Counter | 806 |  | 300807 | 4 |  | Generator Import reactive energy counter, month | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 806 |  | 300807 | 4 |  | Mains Import reactive energy counter, month | INT32s | ABCD | 0 | kWh |  | X
Counter | 806 |  | 300807 | 4 |  | Bus A Import reactive energy counter, month | INT32s | ABCD | 0 | kWh | X
Counter | 808 |  | 300809 | 4 |  | Generator Import reactive energy counter, week | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 808 |  | 300809 | 4 |  | Mains Import reactive energy counter, week | INT32s | ABCD | 0 | kWh |  | X
Counter | 808 |  | 300809 | 4 |  | Bus A Import reactive energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 810 |  | 300811 | 4 |  | Generator Import reactive energy counter, day | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 810 |  | 300811 | 4 |  | Mains Import reactive energy counter, day | INT32s | ABCD | 0 | kWh |  | X
Counter | 810 |  | 300811 | 4 |  | Bus A Import reactive energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 812 |  | 300813 | 4 |  | Pulse counter 01 | INT32s | ABCD | 0 |  | X | X | X
Counter | 814 |  | 300815 | 4 |  | Pulse counter 02 | INT32s | ABCD | 0 |  | X | X | X
AC measurement | 816 |  | 300817 | 4 |  | Demand of peak current 1 | INT16s | AB | 0 |  |  | X | X
AC measurement | 817 |  | 300818 | 4 |  | Demand of peak current 2 | INT16s | AB | 0 |  |  | X | X
AC measurement | 818 |  | 300819 | 4 |  | Demand of peak current 3 | INT16s | AB | 0 |  |  | X | X
AC measurement | 819 |  | 300820 | 4 |  | Demand of avg. peak current 1 | INT16s | AB | 0 |  |  | X | X
AC measurement | 820 |  | 300821 | 4 |  | Demand of avg. peak current 2 | INT16s | AB | 0 |  |  | X | X
AC measurement | 821 |  | 300822 | 4 |  | Demand of avg. peak current 3 | INT16s | AB | 0 |  |  | X | X
Counter | 822 |  | 300823 | 4 |  | Start attempts standard | INT16s | AB | 0 |  |  |  | X
Counter | 823 |  | 300824 | 4 |  | Start attempts double starter | INT16s | AB | 0 |  |  |  | X
AC measurement | 830 |  | 300831 | 4 |  | Fuel tank level | INT16s | AB | 0 |  |  |  | X
EIC measurement | 840 |  | 300841 | 4 |  | Battery Potential / Power Input 1 | INT16s | AB | 0 |  |  |  | X
EIC measurement | 841 |  | 300842 | 4 |  | Engine Turbocharger 2 Boost Pressure | INT16s | AB | 0 |  |  |  | X
EIC measurement | 842 |  | 300843 | 4 |  | Engine Intake Manifold 3 Temperature | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 843 |  | 300844 | 4 |  | Engine Intake Manifold 4 Temperature | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 844 |  | 300845 | 4 |  | Engine Fuel 1 Injector Metering Rail 1 Pressure | INT16s | AB | 0 | bar/psi |  |  | X
EIC measurement | 845 |  | 300846 | 4 |  | Engine Pre-filter Oil Pressure | INT16s | AB | 0 | bar/psi |  |  | X
EIC measurement | 850 |  | 300851 | 4 |  | Aftertreatment 2 Diesel Exhaust Fluid Dosing Requested Quantity | INT16s | AB | 1 | g/h |  |  | X
EIC measurement | 851 |  | 300852 | 4 |  | Aftertreatment 2 SCR Catalyst Intake Gas Temperature | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 852 |  | 300853 | 4 |  | Aftertreatment 2 SCR Catalyst Outlet Gas Temperature | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 853 |  | 300854 | 4 |  | Engine Oil-Filter Outlet Pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 854 |  | 300855 | 4 |  | Engine Operating State | INT16s | AB | 0 |  |  |  | X
EIC measurement | 855 |  | 300856 | 4 |  | Source Address of Controlling Device | INT16s | AB | 0 |  |  |  | X
EIC measurement | 856 |  | 300857 | 4 |  | Engine Rated Speed | INT16s | AB | 0 | rpm |  |  | X
EIC measurement | 857 |  | 300858 | 4 |  | Engine Speed At Idle, Point 1 | INT16s | AB | 0 | rpm |  |  | X
EIC measurement | 858 |  | 300859 | 4 |  | MTU only: Fuel Consumption g/KWh | INT16s | AB | 0 | g/kWh |  |  | X
EIC measurement | 859 |  | 300860 | 4 |  | MTU only: Engine Status of Start procedure | INT16s | AB | 0 |  |  |  | X
EIC measurement | 860 |  | 300861 | 4 |  | UREA Level | INT16s | AB | 1 | perc |  |  | X
EIC measurement | 861 |  | 300862 | 4 |  | Severity status of the operator inducement system | INT16s | AB | 0 |  |  |  | X
EIC measurement | 862 |  | 300863 | 4 |  | Temperature of engine combustion byproducts leaving the diesel particulate filter exhaust in exhaust bank 1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 863 |  | 300864 | 4 |  | Time to activate next regeneration for diesel particulate filter | INT16s | AB | 1 | h |  |  | X
EIC measurement | 864 |  | 300865 | 4 |  | Temperature of combustion air after it exits from the Charge Air Cooler 1 but before any mixing of recirculated exhaust gas. | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 865 |  | 300866 | 4 |  | Aftertreatment 1 Diesel Particulate Filter 1 Soot Load Percent | INT16s | AB | 0 |  |  |  | X
EIC measurement | 866 |  | 300867 | 4 |  | Battery Charger 1 Output Voltage | INT16s | AB | 0 | V |  |  | X
EIC measurement | 867 |  | 300868 | 4 |  | Battery Charger 1 Output Current | INT16s | AB | 0 | A |  |  | X
EIC state | 868 | 0 | 300869 | 4 |  | DPF lamp OFF | BOOL | [5 empty] | X
EIC state | 868 | 1 | 300869 | 4 |  | DPF lamp ON solid | BOOL | [5 empty] | X
EIC state | 868 | 2 | 300869 | 4 |  | DPF lamp ON blink | BOOL | [5 empty] | X
EIC state | 868 | 3 | 300869 | 4 |  | DPF Active Regeneration not activated | BOOL | [5 empty] | X
EIC state | 868 | 4 | 300869 | 4 |  | DPF Active Regeneration activated | BOOL | [5 empty] | X
EIC state | 868 | 5 | 300869 | 4 |  | DPF Active Regeneration needed | BOOL | [5 empty] | X
EIC state | 868 | 6 | 300869 | 4 |  | DPF Regeneration not needed | BOOL | [5 empty] | X
EIC state | 868 | 7 | 300869 | 4 |  | DPF Regeneration needed Lowest | BOOL | [5 empty] | X
EIC state | 868 | 8 | 300869 | 4 |  | DPF Regeneration needed Moderate | BOOL | [5 empty] | X
EIC state | 868 | 9 | 300869 | 4 |  | DPF Regeneration needed Highest | BOOL | [5 empty] | X
EIC state | 868 | 10 | 300869 | 4 |  | DPF Regeneration Not Inhibit | BOOL | [5 empty] | X
EIC state | 868 | 11 | 300869 | 4 |  | DPF Regeneration Inhibit | BOOL | [5 empty] | X
EIC state | 868 | 12 | 300869 | 4 |  | Exhaust system high temperature OFF | BOOL | [5 empty] | X
EIC state | 868 | 13 | 300869 | 4 |  | Exhaust system high temperature ON | BOOL | [5 empty] | X
EIC state | 868 | 14 | 300869 | 4 |  | After run status | BOOL | [5 empty] | X
EIC state | 869 | 0 | 300870 | 4 |  | MTU limit lamp OFF | BOOL | [5 empty] | X
EIC state | 869 | 1 | 300870 | 4 |  | MTU limit lamp ON solid | BOOL | [5 empty] | X
EIC state | 869 | 2 | 300870 | 4 |  | MTU limit lamp ON blink 1Hz | BOOL | [5 empty] | X
EIC state | 869 | 3 | 300870 | 4 |  | DEF level low lamp OFF | BOOL | [5 empty] | X
EIC state | 869 | 4 | 300870 | 4 |  | DEF level low lamp ON solid | BOOL | [5 empty] | X
EIC state | 869 | 5 | 300870 | 4 |  | DEF level low lamp ON blink | BOOL | [5 empty] | X
EIC state | 869 | 6 | 300870 | 4 |  | Volvo Penta Scr Inducement NOT ACTIVE | BOOL | [5 empty] | X
EIC state | 869 | 7 | 300870 | 4 |  | Volvo Penta Scr Inducement WARNING | BOOL | [5 empty] | X
EIC state | 869 | 8 | 300870 | 4 |  | Volvo Penta Scr Derate ACTIVE | BOOL | [5 empty] | X
EIC state | 869 | 9 | 300870 | 4 |  | Volvo Penta Pre severe Derate WARNING | BOOL | [5 empty] | X
EIC state | 869 | 10 | 300870 | 4 |  | Volvo Penta Severe Derate | BOOL | [5 empty] | X
EIC state | 869 | 11 | 300870 | 4 |  | Volvo Penta Temperature Override Derate | BOOL | [5 empty] | X
EIC state | 869 | 12 | 300870 | 4 |  | Volvo Penta Scr Inducement Reason OK | BOOL | [5 empty] | X
EIC state | 869 | 13 | 300870 | 4 |  | Volvo Penta Reagent Tank low | BOOL | [5 empty] | X
EIC state | 869 | 14 | 300870 | 4 |  | Volvo Penta Incorrect Reagent Quality | BOOL | [5 empty] | X
EIC state | 869 | 15 | 300870 | 4 |  | Volvo Penta Absence of Reagent Dosing | BOOL | [5 empty] | X
EIC state | 870 | 0 | 300871 | 4 |  | MTU limit lamp ON blink 2Hz | BOOL | [5 empty] | X
EIC state | 870 | 1 | 300871 | 4 |  | MTU TIER4 lamp ON blink 2Hz | BOOL | [5 empty] | X
EIC state | 870 | 2 | 300871 | 4 |  | MTU buzzer lamp OFF | BOOL | [5 empty] | X
EIC state | 870 | 3 | 300871 | 4 |  | MTU buzzer lamp ON solid | BOOL | [5 empty] | X
EIC state | 870 | 4 | 300871 | 4 |  | MTU buzzer lamp ON blink 1Hz | BOOL | [5 empty] | X
EIC state | 870 | 5 | 300871 | 4 |  | MTU buzzer lamp ON blink 2Hz | BOOL | [5 empty] | X
EIC state | 870 | 6 | 300871 | 4 |  | Alarm Yellow lamp OFF | BOOL | [5 empty] | X
EIC state | 870 | 7 | 300871 | 4 |  | Alarm Yellow lamp ON | BOOL | [5 empty] | X
EIC state | 870 | 8 | 300871 | 4 |  | Alarm Red lamp OFF | BOOL | [5 empty] | X
EIC state | 870 | 9 | 300871 | 4 |  | Alarm Red lamp ON | BOOL | [5 empty] | X
EIC state | 870 | 10 | 300871 | 4 |  | Engine protect system SHUTDOWN | BOOL | [5 empty] | X
EIC state | 870 | 11 | 300871 | 4 |  | Engine over-speed test | BOOL | [5 empty] | X
EIC state | 870 | 12 | 300871 | 4 |  | Engine Alarm acknowledge | BOOL | [5 empty] | X
EIC state | 870 | 13 | 300871 | 4 |  | Manual purge ECU | BOOL | [5 empty] | X
EIC state | 870 | 14 | 300871 | 4 |  | Manual purge EIDSS | BOOL | [5 empty] | X
EIC state | 870 | 15 | 300871 | 4 |  | Force purge | BOOL | [5 empty] | X
EIC measurement | 871 |  | 300872 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Average Consumption | INT16s | AB | 0 |  |  |  | X
EIC measurement | 872 |  | 300873 | 4 |  | Volvo Penta Time left to torque reduction | INT16s | AB | 0 |  |  |  | X
EIC measurement | 873 |  | 300874 | 4 |  | Volvo Penta Time left to severe torque reduction | INT16s | AB | 0 |  |  |  | X
EIC measurement | 874 |  | 300875 | 4 |  | Volvo Penta SCR inducement severity | INT16s | AB | 0 |  |  |  | X
EIC measurement | 875 |  | 300876 | 4 |  | Volvo Penta SCR inducement reason | INT16s | AB | 0 |  |  |  | X
EIC measurement | 876 |  | 300877 | 4 |  | Engine Operating Derate Request | INT16s | AB | 0 |  |  |  | X
EIC measurement | 877 |  | 300878 | 4 |  | Engine Demand - Percent Torque | INT16s | AB | 0 | perc |  |  | X
EIC measurement | 878 |  | 300879 | 4 |  | Engine Throttle Actuator 1 Control Command | INT16s | AB | 0 |  |  |  | X
EIC measurement | 879 |  | 300880 | 4 |  | Long-term Fuel Trim | INT16s | AB | 0 |  |  |  | X
EIC measurement | 880 |  | 300881 | 4 |  | Short-term Fuel Trim | INT16s | AB | 0 |  |  |  | X
EIC measurement | 881 |  | 300882 | 4 |  | Engine Exhaust Gas Oxygen Sensor Closed Loop Operation | INT16s | AB | 0 |  |  |  | X
EIC measurement | 882 |  | 300883 | 4 |  | Engine Desired Ignition Timing #1 | INT16s | AB | 0 |  |  |  | X
EIC measurement | 883 |  | 300884 | 4 |  | Engine Actual Ignition Timing | INT16s | AB | 0 |  |  |  | X
EIC measurement | 884 |  | 300885 | 4 |  | Aftertreatment 1 Intake Percent Oxygen 1 | INT16s | AB | 0 | perc |  |  | X
EIC measurement | 885 |  | 300886 | 4 |  | Aftertreatment 1 Intake Percent Oxygen 2 | INT16s | AB | 0 | perc |  |  | X
EIC measurement | 886 |  | 300887 | 4 |  | Engine Starter Mode | INT16s | AB | 0 |  |  |  | X
EIC measurement | 887 |  | 300888 | 4 |  | Actual Maximum Available Engine-Percent Torque | INT16s | AB | 0 | perc |  |  | X
EIC measurement | 888 |  | 300889 | 4 |  | Engine Coolant Preheated State | INT16s | AB | 0 |  |  |  | X
EIC measurement | 889 |  | 300890 | 4 |  | Engine Safety and Protection Override Status | INT16s | AB | 0 |  |  |  | X
EIC measurement | 890 |  | 300891 | 4 |  | Engine Cylinder Cut-off | INT16s | AB | 0 |  |  |  | X
EIC measurement | 891 |  | 300892 | 4 |  | MTU Engine Running State | INT16s | AB | 0 |  |  |  | X
EIC measurement | 892 |  | 300893 | 4 |  | External Stop State | INT16s | AB | 0 |  |  |  | X
EIC measurement | 893 |  | 300894 | 4 |  | MTU Requested Absolute Torque | INT16s | AB | 0 |  |  |  | X
EIC measurement | 894 |  | 300895 | 4 |  | Source of Current Speed Demand | INT16s | AB | 0 |  |  |  | X
EIC measurement | 895 |  | 300896 | 4 |  | Engine Demanded Operating Speed (Speed Demand Effective) | INT16s | AB | 0 |  |  |  | X
EIC measurement | 896 |  | 300897 | 4 |  | Feedback of Speed Demand CAN | INT16s | AB | 0 |  |  |  | X
EIC measurement | 897 |  | 300898 | 4 |  | Feedback of Speed Demand Analogue Input | INT16s | AB | 0 |  |  |  | X
EIC measurement | 898 |  | 300899 | 4 |  | Speed Demand Fail Mode | INT16s | AB | 0 |  |  |  | X
EIC measurement | 899 |  | 300900 | 4 |  | Inducement Timer | INT16s | AB | 0 |  |  |  | X
EIC measurement | 900 |  | 300901 | 4 |  | Mean Trip Fuel consumption | INT16s | AB | 0 |  |  |  | X
EIC measurement | 901 |  | 300902 | 4 |  | Nominal power | INT16s | AB | 0 | kWm |  |  | X
EIC measurement | 902 |  | 300903 | 4 |  | Engine Trip Fuel | INT32s | ABCD | 0 | L |  |  | X
EIC measurement | 904 |  | 300905 | 4 |  | Engine Total Fuel Used | INT32s | ABCD | 0 | L |  |  | X
EIC measurement | 906 |  | 300907 | 4 |  | Mean Trip Fuel consumption | INT32s | ABCD | 0 | L |  |  | X
EIC measurement | 908 |  | 300909 | 4 |  | Engine power | INT16s | AB | 0 | kW |  |  | X
EIC measurement | 909 |  | 300910 | 4 |  | Engine Hours | INT32s | ABCD | 0 | h |  |  | X
EIC measurement | 911 |  | 300912 | 4 |  | Engine intake Manifold #1 Absolute pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 912 |  | 300913 | 4 |  | Air Filter Differential pressure 2 | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 913 |  | 300914 | 4 |  | Fuel Supply Pump Inlet Pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 914 |  | 300915 | 4 |  | Fuel Filter (suction side) Differential Pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 915 |  | 300916 | 4 |  | Engine Fuel Filter Differential Pressure | INT16s | AB | 2 | bar/psi |  |  | X
DAVR measurement | 916 |  | 300917 | 4 |  | DAVR Generator voltage L1L2 | INT16s | AB | 0 | V |  |  | X
DAVR measurement | 917 |  | 300918 | 4 |  | DAVR Generator frequency L1 | INT16s | AB | 0 | Hz |  |  | X
DAVR measurement | 918 |  | 300919 | 4 |  | DAVR Generator current L1 | INT16s | AB | 0 | A |  |  | X
DAVR measurement | 919 |  | 300920 | 4 |  | DAVR Generator excitation field current | INT16s | AB | 0 |  |  |  | X
DAVR measurement | 921 |  | 300922 | 4 |  | DAVR Generator total reactive power | INT16s | AB | 0 | kvar |  |  | X
DAVR measurement | 922 |  | 300923 | 4 |  | DAVR Generator overall power factor | INT16s | AB | 0 |  |  |  | X
DAVR measurement | 923 |  | 300924 | 4 |  | DAVR Generator overall power factor lagging | INT16s | AB | 0 |  |  |  | X
DAVR measurement | 925 |  | 300926 | 4 |  | DAVR Generator total active power | INT16s | AB | 0 | kW |  |  | X
DAVR measurement | 927 |  | 300928 | 4 |  | DAVR Generator total apparent power | INT16s | AB | 0 | kVA |  |  | X
DAVR measurement | 928 |  | 300929 | 4 |  | DAVR Pt100 #1 | INT16s | AB | 0 | Deg C/F |  |  | X
DAVR measurement | 929 |  | 300930 | 4 |  | DAVR Pt100 #2 | INT16s | AB | 0 | Deg C/F |  |  | X
DAVR measurement | 930 |  | 300931 | 4 |  | DAVR Pt100 #3 | INT16s | AB | 0 | Deg C/F |  |  | X
DAVR measurement | 931 |  | 300932 | 4 |  | DAVR Trip alarm | INT16s | AB | 0 |  |  |  | X
EIC measurement | 932 |  | 300933 | 4 |  | Speed demand switch | INT16s | AB | 0 |  |  |  | X
EIC measurement | 933 |  | 300934 | 4 |  | Pressure: Lube Oil Limit LO | INT16s | AB | 0 | bar/psi |  |  | X
EIC measurement | 934 |  | 300935 | 4 |  | Pressure: Lube Oil Limit LOLO | INT16s | AB | 0 | bar/psi |  |  | X
EIC measurement | 935 |  | 300936 | 4 |  | Pressure: Fuel | INT16s | AB | 0 | bar/psi |  |  | X
EIC measurement | 936 |  | 300937 | 4 |  | Temperature: Coolant Limit HI | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 937 |  | 300938 | 4 |  | Temperature: Coolant Limit HIHI | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 938 |  | 300939 | 4 |  | Temperature: Coolant Intercooler | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 939 |  | 300940 | 4 |  | ECU temperature | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 940 |  | 300941 | 4 |  | Actual Droop | INT16s | AB | 0 |  |  |  | X
EIC measurement | 941 |  | 300942 | 4 |  | Injection Quantity Act.DBR | INT16s | AB | 0 | perc |  |  | X
EIC measurement | 942 |  | 300943 | 4 |  | Engine Speed Camshaft | INT16s | AB | 0 |  |  |  | X
EIC measurement | 943 |  | 300944 | 4 |  | Temperature: Lube Oil Limit HI | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 944 |  | 300945 | 4 |  | Temperature: Lube Oil Limit HIHI | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 945 |  | 300946 | 4 |  | Feedback Speed Demand analog | INT16s | AB | 0 |  |  |  | X
EIC measurement | 946 |  | 300947 | 4 |  | Stop signal activated | INT16s | AB | 0 |  |  |  | X
EIC measurement | 947 |  | 300948 | 4 |  | Exhaust Port Temperature 01 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 948 |  | 300949 | 4 |  | Exhaust Port Temperature 02 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 949 |  | 300950 | 4 |  | Exhaust Port Temperature 03 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 950 |  | 300951 | 4 |  | Exhaust Port Temperature 04 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 951 |  | 300952 | 4 |  | Exhaust Port Temperature 05 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 952 |  | 300953 | 4 |  | Exhaust Port Temperature 06 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 953 |  | 300954 | 4 |  | Exhaust Port Temperature 07 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 954 |  | 300955 | 4 |  | Exhaust Port Temperature 08 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 955 |  | 300956 | 4 |  | Exhaust Port Temperature 09 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 956 |  | 300957 | 4 |  | Exhaust Port Temperature 10 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 957 |  | 300958 | 4 |  | Exhaust Port Temperature 11 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 958 |  | 300959 | 4 |  | Exhaust Port Temperature 12 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 959 |  | 300960 | 4 |  | Exhaust Port Temperature 13 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 960 |  | 300961 | 4 |  | Exhaust Port Temperature 14 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 961 |  | 300962 | 4 |  | Exhaust Port Temperature 15 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 962 |  | 300963 | 4 |  | Exhaust Port Temperature 16 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 963 |  | 300964 | 4 |  | Exhaust Port Temperature 17 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 964 |  | 300965 | 4 |  | Exhaust Port Temperature 18 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 965 |  | 300966 | 4 |  | Exhaust Port Temperature 19 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 966 |  | 300967 | 4 |  | Exhaust Port Temperature 20 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 967 |  | 300968 | 4 |  | Engine Filtered Fuel Delivery Pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 968 |  | 300969 | 4 |  | Engine Coolant Temperature 2 | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 969 |  | 300970 | 4 |  | Engine Coolant Temperature 3 | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 970 |  | 300971 | 4 |  | Engine Coolant Pump Outlet Temperature | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 971 |  | 300972 | 4 |  | Engine Auxiliary Coolant Temperature | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 972 |  | 300973 | 4 |  | Engine Turbocharger 1 Turbine Intake Temperature | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 973 |  | 300974 | 4 |  | Engine Turbocharger 2 Turbine Intake Temperature | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 974 |  | 300975 | 4 |  | Engine Auxiliary Coolant Pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 975 |  | 300976 | 4 |  | Ambient Conditions 2 Specific Humidity | INT16s | AB | 1 | g/kg |  |  | X
EIC measurement | 976 |  | 300977 | 4 |  | Engine Turbocharger 2 Speed | INT16s | AB | 0 | rpm |  |  | X
EIC measurement | 977 |  | 300978 | 4 |  | Engine Turbocharger 3 Speed | INT16s | AB | 0 | rpm |  |  | X
EIC measurement | 978 |  | 300979 | 4 |  | Trip Engine Running Time | INT16s | AB | 0 | h |  |  | X
EIC measurement | 979 |  | 300980 | 4 |  | Trip Idle Time | INT16s | AB | 0 | h |  |  | X
EIC measurement | 980 |  | 300981 | 4 |  | Estimated Percent Fan Speed | INT16s | AB | 1 | perc |  |  | X
EIC measurement | 981 |  | 300982 | 4 |  | Engine Turbocharger 1 Speed | INT16s | AB | 0 | rpm |  |  | X
EIC measurement | 982 |  | 300983 | 4 |  | Nominal Friction - Percent Torque | INT16s | AB | 0 | perc |  |  | X
EIC measurement | 983 |  | 300984 | 4 |  | Engine's Desired Operating Speed | INT16s | AB | 0 | rpm |  |  | X
EIC measurement | 984 |  | 300985 | 4 |  | Temperature of pre-combustion air found in intake manifold of engine air supply system | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 985 |  | 300986 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Level | INT16s | AB | 1 | perc |  |  | X
EIC measurement | 986 |  | 300987 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Temperature | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 987 |  | 300988 | 4 |  | Aftertreatment 1 Intake NOx | INT16s | AB | 1 | ppm |  |  | X
EIC measurement | 988 |  | 300989 | 4 |  | Aftertreatment 1 Outlet NOx | INT16s | AB | 1 | ppm |  |  | X
EIC measurement | 989 |  | 300990 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Actual Dosing Quantity | INT16s | AB | 1 | g/h |  |  | X
EIC measurement | 990 |  | 300991 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Doser Absolute Pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 991 |  | 300992 | 4 |  | Aftertreatment 1 SCR Dosing Air Assist Valve | INT16s | AB | 0 | Deg C/F |  |  | X
EIC measurement | 992 |  | 300993 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Dosing Requested Quantity | INT16s | AB | 0 | g/h |  |  | X
EIC measurement | 993 |  | 300994 | 4 |  | Aftertreatment 1 SCR Catalyst Intake Gas Temperature | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 994 |  | 300995 | 4 |  | Aftertreatment 1 SCR Catalyst Outlet Gas Temperature | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 995 |  | 300996 | 4 |  | Aftertreatment 2 Intake NOx | INT16s | AB | 1 | ppm |  |  | X
EIC measurement | 996 |  | 300997 | 4 |  | Aftertreatment 2 Outlet NOx | INT16s | AB | 1 | ppm |  |  | X
EIC measurement | 997 |  | 300998 | 4 |  | Aftertreatment 2 Diesel Exhaust Fluid Actual Dosing Quantity | INT16s | AB | 1 | Deg C/F |  |  | X
EIC measurement | 998 |  | 300999 | 4 |  | Aftertreatment 2 Diesel Exhaust Fluid Dosing Absolute Pressure | INT16s | AB | 2 | bar/psi |  |  | X
EIC measurement | 999 |  | 301000 | 4 |  | Aftertreatment 2 SCR Dosing Air Assist Valve | INT16s | AB | 0 | Deg C/F |  |  | X
AC alarm | 1000 | 0 | 301001 | 4 | 1000 | G -P> 1 | BOOL | [5 empty] | X
AC alarm | 1000 | 0 | 301001 | 4 | 1000 | M -P> 1 | BOOL |  |  |  |  | X
AC alarm | 1000 | 0 | 301001 | 4 | 1000 | BA -P> 1 | BOOL |  |  |  | X
AC alarm | 1000 | 1 | 301001 | 4 | 1010 | G -P> 2 | BOOL | [5 empty] | X
AC alarm | 1000 | 1 | 301001 | 4 | 1010 | M -P> 2 | BOOL |  |  |  |  | X
AC alarm | 1000 | 1 | 301001 | 4 | 1010 | BA -P> 2 | BOOL |  |  |  | X
AC alarm | 1000 | 2 | 301001 | 4 | 1070 | G -P> 3 | BOOL | [5 empty] | X
AC alarm | 1000 | 2 | 301001 | 4 | 1070 | M -P> 3 | BOOL |  |  |  |  | X
AC alarm | 1000 | 2 | 301001 | 4 | 1070 | BA -P> 3 | BOOL |  |  |  | X
AC alarm | 1000 | 3 | 301001 | 4 | 1030 | G I> 1 | BOOL | [5 empty] | X
AC alarm | 1000 | 3 | 301001 | 4 | 1030 | M I> 1 | BOOL |  |  |  |  | X
AC alarm | 1000 | 3 | 301001 | 4 | 1030 | BA I> 1 | BOOL |  |  |  | X
AC alarm | 1000 | 4 | 301001 | 4 | 1040 | G I> 2 | BOOL | [5 empty] | X
AC alarm | 1000 | 4 | 301001 | 4 | 1040 | M I> 2 | BOOL |  |  |  |  | X
AC alarm | 1000 | 4 | 301001 | 4 | 1040 | BA I> 2 | BOOL |  |  |  | X
AC alarm | 1000 | 5 | 301001 | 4 | 1050 | G I> 3 | BOOL | [5 empty] | X
AC alarm | 1000 | 5 | 301001 | 4 | 1050 | M I> 3 | BOOL |  |  |  |  | X
AC alarm | 1000 | 5 | 301001 | 4 | 1050 | BA I> 3 | BOOL |  |  |  | X
AC alarm | 1000 | 6 | 301001 | 4 | 1060 | G I> 4 | BOOL | [5 empty] | X
AC alarm | 1000 | 6 | 301001 | 4 | 1060 | M I> 4 | BOOL |  |  |  |  | X
AC alarm | 1000 | 6 | 301001 | 4 | 1060 | BA I> 4 | BOOL |  |  |  | X
AC alarm | 1000 | 7 | 301001 | 4 | 1087 | G I> inv. | BOOL | [5 empty] | X
AC alarm | 1000 | 7 | 301001 | 4 | 1087 | M I> inv. | BOOL |  |  |  |  | X
AC alarm | 1000 | 7 | 301001 | 4 | 1087 | BA I> inv. | BOOL |  |  |  | X
AC alarm | 1000 | 8 | 301001 | 4 | 1110 | G Iv> | BOOL |  |  |  | X | X | X
AC alarm | 1000 | 9 | 301001 | 4 | 1130 | G I>> 1 | BOOL | [5 empty] | X
AC alarm | 1000 | 9 | 301001 | 4 | 1130 | M I>> 1 | BOOL |  |  |  |  | X
AC alarm | 1000 | 9 | 301001 | 4 | 1130 | BA I>> 1 | BOOL |  |  |  | X
AC alarm | 1000 | 10 | 301001 | 4 | 1140 | G I>> 2 | BOOL | [5 empty] | X
AC alarm | 1000 | 10 | 301001 | 4 | 1140 | M I>> 2 | BOOL |  |  |  |  | X
AC alarm | 1000 | 10 | 301001 | 4 | 1140 | BA I>> 2 | BOOL |  |  |  | X
AC alarm | 1000 | 11 | 301001 | 4 | 1150 | G U> 1 | BOOL | [5 empty] | X
AC alarm | 1000 | 11 | 301001 | 4 | 1150 | M U> 1 | BOOL |  |  |  |  | X
AC alarm | 1000 | 11 | 301001 | 4 | 1150 | BA U> 1 | BOOL |  |  |  | X
AC alarm | 1000 | 12 | 301001 | 4 | 1160 | M U> 2 | BOOL |  |  |  |  | X
AC alarm | 1000 | 12 | 301001 | 4 | 1160 | G U> 2 | BOOL | [5 empty] | X
AC alarm | 1000 | 12 | 301001 | 4 | 1160 | BA U> 2 | BOOL |  |  |  | X
AC alarm | 1000 | 13 | 301001 | 4 | 1170 | G U< 1 | BOOL | [5 empty] | X
AC alarm | 1000 | 13 | 301001 | 4 | 1170 | M U< 1 | BOOL |  |  |  |  | X
AC alarm | 1000 | 13 | 301001 | 4 | 1170 | BA U< 1 | BOOL |  |  |  | X
AC alarm | 1000 | 14 | 301001 | 4 | 1180 | G U< 2 | BOOL | [5 empty] | X
AC alarm | 1000 | 14 | 301001 | 4 | 1180 | M U< 2 | BOOL |  |  |  |  | X
AC alarm | 1000 | 14 | 301001 | 4 | 1180 | BA U< 2 | BOOL |  |  |  | X
AC alarm | 1000 | 15 | 301001 | 4 | 1190 | G U< 3 | BOOL | [5 empty] | X
AC alarm | 1000 | 15 | 301001 | 4 | 1190 | M U< 3 | BOOL |  |  |  |  | X
AC alarm | 1000 | 15 | 301001 | 4 | 1190 | BA U< 3 | BOOL |  |  |  | X
AC alarm | 1001 | 0 | 301002 | 4 | 1210 | G f> 1 | BOOL | [5 empty] | X
AC alarm | 1001 | 0 | 301002 | 4 | 1210 | M f> 1 | BOOL |  |  |  |  | X
AC alarm | 1001 | 0 | 301002 | 4 | 1210 | BA f> 1 | BOOL |  |  |  | X
AC alarm | 1001 | 1 | 301002 | 4 | 1220 | G f> 2 | BOOL | [5 empty] | X
AC alarm | 1001 | 1 | 301002 | 4 | 1220 | M f> 2 | BOOL |  |  |  |  | X
AC alarm | 1001 | 1 | 301002 | 4 | 1220 | BA f> 2 | BOOL |  |  |  | X
AC alarm | 1001 | 2 | 301002 | 4 | 1230 | G f> 3 | BOOL | [5 empty] | X
AC alarm | 1001 | 2 | 301002 | 4 | 1230 | M f> 3 | BOOL |  |  |  |  | X
AC alarm | 1001 | 2 | 301002 | 4 | 1230 | BA f> 3 | BOOL |  |  |  | X
AC alarm | 1001 | 3 | 301002 | 4 | 1240 | G f< 1 | BOOL | [5 empty] | X
AC alarm | 1001 | 3 | 301002 | 4 | 1240 | M f< 1 | BOOL |  |  |  |  | X
AC alarm | 1001 | 3 | 301002 | 4 | 1240 | BA f< 1 | BOOL |  |  |  | X
AC alarm | 1001 | 4 | 301002 | 4 | 1250 | G f< 2 | BOOL | [5 empty] | X
AC alarm | 1001 | 4 | 301002 | 4 | 1250 | M f< 2 | BOOL |  |  |  |  | X
AC alarm | 1001 | 4 | 301002 | 4 | 1250 | BA f< 2 | BOOL |  |  |  | X
AC alarm | 1001 | 5 | 301002 | 4 | 1260 | G f< 3 | BOOL | [5 empty] | X
AC alarm | 1001 | 5 | 301002 | 4 | 1260 | M f< 3 | BOOL |  |  |  |  | X
AC alarm | 1001 | 5 | 301002 | 4 | 1260 | BA f< 3 | BOOL |  |  |  | X
AC alarm | 1001 | 6 | 301002 | 4 | 1270 | BB U> 1 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 7 | 301002 | 4 | 1280 | BB U> 2 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 8 | 301002 | 4 | 1290 | BB U> 3 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 9 | 301002 | 4 | 1300 | BB U< 1 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 10 | 301002 | 4 | 1310 | BB U< 2 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 11 | 301002 | 4 | 1320 | BB U< 3 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 12 | 301002 | 4 | 1330 | BB U< 4 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 13 | 301002 | 4 | 1350 | BB f> 1 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 14 | 301002 | 4 | 1360 | BB f> 2 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 15 | 301002 | 4 | 1370 | BB f> 3 | BOOL |  |  |  | X | X | X
AC alarm | 1002 | 0 | 301003 | 4 | 1380 | BB f< 1 | BOOL |  |  |  | X | X | X
AC alarm | 1002 | 1 | 301003 | 4 | 1390 | BB f< 2 | BOOL |  |  |  | X | X | X
AC alarm | 1002 | 2 | 301003 | 4 | 1400 | BB f< 3 | BOOL |  |  |  | X | X | X
AC alarm | 1002 | 3 | 301003 | 4 | 1410 | BB f< 4 | BOOL |  |  |  | X | X | X
AC alarm | 1002 | 4 | 301003 | 4 | 1420 | df/dt (ROCOF) | BOOL |  |  |  | X | X | X
AC alarm | 1002 | 5 | 301003 | 4 | 1430 | Vector jump | BOOL |  |  |  | X | X | X
AC alarm | 1002 | 6 | 301003 | 4 | 1440 | BB pos. seq. volt. low | BOOL |  |  |  | X | X | X
AC alarm | 1002 | 7 | 301003 | 4 | 1450 | G P> 1 | BOOL | [5 empty] | X
AC alarm | 1002 | 7 | 301003 | 4 | 1450 | M P> 1 | BOOL |  |  |  |  | X
AC alarm | 1002 | 7 | 301003 | 4 | 1450 | BA P> 1 | BOOL |  |  |  | X
AC alarm | 1002 | 8 | 301003 | 4 | 1460 | G P> 2 | BOOL | [5 empty] | X
AC alarm | 1002 | 8 | 301003 | 4 | 1460 | M P> 2 | BOOL |  |  |  |  | X
AC alarm | 1002 | 8 | 301003 | 4 | 1460 | BA P> 2 | BOOL |  |  |  | X
AC alarm | 1002 | 9 | 301003 | 4 | 1470 | G P> 3 | BOOL | [5 empty] | X
AC alarm | 1002 | 9 | 301003 | 4 | 1470 | M P> 3 | BOOL |  |  |  |  | X
AC alarm | 1002 | 9 | 301003 | 4 | 1470 | BA P> 3 | BOOL |  |  |  | X
AC alarm | 1002 | 10 | 301003 | 4 | 1480 | G P> 4 | BOOL | [5 empty] | X
AC alarm | 1002 | 10 | 301003 | 4 | 1480 | M P> 4 | BOOL |  |  |  |  | X
AC alarm | 1002 | 10 | 301003 | 4 | 1480 | BA P> 4 | BOOL |  |  |  | X
AC alarm | 1002 | 11 | 301003 | 4 | 1490 | G P> 5 | BOOL | [5 empty] | X
AC alarm | 1002 | 11 | 301003 | 4 | 1490 | M P> 5 | BOOL |  |  |  |  | X
AC alarm | 1002 | 11 | 301003 | 4 | 1490 | BA P> 5 | BOOL |  |  |  | X
AC alarm | 1002 | 12 | 301003 | 4 | 1500 | Unbalance curr. 1 | BOOL |  |  |  |  | X | X
AC alarm | 1002 | 13 | 301003 | 4 | 1510 | Unbalance volt. | BOOL |  |  |  |  | X | X
AC alarm | 1002 | 14 | 301003 | 4 | 1520 | G -Q> | BOOL | [5 empty] | X
AC alarm | 1002 | 14 | 301003 | 4 | 1520 | M -Q> | BOOL |  |  |  |  | X
AC alarm | 1002 | 14 | 301003 | 4 | 1520 | BA -Q> | BOOL |  |  |  | X
AC alarm | 1002 | 15 | 301003 | 4 | 1530 | G Q> | BOOL | [5 empty] | X
AC alarm | 1002 | 15 | 301003 | 4 | 1530 | M Q> | BOOL |  |  |  |  | X
AC alarm | 1002 | 15 | 301003 | 4 | 1530 | BA Q> | BOOL |  |  |  | X
AC alarm | 1003 | 0 | 301004 | 4 | 1540 | Gen. neg. seq. I | BOOL | [5 empty] | X
AC alarm | 1003 | 0 | 301004 | 4 | 1540 | Mains neg. seq. I | BOOL |  |  |  |  | X
AC alarm | 1003 | 1 | 301004 | 4 | 1550 | Generator neg. seq. U | BOOL | [5 empty] | X
AC alarm | 1003 | 1 | 301004 | 4 | 1550 | Mains neg. seq. U | BOOL |  |  |  |  | X
AC alarm | 1003 | 1 | 301004 | 4 | 1550 | Bus A neg. seq. U | BOOL |  |  |  | X
AC alarm | 1003 | 2 | 301004 | 4 | 1570 | Gen. zero seq. I | BOOL | [5 empty] | X
AC alarm | 1003 | 2 | 301004 | 4 | 1570 | Mains zero seq. I | BOOL |  |  |  |  | X
AC alarm | 1003 | 2 | 301004 | 4 | 1570 | Bus A zero seq. I | BOOL |  |  |  | X
AC alarm | 1003 | 3 | 301004 | 4 | 1580 | Zero seq. U | BOOL | [5 empty] | X
AC alarm | 1003 | 3 | 301004 | 4 | 1580 | Mains zero seq. U | BOOL |  |  |  |  | X
AC alarm | 1003 | 3 | 301004 | 4 | 1580 | Bus A zero seq. U | BOOL |  |  |  | X
AC alarm | 1003 | 4 | 301004 | 4 | 1600 | Directional overcurrent 1 | BOOL |  |  |  | X | X | X
AC alarm | 1003 | 5 | 301004 | 4 | 1610 | Directional overcurrent 2 | BOOL |  |  |  | X | X | X
AC alarm | 1003 | 6 | 301004 | 4 | 1620 | BB unbalance U | BOOL |  |  |  | X | X | X
AC alarm | 1004 | 6 | 301005 | 4 | 1960 | U and Q< 1 | BOOL |  |  |  |  | X | X
AC alarm | 1004 | 7 | 301005 | 4 | 1970 | U and Q< 2 | BOOL |  |  |  |  | X | X
AC alarm | 1004 | 8 | 301005 | 4 | 1981 | GB ext. trip | BOOL | [5 empty] | X
AC alarm | 1004 | 8 | 301005 | 4 | 1981 | TB ext. trip | BOOL |  |  |  |  | X
AC alarm | 1004 | 8 | 301005 | 4 | 1981 | BTB ext. trip | BOOL |  |  |  | X
AC alarm | 1004 | 9 | 301005 | 4 | 1983 | MB ext. trip | BOOL |  |  |  |  | X | X
AC alarm | 1004 | 10 | 301005 | 4 | 1650 | Ut< 1 monitoring active | BOOL | [5 empty] | X
AC alarm | 1004 | 11 | 301005 | 4 | 1660 | Ut< 1 | BOOL | [5 empty] | X
AC alarm | 1004 | 12 | 301005 | 4 | 1690 | Ut< 2 monitoring active | BOOL | [5 empty] | X
AC alarm | 1004 | 13 | 301005 | 4 | 1700 | Ut< 2 | BOOL | [5 empty] | X
AC alarm | 1004 | 14 | 301005 | 4 | 1760 | G P dep. Q< | BOOL | [5 empty] | X
AC alarm | 1004 | 15 | 301005 | 4 | 1790 | G P dep. Q> | BOOL | [5 empty] | X
Alarm | 1005 | 0 | 301006 | 4 | 2120 | Synchronising window | BOOL |  |  |  | X | X | X
Alarm | 1005 | 1 | 301006 | 4 | 2130 | Synchronising failure GB | BOOL | [5 empty] | X
Alarm | 1005 | 1 | 301006 | 4 | 2130 | Synchronising failure TB | BOOL |  |  |  |  | X
Alarm | 1005 | 1 | 301006 | 4 | 2130 | Synchronising failure BTB | BOOL |  |  |  | X
Alarm | 1005 | 2 | 301006 | 4 | 2140 | Synchronising failure MB | BOOL |  |  |  |  | X | X
AC alarm | 1005 | 3 | 301006 | 4 | 2150 | Phase seq. failure A | BOOL |  |  |  | X | X | X
Alarm | 1005 | 4 | 301006 | 4 | 2160 | GB open failure | BOOL | [5 empty] | X
Alarm | 1005 | 4 | 301006 | 4 | 2160 | TB open failure | BOOL |  |  |  |  | X
Alarm | 1005 | 4 | 301006 | 4 | 2160 | BTB open failure | BOOL |  |  |  | X
Alarm | 1005 | 5 | 301006 | 4 | 2170 | GB close failure | BOOL | [5 empty] | X
Alarm | 1005 | 5 | 301006 | 4 | 2170 | TB close failure | BOOL |  |  |  |  | X
Alarm | 1005 | 5 | 301006 | 4 | 2170 | BTB close failure | BOOL |  |  |  | X
Alarm | 1005 | 6 | 301006 | 4 | 2180 | GB pos. failure | BOOL | [5 empty] | X
Alarm | 1005 | 6 | 301006 | 4 | 2180 | TB pos. failure | BOOL |  |  |  |  | X
Alarm | 1005 | 6 | 301006 | 4 | 2180 | BTB pos. failure | BOOL |  |  |  | X
Alarm | 1005 | 7 | 301006 | 4 | 2200 | MB open failure | BOOL |  |  |  |  | X | X
Alarm | 1005 | 8 | 301006 | 4 | 2210 | MB close failure | BOOL |  |  |  |  | X | X
Alarm | 1005 | 9 | 301006 | 4 | 2220 | MB pos. failure | BOOL |  |  |  |  | X | X
Alarm | 1005 | 10 | 301006 | 4 | 2270 | Close before excitation failure | BOOL | [5 empty] | X
AC alarm | 1005 | 11 | 301006 | 4 | 2155 | Phase seq. failure B | BOOL |  |  |  | X | X | X
Alarm | 1006 | 0 | 301007 | 4 | 2560 | GOVERNOR regulation fail. | BOOL | [5 empty] | X
Alarm | 1006 | 1 | 301007 | 4 | 2630 | Deload error | BOOL | [5 empty] | X
Alarm | 1006 | 2 | 301007 | 4 | 2680 | AVR regulation fail. | BOOL | [5 empty] | X
Alarm | 1007 | 0 | 301008 | 4 | 3000 | Digital alarm input 39 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 1 | 301008 | 4 | 3010 | Digital alarm input 40 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 2 | 301008 | 4 | 3020 | Digital alarm input 41 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 3 | 301008 | 4 | 3030 | Digital alarm input 42 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 4 | 301008 | 4 | 3040 | Digital alarm input 43 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 5 | 301008 | 4 | 3050 | Digital alarm input 44 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 6 | 301008 | 4 | 3060 | Digital alarm input 45 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 7 | 301008 | 4 | 3070 | Digital alarm input 46 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 8 | 301008 | 4 | 3080 | Digital alarm input 47 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 9 | 301008 | 4 | 3090 | Digital alarm input 48 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 10 | 301008 | 4 | 3100 | Digital alarm input 49 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 11 | 301008 | 4 | 3110 | Digital alarm input 50 | BOOL |  |  |  | X | X | X
Alarm | 1010 | 12 | 301011 | 4 | 3490 | Digital alarm input 4 (Emergency stop) | BOOL |  |  |  | X | X | X
Alarm | 1011 | 7 | 301012 | 4 | 3570 | M-Logic alarm 1 | BOOL |  |  |  | X | X | X
Alarm | 1011 | 8 | 301012 | 4 | 3580 | M-Logic alarm 2 | BOOL |  |  |  | X | X | X
Alarm | 1011 | 9 | 301012 | 4 | 3590 | M-Logic alarm 3 | BOOL |  |  |  | X | X | X
Alarm | 1011 | 10 | 301012 | 4 | 3600 | M-Logic alarm 4 | BOOL |  |  |  | X | X | X
Alarm | 1011 | 11 | 301012 | 4 | 3610 | M-Logic alarm 5 | BOOL |  |  |  | X | X | X
Alarm | 1011 | 12 | 301012 | 4 | 3620 | M-Logic extended alarm 1 | BOOL |  |  |  | X | X | X
Alarm | 1011 | 13 | 301012 | 4 | 3630 | M-Logic extended alarm 2 | BOOL |  |  |  | X | X | X
Alarm | 1011 | 14 | 301012 | 4 | 3640 | M-Logic extended alarm 3 | BOOL |  |  |  | X | X | X
Alarm | 1011 | 15 | 301012 | 4 | 3650 | M-Logic extended alarm 4 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 0 | 301014 | 4 | 4120 | Multi input terminal 20.1 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 1 | 301014 | 4 | 4130 | Multi input terminal 20.2 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 2 | 301014 | 4 | 4140 | W. fail. 20 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 3 | 301014 | 4 | 4150 | Multi input terminal 21.1 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 4 | 301014 | 4 | 4160 | Multi input terminal 21.2 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 5 | 301014 | 4 | 4170 | W. fail. 21 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 6 | 301014 | 4 | 4180 | Multi input terminal 22.1 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 7 | 301014 | 4 | 4190 | Multi input terminal 22.2 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 8 | 301014 | 4 | 4200 | W. fail. 22 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 9 | 301014 | 4 | 4510 | Overspeed 1 | BOOL | [5 empty] | X
Alarm | 1013 | 10 | 301014 | 4 | 4520 | Overspeed 2 | BOOL | [5 empty] | X
Alarm | 1013 | 11 | 301014 | 4 | 4530 | Crank failure | BOOL | [5 empty] | X
Alarm | 1013 | 12 | 301014 | 4 | 4540 | Running feedback failure | BOOL | [5 empty] | X
Alarm | 1013 | 13 | 301014 | 4 | 4550 | MPU wire failure | BOOL | [5 empty] | X
Alarm | 1013 | 14 | 301014 | 4 | 4560 | Hz/V failure | BOOL | [5 empty] | X
Alarm | 1013 | 15 | 301014 | 4 | 4570 | Start failure | BOOL | [5 empty] | X
Alarm | 1014 | 0 | 301015 | 4 | 4580 | Stop failure | BOOL | [5 empty] | X
Alarm | 1014 | 1 | 301015 | 4 | 4960 | U< aux. term. 1 | BOOL |  |  |  | X | X | X
Alarm | 1014 | 2 | 301015 | 4 | 4970 | U> aux. term. 1 | BOOL |  |  |  | X | X | X
Alarm | 1014 | 5 | 301015 | 4 | 4590 | Underspeed 1 | BOOL | [5 empty] | X
Alarm | 1014 | 6 | 301015 | 4 | 4210 | Multi input terminal 23.1 | BOOL |  |  |  | X | X | X
Alarm | 1014 | 7 | 301015 | 4 | 4220 | Multi input terminal 23.2 | BOOL |  |  |  | X | X | X
Alarm | 1014 | 8 | 301015 | 4 | 4230 | W. fail. 23 | BOOL |  |  |  | X | X | X
Alarm | 1015 | 0 | 301016 | 4 | 6110 | Service timer 1 | BOOL | [5 empty] | X
Alarm | 1015 | 1 | 301016 | 4 | 6120 | Service timer 2 | BOOL | [5 empty] | X
Alarm | 1015 | 2 | 301016 | 4 | 6270 | Stop coil wire break | BOOL | [5 empty] | X
Alarm | 1015 | 4 | 301016 | 4 | 6330 | Engine heater 1 | BOOL | [5 empty] | X
Alarm | 1015 | 5 | 301016 | 4 | 6410 | Battery test | BOOL | [5 empty] | X
Alarm | 1015 | 6 | 301016 | 4 | 6440 | Battery asymmetry 1 | BOOL | [5 empty] | X
Alarm | 1015 | 7 | 301016 | 4 | 6450 | Battery asymmetry 2 | BOOL | [5 empty] | X
Alarm | 1015 | 8 | 301016 | 4 | 6470 | Max. ventilation 1 | BOOL | [5 empty] | X
Alarm | 1015 | 9 | 301016 | 4 | 6480 | Max. ventilation 2 | BOOL | [5 empty] | X
Alarm | 1015 | 10 | 301016 | 4 | 6500 | Blk. swbd. error | BOOL | [5 empty] | X
Alarm | 1015 | 11 | 301016 | 4 | 6510 | Stp. swbd. error | BOOL | [5 empty] | X
Alarm | 1015 | 12 | 301016 | 4 | 6540 | Unit not in auto | BOOL |  |  |  | X | X | X
Alarm | 1015 | 13 | 301016 | 4 | 6550 | Fuel pump logic | BOOL | [5 empty] | X
Relay state | 1016 | 0 | 301017 | 4 | 5000 | Relay 5 | BOOL |  |  |  | X | X | X
Relay state | 1016 | 1 | 301017 | 4 | 5000 | Relay 6 | BOOL |  |  |  | X | X | X
Relay state | 1016 | 2 | 301017 | 4 | 5000 | Relay 9 | BOOL |  |  |  | X | X | X
Relay state | 1016 | 3 | 301017 | 4 | 5000 | Relay 10 | BOOL |  |  |  | X | X | X
Relay state | 1016 | 4 | 301017 | 4 | 5000 | Relay 11 | BOOL |  |  |  | X | X | X
Relay state | 1016 | 5 | 301017 | 4 | 5000 | Relay 12 | BOOL |  |  |  | X | X | X
Relay state | 1016 | 6 | 301017 | 4 | 5000 | Relay 13 | BOOL |  |  |  | X | X | X
Relay state | 1016 | 7 | 301017 | 4 | 5000 | Relay 14 | BOOL |  |  |  | X | X | X
Relay state | 1016 | 8 | 301017 | 4 | 5080 | Relay 15 | BOOL |  |  |  | X | X | X
Relay state | 1016 | 9 | 301017 | 4 | 8090 | Relay 16 | BOOL |  |  |  | X | X | X
Relay state | 1016 | 10 | 301017 | 4 | 5100 | Relay 17 | BOOL |  |  |  | X | X | X
Relay state | 1016 | 11 | 301017 | 4 | 5110 | Relay 18 | BOOL |  |  |  | X | X | X
Relay state | 1017 | 12 | 301018 | 4 |  | Run. coil relay | BOOL | [5 empty] | X
Relay state | 1017 | 13 | 301018 | 4 |  | Start prepare | BOOL | [5 empty] | X
Relay state | 1017 | 14 | 301018 | 4 |  | Start relay | BOOL | [5 empty] | X
Relay state | 1017 | 15 | 301018 | 4 |  | Stop coil relay | BOOL | [5 empty] | X
Plant logic state | 1018 | 0 | 301019 | 4 |  | Mains failure (Single DG) | BOOL | [5 empty] | X
Plant logic state | 1018 | 0 | 301019 | 4 |  | Mains failure | BOOL |  |  |  |  | X
Plant logic state | 1018 | 1 | 301019 | 4 |  | MB position ON (Single DG) | BOOL | [5 empty] | X
Plant logic state | 1018 | 1 | 301019 | 4 |  | MB position ON | BOOL |  |  |  |  | X
Plant logic state | 1018 | 2 | 301019 | 4 |  | DG ramp down | BOOL | [5 empty] | X
Plant logic state | 1018 | 3 | 301019 | 4 |  | Start GOV/AVR regulation | BOOL | [5 empty] | X
Plant logic state | 1018 | 4 | 301019 | 4 |  | GB position ON | BOOL | [5 empty] | X
Plant logic state | 1018 | 4 | 301019 | 4 |  | TB position ON | BOOL |  |  |  |  | X
Plant logic state | 1018 | 4 | 301019 | 4 |  | BTB position ON | BOOL |  |  |  | X
Plant logic state | 1018 | 5 | 301019 | 4 |  | GB synchronising | BOOL | [5 empty] | X
Plant logic state | 1018 | 5 | 301019 | 4 |  | TB synchronising | BOOL |  |  |  |  | X
Plant logic state | 1018 | 5 | 301019 | 4 |  | BTB synchronising | BOOL |  |  |  | X
Plant logic state | 1018 | 6 | 301019 | 4 |  | Engine running | BOOL | [5 empty] | X
Plant logic state | 1018 | 7 | 301019 | 4 | 6173 | Running detected, timer expired | BOOL | [5 empty] | X
Plant logic state | 1018 | 8 | 301019 | 4 | 6220 | DG Hz/V OK, timer expired | BOOL | [5 empty] | X
Plant logic state | 1018 | 8 | 301019 | 4 | 6220 | BB Hz/V OK, timer expired | BOOL |  |  |  | X | X
Plant logic state | 1018 | 9 | 301019 | 4 | 6410 | Battery test ongoing | BOOL | [5 empty] | X
Plant logic state | 1018 | 10 | 301019 | 4 |  | Shutdown override active | BOOL | [5 empty] | X
Plant logic state | 1018 | 11 | 301019 | 4 |  | GB position OFF | BOOL | [5 empty] | X
Plant logic state | 1018 | 11 | 301019 | 4 |  | TB position OFF | BOOL |  |  |  |  | X
Plant logic state | 1018 | 11 | 301019 | 4 |  | BTB position OFF | BOOL |  |  |  | X
Plant logic state | 1018 | 12 | 301019 | 4 |  | MB position OFF | BOOL |  |  |  |  | X | X
Plant logic state | 1018 | 13 | 301019 | 4 |  | BB Hz/V OK | BOOL |  |  |  | X | X | X
Plant logic state | 1018 | 14 | 301019 | 4 |  | Single DG, MB synchronising | BOOL | [5 empty] | X
Modes | 1018 | 15 | 301019 | 4 |  | Dry mode | BOOL | [5 empty] | X
Modes | 1019 | 0 | 301020 | 4 |  | Block mode | BOOL |  |  |  | X | X | X
Modes | 1019 | 1 | 301020 | 4 |  | Manual mode | BOOL | [5 empty] | X
Modes | 1019 | 2 | 301020 | 4 |  | Semi auto mode | BOOL |  |  |  | X | X | X
Modes | 1019 | 3 | 301020 | 4 |  | Auto mode | BOOL |  |  |  | X | X | X
Modes | 1019 | 4 | 301020 | 4 |  | Test | BOOL |  |  |  |  | X | X
Modes | 1019 | 5 | 301020 | 4 |  | Island | BOOL |  |  |  |  | X | X
Modes | 1019 | 6 | 301020 | 4 |  | AMF | BOOL |  |  |  |  | X | X
Modes | 1019 | 7 | 301020 | 4 |  | Peak shaving | BOOL |  |  |  |  | X | X
Modes | 1019 | 8 | 301020 | 4 |  | Fixed power | BOOL |  |  |  |  | X | X
Modes | 1019 | 9 | 301020 | 4 |  | Mains power export | BOOL |  |  |  |  | X | X
Modes | 1019 | 10 | 301020 | 4 |  | Load takeover | BOOL |  |  |  |  | X | X
Modes | 1019 | 11 | 301020 | 4 |  | Power management | BOOL | [5 empty] | X
Modes | 1019 | 15 | 301020 | 4 |  | AMF active | BOOL |  |  |  |  | X | X
EIC alarm | 1020 | 0 | 301021 | 4 | 7570 | Communication Error | BOOL | [5 empty] | X
EIC alarm | 1020 | 1 | 301021 | 4 | 7580 | Warning / Yellow alarm | BOOL | [5 empty] | X
EIC alarm | 1020 | 2 | 301021 | 4 | 7590 | Shutdown / Red alarm | BOOL | [5 empty] | X
EIC alarm | 1020 | 3 | 301021 | 4 | 7600 | Over-speed | BOOL | [5 empty] | X
EIC alarm | 1020 | 4 | 301021 | 4 | 7610 | Coolant water temperature 1 | BOOL | [5 empty] | X
EIC alarm | 1020 | 5 | 301021 | 4 | 7620 | Coolant water temperature 2 | BOOL | [5 empty] | X
EIC alarm | 1020 | 6 | 301021 | 4 | 7630 | Oil pressure 1 | BOOL | [5 empty] | X
EIC alarm | 1020 | 7 | 301021 | 4 | 7640 | Oil pressure 2 | BOOL | [5 empty] | X
EIC alarm | 1020 | 8 | 301021 | 4 | 7650 | Oil temperature 1 | BOOL | [5 empty] | X
EIC alarm | 1020 | 9 | 301021 | 4 | 7660 | Oil temperature 2 | BOOL | [5 empty] | X
EIC alarm | 1020 | 10 | 301021 | 4 | 7670 | Coolant water level 1 | BOOL | [5 empty] | X
EIC alarm | 1020 | 11 | 301021 | 4 | 7680 | Coolant water level 2 | BOOL | [5 empty] | X
EIC alarm | 1020 | 12 | 301021 | 4 | 7690 | Cylinder exhaust difference 1 | BOOL | [5 empty] | X
EIC alarm | 1020 | 13 | 301021 | 4 | 7700 | Cylinder exhaust difference 2 | BOOL | [5 empty] | X
EIC alarm | 1021 | 0 | 301022 | 4 |  | ECU alarm bit 49 | BOOL | [5 empty] | X
EIC alarm | 1021 | 1 | 301022 | 4 |  | ECU alarm bit 50 | BOOL | [5 empty] | X
EIC alarm | 1021 | 12 | 301022 | 4 |  | Protection lamp | BOOL | [5 empty] | X
EIC alarm | 1021 | 13 | 301022 | 4 |  | Malfunction lamp | BOOL | [5 empty] | X
EIC alarm | 1021 | 14 | 301022 | 4 |  | Yellow lamp | BOOL | [5 empty] | X
EIC alarm | 1021 | 15 | 301022 | 4 |  | Red lamp | BOOL | [5 empty] | X
EIC alarm | 1022 | 0 | 301023 | 4 |  | ECU alarm bit 33 | BOOL | [5 empty] | X
EIC alarm | 1022 | 1 | 301023 | 4 |  | ECU alarm bit 34 | BOOL | [5 empty] | X
EIC alarm | 1022 | 2 | 301023 | 4 |  | ECU alarm bit 35 | BOOL | [5 empty] | X
EIC alarm | 1022 | 3 | 301023 | 4 |  | ECU alarm bit 36 | BOOL | [5 empty] | X
EIC alarm | 1022 | 4 | 301023 | 4 |  | ECU alarm bit 37 | BOOL | [5 empty] | X
EIC alarm | 1022 | 5 | 301023 | 4 |  | ECU alarm bit 38 | BOOL | [5 empty] | X
EIC alarm | 1022 | 6 | 301023 | 4 |  | ECU alarm bit 39 | BOOL | [5 empty] | X
EIC alarm | 1022 | 7 | 301023 | 4 |  | ECU alarm bit 40 | BOOL | [5 empty] | X
EIC alarm | 1022 | 8 | 301023 | 4 |  | ECU alarm bit 41 | BOOL | [5 empty] | X
EIC alarm | 1022 | 9 | 301023 | 4 |  | ECU alarm bit 42 | BOOL | [5 empty] | X
EIC alarm | 1022 | 10 | 301023 | 4 |  | ECU alarm bit 43 | BOOL | [5 empty] | X
EIC alarm | 1022 | 11 | 301023 | 4 |  | ECU alarm bit 44 | BOOL | [5 empty] | X
EIC alarm | 1022 | 12 | 301023 | 4 |  | ECU alarm bit 45 | BOOL | [5 empty] | X
EIC alarm | 1022 | 13 | 301023 | 4 |  | ECU alarm bit 46 | BOOL | [5 empty] | X
EIC alarm | 1022 | 14 | 301023 | 4 |  | ECU alarm bit 47 | BOOL | [5 empty] | X
EIC alarm | 1022 | 15 | 301023 | 4 |  | ECU alarm bit 48 | BOOL | [5 empty] | X
EIC alarm | 1023 | 0 | 301024 | 4 |  | ECU alarm bit 17 | BOOL | [5 empty] | X
EIC alarm | 1023 | 1 | 301024 | 4 |  | ECU alarm bit 18 | BOOL | [5 empty] | X
EIC alarm | 1023 | 2 | 301024 | 4 |  | ECU alarm bit 19 | BOOL | [5 empty] | X
EIC alarm | 1023 | 3 | 301024 | 4 |  | ECU alarm bit 20 | BOOL | [5 empty] | X
EIC alarm | 1023 | 4 | 301024 | 4 |  | ECU alarm bit 21 | BOOL | [5 empty] | X
EIC alarm | 1023 | 5 | 301024 | 4 |  | ECU alarm bit 22 | BOOL | [5 empty] | X
EIC alarm | 1023 | 6 | 301024 | 4 |  | ECU alarm bit 23 | BOOL | [5 empty] | X
EIC alarm | 1023 | 7 | 301024 | 4 |  | ECU alarm bit 24 | BOOL | [5 empty] | X
EIC alarm | 1023 | 8 | 301024 | 4 |  | ECU alarm bit 25 | BOOL | [5 empty] | X
EIC alarm | 1023 | 9 | 301024 | 4 |  | ECU alarm bit 26 | BOOL | [5 empty] | X
EIC alarm | 1023 | 10 | 301024 | 4 |  | ECU alarm bit 27 | BOOL | [5 empty] | X
EIC alarm | 1023 | 11 | 301024 | 4 |  | ECU alarm bit 28 | BOOL | [5 empty] | X
EIC alarm | 1023 | 12 | 301024 | 4 |  | ECU alarm bit 29 | BOOL | [5 empty] | X
EIC alarm | 1023 | 13 | 301024 | 4 |  | ECU alarm bit 30 | BOOL | [5 empty] | X
EIC alarm | 1023 | 14 | 301024 | 4 |  | ECU alarm bit 31 | BOOL | [5 empty] | X
EIC alarm | 1023 | 15 | 301024 | 4 |  | ECU alarm bit 32 | BOOL | [5 empty] | X
EIC alarm | 1024 | 0 | 301025 | 4 |  | ECU alarm bit 1 | BOOL | [5 empty] | X
EIC alarm | 1024 | 1 | 301025 | 4 |  | ECU alarm bit 2 | BOOL | [5 empty] | X
EIC alarm | 1024 | 2 | 301025 | 4 |  | ECU alarm bit 3 | BOOL | [5 empty] | X
EIC alarm | 1024 | 3 | 301025 | 4 |  | ECU alarm bit 4 | BOOL | [5 empty] | X
EIC alarm | 1024 | 4 | 301025 | 4 |  | ECU alarm bit 5 | BOOL | [5 empty] | X
EIC alarm | 1024 | 5 | 301025 | 4 |  | ECU alarm bit 6 | BOOL | [5 empty] | X
EIC alarm | 1024 | 6 | 301025 | 4 |  | ECU alarm bit 7 | BOOL | [5 empty] | X
EIC alarm | 1024 | 7 | 301025 | 4 |  | ECU alarm bit 8 | BOOL | [5 empty] | X
EIC alarm | 1024 | 8 | 301025 | 4 |  | ECU alarm bit 9 | BOOL | [5 empty] | X
EIC alarm | 1024 | 9 | 301025 | 4 |  | ECU alarm bit 10 | BOOL | [5 empty] | X
EIC alarm | 1024 | 10 | 301025 | 4 |  | ECU alarm bit 11 | BOOL | [5 empty] | X
EIC alarm | 1024 | 11 | 301025 | 4 |  | ECU alarm bit 12 | BOOL | [5 empty] | X
EIC alarm | 1024 | 12 | 301025 | 4 |  | ECU alarm bit 13 | BOOL | [5 empty] | X
EIC alarm | 1024 | 13 | 301025 | 4 |  | ECU alarm bit 14 | BOOL | [5 empty] | X
EIC alarm | 1024 | 14 | 301025 | 4 |  | ECU alarm bit 15 | BOOL | [5 empty] | X
EIC alarm | 1024 | 15 | 301025 | 4 |  | ECU alarm bit 16 | BOOL | [5 empty] | X
EIC alarm | 1026 | 0 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Overreving | BOOL | [5 empty] | X
EIC alarm | 1026 | 1 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Speed sensor 1 | BOOL | [5 empty] | X
EIC alarm | 1026 | 2 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Speed sensor 2 | BOOL | [5 empty] | X
EIC alarm | 1026 | 3 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Water temperature sensor | BOOL | [5 empty] | X
EIC alarm | 1026 | 4 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Charge air temperature sensor | BOOL | [5 empty] | X
EIC alarm | 1026 | 5 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Charge air pressure sensor | BOOL | [5 empty] | X
EIC alarm | 1026 | 6 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Oil temperature sensor | BOOL | [5 empty] | X
EIC alarm | 1026 | 7 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Oil pressure sensor | BOOL | [5 empty] | X
EIC alarm | 1026 | 8 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Fault in cor. | BOOL | [5 empty] | X
EIC alarm | 1026 | 9 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Throttle pedal | BOOL | [5 empty] | X
EIC alarm | 1026 | 10 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Emergency stop o.r | BOOL | [5 empty] | X
EIC alarm | 1026 | 11 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Oil pressure protection | BOOL | [5 empty] | X
EIC alarm | 1026 | 12 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Wrong parameter | BOOL | [5 empty] | X
EIC alarm | 1026 | 13 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Battery voltage | BOOL | [5 empty] | X
EIC alarm | 1026 | 14 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Oil pressure protection | BOOL | [5 empty] | X
EIC alarm | 1026 | 15 | 301027 | 4 |  | Scania EMS 2 KWP2000 - Emergency stop cor | BOOL | [5 empty] | X
EIC alarm | 1027 | 0 | 301028 | 4 |  | Scania EMS 2 KWP2000 - CAN-circuit defect | BOOL | [5 empty] | X
EIC alarm | 1027 | 1 | 301028 | 4 |  | Scania EMS 2 KWP2000 - CAN message DLN1 | BOOL | [5 empty] | X
EIC alarm | 1027 | 2 | 301028 | 4 |  | Scania EMS 2 KWP2000 - Wrong CAN version | BOOL | [5 empty] | X
EIC alarm | 1027 | 3 | 301028 | 4 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 1 | BOOL | [5 empty] | X
EIC alarm | 1027 | 4 | 301028 | 4 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 2 | BOOL | [5 empty] | X
EIC alarm | 1027 | 5 | 301028 | 4 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 3 | BOOL | [5 empty] | X
EIC alarm | 1027 | 6 | 301028 | 4 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 4 | BOOL | [5 empty] | X
EIC alarm | 1027 | 7 | 301028 | 4 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 5 | BOOL | [5 empty] | X
EIC alarm | 1027 | 8 | 301028 | 4 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 6 | BOOL | [5 empty] | X
EIC alarm | 1027 | 9 | 301028 | 4 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 7 | BOOL | [5 empty] | X
EIC alarm | 1027 | 10 | 301028 | 4 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 8 | BOOL | [5 empty] | X
EIC alarm | 1027 | 11 | 301028 | 4 |  | Scania EMS 2 KWP2000 - Extra analogue input | BOOL | [5 empty] | X
EIC alarm | 1027 | 12 | 301028 | 4 |  | Scania EMS 2 KWP2000 - System shutdown | BOOL | [5 empty] | X
EIC alarm | 1027 | 13 | 301028 | 4 |  | Scania EMS 2 KWP2000 - Coolant l. protection | BOOL | [5 empty] | X
EIC alarm | 1027 | 14 | 301028 | 4 |  | Scania EMS 2 KWP2000 - hardware watchdog | BOOL | [5 empty] | X
EIC alarm | 1027 | 15 | 301028 | 4 |  | Scania EMS 2 KWP2000 - Fault in RAM | BOOL | [5 empty] | X
EIC alarm | 1028 | 0 | 301029 | 4 |  | Scania EMS 2 KWP2000 - Seal | BOOL | [5 empty] | X
EIC alarm | 1028 | 1 | 301029 | 4 |  | Scania EMS 2 KWP2000 - Coolant shut off | BOOL | [5 empty] | X
EIC alarm | 1028 | 2 | 301029 | 4 |  | Scania EMS 2 KWP2000 - Over heat protection | BOOL | [5 empty] | X
EIC alarm | 1028 | 3 | 301029 | 4 |  | Scania EMS 2 KWP2000 - Fault in TPU | BOOL | [5 empty] | X
PM alarm | 1031 | 1 | 301032 | 4 |  | CAN 1 missing ID 1 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 2 | 301032 | 4 |  | CAN 1 missing ID 2 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 3 | 301032 | 4 |  | CAN 1 missing ID 3 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 4 | 301032 | 4 |  | CAN 1 missing ID 4 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 5 | 301032 | 4 |  | CAN 1 missing ID 5 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 6 | 301032 | 4 |  | CAN 1 missing ID 6 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 7 | 301032 | 4 |  | CAN 1 missing ID 7 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 8 | 301032 | 4 |  | CAN 1 missing ID 8 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 9 | 301032 | 4 |  | CAN 1 missing ID 9 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 10 | 301032 | 4 |  | CAN 1 missing ID 10 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 11 | 301032 | 4 |  | CAN 1 missing ID 11 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 12 | 301032 | 4 |  | CAN 1 missing ID 12 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 13 | 301032 | 4 |  | CAN 1 missing ID 13 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 14 | 301032 | 4 |  | CAN 1 missing ID 14 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 15 | 301032 | 4 |  | CAN 1 missing ID 15 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 0 | 301033 | 4 |  | CAN 1 missing ID 16 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 2 | 301033 | 4 |  | CAN 2 missing ID 1 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 3 | 301033 | 4 |  | CAN 2 missing ID 2 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 4 | 301033 | 4 |  | CAN 2 missing ID 3 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 5 | 301033 | 4 |  | CAN 2 missing ID 4 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 6 | 301033 | 4 |  | CAN 2 missing ID 5 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 7 | 301033 | 4 |  | CAN 2 missing ID 6 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 8 | 301033 | 4 |  | CAN 2 missing ID 7 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 9 | 301033 | 4 |  | CAN 2 missing ID 8 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 10 | 301033 | 4 |  | CAN 2 missing ID 9 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 11 | 301033 | 4 |  | CAN 2 missing ID 10 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 12 | 301033 | 4 |  | CAN 2 missing ID 11 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 13 | 301033 | 4 |  | CAN 2 missing ID 12 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 14 | 301033 | 4 |  | CAN 2 missing ID 13 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 15 | 301033 | 4 |  | CAN 2 missing ID 14 | BOOL |  |  |  | X | X | X
PM alarm | 1033 | 0 | 301034 | 4 |  | CAN 2 missing ID 16 | BOOL |  |  |  | X | X | X
PM alarm | 1033 | 1 | 301034 | 4 |  | CAN 2 missing ID 15 | BOOL |  |  |  | X | X | X
Alarm | 1033 | 2 | 301034 | 4 | 7520 | Communication error ext. | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 1 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 1 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 2 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 2 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 3 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 3 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 4 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 4 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 5 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 5 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 6 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 6 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 7 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 7 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 8 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 8 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 9 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 9 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 10 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 10 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 11 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 11 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 12 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 12 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 13 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 13 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 14 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 14 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 15 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 15 | BOOL |  |  |  | X | X | X
PM alarm | 1035 | 0 | 301036 | 4 |  | Ext. Modbus comm. error, CAN ID 16 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 0 | 301037 | 4 | 12000 | Ext. Analogue in. 1.1 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 1 | 301037 | 4 | 12010 | Ext. Analogue in. 1.2 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 3 | 301037 | 4 | 12030 | Ext. Analogue in. 2.1 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 4 | 301037 | 4 | 12040 | Ext. Analogue in. 2.2 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 6 | 301037 | 4 | 12060 | Ext. Analogue in. 3.1 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 7 | 301037 | 4 | 12070 | Ext. Analogue in. 3.2 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 9 | 301037 | 4 | 12090 | Ext. Analogue in. 4.1 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 10 | 301037 | 4 | 12100 | Ext. Analogue in. 4.2 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 12 | 301037 | 4 | 12120 | Ext. Analogue in. 5.1 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 13 | 301037 | 4 | 12130 | Ext. Analogue in. 5.2 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 15 | 301037 | 4 | 12150 | Ext. Analogue in. 6.1 | BOOL |  |  |  | X | X | X
Alarm | 1037 | 0 | 301038 | 4 | 12160 | Ext. Analogue in. 6.2 | BOOL |  |  |  | X | X | X
Alarm | 1037 | 2 | 301038 | 4 | 12180 | Ext. Analogue in. 7.1 | BOOL |  |  |  | X | X | X
Alarm | 1037 | 3 | 301038 | 4 | 12190 | Ext. Analogue in. 7.2 | BOOL |  |  |  | X | X | X
Alarm | 1037 | 5 | 301038 | 4 | 12210 | Ext. Analogue in. 8.1 | BOOL |  |  |  | X | X | X
Alarm | 1037 | 6 | 301038 | 4 | 12220 | Ext. Analogue in. 8.2 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 0 | 301039 | 4 | 12540 | External digital input 1 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 1 | 301039 | 4 | 12550 | External digital input 2 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 2 | 301039 | 4 | 12560 | External digital input 3 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 3 | 301039 | 4 | 12570 | External digital input 4 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 4 | 301039 | 4 | 12580 | External digital input 5 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 5 | 301039 | 4 | 12590 | External digital input 6 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 6 | 301039 | 4 | 12600 | External digital input 7 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 7 | 301039 | 4 | 12610 | External digital input 8 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 8 | 301039 | 4 | 12620 | External digital input 9 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 9 | 301039 | 4 | 12630 | External digital input 10 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 10 | 301039 | 4 | 12640 | External digital input 11 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 11 | 301039 | 4 | 12650 | External digital input 12 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 12 | 301039 | 4 | 12660 | External digital input 13 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 13 | 301039 | 4 | 12670 | External digital input 14 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 14 | 301039 | 4 | 12680 | External digital input 15 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 15 | 301039 | 4 | 12690 | External digital input 16 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 0 | 301040 | 4 | 12790 | External digital output 1 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 1 | 301040 | 4 | 12800 | External digital output 2 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 2 | 301040 | 4 | 12810 | External digital output 3 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 3 | 301040 | 4 | 12820 | External digital output 4 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 4 | 301040 | 4 | 12830 | External digital output 5 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 5 | 301040 | 4 | 12840 | External digital output 6 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 6 | 301040 | 4 | 12850 | External digital output 7 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 7 | 301040 | 4 | 12860 | External digital output 8 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 8 | 301040 | 4 | 12870 | External digital output 9 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 9 | 301040 | 4 | 12880 | External digital output 10 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 10 | 301040 | 4 | 12890 | External digital output 11 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 11 | 301040 | 4 | 12900 | External digital output 12 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 12 | 301040 | 4 | 12910 | External digital output 13 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 13 | 301040 | 4 | 12920 | External digital output 14 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 14 | 301040 | 4 | 12930 | External digital output 15 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 15 | 301040 | 4 | 12940 | External digital output 16 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 0 | 301041 | 4 |  | CAN 1 missing ID 1 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 1 | 301041 | 4 |  | CAN 1 missing ID 2 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 2 | 301041 | 4 |  | CAN 1 missing ID 3 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 3 | 301041 | 4 |  | CAN 1 missing ID 4 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 4 | 301041 | 4 |  | CAN 1 missing ID 5 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 5 | 301041 | 4 |  | CAN 1 missing ID 6 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 6 | 301041 | 4 |  | CAN 1 missing ID 7 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 7 | 301041 | 4 |  | CAN 1 missing ID 8 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 8 | 301041 | 4 |  | CAN 1 missing ID 9 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 9 | 301041 | 4 |  | CAN 1 missing ID 10 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 10 | 301041 | 4 |  | CAN 1 missing ID 11 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 11 | 301041 | 4 |  | CAN 1 missing ID 12 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 12 | 301041 | 4 |  | CAN 1 missing ID 13 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 13 | 301041 | 4 |  | CAN 1 missing ID 14 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 14 | 301041 | 4 |  | CAN 1 missing ID 15 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 15 | 301041 | 4 |  | CAN 1 missing ID 16 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 0 | 301042 | 4 |  | CAN 1 missing ID 17 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 1 | 301042 | 4 |  | CAN 1 missing ID 18 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 2 | 301042 | 4 |  | CAN 1 missing ID 19 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 3 | 301042 | 4 |  | CAN 1 missing ID 20 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 4 | 301042 | 4 |  | CAN 1 missing ID 21 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 5 | 301042 | 4 |  | CAN 1 missing ID 22 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 6 | 301042 | 4 |  | CAN 1 missing ID 23 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 7 | 301042 | 4 |  | CAN 1 missing ID 24 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 8 | 301042 | 4 |  | CAN 1 missing ID 25 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 9 | 301042 | 4 |  | CAN 1 missing ID 26 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 10 | 301042 | 4 |  | CAN 1 missing ID 27 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 11 | 301042 | 4 |  | CAN 1 missing ID 28 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 12 | 301042 | 4 |  | CAN 1 missing ID 29 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 13 | 301042 | 4 |  | CAN 1 missing ID 30 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 14 | 301042 | 4 |  | CAN 1 missing ID 31 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 15 | 301042 | 4 |  | CAN 1 missing ID 32 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 0 | 301043 | 4 |  | CAN 1 missing ID 33 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 1 | 301043 | 4 |  | CAN 1 missing ID 34 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 2 | 301043 | 4 |  | CAN 1 missing ID 35 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 3 | 301043 | 4 |  | CAN 1 missing ID 36 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 4 | 301043 | 4 |  | CAN 1 missing ID 37 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 5 | 301043 | 4 |  | CAN 1 missing ID 38 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 6 | 301043 | 4 |  | CAN 1 missing ID 39 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 7 | 301043 | 4 |  | CAN 1 missing ID 40 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 0 | 301044 | 4 |  | CAN 2 missing ID 1 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 1 | 301044 | 4 |  | CAN 2 missing ID 2 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 2 | 301044 | 4 |  | CAN 2 missing ID 3 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 3 | 301044 | 4 |  | CAN 2 missing ID 4 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 4 | 301044 | 4 |  | CAN 2 missing ID 5 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 5 | 301044 | 4 |  | CAN 2 missing ID 6 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 6 | 301044 | 4 |  | CAN 2 missing ID 7 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 7 | 301044 | 4 |  | CAN 2 missing ID 8 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 8 | 301044 | 4 |  | CAN 2 missing ID 9 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 9 | 301044 | 4 |  | CAN 2 missing ID 10 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 10 | 301044 | 4 |  | CAN 2 missing ID 11 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 11 | 301044 | 4 |  | CAN 2 missing ID 12 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 12 | 301044 | 4 |  | CAN 2 missing ID 13 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 13 | 301044 | 4 |  | CAN 2 missing ID 14 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 14 | 301044 | 4 |  | CAN 2 missing ID 15 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 15 | 301044 | 4 |  | CAN 2 missing ID 16 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 0 | 301045 | 4 |  | CAN 2 missing ID 17 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 1 | 301045 | 4 |  | CAN 2 missing ID 18 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 2 | 301045 | 4 |  | CAN 2 missing ID 19 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 3 | 301045 | 4 |  | CAN 2 missing ID 20 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 4 | 301045 | 4 |  | CAN 2 missing ID 21 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 5 | 301045 | 4 |  | CAN 2 missing ID 22 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 6 | 301045 | 4 |  | CAN 2 missing ID 23 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 7 | 301045 | 4 |  | CAN 2 missing ID 24 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 8 | 301045 | 4 |  | CAN 2 missing ID 25 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 9 | 301045 | 4 |  | CAN 2 missing ID 26 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 10 | 301045 | 4 |  | CAN 2 missing ID 27 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 11 | 301045 | 4 |  | CAN 2 missing ID 28 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 12 | 301045 | 4 |  | CAN 2 missing ID 29 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 13 | 301045 | 4 |  | CAN 2 missing ID 30 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 14 | 301045 | 4 |  | CAN 2 missing ID 31 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 15 | 301045 | 4 |  | CAN 2 missing ID 32 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 0 | 301046 | 4 |  | CAN 2 missing ID 33 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 1 | 301046 | 4 |  | CAN 2 missing ID 34 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 2 | 301046 | 4 |  | CAN 2 missing ID 35 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 3 | 301046 | 4 |  | CAN 2 missing ID 36 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 4 | 301046 | 4 |  | CAN 2 missing ID 37 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 5 | 301046 | 4 |  | CAN 2 missing ID 38 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 6 | 301046 | 4 |  | CAN 2 missing ID 39 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 7 | 301046 | 4 |  | CAN 2 missing ID 40 | BOOL |  |  |  | X | X | X
Plant logic state | 1050 | 0 | 301051 | 4 |  | Ready to autostart | BOOL | [5 empty] | X
Plant logic state | 1050 | 1 | 301051 | 4 |  | DG U > 30% of U nominal | BOOL | [5 empty] | X
Plant logic state | 1050 | 1 | 301051 | 4 |  | Mains U > 30% of U nominal | BOOL |  |  |  |  | X
Plant logic state | 1050 | 1 | 301051 | 4 |  | BA U > 30% of U nominal | BOOL |  |  |  | X
Plant logic state | 1050 | 2 | 301051 | 4 |  | BB U > 30% of U nominal | BOOL |  |  |  | X | X | X
Plant logic state | 1050 | 3 | 301051 | 4 |  | Power derate state/active | BOOL |  |  |  | X | X | X
Plant logic state | 1050 | 14 | 301051 | 4 |  | This unit using analogue LS instead of PMS | BOOL | [5 empty] | X
Plant logic state | 1050 | 15 | 301051 | 4 |  | Any unit using analogue LS instead of PMS | BOOL | [5 empty] | X
M-Logic state | 1051 |  | 301052 | 4 |  | Virtual events 1-16 | INT16s | AB | 0 |  | X | X | X
M-Logic state | 1052 |  | 301053 | 4 |  | Virtual events 17-32 | INT16s | AB | 0 |  | X | X | X
Alarm | 1053 | 0 | 301054 | 4 | 6590 | Fan A Failure | BOOL | [5 empty] | X
Alarm | 1053 | 1 | 301054 | 4 | 6600 | Fan B Failure | BOOL | [5 empty] | X
Alarm | 1053 | 2 | 301054 | 4 | 6610 | Fan C Failure | BOOL | [5 empty] | X
Alarm | 1053 | 3 | 301054 | 4 | 6620 | Fan D Failure | BOOL | [5 empty] | X
Alarm | 1053 | 4 | 301054 | 4 | 4610 | Delta analogue 1 - fail 1 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 5 | 301054 | 4 | 4620 | Delta analogue 1 - fail 2 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 6 | 301054 | 4 | 4630 | Delta analogue 2 - fail 1 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 7 | 301054 | 4 | 4640 | Delta analogue 2 - fail 2 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 8 | 301054 | 4 | 4650 | Delta analogue 3 - fail 1 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 9 | 301054 | 4 | 4660 | Delta analogue 3 - fail 2 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 10 | 301054 | 4 | 4680 | Delta analogue 4 - fail 1 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 11 | 301054 | 4 | 4690 | Delta analogue 4 - fail 2 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 12 | 301054 | 4 | 4700 | Delta analogue 5 - fail 1 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 13 | 301054 | 4 | 4710 | Delta analogue 5 - fail 2 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 14 | 301054 | 4 | 4720 | Delta analogue 6 - fail 1 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 15 | 301054 | 4 | 4730 | Delta analogue 6 - fail 2 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 0 | 301055 | 4 |  | In> inverse | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 1 | 301055 | 4 |  | Ie> inverse | BOOL |  |  |  | X | X | X
Alarm | 1054 | 3 | 301055 | 4 | 6352 | External Engine Stop | BOOL | [5 empty] | X
AC alarm | 1054 | 4 | 301055 | 4 | 1710 | Unbalance curr. 2 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 5 | 301055 | 4 | 7480 | Avg U BB > 1 | BOOL |  |  |  |  | X | X
AC alarm | 1054 | 6 | 301055 | 4 | 7490 | Avg U BB > 2 | BOOL |  |  |  |  | X | X
AC alarm | 1054 | 7 | 301055 | 4 | 7440 | 4th CT -P> 1 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 8 | 301055 | 4 | 7450 | 4th CT -P> 2 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 9 | 301055 | 4 | 7460 | 4th CT P> 1 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 10 | 301055 | 4 | 7470 | 4th CT P> 2 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 11 | 301055 | 4 | 1920 | BB f> 4 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 12 | 301055 | 4 | 1930 | BB f< 5 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 13 | 301055 | 4 | 1940 | BB U> 4 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 14 | 301055 | 4 | 1950 | BB U< 5 | BOOL |  |  |  | X | X | X
DAVR Alarm | 1056 | 0 | 301057 | 4 | 7830 | Digital AVR Communication Error | BOOL | [5 empty] | X
DAVR Alarm | 1056 | 1 | 301057 | 4 | 7761 | Digital AVR Warning | BOOL | [5 empty] | X
DAVR Alarm | 1056 | 2 | 301057 | 4 | 7763 | Digital AVR Trip | BOOL | [5 empty] | X
Alarm | 1057 | 0 | 301058 | 4 |  | Fail class: Block start + breaker on | BOOL |  |  |  | X | X | X
Alarm | 1057 | 1 | 301058 | 4 |  | Fail class: Warning | BOOL |  |  |  | X | X | X
Alarm | 1057 | 2 | 301058 | 4 |  | Fail class: Trip TB | BOOL |  |  |  |  | X
Alarm | 1057 | 2 | 301058 | 4 |  | Fail class: Trip GB | BOOL | [5 empty] | X
Alarm | 1057 | 2 | 301058 | 4 |  | Fail class: Trip BTB | BOOL |  |  |  | X
Alarm | 1057 | 3 | 301058 | 4 |  | Fail class: Trip GB + stop with cooling down | BOOL | [5 empty] | X
Alarm | 1057 | 4 | 301058 | 4 |  | Fail class: Trip GB + stop without cooling down | BOOL | [5 empty] | X
Alarm | 1057 | 5 | 301058 | 4 |  | Fail class: Trip MB | BOOL |  |  |  |  | X | X
Alarm | 1057 | 6 | 301058 | 4 |  | Fail class: Safety stop | BOOL | [5 empty] | X
Alarm | 1057 | 7 | 301058 | 4 |  | Fail class: If MB present Trip MB else Trip GB | BOOL | [5 empty] | X
Alarm | 1057 | 7 | 301058 | 4 |  | Fail class: If MB present Trip MB else Trip TB | BOOL |  |  |  |  | X
Alarm | 1057 | 8 | 301058 | 4 |  | Fail class: Controlled stop (deload + cooldown) | BOOL | [5 empty] | X
Alarm | 1057 | 9 | 301058 | 4 |  | Fail class: PV shutdown (Hybrid only) | BOOL | [5 empty] | X
M-Logic state | 1058 |  | 301059 | 4 |  | Virtual events 33-48 | INT16s | AB | 0 |  | X | X | X
M-Logic state | 1059 |  | 301060 | 4 |  | Virtual events 49-64 | INT16s | AB | 0 |  | X | X | X
M-Logic state | 1060 |  | 301061 | 4 |  | Virtual events 65-80 | INT16s | AB | 0 |  | X | X | X
M-Logic state | 1061 |  | 301062 | 4 |  | Virtual events 81-96 | INT16s | AB | 0 |  | X | X | X
M-Logic state | 1062 |  | 301063 | 4 |  | Flipflop output 1-16 | INT16s | AB | 0 |  | X | X | X
Alarm | 1063 | 0 | 301064 | 4 |  | Avg L-L AC RMS voltage High 1 | BOOL |  |  |  | X | X | X
Alarm | 1063 | 1 | 301064 | 4 |  | Avg L-L AC RMS voltage High 2 | BOOL |  |  |  | X | X | X
Alarm | 1063 | 2 | 301064 | 4 |  | Avg L-L AC RMS voltage Low 1 | BOOL |  |  |  | X | X | X
Alarm | 1063 | 3 | 301064 | 4 |  | Avg L-L AC RMS voltage Low 2 | BOOL |  |  |  | X | X | X
Alarm | 1063 | 4 | 301064 | 4 |  | Avg L-N AC RMS voltage High 1 | BOOL |  |  |  | X | X | X
Alarm | 1063 | 5 | 301064 | 4 |  | Avg L-N AC RMS voltage High 2 | BOOL |  |  |  | X | X | X
Alarm | 1063 | 6 | 301064 | 4 |  | Avg L-N AC RMS voltage Low 1 | BOOL |  |  |  | X | X | X
Alarm | 1063 | 7 | 301064 | 4 |  | Avg L-N AC RMS voltage Low 2 | BOOL |  |  |  | X | X | X
Alarm | 1063 | 8 | 301064 | 4 |  | Average AC frequency High 1 | BOOL |  |  |  | X | X | X
Alarm | 1063 | 9 | 301064 | 4 |  | Average AC frequency High 2 | BOOL |  |  |  | X | X | X
Alarm | 1063 | 10 | 301064 | 4 |  | Average AC frequency Low 1 | BOOL |  |  |  | X | X | X
Alarm | 1063 | 11 | 301064 | 4 |  | Average AC frequency Low 2 | BOOL |  |  |  | X | X | X
Alarm | 1063 | 12 | 301064 | 4 |  | Average AC RMS current High 1 | BOOL |  |  |  | X | X | X
Alarm | 1063 | 13 | 301064 | 4 |  | Average AC RMS current High 2 | BOOL |  |  |  | X | X | X
EIC state | 1068 | 0 | 301069 | 4 |  | M-Logic command: Reset trip fuel | BOOL | [5 empty] | X
EIC state | 1068 | 1 | 301069 | 4 |  | M-Logic command: MTU Alternate droop setting | BOOL | [5 empty] | X
Plant logic state | 1068 | 2 | 301069 | 4 |  | Nominal frequency 50/60Hz | BOOL |  |  |  | X | X | X
Plant logic state | 1068 | 3 | 301069 | 4 |  | Idle run active | BOOL | [5 empty] | X
EIC state | 1068 | 5 | 301069 | 4 |  | Engine start | BOOL | [5 empty] | X
EIC state | 1068 | 6 | 301069 | 4 |  | Engine stop | BOOL | [5 empty] | X
EIC state | 1068 | 7 | 301069 | 4 |  | Disable Engine Cylinder Cutoff2 | BOOL | [5 empty] | X
EIC state | 1068 | 8 | 301069 | 4 |  | M-Logic command: Engine overspeed test | BOOL | [5 empty] | X
EIC state | 1068 | 9 | 301069 | 4 |  | M-Logic command: Intermittent Oil Priming | BOOL | [5 empty] | X
EIC state | 1068 | 10 | 301069 | 4 |  | Engine preheat active | BOOL | [5 empty] | X
Alarm | 1074 | 0 | 301075 | 4 | 4750 | Delta analogue 7 - fail 1 | BOOL |  |  |  | X | X | X
Alarm | 1074 | 1 | 301075 | 4 | 4760 | Delta analogue 7 - fail 2 | BOOL |  |  |  | X | X | X
Alarm | 1074 | 2 | 301075 | 4 | 4770 | Delta analogue 8 - fail 1 | BOOL |  |  |  | X | X | X
Alarm | 1074 | 3 | 301075 | 4 | 4780 | Delta analogue 8 - fail 2 | BOOL |  |  |  | X | X | X
Alarm | 1074 | 4 | 301075 | 4 | 4790 | Delta analogue 9 - fail 1 | BOOL |  |  |  | X | X | X
Alarm | 1074 | 5 | 301075 | 4 | 4800 | Delta analogue 9 - fail 2 | BOOL |  |  |  | X | X | X
EIC state | 1076 |  | 301077 | 4 |  | JCB: Dosing Module Status | INT16s | AB | 0 |  |  |  | X
EIC state | 1077 |  | 301078 | 4 |  | JCB: Actual Reducing Agent Quantity | INT16s | AB | 0 |  |  |  | X
EIC state | 1078 |  | 301079 | 4 |  | JCB: Aftertreatment Lamp | INT16s | AB | 0 |  |  |  | X
EIC state | 1079 |  | 301080 | 4 |  | JCB: Refresh Status Byte | INT16s | AB | 0 |  |  |  | X
EIC state | 1080 |  | 301081 | 4 |  | JCB: SCR Monitor | INT16s | AB | 0 |  |  |  | X
EIC state | 1081 |  | 301082 | 4 |  | JCB: Successful Running Refreshes | INT16s | AB | 0 |  |  |  | X
EIC state | 1082 |  | 301083 | 4 |  | JCB: Successful Stationary Refreshes | INT16s | AB | 0 |  |  |  | X
EIC state | 1083 |  | 301084 | 4 |  | JCB: Engine Rating | INT16s | AB | 0 |  |  |  | X
EIC state | 1085 |  | 301086 | 4 |  | Emergency Shutdown Indication | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1092 |  | 301093 | 4 |  | HATZ: Remaining Service Hours | INT16s | AB | 0 |  |  |  | X
EIC state | 1093 | 0 | 301094 | 4 |  | HATZ: Engine Running | BOOL | [5 empty] | X
EIC state | 1093 | 1 | 301094 | 4 |  | HATZ: Service Delay | BOOL | [5 empty] | X
EIC state | 1093 | 2 | 301094 | 4 |  | HATZ: Pre-glow Active | BOOL | [5 empty] | X
EIC state | 1093 | 3 | 301094 | 4 |  | HATZ: Oil Pressure Missing | BOOL | [5 empty] | X
EIC state | 1093 | 4 | 301094 | 4 |  | HATZ: Engine Diagnostic Lamp | BOOL | [5 empty] | X
EIC state | 1093 | 5 | 301094 | 4 |  | HATZ: Engine Over temperature | BOOL | [5 empty] | X
EIC state | 1093 | 6 | 301094 | 4 |  | HATZ: Air Filter Switch | BOOL | [5 empty] | X
EIC state | 1093 | 7 | 301094 | 4 |  | HATZ: DPF Regeneration Not Inhibit Park Brake Not Set | BOOL | [5 empty] | X
EIC state | 1093 | 8 | 301094 | 4 |  | HATZ: DPF Regeneration Inhibit Park Brake Not Set | BOOL | [5 empty] | X
EIC state | 1093 | 9 | 301094 | 4 |  | HATZ: DPF Regeneration Not Inhibit Out Of Neutral | BOOL | [5 empty] | X
EIC state | 1093 | 10 | 301094 | 4 |  | HATZ: DPF Regeneration Inhibit Out Of Neutral | BOOL | [5 empty] | X
EIC state | 1093 | 11 | 301094 | 4 |  | HATZ: Parking Brake Switch | BOOL | [5 empty] | X
EIC state | 1093 | 12 | 301094 | 4 |  | HATZ: Brake Switch | BOOL | [5 empty] | X
EIC state | 1093 | 13 | 301094 | 4 |  | HATZ: Transmission Neutral Switch | BOOL | [5 empty] | X
EIC measurement | 1094 |  | 301095 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1095 |  | 301096 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1096 |  | 301097 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1097 |  | 301098 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1098 |  | 301099 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1099 |  | 301100 | 4 |  | Aftertreatment 1 Diesel Oxidation Catalyst Intake Temperature (SPN 4765) | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1100 |  | 301101 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1101 |  | 301102 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1102 |  | 301103 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1103 |  | 301104 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1104 |  | 301105 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1105 |  | 301106 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1106 |  | 301107 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1107 |  | 301108 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1108 |  | 301109 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1109 |  | 301110 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1110 |  | 301111 | 4 |  | Isuzu: Escape Mode Enable Flag | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1111 |  | 301112 | 4 |  | Isuzu: Inducement Level | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1112 |  | 301113 | 4 |  | Isuzu: UREA Tank Level | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1113 |  | 301114 | 4 |  | Isuzu: UREA Tank Level Indicator | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1114 |  | 301115 | 4 |  | Isuzu: Level Indicator (Amber) Action | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1115 |  | 301116 | 4 |  | Isuzu: DPF Amber Lamp Mode | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1116 |  | 301117 | 4 |  | Isuzu: Exhaust system lamp | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1117 |  | 301118 | 4 |  | Isuzu: DPF Green Lamp Mode | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1118 |  | 301119 | 4 |  | Isuzu: NO POWER Lamp | INT16s | AB | 0 |  |  |  | X
Alarm | 1130 | 0 | 301131 | 4 |  | CIO 308-2 Analogue input 8.1 | BOOL |  |  |  | X | X | X
Alarm | 1130 | 1 | 301131 | 4 |  | CIO 308-2 Analogue input 8.2 | BOOL |  |  |  | X | X | X
Alarm | 1130 | 2 | 301131 | 4 |  | CIO 308-2 Analogue input 11.1 | BOOL |  |  |  | X | X | X
Alarm | 1130 | 3 | 301131 | 4 |  | CIO 308-2 Analogue input 11.2 | BOOL |  |  |  | X | X | X
Alarm | 1130 | 4 | 301131 | 4 |  | CIO 308-2 Analogue input 14.1 | BOOL |  |  |  | X | X | X
Alarm | 1130 | 5 | 301131 | 4 |  | CIO 308-2 Analogue input 14.2 | BOOL |  |  |  | X | X | X
Alarm | 1130 | 6 | 301131 | 4 |  | CIO 308-2 Analogue input 17.1 | BOOL |  |  |  | X | X | X
Alarm | 1130 | 7 | 301131 | 4 |  | CIO 308-2 Analogue input 17.2 | BOOL |  |  |  | X | X | X
Alarm | 1130 | 8 | 301131 | 4 |  | CIO 308-2 Analogue input 20.1 | BOOL |  |  |  | X | X | X
Alarm | 1130 | 9 | 301131 | 4 |  | CIO 308-2 Analogue input 20.2 | BOOL |  |  |  | X | X | X
Alarm | 1130 | 10 | 301131 | 4 |  | CIO 308-2 Analogue input 23.1 | BOOL |  |  |  | X | X | X
Alarm | 1130 | 11 | 301131 | 4 |  | CIO 308-2 Analogue input 23.2 | BOOL |  |  |  | X | X | X
Alarm | 1130 | 12 | 301131 | 4 |  | CIO 308-2 Analogue input 26.1 | BOOL |  |  |  | X | X | X
Alarm | 1130 | 13 | 301131 | 4 |  | CIO 308-2 Analogue input 26.2 | BOOL |  |  |  | X | X | X
Alarm | 1130 | 14 | 301131 | 4 |  | CIO 308-2 Analogue input 29.1 | BOOL |  |  |  | X | X | X
Alarm | 1130 | 15 | 301131 | 4 |  | CIO 308-2 Analogue input 29.2 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 0 | 301132 | 4 |  | CIO 308-3 Analogue input 8.1 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 1 | 301132 | 4 |  | CIO 308-3 Analogue input 8.2 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 2 | 301132 | 4 |  | CIO 308-3 Analogue input 11.1 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 3 | 301132 | 4 |  | CIO 308-3 Analogue input 11.2 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 4 | 301132 | 4 |  | CIO 308-3 Analogue input 14.1 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 5 | 301132 | 4 |  | CIO 308-3 Analogue input 14.2 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 6 | 301132 | 4 |  | CIO 308-3 Analogue input 17.1 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 7 | 301132 | 4 |  | CIO 308-3 Analogue input 17.2 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 8 | 301132 | 4 |  | CIO 308-3 Analogue input 20.1 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 9 | 301132 | 4 |  | CIO 308-3 Analogue input 20.2 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 10 | 301132 | 4 |  | CIO 308-3 Analogue input 23.1 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 11 | 301132 | 4 |  | CIO 308-3 Analogue input 23.2 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 12 | 301132 | 4 |  | CIO 308-3 Analogue input 26.1 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 13 | 301132 | 4 |  | CIO 308-3 Analogue input 26.2 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 14 | 301132 | 4 |  | CIO 308-3 Analogue input 29.1 | BOOL |  |  |  | X | X | X
Alarm | 1131 | 15 | 301132 | 4 |  | CIO 308-3 Analogue input 29.2 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 0 | 301133 | 4 |  | CIO 116-2 digital input 10 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 1 | 301133 | 4 |  | CIO 116-2 digital input 11 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 2 | 301133 | 4 |  | CIO 116-2 digital input 12 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 3 | 301133 | 4 |  | CIO 116-2 digital input 13 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 4 | 301133 | 4 |  | CIO 116-2 digital input 14 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 5 | 301133 | 4 |  | CIO 116-2 digital input 15 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 6 | 301133 | 4 |  | CIO 116-2 digital input 16 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 7 | 301133 | 4 |  | CIO 116-2 digital input 17 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 8 | 301133 | 4 |  | CIO 116-2 digital input 18 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 9 | 301133 | 4 |  | CIO 116-2 digital input 20 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 10 | 301133 | 4 |  | CIO 116-2 digital input 21 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 11 | 301133 | 4 |  | CIO 116-2 digital input 22 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 12 | 301133 | 4 |  | CIO 116-2 digital input 23 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 13 | 301133 | 4 |  | CIO 116-2 digital input 24 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 14 | 301133 | 4 |  | CIO 116-2 digital input 25 | BOOL |  |  |  | X | X | X
Alarm | 1132 | 15 | 301133 | 4 |  | CIO 116-2 digital input 26 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 0 | 301134 | 4 |  | CIO 116-3 digital input 10 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 1 | 301134 | 4 |  | CIO 116-3 digital input 11 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 2 | 301134 | 4 |  | CIO 116-3 digital input 12 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 3 | 301134 | 4 |  | CIO 116-3 digital input 13 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 4 | 301134 | 4 |  | CIO 116-3 digital input 14 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 5 | 301134 | 4 |  | CIO 116-3 digital input 15 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 6 | 301134 | 4 |  | CIO 116-3 digital input 16 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 7 | 301134 | 4 |  | CIO 116-3 digital input 17 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 8 | 301134 | 4 |  | CIO 116-3 digital input 19 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 9 | 301134 | 4 |  | CIO 116-3 digital input 20 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 10 | 301134 | 4 |  | CIO 116-3 digital input 21 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 11 | 301134 | 4 |  | CIO 116-3 digital input 22 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 12 | 301134 | 4 |  | CIO 116-3 digital input 23 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 13 | 301134 | 4 |  | CIO 116-3 digital input 24 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 14 | 301134 | 4 |  | CIO 116-3 digital input 25 | BOOL |  |  |  | X | X | X
Alarm | 1133 | 15 | 301134 | 4 |  | CIO 116-3 digital input 26 | BOOL |  |  |  | X | X | X
Alarm | 1136 | 0 | 301137 | 4 |  | CIO 208-3 digital output 9 | BOOL |  |  |  | X | X | X
Alarm | 1136 | 1 | 301137 | 4 |  | CIO 208-3 digital output 11 | BOOL |  |  |  | X | X | X
Alarm | 1136 | 2 | 301137 | 4 |  | CIO 208-3 digital output 13 | BOOL |  |  |  | X | X | X
Alarm | 1136 | 3 | 301137 | 4 |  | CIO 208-3 digital output 15 | BOOL |  |  |  | X | X | X
Alarm | 1136 | 4 | 301137 | 4 |  | CIO 208-3 digital output 18 | BOOL |  |  |  | X | X | X
Alarm | 1136 | 5 | 301137 | 4 |  | CIO 208-3 digital output 21 | BOOL |  |  |  | X | X | X
Alarm | 1136 | 6 | 301137 | 4 |  | CIO 208-3 digital output 24 | BOOL |  |  |  | X | X | X
Alarm | 1136 | 7 | 301137 | 4 |  | CIO 208-3 digital output 27 | BOOL |  |  |  | X | X | X
DAVR measurement | 1214 |  | 301215 | 4 |  | DVC 550 Pt100 #1 | INT16s | AB | 0 |  |  |  | X
DAVR measurement | 1215 |  | 301216 | 4 |  | DVC 550 Pt100 #2 | INT16s | AB | 0 |  |  |  | X
DAVR measurement | 1216 |  | 301217 | 4 |  | DVC 550 Pt100 #3 | INT16s | AB | 0 |  |  |  | X
DAVR measurement | 1217 |  | 301218 | 4 |  | DVC 550 Pt100 #4 | INT16s | AB | 0 |  |  |  | X
DAVR measurement | 1218 |  | 301219 | 4 |  | DVC 550 Pt100 #5 | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1220 | 0 | 301221 | 4 |  | FPT Stage V: Fuel in Oil Detection | BOOL | [5 empty] | X
EIC measurement | 1220 | 1 | 301221 | 4 |  | FPT Stage V: Water in Fuel Detection | BOOL | [5 empty] | X
EIC measurement | 1220 | 2 | 301221 | 4 |  | FPT Stage V: Engine Protection | BOOL | [5 empty] | X
EIC measurement | 1220 | 3 | 301221 | 4 |  | FPT Stage V: Turbo Charger Protection | BOOL | [5 empty] | X
EIC measurement | 1220 | 4 | 301221 | 4 |  | FPT Stage V: Scr Injector Overheat Protection | BOOL | [5 empty] | X
EIC measurement | 1220 | 5 | 301221 | 4 |  | FPT Stage V: Urea Thawing Mode Active | BOOL | [5 empty] | X
EIC measurement | 1220 | 6 | 301221 | 4 |  | FPT Stage V: Engine Over Speed Warning | BOOL | [5 empty] | X
EIC measurement | 1220 | 7 | 301221 | 4 |  | FPT Stage V: Exhaust Over Heat Condition | BOOL | [5 empty] | X
EIC measurement | 1220 | 8 | 301221 | 4 |  | FPT Stage V: Clogged DPF | BOOL | [5 empty] | X
EIC measurement | 1220 | 9 | 301221 | 4 |  | FPT Stage V: Smoke Limitation | BOOL | [5 empty] | X
EIC measurement | 1220 | 10 | 301221 | 4 |  | FPT Stage V: Engine Oil Over Temperature | BOOL | [5 empty] | X
EIC measurement | 1220 | 11 | 301221 | 4 |  | FPT Stage V: Nh3 Slip Detection | BOOL | [5 empty] | X
EIC measurement | 1220 | 12 | 301221 | 4 |  | FPT Stage V: Bad Urea Quality | BOOL | [5 empty] | X
EIC measurement | 1220 | 13 | 301221 | 4 |  | FPT Stage V: Low Catalyst Efficiency | BOOL | [5 empty] | X
AC measurement | 1320 |  | 301321 | 4 |  | Hybrid only: PV power reference | INT16s | AB | 0 | kW |  |  | X
AC measurement | 1321 |  | 301322 | 4 |  | Hybrid only: PV reactive power reference | INT16s | AB | 0 | kW |  |  | X
AC measurement | 1322 |  | 301323 | 4 |  | Hybrid only: PV power actual | INT16s | AB | 0 | kW |  |  | X
AC measurement | 1323 |  | 301324 | 4 |  | Hybrid only: PV reactive power actual | INT16s | AB | 0 | kW |  |  | X
AC measurement | 1324 |  | 301325 | 4 |  | Hybrid only: PV nominal power actual | INT16s | AB | 0 | kW |  |  | X
Plant logic state | 1325 |  | 301326 | 4 |  | Hybrid only: PV breaker status | INT16s | AB | 0 |  |  |  | X
Alarm | 1326 | 0 | 301327 | 4 |  | Hybrid only: PV running status | BOOL |  |  |  | X | X | X
Plant logic state | 1327 |  | 301328 | 4 |  | Hybrid only: Number of PV related alarms present. Plus 1 for any amount of active alarms with PV shutdown fail class. | INT16s | AB | 0 |  |  |  | X
Counter | 1330 |  | 301331 | 4 |  | Hybrid only: PV Export, active energy counter, total | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1332 |  | 301333 | 4 |  | Hybrid only: PV Export, active energy counter, year | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1334 |  | 301335 | 4 |  | Hybrid only: PV Export, active energy counter, month | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1336 |  | 301337 | 4 |  | Hybrid only: PV Export, active energy counter, week | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1338 |  | 301339 | 4 |  | Hybrid only: PV Export, active energy counter, day | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1340 |  | 301341 | 4 |  | Hybrid only: PV Export, reactive energy counter, total | INT32s | ABCD | 0 | kvarh |  |  | X
Counter | 1342 |  | 301343 | 4 |  | Hybrid only: PV Export, reactive energy counter, year | INT32s | ABCD | 0 | kvarh |  |  | X
Counter | 1344 |  | 301345 | 4 |  | Hybrid only: PV Export, reactive energy counter, month | INT32s | ABCD | 0 | kvarh |  |  | X
Counter | 1346 |  | 301347 | 4 |  | Hybrid only: PV Export, reactive energy counter, week | INT32s | ABCD | 0 | kvarh |  |  | X
Counter | 1348 |  | 301349 | 4 |  | Hybrid only: PV Export, reactive energy counter, day | INT32s | ABCD | 0 | kvarh |  |  | X
Counter | 1350 |  | 301351 | 4 |  | Hybrid only: PV curtailed energy counter, day | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1352 |  | 301353 | 4 |  | Hybrid only: PV curtailed energy counter, week | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1354 |  | 301355 | 4 |  | Hybrid only: PV curtailed energy counter, month | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1356 |  | 301357 | 4 |  | Hybrid only: PV curtailed energy counter, year | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1358 |  | 301359 | 4 |  | Hybrid only: PV curtailed energy counter, total | INT32s | ABCD | 0 | kWh |  |  | X
EIC alarm | 1370 |  | 301371 | 4 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #1 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1371 |  | 301372 | 4 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #2 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1372 |  | 301373 | 4 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #3 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1373 |  | 301374 | 4 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #4 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1374 |  | 301375 | 4 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #5 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1375 |  | 301376 | 4 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #6 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1376 |  | 301377 | 4 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #7 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1377 |  | 301378 | 4 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #8 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1378 |  | 301379 | 4 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #9 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1379 |  | 301380 | 4 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #10 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1380 |  | 301381 | 4 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #1 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1381 |  | 301382 | 4 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #2 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1382 |  | 301383 | 4 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #3 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1383 |  | 301384 | 4 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #4 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1384 |  | 301385 | 4 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #5 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1385 |  | 301386 | 4 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #6 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1386 |  | 301387 | 4 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #7 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1387 |  | 301388 | 4 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #8 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1388 |  | 301389 | 4 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #9 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1389 |  | 301390 | 4 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #10 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1402 |  | 301403 | 4 |  | Active fail mode identifier (DM1/FMI): #1 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1403 |  | 301404 | 4 |  | Active fail mode identifier (DM1/FMI): #2 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1404 |  | 301405 | 4 |  | Active fail mode identifier (DM1/FMI): #3 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1405 |  | 301406 | 4 |  | Active fail mode identifier (DM1/FMI): #4 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1406 |  | 301407 | 4 |  | Active fail mode identifier (DM1/FMI): #5 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1407 |  | 301408 | 4 |  | Active fail mode identifier (DM1/FMI): #6 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1408 |  | 301409 | 4 |  | Active fail mode identifier (DM1/FMI): #7 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1409 |  | 301410 | 4 |  | Active fail mode identifier (DM1/FMI): #8 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1410 |  | 301411 | 4 |  | Active fail mode identifier (DM1/FMI): #9 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1411 |  | 301412 | 4 |  | Active fail mode identifier (DM1/FMI): #10 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1418 |  | 301419 | 4 |  | Active occurrence counter (DM1/OC): #1 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1419 |  | 301420 | 4 |  | Active occurrence counter (DM1/OC): #2 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1420 |  | 301421 | 4 |  | Active occurrence counter (DM1/OC): #3 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1421 |  | 301422 | 4 |  | Active occurrence counter (DM1/OC): #4 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1422 |  | 301423 | 4 |  | Active occurrence counter (DM1/OC): #5 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1423 |  | 301424 | 4 |  | Active occurrence counter (DM1/OC): #6 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1424 |  | 301425 | 4 |  | Active occurrence counter (DM1/OC): #7 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1425 |  | 301426 | 4 |  | Active occurrence counter (DM1/OC): #8 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1426 |  | 301427 | 4 |  | Active occurrence counter (DM1/OC): #9 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1427 |  | 301428 | 4 |  | Active occurrence counter (DM1/OC): #10 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1434 |  | 301435 | 4 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #1 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1435 |  | 301436 | 4 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #2 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1436 |  | 301437 | 4 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #3 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1437 |  | 301438 | 4 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #4 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1438 |  | 301439 | 4 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #5 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1439 |  | 301440 | 4 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #6 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1440 |  | 301441 | 4 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #7 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1441 |  | 301442 | 4 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #8 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1442 |  | 301443 | 4 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #9 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1443 |  | 301444 | 4 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #10 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1444 |  | 301445 | 4 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #1 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1445 |  | 301446 | 4 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #2 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1446 |  | 301447 | 4 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #3 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1447 |  | 301448 | 4 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #4 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1448 |  | 301449 | 4 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #5 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1449 |  | 301450 | 4 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #6 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1450 |  | 301451 | 4 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #7 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1451 |  | 301452 | 4 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #8 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1452 |  | 301453 | 4 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #9 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1453 |  | 301454 | 4 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #10 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1466 |  | 301467 | 4 |  | Active fail mode identifier (DM2/FMI): #1 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1467 |  | 301468 | 4 |  | Active fail mode identifier (DM2/FMI): #2 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1468 |  | 301469 | 4 |  | Active fail mode identifier (DM2/FMI): #3 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1469 |  | 301470 | 4 |  | Active fail mode identifier (DM2/FMI): #4 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1470 |  | 301471 | 4 |  | Active fail mode identifier (DM2/FMI): #5 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1471 |  | 301472 | 4 |  | Active fail mode identifier (DM2/FMI): #6 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1472 |  | 301473 | 4 |  | Active fail mode identifier (DM2/FMI): #7 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1473 |  | 301474 | 4 |  | Active fail mode identifier (DM2/FMI): #8 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1474 |  | 301475 | 4 |  | Active fail mode identifier (DM2/FMI): #9 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1475 |  | 301476 | 4 |  | Active fail mode identifier (DM2/FMI): #10 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1482 |  | 301483 | 4 |  | Active occurrence counter (DM2/OC): #1 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1483 |  | 301484 | 4 |  | Active occurrence counter (DM2/OC): #2 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1484 |  | 301485 | 4 |  | Active occurrence counter (DM2/OC): #3 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1485 |  | 301486 | 4 |  | Active occurrence counter (DM2/OC): #4 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1486 |  | 301487 | 4 |  | Active occurrence counter (DM2/OC): #5 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1487 |  | 301488 | 4 |  | Active occurrence counter (DM2/OC): #6 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1488 |  | 301489 | 4 |  | Active occurrence counter (DM2/OC): #7 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1489 |  | 301490 | 4 |  | Active occurrence counter (DM2/OC): #8 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1490 |  | 301491 | 4 |  | Active occurrence counter (DM2/OC): #9 | INT16s | AB | 0 |  |  |  | X
EIC alarm | 1491 |  | 301492 | 4 |  | Active occurrence counter (DM2/OC): #10 | INT16s | AB | 0 |  |  |  | X
PM AC measurement | 1500 |  | 301501 | 4 |  | Total power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1501 |  | 301502 | 4 |  | Available power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1502 |  | 301503 | 4 |  | Total nominal power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1503 |  | 301504 | 4 |  | Total genset power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1504 |  | 301505 | 4 |  | Total reactive power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1505 |  | 301506 | 4 |  | Number of gensets in application | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1506 |  | 301507 | 4 |  | Plant type | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1507 |  | 301508 | 4 |  | Load-dependent stop, active set-point | INT16s | AB | 0 |  |  |  | X
PM AC measurement | 1508 |  | 301509 | 4 |  | Load-dependent start, active set-point | INT16s | AB | 0 |  |  |  | X
PM AC measurement | 1510 |  | 301511 | 4 |  | Nominal power ID 1 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1511 |  | 301512 | 4 |  | Nominal power ID 2 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1512 |  | 301513 | 4 |  | Nominal power ID 3 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1513 |  | 301514 | 4 |  | Nominal power ID 4 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1514 |  | 301515 | 4 |  | Nominal power ID 5 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1515 |  | 301516 | 4 |  | Nominal power ID 6 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1516 |  | 301517 | 4 |  | Nominal power ID 7 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1517 |  | 301518 | 4 |  | Nominal power ID 8 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1518 |  | 301519 | 4 |  | Nominal power ID 9 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1519 |  | 301520 | 4 |  | Nominal power ID 10 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1520 |  | 301521 | 4 |  | Nominal power ID 11 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1521 |  | 301522 | 4 |  | Nominal power ID 12 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1522 |  | 301523 | 4 |  | Nominal power ID 13 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1523 |  | 301524 | 4 |  | Nominal power ID 14 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1524 |  | 301525 | 4 |  | Nominal power ID 15 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1525 |  | 301526 | 4 |  | Nominal power ID 16 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1526 |  | 301527 | 4 |  | Active Power ID 1 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1527 |  | 301528 | 4 |  | Active Power ID 2 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1528 |  | 301529 | 4 |  | Active Power ID 3 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1529 |  | 301530 | 4 |  | Active Power ID 4 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1530 |  | 301531 | 4 |  | Active Power ID 5 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1531 |  | 301532 | 4 |  | Active Power ID 6 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1532 |  | 301533 | 4 |  | Active Power ID 7 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1533 |  | 301534 | 4 |  | Active Power ID 8 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1534 |  | 301535 | 4 |  | Active Power ID 9 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1535 |  | 301536 | 4 |  | Active Power ID 10 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1536 |  | 301537 | 4 |  | Active Power ID 11 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1537 |  | 301538 | 4 |  | Active Power ID 12 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1538 |  | 301539 | 4 |  | Active Power ID 13 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1539 |  | 301540 | 4 |  | Active Power ID 14 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1540 |  | 301541 | 4 |  | Active Power ID 15 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1541 |  | 301542 | 4 |  | Active Power ID 16 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1542 |  | 301543 | 4 |  | Reactive Power ID 1 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1543 |  | 301544 | 4 |  | Reactive Power ID 2 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1544 |  | 301545 | 4 |  | Reactive Power ID 3 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1545 |  | 301546 | 4 |  | Reactive Power ID 4 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1546 |  | 301547 | 4 |  | Reactive Power ID 5 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1547 |  | 301548 | 4 |  | Reactive Power ID 6 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1548 |  | 301549 | 4 |  | Reactive Power ID 7 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1549 |  | 301550 | 4 |  | Reactive Power ID 8 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1550 |  | 301551 | 4 |  | Reactive Power ID 9 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1551 |  | 301552 | 4 |  | Reactive Power ID 10 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1552 |  | 301553 | 4 |  | Reactive Power ID 11 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1553 |  | 301554 | 4 |  | Reactive Power ID 12 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1554 |  | 301555 | 4 |  | Reactive Power ID 13 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1555 |  | 301556 | 4 |  | Reactive Power ID 14 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1556 |  | 301557 | 4 |  | Reactive Power ID 15 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1557 |  | 301558 | 4 |  | Reactive Power ID 16 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1558 |  | 301559 | 4 |  | Priority of genset | INT16s | AB | 0 |  |  |  | X
PM AC measurement | 1560 |  | 301561 | 4 |  | Active Power ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1561 |  | 301562 | 4 |  | Active Power ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1562 |  | 301563 | 4 |  | Active Power ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1563 |  | 301564 | 4 |  | Active Power ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1565 |  | 301566 | 4 |  | Reactive Power ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1566 |  | 301567 | 4 |  | Reactive Power ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1567 |  | 301568 | 4 |  | Reactive Power ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1568 |  | 301569 | 4 |  | Reactive Power ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1569 |  | 301570 | 4 |  | Active Power ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1570 |  | 301571 | 4 |  | Active Power ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1571 |  | 301572 | 4 |  | Active Power ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1572 |  | 301573 | 4 |  | Active Power ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1573 |  | 301574 | 4 |  | Active Power ID 21 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1574 |  | 301575 | 4 |  | Active Power ID 22 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1575 |  | 301576 | 4 |  | Active Power ID 23 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1576 |  | 301577 | 4 |  | Active Power ID 24 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1577 |  | 301578 | 4 |  | Active Power ID 25 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1578 |  | 301579 | 4 |  | Active Power ID 26 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1579 |  | 301580 | 4 |  | Active Power ID 27 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1580 |  | 301581 | 4 |  | Active Power ID 28 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1581 |  | 301582 | 4 |  | Active Power ID 29 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1582 |  | 301583 | 4 |  | Active Power ID 30 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1583 |  | 301584 | 4 |  | Active Power ID 31 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1584 |  | 301585 | 4 |  | Active Power ID 32 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1585 |  | 301586 | 4 |  | Reactive Power ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1586 |  | 301587 | 4 |  | Reactive Power ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1587 |  | 301588 | 4 |  | Reactive Power ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1588 |  | 301589 | 4 |  | Reactive Power ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1589 |  | 301590 | 4 |  | Reactive Power ID 21 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1590 |  | 301591 | 4 |  | Reactive Power ID 22 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1591 |  | 301592 | 4 |  | Reactive Power ID 23 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1592 |  | 301593 | 4 |  | Reactive Power ID 24 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1593 |  | 301594 | 4 |  | Reactive Power ID 25 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1594 |  | 301595 | 4 |  | Reactive Power ID 26 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1595 |  | 301596 | 4 |  | Reactive Power ID 27 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1596 |  | 301597 | 4 |  | Reactive Power ID 28 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1597 |  | 301598 | 4 |  | Reactive Power ID 29 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1598 |  | 301599 | 4 |  | Reactive Power ID 30 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1599 |  | 301600 | 4 |  | Reactive Power ID 31 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1600 |  | 301601 | 4 |  | Reactive Power ID 32 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1601 |  | 301602 | 4 |  | Active Power ID 33 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1602 |  | 301603 | 4 |  | Active Power ID 34 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1603 |  | 301604 | 4 |  | Active Power ID 35 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1604 |  | 301605 | 4 |  | Active Power ID 36 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1605 |  | 301606 | 4 |  | Active Power ID 37 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1606 |  | 301607 | 4 |  | Active Power ID 38 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1607 |  | 301608 | 4 |  | Active Power ID 39 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1608 |  | 301609 | 4 |  | Active Power ID 40 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1609 |  | 301610 | 4 |  | Reactive Power ID 33 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1610 |  | 301611 | 4 |  | Reactive Power ID 34 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1611 |  | 301612 | 4 |  | Reactive Power ID 35 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1612 |  | 301613 | 4 |  | Reactive Power ID 36 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1613 |  | 301614 | 4 |  | Reactive Power ID 37 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1614 |  | 301615 | 4 |  | Reactive Power ID 38 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1615 |  | 301616 | 4 |  | Reactive Power ID 39 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1616 |  | 301617 | 4 |  | Reactive Power ID 40 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1617 |  | 301618 | 4 |  | Plant mode mains 17 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1618 |  | 301619 | 4 |  | Plant mode mains 18 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1619 |  | 301620 | 4 |  | Plant mode mains 19 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1620 |  | 301621 | 4 |  | Plant mode mains 20 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1621 |  | 301622 | 4 |  | Plant mode mains 21 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1622 |  | 301623 | 4 |  | Plant mode mains 22 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1623 |  | 301624 | 4 |  | Plant mode mains 23 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1624 |  | 301625 | 4 |  | Plant mode mains 24 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1625 |  | 301626 | 4 |  | Plant mode mains 25 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1626 |  | 301627 | 4 |  | Plant mode mains 26 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1627 |  | 301628 | 4 |  | Plant mode mains 27 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1628 |  | 301629 | 4 |  | Plant mode mains 28 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1629 |  | 301630 | 4 |  | Plant mode mains 29 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1630 |  | 301631 | 4 |  | Plant mode mains 30 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1631 |  | 301632 | 4 |  | Plant mode mains 31 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1632 |  | 301633 | 4 |  | Plant mode mains 32 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1633 |  | 301634 | 4 |  | Bus power mains 17 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1634 |  | 301635 | 4 |  | Bus power mains 18 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1635 |  | 301636 | 4 |  | Bus power mains 19 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1636 |  | 301637 | 4 |  | Bus power mains 20 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1637 |  | 301638 | 4 |  | Bus power mains 21 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1638 |  | 301639 | 4 |  | Bus power mains 22 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1639 |  | 301640 | 4 |  | Bus power mains 23 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1640 |  | 301641 | 4 |  | Bus power mains 24 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1641 |  | 301642 | 4 |  | Bus power mains 25 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1642 |  | 301643 | 4 |  | Bus power mains 26 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1643 |  | 301644 | 4 |  | Bus power mains 27 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1644 |  | 301645 | 4 |  | Bus power mains 28 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1645 |  | 301646 | 4 |  | Bus power mains 29 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1646 |  | 301647 | 4 |  | Bus power mains 30 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1647 |  | 301648 | 4 |  | Bus power mains 31 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1648 |  | 301649 | 4 |  | Bus power mains 32 | INT16s | AB | 0 |  | X | X | X
PM Plant logic state | 1649 | 0 | 301650 | 4 |  | Mains transducer-configured, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 1 | 301650 | 4 |  | Mains transducer-configured, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 2 | 301650 | 4 |  | Mains transducer-configured, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 3 | 301650 | 4 |  | Mains transducer-configured, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 4 | 301650 | 4 |  | Mains transducer-configured, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 5 | 301650 | 4 |  | Mains transducer-configured, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 6 | 301650 | 4 |  | Mains transducer-configured, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 7 | 301650 | 4 |  | Mains transducer-configured, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 8 | 301650 | 4 |  | Mains transducer-configured, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 9 | 301650 | 4 |  | Mains transducer-configured, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 10 | 301650 | 4 |  | Mains transducer-configured, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 11 | 301650 | 4 |  | Mains transducer-configured, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 12 | 301650 | 4 |  | Mains transducer-configured, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 13 | 301650 | 4 |  | Mains transducer-configured, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 14 | 301650 | 4 |  | Mains transducer-configured, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 15 | 301650 | 4 |  | Mains transducer-configured, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 0 | 301651 | 4 |  | TB transducer-configured, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 1 | 301651 | 4 |  | TB transducer-configured, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 2 | 301651 | 4 |  | TB transducer-configured, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 3 | 301651 | 4 |  | TB transducer-configured, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 4 | 301651 | 4 |  | TB transducer-configured, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 5 | 301651 | 4 |  | TB transducer-configured, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 6 | 301651 | 4 |  | TB transducer-configured, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 7 | 301651 | 4 |  | TB transducer-configured, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 8 | 301651 | 4 |  | TB transducer-configured, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 9 | 301651 | 4 |  | TB transducer-configured, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 10 | 301651 | 4 |  | TB transducer-configured, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 11 | 301651 | 4 |  | TB transducer-configured, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 12 | 301651 | 4 |  | TB transducer-configured, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 13 | 301651 | 4 |  | TB transducer-configured, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 14 | 301651 | 4 |  | TB transducer-configured, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 15 | 301651 | 4 |  | TB transducer-configured, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 0 | 301652 | 4 |  | BTB transducer-configured, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 1 | 301652 | 4 |  | BTB transducer-configured, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 2 | 301652 | 4 |  | BTB transducer-configured, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 3 | 301652 | 4 |  | BTB transducer-configured, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 4 | 301652 | 4 |  | BTB transducer-configured, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 5 | 301652 | 4 |  | BTB transducer-configured, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 6 | 301652 | 4 |  | BTB transducer-configured, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 7 | 301652 | 4 |  | BTB transducer-configured, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 0 | 301653 | 4 |  | ID 33 BTB controlled | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 1 | 301653 | 4 |  | ID 34 BTB controlled | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 2 | 301653 | 4 |  | ID 35 BTB controlled | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 3 | 301653 | 4 |  | ID 36 BTB controlled | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 4 | 301653 | 4 |  | ID 37 BTB controlled | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 5 | 301653 | 4 |  | ID 38 BTB controlled | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 6 | 301653 | 4 |  | ID 39 BTB controlled | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 7 | 301653 | 4 |  | ID 40 BTB controlled | BOOL |  |  |  | X | X | X
PM AC measurement | 1653 |  | 301654 | 4 |  | Nominal power ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1654 |  | 301655 | 4 |  | Nominal power ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1655 |  | 301656 | 4 |  | Nominal power ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1656 |  | 301657 | 4 |  | Nominal power ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1657 |  | 301658 | 4 |  | Nominal power ID 21 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1658 |  | 301659 | 4 |  | Nominal power ID 22 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1659 |  | 301660 | 4 |  | Nominal power ID 23 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1660 |  | 301661 | 4 |  | Nominal power ID 24 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1661 |  | 301662 | 4 |  | Nominal power ID 25 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1662 |  | 301663 | 4 |  | Nominal power ID 26 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1663 |  | 301664 | 4 |  | Nominal power ID 27 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1664 |  | 301665 | 4 |  | Nominal power ID 28 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1665 |  | 301666 | 4 |  | Nominal power ID 29 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1666 |  | 301667 | 4 |  | Nominal power ID 30 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1667 |  | 301668 | 4 |  | Nominal power ID 31 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1668 |  | 301669 | 4 |  | Nominal power ID 32 | INT16s | AB | 0 |  | X | X | X
PM Plant logic state | 1700 | 0 | 301701 | 4 |  | TB available | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 1 | 301701 | 4 |  | Mains unit available | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 2 | 301701 | 4 |  | Any MB pos. ON | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 3 | 301701 | 4 |  | All MB pos. OFF | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 4 | 301701 | 4 |  | TB pos. ON (Mains Command Unit) | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 5 | 301701 | 4 |  | TB pos. OFF (Mains Command Unit) | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 6 | 301701 | 4 |  | Any GB pos. ON | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 7 | 301701 | 4 |  | All GB pos. OFF | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 8 | 301701 | 4 |  | Any TB pos. ON | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 9 | 301701 | 4 |  | All TB pos. OFF | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 10 | 301701 | 4 |  | Any BTB pos. ON | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 11 | 301701 | 4 |  | Any BTB pos. OFF | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 0 | 301702 | 4 |  | GB pos. ON ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 1 | 301702 | 4 |  | GB pos. ON ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 2 | 301702 | 4 |  | GB pos. ON ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 3 | 301702 | 4 |  | GB pos. ON ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 4 | 301702 | 4 |  | GB pos. ON ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 5 | 301702 | 4 |  | GB pos. ON ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 6 | 301702 | 4 |  | GB pos. ON ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 7 | 301702 | 4 |  | GB pos. ON ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 8 | 301702 | 4 |  | GB pos. ON ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 9 | 301702 | 4 |  | GB pos. ON ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 10 | 301702 | 4 |  | GB pos. ON ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 11 | 301702 | 4 |  | GB pos. ON ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 12 | 301702 | 4 |  | GB pos. ON ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 13 | 301702 | 4 |  | GB pos. ON ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 14 | 301702 | 4 |  | GB pos. ON ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 15 | 301702 | 4 |  | GB pos. ON ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 0 | 301703 | 4 |  | GB pos. OFF ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 1 | 301703 | 4 |  | GB pos. OFF ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 2 | 301703 | 4 |  | GB pos. OFF ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 3 | 301703 | 4 |  | GB pos. OFF ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 4 | 301703 | 4 |  | GB pos. OFF ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 5 | 301703 | 4 |  | GB pos. OFF ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 6 | 301703 | 4 |  | GB pos. OFF ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 7 | 301703 | 4 |  | GB pos. OFF ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 8 | 301703 | 4 |  | GB pos. OFF ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 9 | 301703 | 4 |  | GB pos. OFF ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 10 | 301703 | 4 |  | GB pos. OFF ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 11 | 301703 | 4 |  | GB pos. OFF ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 12 | 301703 | 4 |  | GB pos. OFF ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 13 | 301703 | 4 |  | GB pos. OFF ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 14 | 301703 | 4 |  | GB pos. OFF ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 15 | 301703 | 4 |  | GB pos. OFF ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 0 | 301704 | 4 |  | DG Hz/V OK, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 1 | 301704 | 4 |  | DG Hz/V OK, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 2 | 301704 | 4 |  | DG Hz/V OK, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 3 | 301704 | 4 |  | DG Hz/V OK, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 4 | 301704 | 4 |  | DG Hz/V OK, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 5 | 301704 | 4 |  | DG Hz/V OK, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 6 | 301704 | 4 |  | DG Hz/V OK, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 7 | 301704 | 4 |  | DG Hz/V OK, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 8 | 301704 | 4 |  | DG Hz/V OK, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 9 | 301704 | 4 |  | DG Hz/V OK, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 10 | 301704 | 4 |  | DG Hz/V OK, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 11 | 301704 | 4 |  | DG Hz/V OK, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 12 | 301704 | 4 |  | DG Hz/V OK, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 13 | 301704 | 4 |  | DG Hz/V OK, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 14 | 301704 | 4 |  | DG Hz/V OK, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 15 | 301704 | 4 |  | DG Hz/V OK, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1704 | 0 | 301705 | 4 |  | Mains OK, single mains | BOOL |  |  |  | X | X | X
PM Plant logic state | 1704 | 1 | 301705 | 4 |  | Mains OK, mains 1A | BOOL |  |  |  | X | X | X
PM Plant logic state | 1704 | 2 | 301705 | 4 |  | Mains OK, mains 1B | BOOL |  |  |  | X | X | X
PM Plant logic state | 1704 | 3 | 301705 | 4 |  | Mains OK, mains 2A | BOOL |  |  |  | X | X | X
PM Plant logic state | 1704 | 4 | 301705 | 4 |  | Mains OK, mains 2B | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 0 | 301706 | 4 |  | Ready for auto start, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 1 | 301706 | 4 |  | Ready for auto start, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 2 | 301706 | 4 |  | Ready for auto start, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 3 | 301706 | 4 |  | Ready for auto start, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 4 | 301706 | 4 |  | Ready for auto start, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 5 | 301706 | 4 |  | Ready for auto start, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 6 | 301706 | 4 |  | Ready for auto start, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 7 | 301706 | 4 |  | Ready for auto start, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 8 | 301706 | 4 |  | Ready for auto start, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 9 | 301706 | 4 |  | Ready for auto start, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 10 | 301706 | 4 |  | Ready for auto start, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 11 | 301706 | 4 |  | Ready for auto start, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 12 | 301706 | 4 |  | Ready for auto start, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 13 | 301706 | 4 |  | Ready for auto start, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 14 | 301706 | 4 |  | Ready for auto start, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 15 | 301706 | 4 |  | Ready for auto start, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1706 | 0 | 301707 | 4 |  | Mains not in semi, single mains | BOOL |  |  |  | X | X | X
PM Plant logic state | 1706 | 1 | 301707 | 4 |  | Mains not in semi, mains 1A | BOOL |  |  |  | X | X | X
PM Plant logic state | 1706 | 2 | 301707 | 4 |  | Mains not in semi, mains 1B | BOOL |  |  |  | X | X | X
PM Plant logic state | 1706 | 3 | 301707 | 4 |  | Mains not in semi, mains 2A | BOOL |  |  |  | X | X | X
PM Plant logic state | 1706 | 4 | 301707 | 4 |  | Mains not in semi, mains 2B | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 0 | 301708 | 4 |  | Any alarms, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 1 | 301708 | 4 |  | Any alarms, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 2 | 301708 | 4 |  | Any alarms, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 3 | 301708 | 4 |  | Any alarms, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 4 | 301708 | 4 |  | Any alarms, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 5 | 301708 | 4 |  | Any alarms, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 6 | 301708 | 4 |  | Any alarms, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 7 | 301708 | 4 |  | Any alarms, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 8 | 301708 | 4 |  | Any alarms, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 9 | 301708 | 4 |  | Any alarms, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 10 | 301708 | 4 |  | Any alarms, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 11 | 301708 | 4 |  | Any alarms, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 12 | 301708 | 4 |  | Any alarms, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 13 | 301708 | 4 |  | Any alarms, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 14 | 301708 | 4 |  | Any alarms, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 15 | 301708 | 4 |  | Any alarms, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1708 | 0 | 301709 | 4 |  | Any alarms, single mains | BOOL |  |  |  | X | X | X
PM Plant logic state | 1708 | 1 | 301709 | 4 |  | Any alarms, mains 1A | BOOL |  |  |  | X | X | X
PM Plant logic state | 1708 | 2 | 301709 | 4 |  | Any alarms, mains 1B | BOOL |  |  |  | X | X | X
PM Plant logic state | 1708 | 3 | 301709 | 4 |  | Any alarms, mains 2A | BOOL |  |  |  | X | X | X
PM Plant logic state | 1708 | 4 | 301709 | 4 |  | Any alarms, mains 2B | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 0 | 301710 | 4 |  | Engine running, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 1 | 301710 | 4 |  | Engine running, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 2 | 301710 | 4 |  | Engine running, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 3 | 301710 | 4 |  | Engine running, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 4 | 301710 | 4 |  | Engine running, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 5 | 301710 | 4 |  | Engine running, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 6 | 301710 | 4 |  | Engine running, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 7 | 301710 | 4 |  | Engine running, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 8 | 301710 | 4 |  | Engine running, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 9 | 301710 | 4 |  | Engine running, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 10 | 301710 | 4 |  | Engine running, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 11 | 301710 | 4 |  | Engine running, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 12 | 301710 | 4 |  | Engine running, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 13 | 301710 | 4 |  | Engine running, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 14 | 301710 | 4 |  | Engine running, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 15 | 301710 | 4 |  | Engine running, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 0 | 301711 | 4 |  | MB pos. ON, single mains | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 1 | 301711 | 4 |  | MB pos. ON, mains 1A | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 2 | 301711 | 4 |  | MB pos. ON, mains 1B | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 3 | 301711 | 4 |  | MB pos. ON, mains 2A | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 4 | 301711 | 4 |  | MB pos. ON, mains 2B | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 5 | 301711 | 4 |  | MB pos. OFF, single mains | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 6 | 301711 | 4 |  | MB pos. OFF, mains 1A | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 7 | 301711 | 4 |  | MB pos. OFF, mains 1B | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 8 | 301711 | 4 |  | MB pos. OFF, mains 2A | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 9 | 301711 | 4 |  | MB pos. OFF, mains 2B | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 0 | 301712 | 4 |  | GB synchronising, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 1 | 301712 | 4 |  | GB synchronising, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 2 | 301712 | 4 |  | GB synchronising, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 3 | 301712 | 4 |  | GB synchronising, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 4 | 301712 | 4 |  | GB synchronising, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 5 | 301712 | 4 |  | GB synchronising, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 6 | 301712 | 4 |  | GB synchronising, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 7 | 301712 | 4 |  | GB synchronising, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 8 | 301712 | 4 |  | GB synchronising, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 9 | 301712 | 4 |  | GB synchronising, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 10 | 301712 | 4 |  | GB synchronising, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 11 | 301712 | 4 |  | GB synchronising, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 12 | 301712 | 4 |  | GB synchronising, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 13 | 301712 | 4 |  | GB synchronising, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 14 | 301712 | 4 |  | GB synchronising, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 15 | 301712 | 4 |  | GB synchronising, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 0 | 301713 | 4 |  | Mains OK, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 1 | 301713 | 4 |  | Mains OK, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 2 | 301713 | 4 |  | Mains OK, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 3 | 301713 | 4 |  | Mains OK, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 4 | 301713 | 4 |  | Mains OK, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 5 | 301713 | 4 |  | Mains OK, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 6 | 301713 | 4 |  | Mains OK, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 7 | 301713 | 4 |  | Mains OK, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 8 | 301713 | 4 |  | Mains OK, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 9 | 301713 | 4 |  | Mains OK, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 10 | 301713 | 4 |  | Mains OK, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 11 | 301713 | 4 |  | Mains OK, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 12 | 301713 | 4 |  | Mains OK, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 13 | 301713 | 4 |  | Mains OK, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 14 | 301713 | 4 |  | Mains OK, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 15 | 301713 | 4 |  | Mains OK, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 0 | 301714 | 4 |  | Mains not in semi 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 1 | 301714 | 4 |  | Mains not in semi 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 2 | 301714 | 4 |  | Mains not in semi 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 3 | 301714 | 4 |  | Mains not in semi 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 4 | 301714 | 4 |  | Mains not in semi 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 5 | 301714 | 4 |  | Mains not in semi 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 6 | 301714 | 4 |  | Mains not in semi 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 7 | 301714 | 4 |  | Mains not in semi 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 8 | 301714 | 4 |  | Mains not in semi 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 9 | 301714 | 4 |  | Mains not in semi 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 10 | 301714 | 4 |  | Mains not in semi 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 11 | 301714 | 4 |  | Mains not in semi 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 12 | 301714 | 4 |  | Mains not in semi 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 13 | 301714 | 4 |  | Mains not in semi 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 14 | 301714 | 4 |  | Mains not in semi 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 15 | 301714 | 4 |  | Mains not in semi 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 0 | 301715 | 4 |  | Any alarms, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 1 | 301715 | 4 |  | Any alarms, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 2 | 301715 | 4 |  | Any alarms, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 3 | 301715 | 4 |  | Any alarms, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 4 | 301715 | 4 |  | Any alarms, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 5 | 301715 | 4 |  | Any alarms, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 6 | 301715 | 4 |  | Any alarms, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 7 | 301715 | 4 |  | Any alarms, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 8 | 301715 | 4 |  | Any alarms, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 9 | 301715 | 4 |  | Any alarms, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 10 | 301715 | 4 |  | Any alarms, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 11 | 301715 | 4 |  | Any alarms, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 12 | 301715 | 4 |  | Any alarms, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 13 | 301715 | 4 |  | Any alarms, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 14 | 301715 | 4 |  | Any alarms, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 15 | 301715 | 4 |  | Any alarms, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 0 | 301716 | 4 |  | MB pos. ON, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 1 | 301716 | 4 |  | MB pos. ON, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 2 | 301716 | 4 |  | MB pos. ON, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 3 | 301716 | 4 |  | MB pos. ON, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 4 | 301716 | 4 |  | MB pos. ON, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 5 | 301716 | 4 |  | MB pos. ON, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 6 | 301716 | 4 |  | MB pos. ON, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 7 | 301716 | 4 |  | MB pos. ON, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 8 | 301716 | 4 |  | MB pos. ON, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 9 | 301716 | 4 |  | MB pos. ON, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 10 | 301716 | 4 |  | MB pos. ON, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 11 | 301716 | 4 |  | MB pos. ON, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 12 | 301716 | 4 |  | MB pos. ON, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 13 | 301716 | 4 |  | MB pos. ON, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 14 | 301716 | 4 |  | MB pos. ON, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 15 | 301716 | 4 |  | MB pos. ON, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 0 | 301717 | 4 |  | MB pos. OFF, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 1 | 301717 | 4 |  | MB pos. OFF, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 2 | 301717 | 4 |  | MB pos. OFF, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 3 | 301717 | 4 |  | MB pos. OFF, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 4 | 301717 | 4 |  | MB pos. OFF, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 5 | 301717 | 4 |  | MB pos. OFF, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 6 | 301717 | 4 |  | MB pos. OFF, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 7 | 301717 | 4 |  | MB pos. OFF, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 8 | 301717 | 4 |  | MB pos. OFF, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 9 | 301717 | 4 |  | MB pos. OFF, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 10 | 301717 | 4 |  | MB pos. OFF, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 11 | 301717 | 4 |  | MB pos. OFF, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 12 | 301717 | 4 |  | MB pos. OFF, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 13 | 301717 | 4 |  | MB pos. OFF, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 14 | 301717 | 4 |  | MB pos. OFF, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 15 | 301717 | 4 |  | MB pos. OFF, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 0 | 301718 | 4 |  | Mains failure, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 1 | 301718 | 4 |  | Mains failure, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 2 | 301718 | 4 |  | Mains failure, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 3 | 301718 | 4 |  | Mains failure, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 4 | 301718 | 4 |  | Mains failure, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 5 | 301718 | 4 |  | Mains failure, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 6 | 301718 | 4 |  | Mains failure, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 7 | 301718 | 4 |  | Mains failure, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 8 | 301718 | 4 |  | Mains failure, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 9 | 301718 | 4 |  | Mains failure, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 10 | 301718 | 4 |  | Mains failure, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 11 | 301718 | 4 |  | Mains failure, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 12 | 301718 | 4 |  | Mains failure, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 13 | 301718 | 4 |  | Mains failure, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 14 | 301718 | 4 |  | Mains failure, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 15 | 301718 | 4 |  | Mains failure, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 0 | 301719 | 4 |  | MB synchronising, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 1 | 301719 | 4 |  | MB synchronising, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 2 | 301719 | 4 |  | MB synchronising, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 3 | 301719 | 4 |  | MB synchronising, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 4 | 301719 | 4 |  | MB synchronising, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 5 | 301719 | 4 |  | MB synchronising, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 6 | 301719 | 4 |  | MB synchronising, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 7 | 301719 | 4 |  | MB synchronising, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 8 | 301719 | 4 |  | MB synchronising, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 9 | 301719 | 4 |  | MB synchronising, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 10 | 301719 | 4 |  | MB synchronising, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 11 | 301719 | 4 |  | MB synchronising, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 12 | 301719 | 4 |  | MB synchronising, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 13 | 301719 | 4 |  | MB synchronising, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 14 | 301719 | 4 |  | MB synchronising, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 15 | 301719 | 4 |  | MB synchronising, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 0 | 301720 | 4 |  | TB pos. ON, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 1 | 301720 | 4 |  | TB pos. ON, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 2 | 301720 | 4 |  | TB pos. ON, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 3 | 301720 | 4 |  | TB pos. ON, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 4 | 301720 | 4 |  | TB pos. ON, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 5 | 301720 | 4 |  | TB pos. ON, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 6 | 301720 | 4 |  | TB pos. ON, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 7 | 301720 | 4 |  | TB pos. ON, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 8 | 301720 | 4 |  | TB pos. ON, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 9 | 301720 | 4 |  | TB pos. ON, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 10 | 301720 | 4 |  | TB pos. ON, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 11 | 301720 | 4 |  | TB pos. ON, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 12 | 301720 | 4 |  | TB pos. ON, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 13 | 301720 | 4 |  | TB pos. ON, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 14 | 301720 | 4 |  | TB pos. ON, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 15 | 301720 | 4 |  | TB pos. ON, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 0 | 301721 | 4 |  | TB pos. OFF, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 1 | 301721 | 4 |  | TB pos. OFF, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 2 | 301721 | 4 |  | TB pos. OFF, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 3 | 301721 | 4 |  | TB pos. OFF, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 4 | 301721 | 4 |  | TB pos. OFF, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 5 | 301721 | 4 |  | TB pos. OFF, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 6 | 301721 | 4 |  | TB pos. OFF, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 7 | 301721 | 4 |  | TB pos. OFF, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 8 | 301721 | 4 |  | TB pos. OFF, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 9 | 301721 | 4 |  | TB pos. OFF, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 10 | 301721 | 4 |  | TB pos. OFF, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 11 | 301721 | 4 |  | TB pos. OFF, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 12 | 301721 | 4 |  | TB pos. OFF, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 13 | 301721 | 4 |  | TB pos. OFF, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 14 | 301721 | 4 |  | TB pos. OFF, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 15 | 301721 | 4 |  | TB pos. OFF, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 0 | 301722 | 4 |  | TB synchronising, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 1 | 301722 | 4 |  | TB synchronising, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 2 | 301722 | 4 |  | TB synchronising, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 3 | 301722 | 4 |  | TB synchronising, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 4 | 301722 | 4 |  | TB synchronising, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 5 | 301722 | 4 |  | TB synchronising, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 6 | 301722 | 4 |  | TB synchronising, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 7 | 301722 | 4 |  | TB synchronising, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 8 | 301722 | 4 |  | TB synchronising, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 9 | 301722 | 4 |  | TB synchronising, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 10 | 301722 | 4 |  | TB synchronising, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 11 | 301722 | 4 |  | TB synchronising, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 12 | 301722 | 4 |  | TB synchronising, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 13 | 301722 | 4 |  | TB synchronising, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 14 | 301722 | 4 |  | TB synchronising, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 15 | 301722 | 4 |  | TB synchronising, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 0 | 301723 | 4 |  | Any alarms, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 1 | 301723 | 4 |  | Any alarms, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 2 | 301723 | 4 |  | Any alarms, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 3 | 301723 | 4 |  | Any alarms, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 4 | 301723 | 4 |  | Any alarms, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 5 | 301723 | 4 |  | Any alarms, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 6 | 301723 | 4 |  | Any alarms, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 7 | 301723 | 4 |  | Any alarms, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 0 | 301726 | 4 |  | BTB synchronising, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 1 | 301726 | 4 |  | BTB synchronising, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 2 | 301726 | 4 |  | BTB synchronising, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 3 | 301726 | 4 |  | BTB synchronising, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 4 | 301726 | 4 |  | BTB synchronising, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 5 | 301726 | 4 |  | BTB synchronising, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 6 | 301726 | 4 |  | BTB synchronising, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 7 | 301726 | 4 |  | BTB synchronising, ID 40 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 0 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 17 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 1 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 18 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 2 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 19 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 3 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 20 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 4 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 21 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 5 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 22 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 6 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 23 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 7 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 24 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 8 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 25 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 9 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 26 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 10 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 27 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 11 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 28 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 12 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 29 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 13 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 30 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 14 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 31 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 15 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 32 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 0 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 33 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 1 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 34 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 2 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 35 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 3 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 36 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 4 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 37 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 5 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 38 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 6 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 39 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 7 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 0 | 301733 | 4 |  | BB Hz/V OK, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 1 | 301733 | 4 |  | BB Hz/V OK, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 2 | 301733 | 4 |  | BB Hz/V OK, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 3 | 301733 | 4 |  | BB Hz/V OK, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 4 | 301733 | 4 |  | BB Hz/V OK, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 5 | 301733 | 4 |  | BB Hz/V OK, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 6 | 301733 | 4 |  | BB Hz/V OK, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 7 | 301733 | 4 |  | BB Hz/V OK, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 8 | 301733 | 4 |  | BB Hz/V OK, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 9 | 301733 | 4 |  | BB Hz/V OK, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 10 | 301733 | 4 |  | BB Hz/V OK, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 11 | 301733 | 4 |  | BB Hz/V OK, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 12 | 301733 | 4 |  | BB Hz/V OK, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 13 | 301733 | 4 |  | BB Hz/V OK, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 14 | 301733 | 4 |  | BB Hz/V OK, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 15 | 301733 | 4 |  | BB Hz/V OK, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 0 | 301734 | 4 |  | BB Hz/V OK, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 1 | 301734 | 4 |  | BB Hz/V OK, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 2 | 301734 | 4 |  | BB Hz/V OK, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 3 | 301734 | 4 |  | BB Hz/V OK, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 4 | 301734 | 4 |  | BB Hz/V OK, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 5 | 301734 | 4 |  | BB Hz/V OK, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 6 | 301734 | 4 |  | BB Hz/V OK, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 7 | 301734 | 4 |  | BB Hz/V OK, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 8 | 301734 | 4 |  | BB Hz/V OK, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 9 | 301734 | 4 |  | BB Hz/V OK, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 10 | 301734 | 4 |  | BB Hz/V OK, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 11 | 301734 | 4 |  | BB Hz/V OK, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 12 | 301734 | 4 |  | BB Hz/V OK, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 13 | 301734 | 4 |  | BB Hz/V OK, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 14 | 301734 | 4 |  | BB Hz/V OK, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 15 | 301734 | 4 |  | BB Hz/V OK, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 0 | 301735 | 4 |  | BB Hz/V OK, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 1 | 301735 | 4 |  | BB Hz/V OK, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 2 | 301735 | 4 |  | BB Hz/V OK, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 3 | 301735 | 4 |  | BB Hz/V OK, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 4 | 301735 | 4 |  | BB Hz/V OK, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 5 | 301735 | 4 |  | BB Hz/V OK, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 6 | 301735 | 4 |  | BB Hz/V OK, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 7 | 301735 | 4 |  | BB Hz/V OK, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 0 | 301736 | 4 |  | BB Hz/V present, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 1 | 301736 | 4 |  | BB Hz/V present, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 2 | 301736 | 4 |  | BB Hz/V present, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 3 | 301736 | 4 |  | BB Hz/V present, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 4 | 301736 | 4 |  | BB Hz/V present, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 5 | 301736 | 4 |  | BB Hz/V present, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 6 | 301736 | 4 |  | BB Hz/V present, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 7 | 301736 | 4 |  | BB Hz/V present, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 8 | 301736 | 4 |  | BB Hz/V present, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 9 | 301736 | 4 |  | BB Hz/V present, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 10 | 301736 | 4 |  | BB Hz/V present, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 11 | 301736 | 4 |  | BB Hz/V present, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 12 | 301736 | 4 |  | BB Hz/V present, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 13 | 301736 | 4 |  | BB Hz/V present, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 14 | 301736 | 4 |  | BB Hz/V present, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 15 | 301736 | 4 |  | BB Hz/V present, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 0 | 301737 | 4 |  | BB Hz/V present, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 1 | 301737 | 4 |  | BB Hz/V present, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 2 | 301737 | 4 |  | BB Hz/V present, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 3 | 301737 | 4 |  | BB Hz/V present, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 4 | 301737 | 4 |  | BB Hz/V present, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 5 | 301737 | 4 |  | BB Hz/V present, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 6 | 301737 | 4 |  | BB Hz/V present, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 7 | 301737 | 4 |  | BB Hz/V present, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 8 | 301737 | 4 |  | BB Hz/V present, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 9 | 301737 | 4 |  | BB Hz/V present, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 10 | 301737 | 4 |  | BB Hz/V present, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 11 | 301737 | 4 |  | BB Hz/V present, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 12 | 301737 | 4 |  | BB Hz/V present, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 13 | 301737 | 4 |  | BB Hz/V present, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 14 | 301737 | 4 |  | BB Hz/V present, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 15 | 301737 | 4 |  | BB Hz/V present, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 0 | 301738 | 4 |  | BB Hz/V present, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 1 | 301738 | 4 |  | BB Hz/V present, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 2 | 301738 | 4 |  | BB Hz/V present, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 3 | 301738 | 4 |  | BB Hz/V present, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 4 | 301738 | 4 |  | BB Hz/V present, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 5 | 301738 | 4 |  | BB Hz/V present, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 6 | 301738 | 4 |  | BB Hz/V present, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 7 | 301738 | 4 |  | BB Hz/V present, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 0 | 301739 | 4 |  | BA Hz/V OK, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 1 | 301739 | 4 |  | BA Hz/V OK, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 2 | 301739 | 4 |  | BA Hz/V OK, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 3 | 301739 | 4 |  | BA Hz/V OK, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 4 | 301739 | 4 |  | BA Hz/V OK, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 5 | 301739 | 4 |  | BA Hz/V OK, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 6 | 301739 | 4 |  | BA Hz/V OK, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 7 | 301739 | 4 |  | BA Hz/V OK, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 0 | 301740 | 4 |  | DG Hz/V present, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 1 | 301740 | 4 |  | DG Hz/V present, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 2 | 301740 | 4 |  | DG Hz/V present, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 3 | 301740 | 4 |  | DG Hz/V present, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 4 | 301740 | 4 |  | DG Hz/V present, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 5 | 301740 | 4 |  | DG Hz/V present, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 6 | 301740 | 4 |  | DG Hz/V present, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 7 | 301740 | 4 |  | DG Hz/V present, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 8 | 301740 | 4 |  | DG Hz/V present, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 9 | 301740 | 4 |  | DG Hz/V present, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 10 | 301740 | 4 |  | DG Hz/V present, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 11 | 301740 | 4 |  | DG Hz/V present, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 12 | 301740 | 4 |  | DG Hz/V present, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 13 | 301740 | 4 |  | DG Hz/V present, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 14 | 301740 | 4 |  | DG Hz/V present, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 15 | 301740 | 4 |  | DG Hz/V present, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 0 | 301741 | 4 |  | Hz/V present, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 1 | 301741 | 4 |  | Hz/V present, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 2 | 301741 | 4 |  | Hz/V present, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 3 | 301741 | 4 |  | Hz/V present, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 4 | 301741 | 4 |  | Hz/V present, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 5 | 301741 | 4 |  | Hz/V present, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 6 | 301741 | 4 |  | Hz/V present, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 7 | 301741 | 4 |  | Hz/V present, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 8 | 301741 | 4 |  | Hz/V present, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 9 | 301741 | 4 |  | Hz/V present, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 10 | 301741 | 4 |  | Hz/V present, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 11 | 301741 | 4 |  | Hz/V present, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 12 | 301741 | 4 |  | Hz/V present, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 13 | 301741 | 4 |  | Hz/V present, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 14 | 301741 | 4 |  | Hz/V present, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 15 | 301741 | 4 |  | Hz/V present, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 0 | 301742 | 4 |  | BA Hz/V present, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 1 | 301742 | 4 |  | BA Hz/V present, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 2 | 301742 | 4 |  | BA Hz/V present, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 3 | 301742 | 4 |  | BA Hz/V present, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 4 | 301742 | 4 |  | BA Hz/V present, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 5 | 301742 | 4 |  | BA Hz/V present, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 6 | 301742 | 4 |  | BA Hz/V present, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 7 | 301742 | 4 |  | BA Hz/V present, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 0 | 301750 | 4 |  | Dry Mode active on ID1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 1 | 301750 | 4 |  | Dry Mode active on ID2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 2 | 301750 | 4 |  | Dry Mode active on ID3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 3 | 301750 | 4 |  | Dry Mode active on ID4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 4 | 301750 | 4 |  | Dry Mode active on ID5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 5 | 301750 | 4 |  | Dry Mode active on ID6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 6 | 301750 | 4 |  | Dry Mode active on ID7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 7 | 301750 | 4 |  | Dry Mode active on ID8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 8 | 301750 | 4 |  | Dry Mode active on ID9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 9 | 301750 | 4 |  | Dry Mode active on ID10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 10 | 301750 | 4 |  | Dry Mode active on ID11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 11 | 301750 | 4 |  | Dry Mode active on ID12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 12 | 301750 | 4 |  | Dry Mode active on ID13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 13 | 301750 | 4 |  | Dry Mode active on ID14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 14 | 301750 | 4 |  | Dry Mode active on ID15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 15 | 301750 | 4 |  | Dry Mode active on ID16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 0 | 301751 | 4 |  | GB Pos ON, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 1 | 301751 | 4 |  | GB Pos ON, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 2 | 301751 | 4 |  | GB Pos ON, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 3 | 301751 | 4 |  | GB Pos ON, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 4 | 301751 | 4 |  | GB Pos ON, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 5 | 301751 | 4 |  | GB Pos ON, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 6 | 301751 | 4 |  | GB Pos ON, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 7 | 301751 | 4 |  | GB Pos ON, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 8 | 301751 | 4 |  | GB Pos ON, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 9 | 301751 | 4 |  | GB Pos ON, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 10 | 301751 | 4 |  | GB Pos ON, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 11 | 301751 | 4 |  | GB Pos ON, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 12 | 301751 | 4 |  | GB Pos ON, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 13 | 301751 | 4 |  | GB Pos ON, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 14 | 301751 | 4 |  | GB Pos ON, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 15 | 301751 | 4 |  | GB Pos ON, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 0 | 301752 | 4 |  | GB Pos OFF, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 1 | 301752 | 4 |  | GB Pos OFF, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 2 | 301752 | 4 |  | GB Pos OFF, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 3 | 301752 | 4 |  | GB Pos OFF, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 4 | 301752 | 4 |  | GB Pos OFF, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 5 | 301752 | 4 |  | GB Pos OFF, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 6 | 301752 | 4 |  | GB Pos OFF, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 7 | 301752 | 4 |  | GB Pos OFF, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 8 | 301752 | 4 |  | GB Pos OFF, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 9 | 301752 | 4 |  | GB Pos OFF, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 10 | 301752 | 4 |  | GB Pos OFF, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 11 | 301752 | 4 |  | GB Pos OFF, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 12 | 301752 | 4 |  | GB Pos OFF, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 13 | 301752 | 4 |  | GB Pos OFF, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 14 | 301752 | 4 |  | GB Pos OFF, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 15 | 301752 | 4 |  | GB Pos OFF, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 0 | 301753 | 4 |  | GB synchronising, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 1 | 301753 | 4 |  | GB synchronising, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 2 | 301753 | 4 |  | GB synchronising, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 3 | 301753 | 4 |  | GB synchronising, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 4 | 301753 | 4 |  | GB synchronising, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 5 | 301753 | 4 |  | GB synchronising, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 6 | 301753 | 4 |  | GB synchronising, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 7 | 301753 | 4 |  | GB synchronising, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 8 | 301753 | 4 |  | GB synchronising, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 9 | 301753 | 4 |  | GB synchronising, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 10 | 301753 | 4 |  | GB synchronising, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 11 | 301753 | 4 |  | GB synchronising, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 12 | 301753 | 4 |  | GB synchronising, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 13 | 301753 | 4 |  | GB synchronising, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 14 | 301753 | 4 |  | GB synchronising, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 15 | 301753 | 4 |  | GB synchronising, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 0 | 301754 | 4 |  | Hz/V OK, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 1 | 301754 | 4 |  | Hz/V OK, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 2 | 301754 | 4 |  | Hz/V OK, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 3 | 301754 | 4 |  | Hz/V OK, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 4 | 301754 | 4 |  | Hz/V OK, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 5 | 301754 | 4 |  | Hz/V OK, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 6 | 301754 | 4 |  | Hz/V OK, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 7 | 301754 | 4 |  | Hz/V OK, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 8 | 301754 | 4 |  | Hz/V OK, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 9 | 301754 | 4 |  | Hz/V OK, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 10 | 301754 | 4 |  | Hz/V OK, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 11 | 301754 | 4 |  | Hz/V OK, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 12 | 301754 | 4 |  | Hz/V OK, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 13 | 301754 | 4 |  | Hz/V OK, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 14 | 301754 | 4 |  | Hz/V OK, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 15 | 301754 | 4 |  | Hz/V OK, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 0 | 301755 | 4 |  | Ready for auto start, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 1 | 301755 | 4 |  | Ready for auto start, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 2 | 301755 | 4 |  | Ready for auto start, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 3 | 301755 | 4 |  | Ready for auto start, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 4 | 301755 | 4 |  | Ready for auto start, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 5 | 301755 | 4 |  | Ready for auto start, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 6 | 301755 | 4 |  | Ready for auto start, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 7 | 301755 | 4 |  | Ready for auto start, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 8 | 301755 | 4 |  | Ready for auto start, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 9 | 301755 | 4 |  | Ready for auto start, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 10 | 301755 | 4 |  | Ready for auto start, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 11 | 301755 | 4 |  | Ready for auto start, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 12 | 301755 | 4 |  | Ready for auto start, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 13 | 301755 | 4 |  | Ready for auto start, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 14 | 301755 | 4 |  | Ready for auto start, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 15 | 301755 | 4 |  | Ready for auto start, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 0 | 301756 | 4 |  | Running, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 1 | 301756 | 4 |  | Running, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 2 | 301756 | 4 |  | Running, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 3 | 301756 | 4 |  | Running, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 4 | 301756 | 4 |  | Running, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 5 | 301756 | 4 |  | Running, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 6 | 301756 | 4 |  | Running, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 7 | 301756 | 4 |  | Running, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 8 | 301756 | 4 |  | Running, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 9 | 301756 | 4 |  | Running, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 10 | 301756 | 4 |  | Running, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 11 | 301756 | 4 |  | Running, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 12 | 301756 | 4 |  | Running, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 13 | 301756 | 4 |  | Running, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 14 | 301756 | 4 |  | Running, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 15 | 301756 | 4 |  | Running, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 0 | 301757 | 4 |  | Dry Mode active on ID17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 1 | 301757 | 4 |  | Dry Mode active on ID18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 2 | 301757 | 4 |  | Dry Mode active on ID19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 3 | 301757 | 4 |  | Dry Mode active on ID20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 4 | 301757 | 4 |  | Dry Mode active on ID21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 5 | 301757 | 4 |  | Dry Mode active on ID22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 6 | 301757 | 4 |  | Dry Mode active on ID23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 7 | 301757 | 4 |  | Dry Mode active on ID24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 8 | 301757 | 4 |  | Dry Mode active on ID25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 9 | 301757 | 4 |  | Dry Mode active on ID26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 10 | 301757 | 4 |  | Dry Mode active on ID27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 11 | 301757 | 4 |  | Dry Mode active on ID28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 12 | 301757 | 4 |  | Dry Mode active on ID29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 13 | 301757 | 4 |  | Dry Mode active on ID30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 14 | 301757 | 4 |  | Dry Mode active on ID31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 15 | 301757 | 4 |  | Dry Mode active on ID32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 0 | 301758 | 4 |  | MB pos. ON, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 1 | 301758 | 4 |  | MB pos. ON, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 2 | 301758 | 4 |  | MB pos. ON, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 3 | 301758 | 4 |  | MB pos. ON, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 4 | 301758 | 4 |  | MB pos. ON, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 5 | 301758 | 4 |  | MB pos. ON, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 6 | 301758 | 4 |  | MB pos. ON, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 7 | 301758 | 4 |  | MB pos. ON, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 8 | 301758 | 4 |  | MB pos. ON, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 9 | 301758 | 4 |  | MB pos. ON, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 10 | 301758 | 4 |  | MB pos. ON, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 11 | 301758 | 4 |  | MB pos. ON, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 12 | 301758 | 4 |  | MB pos. ON, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 13 | 301758 | 4 |  | MB pos. ON, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 14 | 301758 | 4 |  | MB pos. ON, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 15 | 301758 | 4 |  | MB pos. ON, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 0 | 301759 | 4 |  | MB pos. OFF, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 1 | 301759 | 4 |  | MB pos. OFF, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 2 | 301759 | 4 |  | MB pos. OFF, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 3 | 301759 | 4 |  | MB pos. OFF, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 4 | 301759 | 4 |  | MB pos. OFF, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 5 | 301759 | 4 |  | MB pos. OFF, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 6 | 301759 | 4 |  | MB pos. OFF, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 7 | 301759 | 4 |  | MB pos. OFF, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 8 | 301759 | 4 |  | MB pos. OFF, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 9 | 301759 | 4 |  | MB pos. OFF, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 10 | 301759 | 4 |  | MB pos. OFF, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 11 | 301759 | 4 |  | MB pos. OFF, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 12 | 301759 | 4 |  | MB pos. OFF, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 13 | 301759 | 4 |  | MB pos. OFF, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 14 | 301759 | 4 |  | MB pos. OFF, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 15 | 301759 | 4 |  | MB pos. OFF, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 0 | 301760 | 4 |  | MB synchronising, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 1 | 301760 | 4 |  | MB synchronising, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 2 | 301760 | 4 |  | MB synchronising, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 3 | 301760 | 4 |  | MB synchronising, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 4 | 301760 | 4 |  | MB synchronising, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 5 | 301760 | 4 |  | MB synchronising, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 6 | 301760 | 4 |  | MB synchronising, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 7 | 301760 | 4 |  | MB synchronising, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 8 | 301760 | 4 |  | MB synchronising, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 9 | 301760 | 4 |  | MB synchronising, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 10 | 301760 | 4 |  | MB synchronising, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 11 | 301760 | 4 |  | MB synchronising, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 12 | 301760 | 4 |  | MB synchronising, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 13 | 301760 | 4 |  | MB synchronising, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 14 | 301760 | 4 |  | MB synchronising, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 15 | 301760 | 4 |  | MB synchronising, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 0 | 301761 | 4 |  | TB pos. ON, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 1 | 301761 | 4 |  | TB pos. ON, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 2 | 301761 | 4 |  | TB pos. ON, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 3 | 301761 | 4 |  | TB pos. ON, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 4 | 301761 | 4 |  | TB pos. ON, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 5 | 301761 | 4 |  | TB pos. ON, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 6 | 301761 | 4 |  | TB pos. ON, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 7 | 301761 | 4 |  | TB pos. ON, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 8 | 301761 | 4 |  | TB pos. ON, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 9 | 301761 | 4 |  | TB pos. ON, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 10 | 301761 | 4 |  | TB pos. ON, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 11 | 301761 | 4 |  | TB pos. ON, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 12 | 301761 | 4 |  | TB pos. ON, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 13 | 301761 | 4 |  | TB pos. ON, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 14 | 301761 | 4 |  | TB pos. ON, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 15 | 301761 | 4 |  | TB pos. ON, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 0 | 301762 | 4 |  | TB pos. OFF, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 1 | 301762 | 4 |  | TB pos. OFF, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 2 | 301762 | 4 |  | TB pos. OFF, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 3 | 301762 | 4 |  | TB pos. OFF, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 4 | 301762 | 4 |  | TB pos. OFF, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 5 | 301762 | 4 |  | TB pos. OFF, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 6 | 301762 | 4 |  | TB pos. OFF, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 7 | 301762 | 4 |  | TB pos. OFF, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 8 | 301762 | 4 |  | TB pos. OFF, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 9 | 301762 | 4 |  | TB pos. OFF, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 10 | 301762 | 4 |  | TB pos. OFF, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 11 | 301762 | 4 |  | TB pos. OFF, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 12 | 301762 | 4 |  | TB pos. OFF, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 13 | 301762 | 4 |  | TB pos. OFF, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 14 | 301762 | 4 |  | TB pos. OFF, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 15 | 301762 | 4 |  | TB pos. OFF, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 0 | 301763 | 4 |  | TB synchronising, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 1 | 301763 | 4 |  | TB synchronising, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 2 | 301763 | 4 |  | TB synchronising, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 3 | 301763 | 4 |  | TB synchronising, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 4 | 301763 | 4 |  | TB synchronising, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 5 | 301763 | 4 |  | TB synchronising, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 6 | 301763 | 4 |  | TB synchronising, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 7 | 301763 | 4 |  | TB synchronising, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 8 | 301763 | 4 |  | TB synchronising, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 9 | 301763 | 4 |  | TB synchronising, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 10 | 301763 | 4 |  | TB synchronising, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 11 | 301763 | 4 |  | TB synchronising, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 12 | 301763 | 4 |  | TB synchronising, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 13 | 301763 | 4 |  | TB synchronising, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 14 | 301763 | 4 |  | TB synchronising, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 15 | 301763 | 4 |  | TB synchronising, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 0 | 301764 | 4 |  | Mains transducer-configured, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 1 | 301764 | 4 |  | Mains transducer-configured, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 2 | 301764 | 4 |  | Mains transducer-configured, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 3 | 301764 | 4 |  | Mains transducer-configured, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 4 | 301764 | 4 |  | Mains transducer-configured, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 5 | 301764 | 4 |  | Mains transducer-configured, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 6 | 301764 | 4 |  | Mains transducer-configured, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 7 | 301764 | 4 |  | Mains transducer-configured, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 8 | 301764 | 4 |  | Mains transducer-configured, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 9 | 301764 | 4 |  | Mains transducer-configured, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 10 | 301764 | 4 |  | Mains transducer-configured, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 11 | 301764 | 4 |  | Mains transducer-configured, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 12 | 301764 | 4 |  | Mains transducer-configured, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 13 | 301764 | 4 |  | Mains transducer-configured, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 14 | 301764 | 4 |  | Mains transducer-configured, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 15 | 301764 | 4 |  | Mains transducer-configured, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 0 | 301765 | 4 |  | TB transducer-configured, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 1 | 301765 | 4 |  | TB transducer-configured, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 2 | 301765 | 4 |  | TB transducer-configured, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 3 | 301765 | 4 |  | TB transducer-configured, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 4 | 301765 | 4 |  | TB transducer-configured, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 5 | 301765 | 4 |  | TB transducer-configured, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 6 | 301765 | 4 |  | TB transducer-configured, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 7 | 301765 | 4 |  | TB transducer-configured, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 8 | 301765 | 4 |  | TB transducer-configured, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 9 | 301765 | 4 |  | TB transducer-configured, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 10 | 301765 | 4 |  | TB transducer-configured, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 11 | 301765 | 4 |  | TB transducer-configured, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 12 | 301765 | 4 |  | TB transducer-configured, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 13 | 301765 | 4 |  | TB transducer-configured, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 14 | 301765 | 4 |  | TB transducer-configured, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 15 | 301765 | 4 |  | TB transducer-configured, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 0 | 301766 | 4 |  | Mains OK, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 1 | 301766 | 4 |  | Mains OK, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 2 | 301766 | 4 |  | Mains OK, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 3 | 301766 | 4 |  | Mains OK, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 4 | 301766 | 4 |  | Mains OK, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 5 | 301766 | 4 |  | Mains OK, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 6 | 301766 | 4 |  | Mains OK, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 7 | 301766 | 4 |  | Mains OK, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 8 | 301766 | 4 |  | Mains OK, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 9 | 301766 | 4 |  | Mains OK, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 10 | 301766 | 4 |  | Mains OK, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 11 | 301766 | 4 |  | Mains OK, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 12 | 301766 | 4 |  | Mains OK, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 13 | 301766 | 4 |  | Mains OK, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 14 | 301766 | 4 |  | Mains OK, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 15 | 301766 | 4 |  | Mains OK, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 0 | 301767 | 4 |  | Mains not in semi 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 1 | 301767 | 4 |  | Mains not in semi 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 2 | 301767 | 4 |  | Mains not in semi 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 3 | 301767 | 4 |  | Mains not in semi 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 4 | 301767 | 4 |  | Mains not in semi 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 5 | 301767 | 4 |  | Mains not in semi 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 6 | 301767 | 4 |  | Mains not in semi 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 7 | 301767 | 4 |  | Mains not in semi 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 8 | 301767 | 4 |  | Mains not in semi 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 9 | 301767 | 4 |  | Mains not in semi 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 10 | 301767 | 4 |  | Mains not in semi 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 11 | 301767 | 4 |  | Mains not in semi 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 12 | 301767 | 4 |  | Mains not in semi 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 13 | 301767 | 4 |  | Mains not in semi 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 14 | 301767 | 4 |  | Mains not in semi 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 15 | 301767 | 4 |  | Mains not in semi 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 0 | 301768 | 4 |  | Mains failure, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 1 | 301768 | 4 |  | Mains failure, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 2 | 301768 | 4 |  | Mains failure, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 3 | 301768 | 4 |  | Mains failure, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 4 | 301768 | 4 |  | Mains failure, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 5 | 301768 | 4 |  | Mains failure, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 6 | 301768 | 4 |  | Mains failure, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 7 | 301768 | 4 |  | Mains failure, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 8 | 301768 | 4 |  | Mains failure, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 9 | 301768 | 4 |  | Mains failure, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 10 | 301768 | 4 |  | Mains failure, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 11 | 301768 | 4 |  | Mains failure, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 12 | 301768 | 4 |  | Mains failure, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 13 | 301768 | 4 |  | Mains failure, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 14 | 301768 | 4 |  | Mains failure, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 15 | 301768 | 4 |  | Mains failure, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 0 | 301771 | 4 |  | Breaker synchronising, PV ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 1 | 301771 | 4 |  | Breaker synchronising, PV ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 2 | 301771 | 4 |  | Breaker synchronising, PV ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 3 | 301771 | 4 |  | Breaker synchronising, PV ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 4 | 301771 | 4 |  | Breaker synchronising, PV ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 5 | 301771 | 4 |  | Breaker synchronising, PV ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 6 | 301771 | 4 |  | Breaker synchronising, PV ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 7 | 301771 | 4 |  | Breaker synchronising, PV ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 0 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 1 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 2 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 3 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 4 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 5 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 6 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 7 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 8 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 9 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 10 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 11 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 12 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 13 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 14 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 15 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 0 | 301773 | 4 |  | Ready to autostart, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 1 | 301773 | 4 |  | Ready to autostart, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 2 | 301773 | 4 |  | Ready to autostart, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 3 | 301773 | 4 |  | Ready to autostart, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 4 | 301773 | 4 |  | Ready to autostart, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 5 | 301773 | 4 |  | Ready to autostart, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 6 | 301773 | 4 |  | Ready to autostart, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 7 | 301773 | 4 |  | Ready to autostart, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 8 | 301773 | 4 |  | Ready to autostart, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 9 | 301773 | 4 |  | Ready to autostart, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 10 | 301773 | 4 |  | Ready to autostart, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 11 | 301773 | 4 |  | Ready to autostart, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 12 | 301773 | 4 |  | Ready to autostart, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 13 | 301773 | 4 |  | Ready to autostart, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 14 | 301773 | 4 |  | Ready to autostart, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 15 | 301773 | 4 |  | Ready to autostart, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 0 | 301774 | 4 |  | Load Group 1 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 1 | 301774 | 4 |  | Load Group 1 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 2 | 301774 | 4 |  | Load Group 1 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 3 | 301774 | 4 |  | Load Group 1 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 4 | 301774 | 4 |  | Load Group 1 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 5 | 301774 | 4 |  | Load Group 1 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 6 | 301774 | 4 |  | Load Group 1 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 7 | 301774 | 4 |  | Load Group 1 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 8 | 301774 | 4 |  | Load Group 1 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 9 | 301774 | 4 |  | Load Group 1 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 10 | 301774 | 4 |  | Load Group 1 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 11 | 301774 | 4 |  | Load Group 1 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 12 | 301774 | 4 |  | Load Group 1 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 13 | 301774 | 4 |  | Load Group 1 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 14 | 301774 | 4 |  | Load Group 1 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 15 | 301774 | 4 |  | Load Group 1 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 0 | 301775 | 4 |  | Load Group 2 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 1 | 301775 | 4 |  | Load Group 2 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 2 | 301775 | 4 |  | Load Group 2 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 3 | 301775 | 4 |  | Load Group 2 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 4 | 301775 | 4 |  | Load Group 2 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 5 | 301775 | 4 |  | Load Group 2 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 6 | 301775 | 4 |  | Load Group 2 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 7 | 301775 | 4 |  | Load Group 2 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 8 | 301775 | 4 |  | Load Group 2 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 9 | 301775 | 4 |  | Load Group 2 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 10 | 301775 | 4 |  | Load Group 2 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 11 | 301775 | 4 |  | Load Group 2 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 12 | 301775 | 4 |  | Load Group 2 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 13 | 301775 | 4 |  | Load Group 2 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 14 | 301775 | 4 |  | Load Group 2 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 15 | 301775 | 4 |  | Load Group 2 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 0 | 301776 | 4 |  | Load Group 3 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 1 | 301776 | 4 |  | Load Group 3 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 2 | 301776 | 4 |  | Load Group 3 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 3 | 301776 | 4 |  | Load Group 3 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 4 | 301776 | 4 |  | Load Group 3 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 5 | 301776 | 4 |  | Load Group 3 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 6 | 301776 | 4 |  | Load Group 3 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 7 | 301776 | 4 |  | Load Group 3 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 8 | 301776 | 4 |  | Load Group 3 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 9 | 301776 | 4 |  | Load Group 3 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 10 | 301776 | 4 |  | Load Group 3 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 11 | 301776 | 4 |  | Load Group 3 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 12 | 301776 | 4 |  | Load Group 3 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 13 | 301776 | 4 |  | Load Group 3 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 14 | 301776 | 4 |  | Load Group 3 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 15 | 301776 | 4 |  | Load Group 3 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 0 | 301777 | 4 |  | Load Group 4 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 1 | 301777 | 4 |  | Load Group 4 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 2 | 301777 | 4 |  | Load Group 4 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 3 | 301777 | 4 |  | Load Group 4 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 4 | 301777 | 4 |  | Load Group 4 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 5 | 301777 | 4 |  | Load Group 4 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 6 | 301777 | 4 |  | Load Group 4 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 7 | 301777 | 4 |  | Load Group 4 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 8 | 301777 | 4 |  | Load Group 4 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 9 | 301777 | 4 |  | Load Group 4 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 10 | 301777 | 4 |  | Load Group 4 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 11 | 301777 | 4 |  | Load Group 4 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 12 | 301777 | 4 |  | Load Group 4 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 13 | 301777 | 4 |  | Load Group 4 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 14 | 301777 | 4 |  | Load Group 4 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 15 | 301777 | 4 |  | Load Group 4 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 0 | 301778 | 4 |  | Load Group 5 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 1 | 301778 | 4 |  | Load Group 5 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 2 | 301778 | 4 |  | Load Group 5 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 3 | 301778 | 4 |  | Load Group 5 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 4 | 301778 | 4 |  | Load Group 5 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 5 | 301778 | 4 |  | Load Group 5 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 6 | 301778 | 4 |  | Load Group 5 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 7 | 301778 | 4 |  | Load Group 5 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 8 | 301778 | 4 |  | Load Group 5 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 9 | 301778 | 4 |  | Load Group 5 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 10 | 301778 | 4 |  | Load Group 5 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 11 | 301778 | 4 |  | Load Group 5 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 12 | 301778 | 4 |  | Load Group 5 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 13 | 301778 | 4 |  | Load Group 5 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 14 | 301778 | 4 |  | Load Group 5 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 15 | 301778 | 4 |  | Load Group 5 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 0 | 301779 | 4 |  | Load Group 6 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 1 | 301779 | 4 |  | Load Group 6 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 2 | 301779 | 4 |  | Load Group 6 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 3 | 301779 | 4 |  | Load Group 6 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 4 | 301779 | 4 |  | Load Group 6 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 5 | 301779 | 4 |  | Load Group 6 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 6 | 301779 | 4 |  | Load Group 6 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 7 | 301779 | 4 |  | Load Group 6 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 8 | 301779 | 4 |  | Load Group 6 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 9 | 301779 | 4 |  | Load Group 6 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 10 | 301779 | 4 |  | Load Group 6 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 11 | 301779 | 4 |  | Load Group 6 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 12 | 301779 | 4 |  | Load Group 6 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 13 | 301779 | 4 |  | Load Group 6 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 14 | 301779 | 4 |  | Load Group 6 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 15 | 301779 | 4 |  | Load Group 6 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 0 | 301780 | 4 |  | Load Group 7 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 1 | 301780 | 4 |  | Load Group 7 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 2 | 301780 | 4 |  | Load Group 7 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 3 | 301780 | 4 |  | Load Group 7 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 4 | 301780 | 4 |  | Load Group 7 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 5 | 301780 | 4 |  | Load Group 7 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 6 | 301780 | 4 |  | Load Group 7 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 7 | 301780 | 4 |  | Load Group 7 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 8 | 301780 | 4 |  | Load Group 7 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 9 | 301780 | 4 |  | Load Group 7 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 10 | 301780 | 4 |  | Load Group 7 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 11 | 301780 | 4 |  | Load Group 7 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 12 | 301780 | 4 |  | Load Group 7 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 13 | 301780 | 4 |  | Load Group 7 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 14 | 301780 | 4 |  | Load Group 7 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 15 | 301780 | 4 |  | Load Group 7 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 0 | 301781 | 4 |  | Load Group 8 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 1 | 301781 | 4 |  | Load Group 8 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 2 | 301781 | 4 |  | Load Group 8 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 3 | 301781 | 4 |  | Load Group 8 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 4 | 301781 | 4 |  | Load Group 8 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 5 | 301781 | 4 |  | Load Group 8 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 6 | 301781 | 4 |  | Load Group 8 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 7 | 301781 | 4 |  | Load Group 8 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 8 | 301781 | 4 |  | Load Group 8 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 9 | 301781 | 4 |  | Load Group 8 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 10 | 301781 | 4 |  | Load Group 8 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 11 | 301781 | 4 |  | Load Group 8 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 12 | 301781 | 4 |  | Load Group 8 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 13 | 301781 | 4 |  | Load Group 8 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 14 | 301781 | 4 |  | Load Group 8 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 15 | 301781 | 4 |  | Load Group 8 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 0 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 1 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 2 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 3 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 4 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 5 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 6 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 7 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 8 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 9 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 10 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 11 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 12 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 13 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 14 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 15 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 0 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 1 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 2 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 3 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 4 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 5 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 6 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 7 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 8 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 9 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 10 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 11 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 12 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 13 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 14 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 15 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 0 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 1 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 2 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 3 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 4 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 5 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 6 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 7 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 8 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 9 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 10 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 11 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 12 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 13 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 14 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 15 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 0 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 1 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 2 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 3 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 4 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 5 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 6 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 7 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 8 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 9 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 10 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 11 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 12 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 13 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 14 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 15 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 0 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 1 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 2 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 3 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 4 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 5 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 6 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 7 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 8 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 9 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 10 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 11 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 12 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 13 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 14 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 15 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 0 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 1 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 2 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 3 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 4 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 5 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 6 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 7 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 8 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 9 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 10 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 11 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 12 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 13 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 14 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 15 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 0 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 1 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 2 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 3 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 4 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 5 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 6 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 7 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 8 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 9 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 10 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 11 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 12 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 13 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 14 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 15 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 0 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 1 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 2 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 3 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 4 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 5 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 6 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 7 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 8 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 9 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 10 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 11 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 12 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 13 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 14 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 15 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 0 | 301790 | 4 |  | Load Group 1 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 1 | 301790 | 4 |  | Load Group 1 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 2 | 301790 | 4 |  | Load Group 1 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 3 | 301790 | 4 |  | Load Group 1 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 4 | 301790 | 4 |  | Load Group 1 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 5 | 301790 | 4 |  | Load Group 1 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 6 | 301790 | 4 |  | Load Group 1 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 7 | 301790 | 4 |  | Load Group 1 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 8 | 301790 | 4 |  | Load Group 1 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 9 | 301790 | 4 |  | Load Group 1 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 10 | 301790 | 4 |  | Load Group 1 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 11 | 301790 | 4 |  | Load Group 1 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 12 | 301790 | 4 |  | Load Group 1 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 13 | 301790 | 4 |  | Load Group 1 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 14 | 301790 | 4 |  | Load Group 1 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 15 | 301790 | 4 |  | Load Group 1 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 0 | 301791 | 4 |  | Load Group 2 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 1 | 301791 | 4 |  | Load Group 2 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 2 | 301791 | 4 |  | Load Group 2 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 3 | 301791 | 4 |  | Load Group 2 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 4 | 301791 | 4 |  | Load Group 2 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 5 | 301791 | 4 |  | Load Group 2 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 6 | 301791 | 4 |  | Load Group 2 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 7 | 301791 | 4 |  | Load Group 2 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 8 | 301791 | 4 |  | Load Group 2 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 9 | 301791 | 4 |  | Load Group 2 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 10 | 301791 | 4 |  | Load Group 2 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 11 | 301791 | 4 |  | Load Group 2 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 12 | 301791 | 4 |  | Load Group 2 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 13 | 301791 | 4 |  | Load Group 2 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 14 | 301791 | 4 |  | Load Group 2 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 15 | 301791 | 4 |  | Load Group 2 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 0 | 301792 | 4 |  | Load Group 3 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 1 | 301792 | 4 |  | Load Group 3 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 2 | 301792 | 4 |  | Load Group 3 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 3 | 301792 | 4 |  | Load Group 3 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 4 | 301792 | 4 |  | Load Group 3 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 5 | 301792 | 4 |  | Load Group 3 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 6 | 301792 | 4 |  | Load Group 3 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 7 | 301792 | 4 |  | Load Group 3 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 8 | 301792 | 4 |  | Load Group 3 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 9 | 301792 | 4 |  | Load Group 3 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 10 | 301792 | 4 |  | Load Group 3 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 11 | 301792 | 4 |  | Load Group 3 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 12 | 301792 | 4 |  | Load Group 3 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 13 | 301792 | 4 |  | Load Group 3 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 14 | 301792 | 4 |  | Load Group 3 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 15 | 301792 | 4 |  | Load Group 3 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 0 | 301793 | 4 |  | Load Group 4 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 1 | 301793 | 4 |  | Load Group 4 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 2 | 301793 | 4 |  | Load Group 4 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 3 | 301793 | 4 |  | Load Group 4 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 4 | 301793 | 4 |  | Load Group 4 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 5 | 301793 | 4 |  | Load Group 4 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 6 | 301793 | 4 |  | Load Group 4 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 7 | 301793 | 4 |  | Load Group 4 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 8 | 301793 | 4 |  | Load Group 4 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 9 | 301793 | 4 |  | Load Group 4 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 10 | 301793 | 4 |  | Load Group 4 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 11 | 301793 | 4 |  | Load Group 4 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 12 | 301793 | 4 |  | Load Group 4 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 13 | 301793 | 4 |  | Load Group 4 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 14 | 301793 | 4 |  | Load Group 4 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 15 | 301793 | 4 |  | Load Group 4 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 0 | 301794 | 4 |  | Load Group 5 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 1 | 301794 | 4 |  | Load Group 5 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 2 | 301794 | 4 |  | Load Group 5 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 3 | 301794 | 4 |  | Load Group 5 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 4 | 301794 | 4 |  | Load Group 5 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 5 | 301794 | 4 |  | Load Group 5 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 6 | 301794 | 4 |  | Load Group 5 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 7 | 301794 | 4 |  | Load Group 5 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 8 | 301794 | 4 |  | Load Group 5 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 9 | 301794 | 4 |  | Load Group 5 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 10 | 301794 | 4 |  | Load Group 5 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 11 | 301794 | 4 |  | Load Group 5 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 12 | 301794 | 4 |  | Load Group 5 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 13 | 301794 | 4 |  | Load Group 5 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 14 | 301794 | 4 |  | Load Group 5 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 15 | 301794 | 4 |  | Load Group 5 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 0 | 301795 | 4 |  | Load Group 6 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 1 | 301795 | 4 |  | Load Group 6 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 2 | 301795 | 4 |  | Load Group 6 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 3 | 301795 | 4 |  | Load Group 6 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 4 | 301795 | 4 |  | Load Group 6 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 5 | 301795 | 4 |  | Load Group 6 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 6 | 301795 | 4 |  | Load Group 6 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 7 | 301795 | 4 |  | Load Group 6 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 8 | 301795 | 4 |  | Load Group 6 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 9 | 301795 | 4 |  | Load Group 6 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 10 | 301795 | 4 |  | Load Group 6 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 11 | 301795 | 4 |  | Load Group 6 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 12 | 301795 | 4 |  | Load Group 6 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 13 | 301795 | 4 |  | Load Group 6 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 14 | 301795 | 4 |  | Load Group 6 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 15 | 301795 | 4 |  | Load Group 6 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 0 | 301796 | 4 |  | Load Group 7 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 1 | 301796 | 4 |  | Load Group 7 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 2 | 301796 | 4 |  | Load Group 7 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 3 | 301796 | 4 |  | Load Group 7 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 4 | 301796 | 4 |  | Load Group 7 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 5 | 301796 | 4 |  | Load Group 7 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 6 | 301796 | 4 |  | Load Group 7 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 7 | 301796 | 4 |  | Load Group 7 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 8 | 301796 | 4 |  | Load Group 7 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 9 | 301796 | 4 |  | Load Group 7 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 10 | 301796 | 4 |  | Load Group 7 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 11 | 301796 | 4 |  | Load Group 7 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 12 | 301796 | 4 |  | Load Group 7 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 13 | 301796 | 4 |  | Load Group 7 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 14 | 301796 | 4 |  | Load Group 7 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 15 | 301796 | 4 |  | Load Group 7 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 0 | 301797 | 4 |  | Load Group 8 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 1 | 301797 | 4 |  | Load Group 8 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 2 | 301797 | 4 |  | Load Group 8 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 3 | 301797 | 4 |  | Load Group 8 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 4 | 301797 | 4 |  | Load Group 8 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 5 | 301797 | 4 |  | Load Group 8 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 6 | 301797 | 4 |  | Load Group 8 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 7 | 301797 | 4 |  | Load Group 8 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 8 | 301797 | 4 |  | Load Group 8 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 9 | 301797 | 4 |  | Load Group 8 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 10 | 301797 | 4 |  | Load Group 8 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 11 | 301797 | 4 |  | Load Group 8 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 12 | 301797 | 4 |  | Load Group 8 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 13 | 301797 | 4 |  | Load Group 8 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 14 | 301797 | 4 |  | Load Group 8 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 15 | 301797 | 4 |  | Load Group 8 Enabled - ID 32 | BOOL |  |  |  | X | X | X
EIC measurements value | 26000 |  | 326001 | 4 |  | Engine Speed (SPN 190) | INT16u | AB | 0 | rpm |  |  | X
EIC measurements value | 26001 |  | 326002 | 4 |  | Engine Coolant Temperature (SPN 110) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26002 |  | 326003 | 4 |  | Engine Oil Pressure (SPN 100) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26003 |  | 326004 | 4 |  | Active Diagnostic Trouble Code Count (SPN 1218) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26004 |  | 326005 | 4 |  | Engine Oil Temperature 1 (SPN 175) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26005 |  | 326006 | 4 |  | Engine Fuel 1 Temperature 1 (SPN 174) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26006 |  | 326007 | 4 |  | Engine Intake Manifold #1 Pressure (SPN 102) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26007 |  | 326008 | 4 |  | Engine Intake 1 Air Temperature (SPN 172) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26008 |  | 326009 | 4 |  | Engine Coolant Level 1 (SPN 111) | INT16u | AB | 1 | perc |  |  | X
EIC measurements value | 26009 |  | 326010 | 4 |  | Engine Fuel Rate (SPN 183) | INT16u | AB | 1 | L/h |  |  | X
EIC measurements value | 26010 |  | 326011 | 4 |  | Charge air pressure (MDEC) | INT16u | AB | 0 | bar/psi |  |  | X
EIC measurements value | 26011 |  | 326012 | 4 |  | Engine Intake Manifold 1 Temperature (SPN 105) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26012 |  | 326013 | 4 |  | Driver's Demand Engine, Percent Torque (SPN 512) | INT16u | AB | 0 | perc |  |  | X
EIC measurements value | 26013 |  | 326014 | 4 |  | Actual Engine, Percent Torque (SPN 513) | INT16u | AB | 0 | perc |  |  | X
EIC measurements value | 26014 |  | 326015 | 4 |  | Accelerator Pedal Position 1 (SPN 91) | INT16u | AB | 0 | perc |  |  | X
EIC measurements value | 26015 |  | 326016 | 4 |  | Engine Percent Load At Current Speed (SPN 92) | INT16u | AB | 0 | perc |  |  | X
EIC measurements value | 26016 |  | 326017 | 4 |  | Engine Intake Air Pressure (SPN 106) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26017 |  | 326018 | 4 |  | Engine Exhaust Temperature (SPN 173) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26018 |  | 326019 | 4 |  | Engine Total Hours of Operation (SPN 247) | INT32u | ABCD | 0 | h |  |  | X
EIC measurements value | 26020 |  | 326021 | 4 |  | Engine Oil Filter Differential Pressure (SPN 99) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26021 |  | 326022 | 4 |  | Key Switch Battery Potential (SPN 158) | INT16u | AB | 1 | V |  |  | X
EIC measurements value | 26022 |  | 326023 | 4 |  | Engine Fuel Delivery Pressure (SPN 94) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26023 |  | 326024 | 4 |  | Engine Oil Level (SPN 98) | INT16u | AB | 1 | perc |  |  | X
EIC measurements value | 26024 |  | 326025 | 4 |  | Engine Crankcase Pressure 1 (SPN 101) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26025 |  | 326026 | 4 |  | Engine Coolant Pressure 1 (SPN 109) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26026 |  | 326027 | 4 |  | Water In Fuel Indicator 1 (SPN 97) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26027 |  | 326028 | 4 |  | Engine Turbocharger 1 Oil Temperature (SPN 176) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26028 |  | 326029 | 4 |  | Aftertreatment 1 Diesel Particulate Filter Intake Pressure (SPN 81) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26029 |  | 326030 | 4 |  | Engine Air Filter 1 Differential Pressure (SPN 107) | INT16u | AB | 3 | bar/psi |  |  | X
EIC measurements value | 26030 |  | 326031 | 4 |  | Engine Coolant Filter Differential Pressure (SPN 112) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26031 |  | 326032 | 4 |  | Barometric Pressure (SPN 108) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26032 |  | 326033 | 4 |  | Ambient Air Temperature (SPN 171) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26033 |  | 326034 | 4 |  | Engine Exhaust Manifold Bank 2 Temperature 1 (SPN 2433) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26034 |  | 326035 | 4 |  | Engine Exhaust Manifold Bank 1 Temperature 1 (SPN 2434) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26035 |  | 326036 | 4 |  | Temp. Winding 1 (ADEC) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26036 |  | 326037 | 4 |  | Temp. Winding 2 (ADEC) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26037 |  | 326038 | 4 |  | Temp. Winding 3 (ADEC) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26038 |  | 326039 | 4 |  | Auxiliary_Analog_Info (ADEC) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26039 |  | 326040 | 4 |  | Auxiliary_Analog_Info (ADEC) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26040 |  | 326041 | 4 |  | Engine Turbocharger 1 Compressor Outlet Temperature (ADEC) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26041 |  | 326042 | 4 |  | Engine Intercooler Temperature (SPN 52) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26042 |  | 326043 | 4 |  | Engine Trip Fuel (SPN 182) | INT32u | ABCD | 0 | L |  |  | X
EIC measurements value | 26044 |  | 326045 | 4 |  | Engine Total Fuel Used (SPN 250) | INT32u | ABCD | 0 | kL |  |  | X
EIC measurements value | 26046 |  | 326047 | 4 |  | Trip Fuel (Gaseous) (SPN 1039) | INT32u | ABCD | 0 | kg |  |  | X
EIC measurements value | 26048 |  | 326049 | 4 |  | Total Fuel Used (Gaseous) (SPN 1040) | INT32u | ABCD | 1 | ton |  |  | X
EIC measurements value | 26050 |  | 326051 | 4 |  | Trip Average Fuel Rate (SPN 1029) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26051 |  | 326052 | 4 |  | Engine Rated Power (SPN 166) | INT16u | AB | 0 | kWm |  |  | X
EIC measurements value | 26052 |  | 326053 | 4 |  | Engine power (ADEC) | INT16u | AB | 0 | kW |  |  | X
EIC measurements value | 26053 |  | 326054 | 4 |  | Engine Intake Manifold #1 Absolute Pressure (SPN 3563) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26054 |  | 326055 | 4 |  | Diesel Particulate Filter Lamp Command (SPN 3697) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26055 |  | 326056 | 4 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Inhibit Switch (SPN 3703) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26056 |  | 326057 | 4 |  | Aftertreatment Diesel Particulate Filter Active Regeneration Status (SPN 3700) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26057 |  | 326058 | 4 |  | Aftertreatment Diesel Particulate Filter Status (SPN 3701) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26058 |  | 326059 | 4 |  | Exhaust System High Temperature Lamp Command (SPN 3698) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26059 |  | 326060 | 4 |  | Engine Air Filter 2 Differential Pressure (SPN 2809) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26060 |  | 326061 | 4 |  | Engine Fuel Supply Pump Intake Absolute Pressure (SPN 1381) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26061 |  | 326062 | 4 |  | Engine Fuel Filter (suction side) Differential Pressure (SPN 1382) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26062 |  | 326063 | 4 |  | Engine Fuel Filter Differential Pressure (SPN 95) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26063 |  | 326064 | 4 |  | Speed demand Source (MDEC) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26064 |  | 326065 | 4 |  | P-Lube Oil Limit LO (MDEC) | INT16u | AB | 0 | bar/psi |  |  | X
EIC measurements value | 26065 |  | 326066 | 4 |  | P-Lube Oil Limit LOLO (MDEC) | INT16u | AB | 0 | bar/psi |  |  | X
EIC measurements value | 26066 |  | 326067 | 4 |  | P-Fuel (MDEC) | INT16u | AB | 0 | bar/psi |  |  | X
EIC measurements value | 26067 |  | 326068 | 4 |  | T-Coolant Limit HI (MDEC) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26068 |  | 326069 | 4 |  | T-Coolant Limit HIHI (MDEC) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26069 |  | 326070 | 4 |  | T-Coolant Intercooler (MDEC) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26070 |  | 326071 | 4 |  | Engine ECU Temperature (SPN 1136) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26071 |  | 326072 | 4 |  | Actual Droop (MDEC) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26072 |  | 326073 | 4 |  | Injection Quantity Act.DBR % (MDEC) | INT16u | AB | 0 | perc |  |  | X
EIC measurements value | 26073 |  | 326074 | 4 |  | Engine Speed Camshaft (MDEC) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26074 |  | 326075 | 4 |  | T-Lube Oil Limit HI (MDEC) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26075 |  | 326076 | 4 |  | T-Lube Oil Limit HIHI (MDEC) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26076 |  | 326077 | 4 |  | Feedback Speed Demand analog (MDEC) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26077 |  | 326078 | 4 |  | Stop signal active (MDEC) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26078 |  | 326079 | 4 |  | Exhaust Port Temperature 01 (SPN 1137) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26079 |  | 326080 | 4 |  | Exhaust Port Temperature 02 (SPN 1138) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26080 |  | 326081 | 4 |  | Exhaust Port Temperature 03 (SPN 1139) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26081 |  | 326082 | 4 |  | Exhaust Port Temperature 04 (SPN 1140) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26082 |  | 326083 | 4 |  | Exhaust Port Temperature 05 (SPN 1141) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26083 |  | 326084 | 4 |  | Exhaust Port Temperature 06 (SPN 1142) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26084 |  | 326085 | 4 |  | Exhaust Port Temperature 07 (SPN 1143) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26085 |  | 326086 | 4 |  | Exhaust Port Temperature 08 (SPN 1144) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26086 |  | 326087 | 4 |  | Exhaust Port Temperature 09 (SPN 1145) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26087 |  | 326088 | 4 |  | Exhaust Port Temperature 10 (SPN 1146) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26088 |  | 326089 | 4 |  | Exhaust Port Temperature 11 (SPN 1147) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26089 |  | 326090 | 4 |  | Exhaust Port Temperature 12 (SPN 1148) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26090 |  | 326091 | 4 |  | Exhaust Port Temperature 13 (SPN 1149) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26091 |  | 326092 | 4 |  | Exhaust Port Temperature 14 (SPN 1150) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26092 |  | 326093 | 4 |  | Exhaust Port Temperature 15 (SPN 1151) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26093 |  | 326094 | 4 |  | Exhaust Port Temperature 16 (SPN 1152) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26094 |  | 326095 | 4 |  | Engine Filtered Fuel Delivery Pressure (SPN 5579) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26095 |  | 326096 | 4 |  | Engine Coolant Temperature 2 (SPN 4076) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26096 |  | 326097 | 4 |  | Engine Coolant Temperature 3 (SPN 6209) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26097 |  | 326098 | 4 |  | Engine Coolant Pump Outlet Temperature (SPN 4193) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26098 |  | 326099 | 4 |  | Engine Auxiliary Coolant Temperature (SPN 1212) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26099 |  | 326100 | 4 |  | Engine Turbocharger 1 Turbine Intake Temperature (SPN 1180) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26100 |  | 326101 | 4 |  | Engine Turbocharger 2 Turbine Intake Temperature (SPN 1181) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26101 |  | 326102 | 4 |  | Engine Auxiliary Coolant Pressure (SPN 1203) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26102 |  | 326103 | 4 |  | Specific Humidity (SPN 4490) | INT16u | AB | 1 | g/kg |  |  | X
EIC measurements value | 26103 |  | 326104 | 4 |  | Engine Turbocharger 2 Speed (SPN 1169) | INT16u | AB | 0 | rpm |  |  | X
EIC measurements value | 26104 |  | 326105 | 4 |  | Engine Turbocharger 3 Speed (SPN 1170) | INT16u | AB | 0 | rpm |  |  | X
EIC measurements value | 26105 |  | 326106 | 4 |  | Trip Engine Running Time (SPN 1036) | INT32u | ABCD | 0 | h |  |  | X
EIC measurements value | 26107 |  | 326108 | 4 |  | Trip Idle Time (SPN 1037) | INT32u | ABCD | 0 | h |  |  | X
EIC measurements value | 26109 |  | 326110 | 4 |  | Engine Fan 1 Estimated Percent Speed (SPN 975) | INT16u | AB | 1 | perc |  |  | X
EIC measurements value | 26110 |  | 326111 | 4 |  | Engine Turbocharger 1 Speed (SPN 103) | INT16u | AB | 0 | rpm |  |  | X
EIC measurements value | 26111 |  | 326112 | 4 |  | Nominal Friction - Percent Torque (SPN 514) | INT16u | AB | 0 | perc |  |  | X
EIC measurements value | 26112 |  | 326113 | 4 |  | Engine's Desired Operating Speed (SPN 515) | INT16u | AB | 0 | rpm |  |  | X
EIC measurements value | 26113 |  | 326114 | 4 |  | Engine Intake Manifold 2 Temperature (SPN 1131) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26114 |  | 326115 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Volume (SPN 1761) | INT16u | AB | 1 | perc |  |  | X
EIC measurements value | 26115 |  | 326116 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Temperature 1 (SPN 3031) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26116 |  | 326117 | 4 |  | Aftertreatment 1 SCR Intake NOx 1 (SPN 3216) | INT16u | AB | 0 | ppm |  |  | X
EIC measurements value | 26117 |  | 326118 | 4 |  | Aftertreatment 1 Outlet NOx 1 (SPN 3226) | INT16u | AB | 0 | ppm |  |  | X
EIC measurements value | 26118 |  | 326119 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Actual Dosing Quantity (SPN 4331) | INT16u | AB | 1 | g/h |  |  | X
EIC measurements value | 26119 |  | 326120 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Doser 1 Absolute Pressure (SPN 4334) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26120 |  | 326121 | 4 |  | Aftertreatment 1 SCR Dosing Air Assist Valve (SPN 4336) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26121 |  | 326122 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Dosing Requested Quantity (SPN 4348) | INT16u | AB | 0 | g/h |  |  | X
EIC measurements value | 26122 |  | 326123 | 4 |  | Aftertreatment 1 SCR Intake Temperature (SPN 4360) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26123 |  | 326124 | 4 |  | Aftertreatment 1 SCR Outlet Temperature (SPN 4363) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26124 |  | 326125 | 4 |  | Aftertreatment 2 SCR Intake NOx 1 (SPN 3255) | INT16u | AB | 0 | ppm |  |  | X
EIC measurements value | 26125 |  | 326126 | 4 |  | Aftertreatment 2 Outlet NOx 1 (SPN 3265) | INT16u | AB | 0 | ppm |  |  | X
EIC measurements value | 26126 |  | 326127 | 4 |  | Aftertreatment 2 Diesel Exhaust Fluid Actual Dosing Quantity (SPN 4384) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26127 |  | 326128 | 4 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser 1 Absolute Pressure (SPN 4387) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26128 |  | 326129 | 4 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser 1 Temperature (SPN 4390) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26129 |  | 326130 | 4 |  | Aftertreatment 2 Diesel Exhaust Fluid Dosing Requested Quantity (SPN 4401) | INT16u | AB | 1 | g/h |  |  | X
EIC measurements value | 26130 |  | 326131 | 4 |  | Aftertreatment 2 SCR Intake Temperature (SPN 4413) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26131 |  | 326132 | 4 |  | Aftertreatment 2 SCR Outlet Temperature (SPN 4415) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26132 |  | 326133 | 4 |  | Engine Oil Filter Outlet Pressure (SPN 3549) | INT16u | AB | 2 | bar/psi |  |  | X
EIC measurements value | 26133 |  | 326134 | 4 |  | Engine Operating State (SPN 3543) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26134 |  | 326135 | 4 |  | Source Address of Controlling Device for Engine Control (SPN 1483) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26135 |  | 326136 | 4 |  | Engine Rated Speed (SPN 189) | INT16u | AB | 0 | rpm |  |  | X
EIC measurements value | 26136 |  | 326137 | 4 |  | Engine Speed At Idle, Point 1 (SPN 188) | INT16u | AB | 0 | rpm |  |  | X
EIC measurements value | 26137 |  | 326138 | 4 |  | Fuel Consumption g/KWh (MTU) | INT16u | AB | 0 | g/kWh |  |  | X
EIC measurements value | 26138 |  | 326139 | 4 |  | Engine Status of Start procedure (MTU) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26139 |  | 326140 | 4 |  | Exhaust Port Temperature 17 (SPN 1153) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26140 |  | 326141 | 4 |  | Exhaust Port Temperature 18 (SPN 1154) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26141 |  | 326142 | 4 |  | Exhaust Port Temperature 19 (SPN 1155) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26142 |  | 326143 | 4 |  | Exhaust Port Temperature 20 (SPN 1156) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26143 |  | 326144 | 4 |  | UREA Level (Scania) | INT16u | AB | 0 | perc |  |  | X
EIC measurements value | 26144 |  | 326145 | 4 |  | Aftertreatment SCR Operator Inducement Severity (SPN 5246) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26145 |  | 326146 | 4 |  | Aftertreatment Diesel Exhaust Fluid Tank Low Level Indicator (SPN 5245) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26146 |  | 326147 | 4 |  | Aftertreatment 1 Diesel Particulate Filter Outlet Temperature (SPN 3246) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26147 |  | 326148 | 4 |  | Aftertreatment 1 Diesel Particulate Filter Time to Next Active Regeneration (SPN 5978) | INT32u | ABCD | 1 | h |  |  | X
EIC measurements value | 26149 |  | 326150 | 4 |  | Engine Charge Air Cooler 1 Outlet Temperature (SPN 2630) | INT16u | AB | 1 | Deg C/F |  |  | X
EIC measurements value | 26150 |  | 326151 | 4 |  | Aftertreatment 1 Diesel Particulate Filter Soot Load Percent (SPN 3719) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26151 |  | 326152 | 4 |  | Purging Active (Scania) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26152 |  | 326153 | 4 |  | Limit Lamp Status (MTU) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26153 |  | 326154 | 4 |  | Battery Charger 1 Output Voltage (SPN 4992) | INT16u | AB | 0 | V |  |  | X
EIC measurements value | 26154 |  | 326155 | 4 |  | Battery Charger 1 Output Current (SPN 4993) | INT16u | AB | 0 | A |  |  | X
EIC measurements value | 26155 |  | 326156 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Average Consumption (SPN 3829) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26156 |  | 326157 | 4 |  | Time left to torque reduction (Volvo) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26157 |  | 326158 | 4 |  | Time left to servere torque reduction (Volvo) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26158 |  | 326159 | 4 |  | SCR inducement severity (Volvo) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26159 |  | 326160 | 4 |  | SCR inducement reason (Volvo) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26160 |  | 326161 | 4 |  | Engine Derate Request (SPN 3644) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26161 |  | 326162 | 4 |  | Engine Demand, Percent Torque (SPN 2432) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26162 |  | 326163 | 4 |  | Aftertreatment 1 Intake Percent Oxygen 1 (SPN 3217) | INT16u | AB | 0 | perc |  |  | X
EIC measurements value | 26163 |  | 326164 | 4 |  | Aftertreatment 1 Outlet Percent Oxygen 1 (SPN 3227) | INT16u | AB | 0 | perc |  |  | X
EIC measurements value | 26164 |  | 326165 | 4 |  | Engine Throttle Actuator 1 Control Command (SPN 3464) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26165 |  | 326166 | 4 |  | Long-term Fuel Trim - Bank 1 (SPN 4237) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26166 |  | 326167 | 4 |  | Short-term Fuel Trim - Bank 1 (SPN 4236) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26167 |  | 326168 | 4 |  | Engine Exhaust Bank 1 O2 Sensor Closed Loop Operation (SPN 4240) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26168 |  | 326169 | 4 |  | Engine Desired Ignition Timing 1 (SPN 1433) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26169 |  | 326170 | 4 |  | Engine Actual Ignition Timing (SPN 1436) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26170 |  | 326171 | 4 |  | EDC4 CAN Status (EMR) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26171 |  | 326172 | 4 |  | Engine Starter Mode (SPN 1675) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26172 |  | 326173 | 4 |  | Actual Maximum Available Engine - Percent Torque (SPN 3357) | INT16u | AB | 0 | perc |  |  | X
EIC measurements value | 26173 |  | 326174 | 4 |  | Engine Coolant Pre-heated State (SPN 3553) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26174 |  | 326175 | 4 |  | Engine Safety and Protection Override Status (MTU) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26175 |  | 326176 | 4 |  | Engine Cylinder Cut-off (MTU) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26176 |  | 326177 | 4 |  | Engine Running State (MTU) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26177 |  | 326178 | 4 |  | External Stop State (MTU) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26178 |  | 326179 | 4 |  | Requested Absolute Torque (MTU) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26179 |  | 326180 | 4 |  | Source of Current Speed Demand (MTU) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26180 |  | 326181 | 4 |  | Engine Demanded Operating Speed (MTU) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26181 |  | 326182 | 4 |  | Feedback of Speed Demand CAN (MTU) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26182 |  | 326183 | 4 |  | Feedback of Speed Demand Analogue Input (MTU) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26183 |  | 326184 | 4 |  | Speed Demand Fail Mode (MTU) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26184 |  | 326185 | 4 |  | Engine Shutdown Override Switch (SPN 1237) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26185 |  | 326186 | 4 |  | Engine Requested Speed (SPN 898) | INT16u | AB | 0 | rpm |  |  | X
EIC measurements value | 26186 |  | 326187 | 4 |  | Escape Mode Enable Flag (Isuzu) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26187 |  | 326188 | 4 |  | Inducement Timer (Isuzu) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26188 |  | 326189 | 4 |  | Inducement Level (Isuzu) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26189 |  | 326190 | 4 |  | Urea Tank Level (Isuzu) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26190 |  | 326191 | 4 |  | Urea Tank Level Indicator (Isuzu) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26191 |  | 326192 | 4 |  | Level Indicator (Amber) Action (Isuzu) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26192 |  | 326193 | 4 |  | DPF Amber Lamp Mode (Isuzu) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26193 |  | 326194 | 4 |  | EXH.SYSTEM lamp (Isuzu) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26194 |  | 326195 | 4 |  | DPF Green Lamp Mode (Isuzu) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26195 |  | 326196 | 4 |  | NO POWER Lamp (Isuzu) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26196 |  | 326197 | 4 |  | Engine Intake Manifold 3 Temperature (SPN 1132) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26197 |  | 326198 | 4 |  | Engine Intake Manifold 4 Temperature (SPN 1133) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26198 |  | 326199 | 4 |  | Engine Oil Filter Intake Pressure (SPN 1208) | INT16u | AB | 0 | bar/psi |  |  | X
EIC measurements value | 26199 |  | 326200 | 4 |  | Engine Turbocharger 2 Boost Pressure (SPN 1128) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26200 |  | 326201 | 4 |  | Engine Fuel 1 Injector Metering Rail 1 Pressure (SPN 157) | INT16u | AB | 0 | bar/psi |  |  | X
EIC measurements value | 26201 |  | 326202 | 4 |  | Battery Potential / Power Input 1 (SPN 168) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26202 |  | 326203 | 4 |  | Dosing Module Status (JCB) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26203 |  | 326204 | 4 |  | Actual Reducing Agent Quantity (JCB) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26204 |  | 326205 | 4 |  | Aftertreatment Lamp (JCB) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26205 |  | 326206 | 4 |  | Refresh Status Byte (JCB) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26206 |  | 326207 | 4 |  | SCR Monitor (JCB) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26207 |  | 326208 | 4 |  | Successful Running Refreshes (JCB) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26208 |  | 326209 | 4 |  | Successful Stationary Refreshes (JCB) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26209 |  | 326210 | 4 |  | Engine Rating (JCB) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26210 |  | 326211 | 4 |  | Aftertreatment 1 Exhaust Temperature 1 (SPN 3241) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26211 |  | 326212 | 4 |  | Humidity Derate Percentage (Perkins/CAT) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26212 |  | 326213 | 4 |  | Engine Emergency (Immediate) Shutdown Indication (SPN 3607) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26213 |  | 326214 | 4 |  | Number of EIO Activations (Volvo EMS2.4) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26214 |  | 326215 | 4 |  | Accumulated EIO time (Volvo EMS2.4) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26215 |  | 326216 | 4 |  | Time left of EIO Operation (Volvo EMS2.4) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26216 |  | 326217 | 4 |  | Remaining Service Hours (Hatz) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26217 |  | 326218 | 4 |  | Wheel Based Vehicle Speed (SPN 84) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26218 |  | 326219 | 4 |  | Aftertreatment 1 Exhaust Gas Mass Flow Rate (SPN 3236) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26219 |  | 326220 | 4 |  | Aftertreatment 1 Diesel Particulate Filter Differential Pressure (SPN 3251) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26220 |  | 326221 | 4 |  | Aftertreatment 1 Diesel Oxidation Catalyst Intake Temperature (SPN 4765) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26221 |  | 326222 | 4 |  | Aftertreatment 1 Diesel Particulate Filter Intake Temperature (SPN 3242) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26222 |  | 326223 | 4 |  | Phys. Injection quantity (Hatz) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26223 |  | 326224 | 4 |  | Phys. Torque (Hatz) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26224 |  | 326225 | 4 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Out of Neutral (SPN 3708) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26225 |  | 326226 | 4 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Parking Brake Not Set (SPN 3710) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26226 |  | 326227 | 4 |  | Operator Inducement Time to Torque Derate Level 1 (SPN 7426) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26227 |  | 326228 | 4 |  | Operator Inducement Time to Torque Derate Level 2 (SPN 7428) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26228 |  | 326229 | 4 |  | Alternator 1 Status (SPN 3353) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26252 |  | 326253 | 4 |  | Engine Throttle Valve 1 Position 1 (SPN 51) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26253 |  | 326254 | 4 |  | Engine Fuel Valve 1 Intake Absolute Pressure (SPN 1390) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26254 |  | 326255 | 4 |  | Engine Turbocharger 1 Boost Pressure (SPN 1127) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26255 |  | 326256 | 4 |  | Engine Cylinder 1 Ignition Timing (SPN 1413) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26256 |  | 326257 | 4 |  | Engine Intake Air Mass Flow Rate (SPN 132) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26257 |  | 326258 | 4 |  | Engine Lambda (Yuchai) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26258 |  | 326259 | 4 |  | Aftertreatment 1 Diesel Particulate Filter Ash Load Percent (SPN 3720) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26259 |  | 326260 | 4 |  | DPF Regeneration State (Scania) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26260 |  | 326261 | 4 |  | DPF Regeneration Countdown Timer (Scania) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26261 |  | 326262 | 4 |  | DEF Level (FPT) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26262 |  | 326263 | 4 |  | DEF Quality (FPT) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26263 |  | 326264 | 4 |  | DEF Technical Failure (FPT) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26264 |  | 326265 | 4 |  | Cold Start Heater Status (FPT) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26265 |  | 326266 | 4 |  | Fuel Filter Heater Status (FPT) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26266 |  | 326267 | 4 |  | Low Idle Increase Desired (FPT) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26267 |  | 326268 | 4 |  | Urea level inducement state (Scania) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26268 |  | 326269 | 4 |  | Emission-OBD inducement state (Scania) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26269 |  | 326270 | 4 |  | Emission-OBD inducement failure reason (Scania) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26270 |  | 326271 | 4 |  | Engine Diesel Particulate Filter Regeneration State (JDEC STAGE V) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26271 |  | 326272 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Concentration (SPN 3516) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26272 |  | 326273 | 4 |  | Engine Requested Fuel Valve 1 Position (SPN 1765) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26273 |  | 326274 | 4 |  | Engine Oil Priming State (SPN 3551) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26274 |  | 326275 | 4 |  | Fuel Pump Primer Status (SPN 4083) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26275 |  | 326276 | 4 |  | Sensor supply voltage 1 (SPN 3509) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26276 |  | 326277 | 4 |  | Sensor supply voltage 2 (SPN 3510) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26277 |  | 326278 | 4 |  | Accelerator Pedal Position 2 (SPN 29) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26278 |  | 326279 | 4 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Temporary System Lockout (SPN 3714) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26279 |  | 326280 | 4 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Permanent System Lockout (SPN 3715) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26280 |  | 326281 | 4 |  | Aftertreatment Ambient Air Temperature (SPN 7441) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26281 |  | 326282 | 4 |  | Aftertreatment Thermal Management Status (SPN 7332) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26282 |  | 326283 | 4 |  | Aftertreatment Engine Speed Increase request (SPN 7502) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26283 |  | 326284 | 4 |  | Aftertreatment Engine Load Request (SPN 7503) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26284 |  | 326285 | 4 |  | Feedback Engine Fueling State (SPN 5794) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26285 |  | 326286 | 4 |  | Engine Fueling Inhibit Allowed (SPN 5795) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26286 |  | 326287 | 4 |  | Blowby flow (Cummins H6) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26287 |  | 326288 | 4 |  | Fuel rail pressure (Cummins H6) | INT16u | AB | 0 | bar/psi |  |  | X
EIC measurements value | 26288 |  | 326289 | 4 |  | Timing rail pressure (Cummins H6) | INT16u | AB | 0 | bar/psi |  |  | X
EIC measurements value | 26289 |  | 326290 | 4 |  | Aftercooler water inlet temperature (Cummins H6) | INT16u | AB | 0 | Deg C/F |  |  | X
EIC measurements value | 26290 |  | 326291 | 4 |  | Fuel Rank position left (Cummins H6) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26291 |  | 326292 | 4 |  | Fuel Rank position right (Cummins H6) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26292 |  | 326293 | 4 |  | Intake Manifold pressure left (Cummins H6) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26293 |  | 326294 | 4 |  | Intake Manifold pressure right (Cummins H6) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26294 |  | 326295 | 4 |  | Intake Manifold Temperature left (Cummins H6) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26295 |  | 326296 | 4 |  | Intake Manifold Temperature right (Cummins H6) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26296 | 7 | 326297 | 4 |  | DPF lamp OFF | BOOL | [5 empty] | X
EIC measurements value | 26296 | 6 | 326297 | 4 |  | DPF lamp ON solid | BOOL | [5 empty] | X
EIC measurements value | 26296 | 5 | 326297 | 4 |  | DPF lamp ON blink | BOOL | [5 empty] | X
EIC measurements value | 26296 | 4 | 326297 | 4 |  | DPF Active Regeneration not activated | BOOL | [5 empty] | X
EIC measurements value | 26296 | 3 | 326297 | 4 |  | DPF Active Regeneration activated | BOOL | [5 empty] | X
EIC measurements value | 26296 | 2 | 326297 | 4 |  | DPF Active Regeneration needed | BOOL | [5 empty] | X
EIC measurements value | 26296 | 1 | 326297 | 4 |  | DPF Regeneration not needed | BOOL | [5 empty] | X
EIC measurements value | 26296 | 0 | 326297 | 4 |  | DPF Regeneration needed Lowest | BOOL | [5 empty] | X
EIC measurements value | 26297 | 7 | 326298 | 4 |  | DPF Regeneration needed Moderate | BOOL | [5 empty] | X
EIC measurements value | 26297 | 6 | 326298 | 4 |  | DPF Regeneration needed Highest | BOOL | [5 empty] | X
EIC measurements value | 26297 | 5 | 326298 | 4 |  | DPF Regeneration Not Inhibit | BOOL | [5 empty] | X
EIC measurements value | 26297 | 4 | 326298 | 4 |  | DPF Regeneration Inhibit | BOOL | [5 empty] | X
EIC measurements value | 26297 | 3 | 326298 | 4 |  | Exhaust system high temperature OFF | BOOL | [5 empty] | X
EIC measurements value | 26297 | 2 | 326298 | 4 |  | Exhaust system high temperature ON | BOOL | [5 empty] | X
EIC measurements value | 26297 | 1 | 326298 | 4 |  | MTU limit lamp OFF | BOOL | [5 empty] | X
EIC measurements value | 26297 | 0 | 326298 | 4 |  | MTU limit lamp ON solid | BOOL | [5 empty] | X
EIC measurements value | 26298 | 7 | 326299 | 4 |  | MTU limit lamp ON blink 1Hz | BOOL | [5 empty] | X
EIC measurements value | 26298 | 6 | 326299 | 4 |  | DEF level low lamp OFF | BOOL | [5 empty] | X
EIC measurements value | 26298 | 5 | 326299 | 4 |  | DEF level low lamp ON solid | BOOL | [5 empty] | X
EIC measurements value | 26298 | 4 | 326299 | 4 |  | DEF level low lamp ON blink | BOOL | [5 empty] | X
EIC measurements value | 26298 | 3 | 326299 | 4 |  | After run status | BOOL | [5 empty] | X
EIC measurements value | 26298 | 2 | 326299 | 4 |  | Volvo Penta Scr Inducement NOT ACTIVE | BOOL | [5 empty] | X
EIC measurements value | 26298 | 1 | 326299 | 4 |  | Volvo Penta Scr Inducement WARNING | BOOL | [5 empty] | X
EIC measurements value | 26298 | 1 | 326299 | 4 |  | EMPTY | BOOL | [5 empty] | X
EIC measurements value | 26299 | 7 | 326300 | 4 |  | Volvo Penta Scr Derate ACTIVE | BOOL | [5 empty] | X
EIC measurements value | 26299 | 6 | 326300 | 4 |  | Volvo Penta Pre severe Derate WARNING | BOOL | [5 empty] | X
EIC measurements value | 26299 | 5 | 326300 | 4 |  | Volvo Penta Severe Derate | BOOL | [5 empty] | X
EIC measurements value | 26299 | 4 | 326300 | 4 |  | Volvo Penta Temperature Override Derate | BOOL | [5 empty] | X
EIC measurements value | 26299 | 3 | 326300 | 4 |  | Volvo Penta Scr Inducement Reason OK | BOOL | [5 empty] | X
EIC measurements value | 26299 | 2 | 326300 | 4 |  | Volvo Penta Reagent Tank low | BOOL | [5 empty] | X
EIC measurements value | 26299 | 1 | 326300 | 4 |  | Volvo Penta Incorrect Reagent Quality | BOOL | [5 empty] | X
EIC measurements value | 26299 | 0 | 326300 | 4 |  | Volvo Penta Absence of Reagent Dosing | BOOL | [5 empty] | X
EIC measurements value | 26300 | 7 | 326301 | 4 |  | MTU TIER4 lamp ON blink 2Hz | BOOL | [5 empty] | X
EIC measurements value | 26300 | 6 | 326301 | 4 |  | MTU buzzer lamp OFF | BOOL | [5 empty] | X
EIC measurements value | 26300 | 5 | 326301 | 4 |  | MTU buzzer lamp ON solid | BOOL | [5 empty] | X
EIC measurements value | 26300 | 4 | 326301 | 4 |  | MTU buzzer lamp ON blink 1Hz | BOOL | [5 empty] | X
EIC measurements value | 26300 | 3 | 326301 | 4 |  | MTU buzzer lamp ON blink 2Hz | BOOL | [5 empty] | X
EIC measurements value | 26300 | 2 | 326301 | 4 |  | Alarm Yellow lamp OFF | BOOL | [5 empty] | X
EIC measurements value | 26300 | 1 | 326301 | 4 |  | Alarm Yellow lamp ON | BOOL | [5 empty] | X
EIC measurements value | 26300 | 0 | 326301 | 4 |  | Alarm Red lamp OFF | BOOL | [5 empty] | X
EIC measurements value | 26301 | 7 | 326302 | 4 |  | Alarm Red lamp ON | BOOL | [5 empty] | X
EIC measurements value | 26301 | 6 | 326302 | 4 |  | Engine fuel leak | BOOL | [5 empty] | X
EIC measurements value | 26301 | 5 | 326302 | 4 |  | Engine Wait to start | BOOL | [5 empty] | X
EIC measurements value | 26301 | 4 | 326302 | 4 |  | Engine Protect system shutdown | BOOL | [5 empty] | X
EIC measurements value | 26301 | 3 | 326302 | 4 |  | Engine Protect system appro shutdown | BOOL | [5 empty] | X
EIC measurements value | 26301 | 2 | 326302 | 4 |  | Engine alarm acknowledge | BOOL | [5 empty] | X
EIC measurements value | 26301 | 1 | 326302 | 4 |  | Engine ait shutoff command status | BOOL | [5 empty] | X
EIC measurements value | 26301 | 0 | 326302 | 4 |  | Engine overspeed test | BOOL | [5 empty] | X
EIC measurements value | 26302 | 7 | 326303 | 4 |  | Engine shutoff status | BOOL | [5 empty] | X
EIC measurements value | 26302 | 6 | 326303 | 4 |  | Manual purge ECU | BOOL | [5 empty] | X
EIC measurements value | 26302 | 5 | 326303 | 4 |  | Manual purge EIDSS | BOOL | [5 empty] | X
EIC measurements value | 26302 | 4 | 326303 | 4 |  | Force purge | BOOL | [5 empty] | X
EIC measurements value | 26302 | 3 | 326303 | 4 |  | JCB Amber blink | BOOL | [5 empty] | X
EIC measurements value | 26302 | 2 | 326303 | 4 |  | JCB Amber solid | BOOL | [5 empty] | X
EIC measurements value | 26302 | 1 | 326303 | 4 |  | JCB Red blink | BOOL | [5 empty] | X
EIC measurements value | 26302 | 0 | 326303 | 4 |  | JCB Red solid | BOOL | [5 empty] | X
EIC measurements value | 26303 | 7 | 326304 | 4 |  | JCB Engine emission system failure warning | BOOL | [5 empty] | X
EIC measurements value | 26303 | 6 | 326304 | 4 |  | JCB Engine emission system failure low | BOOL | [5 empty] | X
EIC measurements value | 26303 | 5 | 326304 | 4 |  | JCB Engine emission system failure high | BOOL | [5 empty] | X
EIC measurements value | 26303 | 4 | 326304 | 4 |  | JCB Particulate filter restricted high | BOOL | [5 empty] | X
EIC measurements value | 26303 | 3 | 326304 | 4 |  | JCB Particulate filter restricted very high | BOOL | [5 empty] | X
EIC measurements value | 26303 | 2 | 326304 | 4 |  | JCB Particulate filter restricted critical | BOOL | [5 empty] | X
EIC measurements value | 26303 | 1 | 326304 | 4 |  | DPF lamp - fast blink | BOOL | [5 empty] | X
EIC measurements value | 26303 | 0 | 326304 | 4 |  | DEF low level - Fast blink | BOOL | [5 empty] | X
EIC measurements value | 26304 | 7 | 326305 | 4 |  | Red lamp OFF | BOOL | [5 empty] | X
EIC measurements value | 26304 | 6 | 326305 | 4 |  | Red lamp solid | BOOL | [5 empty] | X
EIC measurements value | 26304 | 5 | 326305 | 4 |  | Red lamp blink | BOOL | [5 empty] | X
EIC measurements value | 26304 | 4 | 326305 | 4 |  | Red lamp fast blink | BOOL | [5 empty] | X
EIC measurements value | 26304 | 3 | 326305 | 4 |  | Yellow lamp OFF | BOOL | [5 empty] | X
EIC measurements value | 26304 | 2 | 326305 | 4 |  | Yellow lamp solid | BOOL | [5 empty] | X
EIC measurements value | 26304 | 1 | 326305 | 4 |  | Yellow lamp blink | BOOL | [5 empty] | X
EIC measurements value | 26304 | 0 | 326305 | 4 |  | Yellow lamp fast blink | BOOL | [5 empty] | X
EIC measurements value | 26305 | 7 | 326306 | 4 |  | MIL lamp OFF | BOOL | [5 empty] | X
EIC measurements value | 26305 | 6 | 326306 | 4 |  | MIL lamp solid | BOOL | [5 empty] | X
EIC measurements value | 26305 | 5 | 326306 | 4 |  | MIL lamp blink | BOOL | [5 empty] | X
EIC measurements value | 26305 | 4 | 326306 | 4 |  | MIL lamp fast blink | BOOL | [5 empty] | X
EIC measurements value | 26305 | 3 | 326306 | 4 |  | Engine emission system failure lamp off | BOOL | [5 empty] | X
EIC measurements value | 26305 | 2 | 326306 | 4 |  | Engine emission system failure lamp solid | BOOL | [5 empty] | X
EIC measurements value | 26305 | 1 | 326306 | 4 |  | Engine emission system failure lamp blink | BOOL | [5 empty] | X
EIC measurements value | 26305 | 0 | 326306 | 4 |  | Engine emission system failure lamp fast blink | BOOL | [5 empty] | X
EIC measurements value | 26306 | 7 | 326307 | 4 |  | DPF Regeneration Not Inhibit Park Brake Not Set | BOOL | [5 empty] | X
EIC measurements value | 26306 | 6 | 326307 | 4 |  | DPF Regeneration Inhibit Park Brake Not Set | BOOL | [5 empty] | X
EIC measurements value | 26306 | 5 | 326307 | 4 |  | DPF Regeneration Not Inhibit Out Of Neutral | BOOL | [5 empty] | X
EIC measurements value | 26306 | 4 | 326307 | 4 |  | DPF Regeneration Inhibit Out Of Neutral | BOOL | [5 empty] | X
EIC measurements value | 26306 | 3 | 326307 | 4 |  | Engine Running (Hatz) | BOOL | [5 empty] | X
EIC measurements value | 26306 | 2 | 326307 | 4 |  | Service Delay (Hatz) | BOOL | [5 empty] | X
EIC measurements value | 26306 | 1 | 326307 | 4 |  | Pre-glow Active (Hatz) | BOOL | [5 empty] | X
EIC measurements value | 26306 | 0 | 326307 | 4 |  | Oil Pressure Missing (Hatz) | BOOL | [5 empty] | X
EIC measurements value | 26307 | 7 | 326308 | 4 |  | Engine Diagnostic Lamp (Hatz) | BOOL | [5 empty] | X
EIC measurements value | 26307 | 6 | 326308 | 4 |  | Engine Overtemperature (Hatz) | BOOL | [5 empty] | X
EIC measurements value | 26307 | 5 | 326308 | 4 |  | Air Filter Switch (Hatz) | BOOL | [5 empty] | X
EIC measurements value | 26307 | 4 | 326308 | 4 |  | Transmission Neutral Switch (SPN 604) | BOOL | [5 empty] | X
EIC measurements value | 26307 | 3 | 326308 | 4 |  | Parking Brake Switch (SPN 70) | BOOL | [5 empty] | X
EIC measurements value | 26307 | 2 | 326308 | 4 |  | Brake Switch (SPN 597) | BOOL | [5 empty] | X
EIC measurements value | 26309 | 6 | 326310 | 4 |  | Exhaust Over Heat Condition (FPT) | BOOL | [5 empty] | X
EIC measurements value | 26309 | 5 | 326310 | 4 |  | Engine Over Speed Warning (FPT) | BOOL | [5 empty] | X
EIC measurements value | 26309 | 4 | 326310 | 4 |  | Urea Thawing Mode Active (FPT) | BOOL | [5 empty] | X
EIC measurements value | 26309 | 3 | 326310 | 4 |  | Scr Injector Overheat Protection (FPT) | BOOL | [5 empty] | X
EIC measurements value | 26309 | 2 | 326310 | 4 |  | Turbo Charger Protection (FPT) | BOOL | [5 empty] | X
EIC measurements value | 26309 | 1 | 326310 | 4 |  | Engine Protection (FPT) | BOOL | [5 empty] | X
EIC measurements value | 26309 | 0 | 326310 | 4 |  | Water in Fuel Detection (FPT) | BOOL | [5 empty] | X
EIC measurements value | 26310 | 7 | 326311 | 4 |  | Fuel in Oil Detection (FPT) | BOOL | [5 empty] | X
EIC measurements value | 26310 | 6 | 326311 | 4 |  | Low Catalyst Efficiency (FPT) | BOOL | [5 empty] | X
EIC measurements value | 26310 | 5 | 326311 | 4 |  | Bad Urea Quality (FPT) | BOOL | [5 empty] | X
EIC measurements value | 26310 | 4 | 326311 | 4 |  | Nh3 Slip Detection (FPT) | BOOL | [5 empty] | X
EIC measurements value | 26310 | 3 | 326311 | 4 |  | Engine Oil Over Temperature (FPT) | BOOL | [5 empty] | X
EIC measurements value | 26310 | 2 | 326311 | 4 |  | Smoke Limitation (FPT) | BOOL | [5 empty] | X
EIC measurements value | 26310 | 1 | 326311 | 4 |  | Clogged DPF (FPT) | BOOL | [5 empty] | X
EIC measurements value | 26311 |  | 326312 | 4 |  | Trip Average Fuel Rate (SPN 1029) RAW | INT32u | ABCD | 0 |  |  |  | X
EIC measurements value | 26313 |  | 326314 | 4 |  | Engine Trip Fuel (SPN 182) RAW | INT32u | ABCD | 0 |  |  |  | X
EIC measurements value | 26315 |  | 326316 | 4 |  | Engine Total Fuel Used (SPN 250) RAW | INT32u | ABCD | 0 |  |  |  | X
EIC measurements value | 26317 |  | 326318 | 4 |  | Engine Controlled Shutdown Request (SPN 5795) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26318 |  | 326319 | 4 |  | Engine Oil Pre-Heated State (SPN 3552) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26319 |  | 326320 | 4 |  | Engine Ventilation Status (SPN 3554) | INT16u | AB | 0 |  |  |  | X
EIC measurements value | 26320 |  | 326321 | 4 |  | Rail pressure (Jichai) | INT16u | AB | 2 |  |  |  | X
EIC measurements value | 26320 |  | 326321 | 4 |  | Engine Actual Exhaust 1 Oxygen (SPN 1119) | INT16u | AB | 2 |  |  |  | X
EIC measurements validity | 26296 | 15 | 326297 | 4 |  | DPF lamp OFF Validity | BOOL | [5 empty] | X
EIC measurements validity | 26296 | 14 | 326297 | 4 |  | DPF lamp ON solid Validity | BOOL | [5 empty] | X
EIC measurements validity | 26296 | 13 | 326297 | 4 |  | DPF lamp ON blink Validity | BOOL | [5 empty] | X
EIC measurements validity | 26296 | 12 | 326297 | 4 |  | DPF Active Regeneration not activated Validity | BOOL | [5 empty] | X
EIC measurements validity | 26296 | 11 | 326297 | 4 |  | DPF Active Regeneration activated Validity | BOOL | [5 empty] | X
EIC measurements validity | 26296 | 10 | 326297 | 4 |  | DPF Active Regeneration needed Validity | BOOL | [5 empty] | X
EIC measurements validity | 26296 | 9 | 326297 | 4 |  | DPF Regeneration not needed Validity | BOOL | [5 empty] | X
EIC measurements validity | 26296 | 8 | 326297 | 4 |  | DPF Regeneration needed Lowest Validity | BOOL | [5 empty] | X
EIC measurements validity | 26297 | 15 | 326298 | 4 |  | DPF Regeneration needed Moderate Validity | BOOL | [5 empty] | X
EIC measurements validity | 26297 | 14 | 326298 | 4 |  | DPF Regeneration needed Highest Validity | BOOL | [5 empty] | X
EIC measurements validity | 26297 | 13 | 326298 | 4 |  | DPF Regeneration Not Inhibit Validity | BOOL | [5 empty] | X
EIC measurements validity | 26297 | 12 | 326298 | 4 |  | DPF Regeneration Inhibit Validity | BOOL | [5 empty] | X
EIC measurements validity | 26297 | 11 | 326298 | 4 |  | Exhaust system high temperature OFF Validity | BOOL | [5 empty] | X
EIC measurements validity | 26297 | 10 | 326298 | 4 |  | Exhaust system high temperature ON Validity | BOOL | [5 empty] | X
EIC measurements validity | 26297 | 9 | 326298 | 4 |  | MTU limit lamp OFF Validity | BOOL | [5 empty] | X
EIC measurements validity | 26297 | 8 | 326298 | 4 |  | MTU limit lamp ON solid Validity | BOOL | [5 empty] | X
EIC measurements validity | 26298 | 15 | 326299 | 4 |  | MTU limit lamp ON blink 1Hz Validity | BOOL | [5 empty] | X
EIC measurements validity | 26298 | 14 | 326299 | 4 |  | DEF level low lamp OFF Validity | BOOL | [5 empty] | X
EIC measurements validity | 26298 | 13 | 326299 | 4 |  | DEF level low lamp ON solid Validity | BOOL | [5 empty] | X
EIC measurements validity | 26298 | 12 | 326299 | 4 |  | DEF level low lamp ON blink Validity | BOOL | [5 empty] | X
EIC measurements validity | 26298 | 11 | 326299 | 4 |  | After run status Validity | BOOL | [5 empty] | X
EIC measurements validity | 26298 | 10 | 326299 | 4 |  | Volvo Penta Scr Inducement NOT ACTIVE Validity | BOOL | [5 empty] | X
EIC measurements validity | 26298 | 19 | 326299 | 4 |  | Volvo Penta Scr Inducement WARNING Validity | BOOL | [5 empty] | X
EIC measurements validity | 26298 | 19 | 326299 | 4 |  | EMPTY validity | BOOL | [5 empty] | X
EIC measurements validity | 26299 | 15 | 326300 | 4 |  | Volvo Penta Scr Derate ACTIVE Validity | BOOL | [5 empty] | X
EIC measurements validity | 26299 | 14 | 326300 | 4 |  | Volvo Penta Pre severe Derate WARNING Validity | BOOL | [5 empty] | X
EIC measurements validity | 26299 | 13 | 326300 | 4 |  | Volvo Penta Severe Derate Validity | BOOL | [5 empty] | X
EIC measurements validity | 26299 | 12 | 326300 | 4 |  | Volvo Penta Temperature Override Derate Validity | BOOL | [5 empty] | X
EIC measurements validity | 26299 | 11 | 326300 | 4 |  | Volvo Penta Scr Inducement Reason OK Validity | BOOL | [5 empty] | X
EIC measurements validity | 26299 | 10 | 326300 | 4 |  | Volvo Penta Reagent Tank low Validity | BOOL | [5 empty] | X
EIC measurements validity | 26299 | 9 | 326300 | 4 |  | Volvo Penta Incorrect Reagent Quality Validity | BOOL | [5 empty] | X
EIC measurements validity | 26299 | 8 | 326300 | 4 |  | Volvo Penta Absence of Reagent Dosing Validity | BOOL | [5 empty] | X
EIC measurements validity | 26300 | 15 | 326301 | 4 |  | MTU TIER4 lamp ON blink 2Hz Validity | BOOL | [5 empty] | X
EIC measurements validity | 26300 | 14 | 326301 | 4 |  | MTU buzzer lamp OFF Validity | BOOL | [5 empty] | X
EIC measurements validity | 26300 | 13 | 326301 | 4 |  | MTU buzzer lamp ON solid Validity | BOOL | [5 empty] | X
EIC measurements validity | 26300 | 12 | 326301 | 4 |  | MTU buzzer lamp ON blink 1Hz Validity | BOOL | [5 empty] | X
EIC measurements validity | 26300 | 11 | 326301 | 4 |  | MTU buzzer lamp ON blink 2Hz Validity | BOOL | [5 empty] | X
EIC measurements validity | 26300 | 10 | 326301 | 4 |  | Alarm Yellow lamp OFF Validity | BOOL | [5 empty] | X
EIC measurements validity | 26300 | 9 | 326301 | 4 |  | Alarm Yellow lamp ON Validity | BOOL | [5 empty] | X
EIC measurements validity | 26300 | 8 | 326301 | 4 |  | Alarm Red lamp OFF Validity | BOOL | [5 empty] | X
EIC measurements validity | 26301 | 15 | 326302 | 4 |  | Alarm Red lamp ON Validity | BOOL | [5 empty] | X
EIC measurements validity | 26301 | 14 | 326302 | 4 |  | Engine fuel leak Validity | BOOL | [5 empty] | X
EIC measurements validity | 26301 | 13 | 326302 | 4 |  | Engine Wait to start Validity | BOOL | [5 empty] | X
EIC measurements validity | 26301 | 12 | 326302 | 4 |  | Engine Protect system shutdown Validity | BOOL | [5 empty] | X
EIC measurements validity | 26301 | 11 | 326302 | 4 |  | Engine Protect system appro shutdown Validity | BOOL | [5 empty] | X
EIC measurements validity | 26301 | 10 | 326302 | 4 |  | Engine alarm acknowledg Validity | BOOL | [5 empty] | X
EIC measurements validity | 26301 | 9 | 326302 | 4 |  | Engine ait shutoff command status Validity | BOOL | [5 empty] | X
EIC measurements validity | 26301 | 8 | 326302 | 4 |  | Engine overspeed test Validity | BOOL | [5 empty] | X
EIC measurements validity | 26302 | 15 | 326303 | 4 |  | Engine shutoff status Validity | BOOL | [5 empty] | X
EIC measurements validity | 26302 | 14 | 326303 | 4 |  | Manual purge ECU | BOOL | [5 empty] | X
EIC measurements validity | 26302 | 13 | 326303 | 4 |  | Manual purge EIDSS Validity | BOOL | [5 empty] | X
EIC measurements validity | 26302 | 12 | 326303 | 4 |  | Force purge Validity | BOOL | [5 empty] | X
EIC measurements validity | 26302 | 11 | 326303 | 4 |  | JCB Amber blink Validity | BOOL | [5 empty] | X
EIC measurements validity | 26302 | 10 | 326303 | 4 |  | JCB Amber solid Validity | BOOL | [5 empty] | X
EIC measurements validity | 26302 | 9 | 326303 | 4 |  | JCB Red blink Validity | BOOL | [5 empty] | X
EIC measurements validity | 26302 | 8 | 326303 | 4 |  | JCB Red solid Validity | BOOL | [5 empty] | X
EIC measurements validity | 26303 | 15 | 326304 | 4 |  | JCB Engine emission system failure warning Validity | BOOL | [5 empty] | X
EIC measurements validity | 26303 | 14 | 326304 | 4 |  | JCB Engine emission system failure low Validity | BOOL | [5 empty] | X
EIC measurements validity | 26303 | 13 | 326304 | 4 |  | JCB Engine emission system failure high Validity | BOOL | [5 empty] | X
EIC measurements validity | 26303 | 12 | 326304 | 4 |  | JCB Particulate filter restricted high Validity | BOOL | [5 empty] | X
EIC measurements validity | 26303 | 11 | 326304 | 4 |  | JCB Particulate filter restricted very high Validity | BOOL | [5 empty] | X
EIC measurements validity | 26303 | 10 | 326304 | 4 |  | JCB Particulate filter restricted critical Validity | BOOL | [5 empty] | X
EIC measurements validity | 26303 | 9 | 326304 | 4 |  | DPF lamp - fast blink Validity | BOOL | [5 empty] | X
EIC measurements validity | 26303 | 8 | 326304 | 4 |  | DEF low level - Fast blink Validity | BOOL | [5 empty] | X
EIC measurements validity | 26304 | 15 | 326305 | 4 |  | Red lamp OFF Validity | BOOL | [5 empty] | X
EIC measurements validity | 26304 | 14 | 326305 | 4 |  | Red lamp solid Validity | BOOL | [5 empty] | X
EIC measurements validity | 26304 | 13 | 326305 | 4 |  | Red lamp blink Validity | BOOL | [5 empty] | X
EIC measurements validity | 26304 | 12 | 326305 | 4 |  | Red lamp fast blink Validity | BOOL | [5 empty] | X
EIC measurements validity | 26304 | 11 | 326305 | 4 |  | Yellow lamp OFF Validity | BOOL | [5 empty] | X
EIC measurements validity | 26304 | 10 | 326305 | 4 |  | Yellow lamp solid Validity | BOOL | [5 empty] | X
EIC measurements validity | 26304 | 9 | 326305 | 4 |  | Yellow lamp blink Validity | BOOL | [5 empty] | X
EIC measurements validity | 26304 | 8 | 326305 | 4 |  | Yellow lamp fast blink Validity | BOOL | [5 empty] | X
EIC measurements validity | 26305 | 15 | 326306 | 4 |  | MIL lamp OFF Validity | BOOL | [5 empty] | X
EIC measurements validity | 26305 | 14 | 326306 | 4 |  | MIL lamp solid Validity | BOOL | [5 empty] | X
EIC measurements validity | 26305 | 13 | 326306 | 4 |  | MIL lamp blink Validity | BOOL | [5 empty] | X
EIC measurements validity | 26305 | 12 | 326306 | 4 |  | MIL lamp fast blink Validity | BOOL | [5 empty] | X
EIC measurements validity | 26305 | 11 | 326306 | 4 |  | Engine emission system failure lamp off Validity | BOOL | [5 empty] | X
EIC measurements validity | 26305 | 10 | 326306 | 4 |  | Engine emission system failure lamp solid Validity | BOOL | [5 empty] | X
EIC measurements validity | 26305 | 9 | 326306 | 4 |  | Engine emission system failure lamp blink Validity | BOOL | [5 empty] | X
EIC measurements validity | 26305 | 8 | 326306 | 4 |  | Engine emission system failure lamp fast blink Validity | BOOL | [5 empty] | X
EIC measurements validity | 26306 | 15 | 326307 | 4 |  | DPF Regeneration Not Inhibit Park Brake Not Set Validity | BOOL | [5 empty] | X
EIC measurements validity | 26306 | 14 | 326307 | 4 |  | DPF Regeneration Inhibit Park Brake Not Set Validity | BOOL | [5 empty] | X
EIC measurements validity | 26306 | 13 | 326307 | 4 |  | DPF Regeneration Not Inhibit Out Of Neutral Validity | BOOL | [5 empty] | X
EIC measurements validity | 26306 | 12 | 326307 | 4 |  | DPF Regeneration Inhibit Out Of Neutral Validity | BOOL | [5 empty] | X
EIC measurements validity | 26306 | 11 | 326307 | 4 |  | Engine Running (Hatz) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26306 | 10 | 326307 | 4 |  | Service Delay (Hatz) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26306 | 9 | 326307 | 4 |  | Pre-glow Active (Hatz) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26306 | 8 | 326307 | 4 |  | Oil Pressure Missing (Hatz) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26307 | 15 | 326308 | 4 |  | Engine Diagnostic Lamp (Hatz) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26307 | 14 | 326308 | 4 |  | Engine Overtemperature (Hatz) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26307 | 13 | 326308 | 4 |  | Air Filter Switch (Hatz) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26307 | 12 | 326308 | 4 |  | Transmission Neutral Switch (SPN 604) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26307 | 11 | 326308 | 4 |  | Parking Brake Switch (SPN 70) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26307 | 10 | 326308 | 4 |  | Brake Switch (SPN 597) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26309 | 14 | 326310 | 4 |  | Exhaust Over Heat Condition (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26309 | 13 | 326310 | 4 |  | Engine Over Speed Warning (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26309 | 12 | 326310 | 4 |  | Urea Thawing Mode Active (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26309 | 11 | 326310 | 4 |  | Scr Injector Overheat Protection (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26309 | 10 | 326310 | 4 |  | Turbo Charger Protection (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26309 | 9 | 326310 | 4 |  | Engine Protection (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26309 | 8 | 326310 | 4 |  | Water in Fuel Detection (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26310 | 15 | 326311 | 4 |  | Fuel in Oil Detection (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26310 | 14 | 326311 | 4 |  | Low Catalyst Efficiency (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26310 | 13 | 326311 | 4 |  | Bad Urea Quality (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26310 | 12 | 326311 | 4 |  | Nh3 Slip Detection (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26310 | 11 | 326311 | 4 |  | Engine Oil Over Temperature (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26310 | 10 | 326311 | 4 |  | Smoke Limitation (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26310 | 9 | 326311 | 4 |  | Clogged DPF (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 15 | 326901 | 4 |  | Engine Speed (SPN 190) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 14 | 326901 | 4 |  | Engine Coolant Temperature (SPN 110) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 13 | 326901 | 4 |  | Engine Oil Pressure (SPN 100) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 12 | 326901 | 4 |  | Active Diagnostic Trouble Code Count (SPN 1218) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 11 | 326901 | 4 |  | Engine Oil Temperature 1 (SPN 175) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 10 | 326901 | 4 |  | Engine Fuel 1 Temperature 1 (SPN 174) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 9 | 326901 | 4 |  | Engine Intake Manifold #1 Pressure (SPN 102) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 8 | 326901 | 4 |  | Engine Intake 1 Air Temperature (SPN 172) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 7 | 326901 | 4 |  | Engine Coolant Level 1 (SPN 111) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 6 | 326901 | 4 |  | Engine Fuel Rate (SPN 183) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 5 | 326901 | 4 |  | Charge air pressure (MDEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 4 | 326901 | 4 |  | Engine Intake Manifold 1 Temperature (SPN 105) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 3 | 326901 | 4 |  | Driver's Demand Engine, Percent Torque (SPN 512) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 2 | 326901 | 4 |  | Actual Engine, Percent Torque (SPN 513) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 1 | 326901 | 4 |  | Accelerator Pedal Position 1 (SPN 91) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26900 | 0 | 326901 | 4 |  | Engine Percent Load At Current Speed (SPN 92) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26901 | 15 | 326902 | 4 |  | Engine Intake Air Pressure (SPN 106) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26901 | 14 | 326902 | 4 |  | Engine Exhaust Temperature (SPN 173) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26901 | 13 | 326902 | 4 |  | Engine Total Hours of Operation (SPN 247) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26901 | 11 | 326902 | 4 |  | Engine Oil Filter Differential Pressure (SPN 99) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26901 | 10 | 326902 | 4 |  | Key Switch Battery Potential (SPN 158) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26901 | 9 | 326902 | 4 |  | Engine Fuel Delivery Pressure (SPN 94) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26901 | 8 | 326902 | 4 |  | Engine Oil Level (SPN 98) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26901 | 7 | 326902 | 4 |  | Engine Crankcase Pressure 1 (SPN 101) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26901 | 6 | 326902 | 4 |  | Engine Coolant Pressure 1 (SPN 109) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26901 | 5 | 326902 | 4 |  | Water In Fuel Indicator 1 (SPN 97) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26901 | 4 | 326902 | 4 |  | Engine Turbocharger 1 Oil Temperature (SPN 176) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26901 | 3 | 326902 | 4 |  | Aftertreatment 1 Diesel Particulate Filter Intake Pressure (SPN 81) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26901 | 2 | 326902 | 4 |  | Engine Air Filter 1 Differential Pressure (SPN 107) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26901 | 1 | 326902 | 4 |  | Engine Coolant Filter Differential Pressure (SPN 112) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26901 | 0 | 326902 | 4 |  | Barometric Pressure (SPN 108) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26902 | 15 | 326903 | 4 |  | Ambient Air Temperature (SPN 171) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26902 | 14 | 326903 | 4 |  | Engine Exhaust Manifold Bank 2 Temperature 1 (SPN 2433) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26902 | 13 | 326903 | 4 |  | Engine Exhaust Manifold Bank 1 Temperature 1 (SPN 2434) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26902 | 12 | 326903 | 4 |  | Temp. Winding 1 (ADEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26902 | 11 | 326903 | 4 |  | Temp. Winding 2 (ADEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26902 | 10 | 326903 | 4 |  | Temp. Winding 3 (ADEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26902 | 9 | 326903 | 4 |  | Auxiliary_Analog_Info (ADEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26902 | 8 | 326903 | 4 |  | Auxiliary_Analog_Info Validity | BOOL | [5 empty] | X
EIC measurements validity | 26902 | 7 | 326903 | 4 |  | Engine Turbocharger 1 Compressor Outlet Temperature (ADEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26902 | 6 | 326903 | 4 |  | Engine Intercooler Temperature (SPN 52) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26902 | 5 | 326903 | 4 |  | Engine Trip Fuel (SPN 182) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26902 | 3 | 326903 | 4 |  | Engine Total Fuel Used (SPN 250) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26902 | 1 | 326903 | 4 |  | Trip Fuel (Gaseous) (SPN 1039) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26903 | 15 | 326904 | 4 |  | Total Fuel Used (Gaseous) (SPN 1040) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26903 | 13 | 326904 | 4 |  | Trip Average Fuel Rate (SPN 1029) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26903 | 12 | 326904 | 4 |  | Engine Rated Power (SPN 166) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26903 | 11 | 326904 | 4 |  | Engine power (ADEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26903 | 10 | 326904 | 4 |  | Engine Intake Manifold #1 Absolute Pressure (SPN 3563) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26903 | 9 | 326904 | 4 |  | Diesel Particulate Filter Lamp Command (SPN 3697) | BOOL | [5 empty] | X
EIC measurements validity | 26903 | 8 | 326904 | 4 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Inhibit Switch (SPN 3703) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26903 | 7 | 326904 | 4 |  | Aftertreatment Diesel Particulate Filter Active Regeneration Status (SPN 3700) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26903 | 6 | 326904 | 4 |  | Aftertreatment Diesel Particulate Filter Status (SPN 3701) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26903 | 5 | 326904 | 4 |  | Exhaust System High Temperature Lamp Command (SPN 3698) | BOOL | [5 empty] | X
EIC measurements validity | 26903 | 4 | 326904 | 4 |  | Engine Air Filter 2 Differential Pressure (SPN 2809) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26903 | 3 | 326904 | 4 |  | Engine Fuel Supply Pump Intake Absolute Pressure (SPN 1381) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26903 | 2 | 326904 | 4 |  | Engine Fuel Filter (suction side) Differential Pressure (SPN 1382) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26903 | 1 | 326904 | 4 |  | Engine Fuel Filter Differential Pressure (SPN 95) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26903 | 0 | 326904 | 4 |  | Speed demand Source (MDEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 15 | 326905 | 4 |  | P-Lube Oil Limit LO (MDEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 14 | 326905 | 4 |  | P-Lube Oil Limit LOLO (MDEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 13 | 326905 | 4 |  | P-Fuel (MDEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 12 | 326905 | 4 |  | T-Coolant Limit HI (MDEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 11 | 326905 | 4 |  | T-Coolant Limit HIHI (MDEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 10 | 326905 | 4 |  | T-Coolant Intercooler (MDEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 9 | 326905 | 4 |  | Engine ECU Temperature (SPN 1136) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 8 | 326905 | 4 |  | Actual Droop (MDEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 7 | 326905 | 4 |  | Injection Quantity Act.DBR % (MDEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 6 | 326905 | 4 |  | Engine Speed Camshaft (MDEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 5 | 326905 | 4 |  | T-Lube Oil Limit HI (MDEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 4 | 326905 | 4 |  | T-Lube Oil Limit HIHI (MDEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 3 | 326905 | 4 |  | Feedback Speed Demand analog (MDEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 2 | 326905 | 4 |  | Stop signal active (MDEC) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 1 | 326905 | 4 |  | Exhaust Port Temperature 01 (SPN 1137) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26904 | 0 | 326905 | 4 |  | Exhaust Port Temperature 02 (SPN 1138) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 15 | 326906 | 4 |  | Exhaust Port Temperature 03 (SPN 1139) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 14 | 326906 | 4 |  | Exhaust Port Temperature 04 (SPN 1140) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 13 | 326906 | 4 |  | Exhaust Port Temperature 05 (SPN 1141) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 12 | 326906 | 4 |  | Exhaust Port Temperature 06 (SPN 1142) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 11 | 326906 | 4 |  | Exhaust Port Temperature 07 (SPN 1143) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 10 | 326906 | 4 |  | Exhaust Port Temperature 08 (SPN 1144) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 9 | 326906 | 4 |  | Exhaust Port Temperature 09 (SPN 1145) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 8 | 326906 | 4 |  | Exhaust Port Temperature 10 (SPN 1146) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 7 | 326906 | 4 |  | Exhaust Port Temperature 11 (SPN 1147) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 6 | 326906 | 4 |  | Exhaust Port Temperature 12 (SPN 1148) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 5 | 326906 | 4 |  | Exhaust Port Temperature 13 (SPN 1149) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 4 | 326906 | 4 |  | Exhaust Port Temperature 14 (SPN 1150) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 3 | 326906 | 4 |  | Exhaust Port Temperature 15 (SPN 1151) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 2 | 326906 | 4 |  | Exhaust Port Temperature 16 (SPN 1152) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 1 | 326906 | 4 |  | Engine Filtered Fuel Delivery Pressure (SPN 5579) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26905 | 0 | 326906 | 4 |  | Engine Coolant Temperature 2 (SPN 4076) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26906 | 15 | 326907 | 4 |  | Engine Coolant Temperature 3 (SPN 6209) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26906 | 14 | 326907 | 4 |  | Engine Coolant Pump Outlet Temperature (SPN 4193) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26906 | 13 | 326907 | 4 |  | Engine Auxiliary Coolant Temperature (SPN 1212) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26906 | 12 | 326907 | 4 |  | Engine Turbocharger 1 Turbine Intake Temperature (SPN 1180) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26906 | 11 | 326907 | 4 |  | Engine Turbocharger 2 Turbine Intake Temperature (SPN 1181) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26906 | 10 | 326907 | 4 |  | Engine Auxiliary Coolant Pressure (SPN 1203) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26906 | 9 | 326907 | 4 |  | Specific Humidity (SPN 4490) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26906 | 8 | 326907 | 4 |  | Engine Turbocharger 2 Speed (SPN 1169) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26906 | 7 | 326907 | 4 |  | Engine Turbocharger 3 Speed (SPN 1170) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26906 | 6 | 326907 | 4 |  | Trip Engine Running Time (SPN 1036) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26906 | 4 | 326907 | 4 |  | Trip Idle Time (SPN 1037) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26906 | 2 | 326907 | 4 |  | Engine Fan 1 Estimated Percent Speed (SPN 975) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26906 | 1 | 326907 | 4 |  | Engine Turbocharger 1 Speed (SPN 103) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26906 | 0 | 326907 | 4 |  | Nominal Friction - Percent Torque (SPN 514) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26907 | 15 | 326908 | 4 |  | Engine's Desired Operating Speed (SPN 515) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26907 | 14 | 326908 | 4 |  | Engine Intake Manifold 2 Temperature (SPN 1131) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26907 | 13 | 326908 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Volume (SPN 1761) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26907 | 12 | 326908 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Temperature 1 (SPN 3031) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26907 | 11 | 326908 | 4 |  | Aftertreatment 1 SCR Intake NOx 1 (SPN 3216) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26907 | 10 | 326908 | 4 |  | Aftertreatment 1 Outlet NOx 1 (SPN 3226) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26907 | 9 | 326908 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Actual Dosing Quantity (SPN 4331) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26907 | 8 | 326908 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Doser 1 Absolute Pressure (SPN 4334) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26907 | 7 | 326908 | 4 |  | Aftertreatment 1 SCR Dosing Air Assist Valve (SPN 4336) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26907 | 6 | 326908 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Dosing Requested Quantity (SPN 4348) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26907 | 5 | 326908 | 4 |  | Aftertreatment 1 SCR Intake Temperature (SPN 4360) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26907 | 4 | 326908 | 4 |  | Aftertreatment 1 SCR Outlet Temperature (SPN 4363) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26907 | 3 | 326908 | 4 |  | Aftertreatment 2 SCR Intake NOx 1 (SPN 3255) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26907 | 2 | 326908 | 4 |  | Aftertreatment 2 Outlet NOx 1 (SPN 3265) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26907 | 1 | 326908 | 4 |  | Aftertreatment 2 Diesel Exhaust Fluid Actual Dosing Quantity (SPN 4384) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 0 | 326909 | 4 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser 1 Absolute Pressure (SPN 4387) | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 15 | 326909 | 4 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser 1 Temperature (SPN 4390) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 14 | 326909 | 4 |  | Aftertreatment 2 Diesel Exhaust Fluid Dosing Requested Quantity (SPN 4401) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 13 | 326909 | 4 |  | Aftertreatment 2 SCR Intake Temperature (SPN 4413) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 12 | 326909 | 4 |  | Aftertreatment 2 SCR Outlet Temperature (SPN 4415) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 11 | 326909 | 4 |  | Engine Oil Filter Outlet Pressure (SPN 3549) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 10 | 326909 | 4 |  | Engine Operating State (SPN 3543) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 9 | 326909 | 4 |  | Source Address of Controlling Device for Engine Control (SPN 1483) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 8 | 326909 | 4 |  | Engine Rated Speed (SPN 189) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 7 | 326909 | 4 |  | Engine Speed At Idle, Point 1 (SPN 188) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 6 | 326909 | 4 |  | Fuel Consumption g/KWh (MTU) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 5 | 326909 | 4 |  | Engine Status of Start procedure (MTU) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 4 | 326909 | 4 |  | Exhaust Port Temperature 17 (SPN 1153) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 3 | 326909 | 4 |  | Exhaust Port Temperature 18 (SPN 1154) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 2 | 326909 | 4 |  | Exhaust Port Temperature 19 (SPN 1155) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 1 | 326909 | 4 |  | Exhaust Port Temperature 20 (SPN 1156) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26908 | 0 | 326909 | 4 |  | UREA Level (Scania) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26909 | 15 | 326910 | 4 |  | Aftertreatment SCR Operator Inducement Severity (SPN 5246) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26909 | 14 | 326910 | 4 |  | Aftertreatment Diesel Exhaust Fluid Tank Low Level Indicator (SPN 5245) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26909 | 13 | 326910 | 4 |  | Aftertreatment 1 Diesel Particulate Filter Outlet Temperature (SPN 3246) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26909 | 12 | 326910 | 4 |  | Aftertreatment 1 Diesel Particulate Filter Time to Next Active Regeneration (SPN 5978) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26909 | 10 | 326910 | 4 |  | Engine Charge Air Cooler 1 Outlet Temperature (SPN 2630) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26909 | 9 | 326910 | 4 |  | Aftertreatment 1 Diesel Particulate Filter Soot Load Percent (SPN 3719) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26909 | 8 | 326910 | 4 |  | Purging Active (Scania) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26909 | 7 | 326910 | 4 |  | Limit Lamp Status (MTU) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26909 | 6 | 326910 | 4 |  | Battery Charger 1 Output Voltage (SPN 4992) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26909 | 5 | 326910 | 4 |  | Battery Charger 1 Output Current (SPN 4993) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26909 | 4 | 326910 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Average Consumption (SPN 3829) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26909 | 3 | 326910 | 4 |  | Time left to torque reduction (Volvo) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26909 | 2 | 326910 | 4 |  | Time left to servere torque reduction (Volvo) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26909 | 1 | 326910 | 4 |  | SCR inducement severity (Volvo) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26909 | 0 | 326910 | 4 |  | SCR inducement reason (Volvo) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 15 | 326911 | 4 |  | Engine Derate Request (SPN 3644) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 14 | 326911 | 4 |  | Engine Demand, Percent Torque (SPN 2432) | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 13 | 326911 | 4 |  | Aftertreatment 1 Intake Percent Oxygen 1 (SPN 3217) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 12 | 326911 | 4 |  | Aftertreatment 1 Outlet Percent Oxygen 1 (SPN 3227) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 11 | 326911 | 4 |  | Engine Throttle Actuator 1 Control Command (SPN 3464) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 10 | 326911 | 4 |  | Long-term Fuel Trim - Bank 1 (SPN 4237) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 9 | 326911 | 4 |  | Short-term Fuel Trim - Bank 1 (SPN 4236) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 8 | 326911 | 4 |  | Engine Exhaust Bank 1 O2 Sensor Closed Loop Operation (SPN 4240) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 7 | 326911 | 4 |  | Engine Desired Ignition Timing 1 (SPN 1433) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 6 | 326911 | 4 |  | Engine Actual Ignition Timing (SPN 1436) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 5 | 326911 | 4 |  | EDC4 CAN Status (EMR) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 4 | 326911 | 4 |  | Engine Starter Mode (SPN 1675) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 3 | 326911 | 4 |  | Actual Maximum Available Engine - Percent Torque (SPN 3357) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 2 | 326911 | 4 |  | Engine Coolant Pre-heated State (SPN 3553) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 1 | 326911 | 4 |  | Engine Safety and Protection Override Status (MTU) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26910 | 0 | 326911 | 4 |  | Engine Cylinder Cut-off (MTU) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 15 | 326912 | 4 |  | Engine Running State (MTU) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 14 | 326912 | 4 |  | External Stop State (MTU) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 13 | 326912 | 4 |  | Requested Absolute Torque (MTU) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 12 | 326912 | 4 |  | Source of Current Speed Demand (MTU) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 11 | 326912 | 4 |  | Engine Demanded Operating Speed (MTU) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 10 | 326912 | 4 |  | Feedback of Speed Demand CAN (MTU) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 9 | 326912 | 4 |  | Feedback of Speed Demand Analogue Input (MTU) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 8 | 326912 | 4 |  | Speed Demand Fail Mode (MTU) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 7 | 326912 | 4 |  | Engine Shutdown Override Switch (SPN 1237) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 6 | 326912 | 4 |  | Engine Requested Speed (SPN 898) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 5 | 326912 | 4 |  | Escape Mode Enable Flag (Isuzu) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 4 | 326912 | 4 |  | Inducement Timer (Isuzu) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 3 | 326912 | 4 |  | Inducement Level (Isuzu) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 2 | 326912 | 4 |  | Urea Tank Level (Isuzu) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 1 | 326912 | 4 |  | Urea Tank Level Indicator (Isuzu) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26911 | 0 | 326912 | 4 |  | Level Indicator (Amber) Action (Isuzu) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 15 | 326913 | 4 |  | DPF Amber Lamp Mode (Isuzu) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 14 | 326913 | 4 |  | EXH.SYSTEM lamp (Isuzu) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 13 | 326913 | 4 |  | DPF Green Lamp Mode (Isuzu) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 12 | 326913 | 4 |  | NO POWER Lamp (Isuzu) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 11 | 326913 | 4 |  | Engine Intake Manifold 3 Temperature (SPN 1132) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 10 | 326913 | 4 |  | Engine Intake Manifold 4 Temperature (SPN 1133) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 9 | 326913 | 4 |  | Engine Oil Filter Intake Pressure (SPN 1208) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 8 | 326913 | 4 |  | Engine Turbocharger 2 Boost Pressure (SPN 1128) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 7 | 326913 | 4 |  | Engine Fuel 1 Injector Metering Rail 1 Pressure (SPN 157) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 6 | 326913 | 4 |  | Battery Potential / Power Input 1 (SPN 168) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 5 | 326913 | 4 |  | Dosing Module Status (JCB) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 4 | 326913 | 4 |  | Actual Reducing Agent Quantity (JCB) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 3 | 326913 | 4 |  | Aftertreatment Lamp (JCB) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 2 | 326913 | 4 |  | Refresh Status Byte (JCB) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 1 | 326913 | 4 |  | SCR Monitor (JCB) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26912 | 0 | 326913 | 4 |  | Successful Running Refreshes (JCB) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 15 | 326914 | 4 |  | Successful Stationary Refreshes (JCB) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 14 | 326914 | 4 |  | Engine Rating (JCB) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 13 | 326914 | 4 |  | Aftertreatment 1 Exhaust Temperature 1 (SPN 3241) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 12 | 326914 | 4 |  | Humidity Derate Percentage (Perkins/CAT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 11 | 326914 | 4 |  | Engine Emergency (Immediate) Shutdown Indication (SPN 3607 Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 10 | 326914 | 4 |  | Number of EIO Activations (Volvo EMS2.4) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 9 | 326914 | 4 |  | Accumulated EIO time (Volvo EMS2.4) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 8 | 326914 | 4 |  | Time left of EIO Operation (Volvo EMS2.4) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 7 | 326914 | 4 |  | Remaining Service Hours (Hatz) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 6 | 326914 | 4 |  | Wheel Based Vehicle Speed (SPN 84) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 5 | 326914 | 4 |  | Aftertreatment 1 Exhaust Gas Mass Flow Rate (SPN 3236) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 4 | 326914 | 4 |  | Aftertreatment 1 Diesel Particulate Filter Differential Pressure (SPN 3251) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 3 | 326914 | 4 |  | Aftertreatment 1 Diesel Oxidation Catalyst Intake Temperature (SPN 4765) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 2 | 326914 | 4 |  | Aftertreatment 1 Diesel Particulate Filter Intake Temperature (SPN 3242) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 1 | 326914 | 4 |  | Phys. Injection quantity (Hatz) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26913 | 0 | 326914 | 4 |  | Phys. Torque (Hatz) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26914 | 15 | 326915 | 4 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Out of Neutral (SPN 3708) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26914 | 14 | 326915 | 4 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Parking Brake Not Set (SPN 3710) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26914 | 13 | 326915 | 4 |  | Engine Coolant Level 1 (SPN 111) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26914 | 12 | 326915 | 4 |  | Operator Inducement Time to Torque Derate Level 2 (SPN 7428) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26914 | 11 | 326915 | 4 |  | Alternator 1 Status (SPN 3353) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26915 | 3 | 326916 | 4 |  | Engine Throttle Valve 1 Position 1 (SPN 51) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26915 | 2 | 326916 | 4 |  | Engine Fuel Valve 1 Intake Absolute Pressure (SPN 1390) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26915 | 1 | 326916 | 4 |  | Engine Turbocharger 1 Boost Pressure (SPN 1127) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26915 | 0 | 326916 | 4 |  | Engine Cylinder 1 Ignition Timing (SPN 1413) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26916 | 15 | 326917 | 4 |  | Engine Intake Air Mass Flow Rate (SPN 132) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26916 | 14 | 326917 | 4 |  | Engine Lambda (Yuchai) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26916 | 13 | 326917 | 4 |  | Aftertreatment 1 Diesel Particulate Filter Ash Load Percent (SPN 3720) | BOOL | [5 empty] | X
EIC measurements validity | 26916 | 12 | 326917 | 4 |  | DPF Regeneration State (Scania) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26916 | 11 | 326917 | 4 |  | DPF Regeneration Countdown Timer (Scania) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26916 | 10 | 326917 | 4 |  | DEF Level (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26916 | 9 | 326917 | 4 |  | DEF Quality (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26916 | 8 | 326917 | 4 |  | DEF Technical Failure (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26916 | 7 | 326917 | 4 |  | Cold Start Heater Status (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26916 | 6 | 326917 | 4 |  | Fuel Filter Heater Status (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26916 | 5 | 326917 | 4 |  | Low Idle Increase Desired (FPT) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26916 | 4 | 326917 | 4 |  | Urea level inducement state (Scania) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26916 | 3 | 326917 | 4 |  | Emission-OBD inducement state (Scania) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26916 | 2 | 326917 | 4 |  | Emission-OBD inducement failure reason (Scania) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26916 | 1 | 326917 | 4 |  | Engine Diesel Particulate Filter Regeneration State (JDEC STAGE V) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 0 | 326918 | 4 |  | Aftertreatment 1 Diesel Exhaust Fluid Concentration (SPN 3516) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 15 | 326918 | 4 |  | Engine Requested Fuel Valve 1 Position (SPN 1765) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 14 | 326918 | 4 |  | Engine Oil Priming State (SPN 3551) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 13 | 326918 | 4 |  | Fuel Pump Primer Status (SPN 4083) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 12 | 326918 | 4 |  | Sensor supply voltage 1 (SPN 3509) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 11 | 326918 | 4 |  | Sensor supply voltage 2 (SPN 3510) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 10 | 326918 | 4 |  | Accelerator Pedal Position 2 (SPN 29) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 9 | 326918 | 4 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Temporary System Lockout (SPN 3714) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 8 | 326918 | 4 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Permanent System Lockout (SPN 3715) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 7 | 326918 | 4 |  | Aftertreatment Ambient Air Temperature (SPN 7441) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 6 | 326918 | 4 |  | Aftertreatment Thermal Management Status (SPN 7332) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 5 | 326918 | 4 |  | Aftertreatment Engine Speed Increase request (SPN 7502) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 4 | 326918 | 4 |  | Aftertreatment Engine Load Request (SPN 7503) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 3 | 326918 | 4 |  | Feedback Engine Fueling State (SPN 5794) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 2 | 326918 | 4 |  | Engine Fueling Inhibit Allowed (SPN 5795) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 1 | 326918 | 4 |  | Blowby flow (Cummins H6) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26917 | 0 | 326918 | 4 |  | Fuel rail pressure (Cummins H6) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 15 | 326919 | 4 |  | Timing rail pressure (Cummins H6) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 14 | 326919 | 4 |  | Aftercooler water inlet temperature (Cummins H6) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 13 | 326919 | 4 |  | Fuel Rank position left (Cummins H6) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 12 | 326919 | 4 |  | Fuel Rank position right (Cummins H6) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 11 | 326919 | 4 |  | Intake Manifold pressure left (Cummins H6) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 10 | 326919 | 4 |  | Intake Manifold pressure right (Cummins H6) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 9 | 326919 | 4 |  | Intake Manifold Temperature left (Cummins H6) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 8 | 326919 | 4 |  | Intake Manifold Temperature right (Cummins H6) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 7 | 326919 | 4 |  | Reserved for BOOL | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 6 | 326919 | 4 |  | Reserved for BOOL | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 5 | 326919 | 4 |  | Reserved for BOOL | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 4 | 326919 | 4 |  | Reserved for BOOL | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 3 | 326919 | 4 |  | Reserved for BOOL | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 2 | 326919 | 4 |  | Reserved for BOOL | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 1 | 326919 | 4 |  | Reserved for BOOL | BOOL | [5 empty] | X
EIC measurements validity | 26918 | 0 | 326919 | 4 |  | Reserved for BOOL | BOOL | [5 empty] | X
EIC measurements validity | 26919 | 15 | 326920 | 4 |  | Reserved for BOOL | BOOL | [5 empty] | X
EIC measurements validity | 26919 | 14 | 326920 | 4 |  | Reserved for BOOL | BOOL | [5 empty] | X
EIC measurements validity | 26919 | 13 | 326920 | 4 |  | Reserved for BOOL | BOOL | [5 empty] | X
EIC measurements validity | 26919 | 12 | 326920 | 4 |  | Reserved for BOOL | BOOL | [5 empty] | X
EIC measurements validity | 26919 | 11 | 326920 | 4 |  | Reserved for BOOL | BOOL | [5 empty] | X
EIC measurements validity | 26919 | 10 | 326920 | 4 |  | Reserved for BOOL | BOOL | [5 empty] | X
EIC measurements validity | 26919 | 9 | 326920 | 4 |  | Reserved for BOOL | BOOL | [5 empty] | X
EIC measurements validity | 26919 | 8 | 326920 | 4 |  | Trip Average Fuel Rate (SPN 1029) RAW Validity | BOOL | [5 empty] | X
EIC measurements validity | 26919 | 6 | 326920 | 4 |  | Engine Trip Fuel (SPN 182) RAW Validity | BOOL | [5 empty] | X
EIC measurements validity | 26919 | 4 | 326920 | 4 |  | Engine Total Fuel Used (SPN 250) RAW Validity | BOOL | [5 empty] | X
EIC measurements validity | 26919 | 3 | 326920 | 4 |  | Engine Controlled Shutdown Request (SPN 5795) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26919 | 2 | 326920 | 4 |  | Engine Oil Pre-Heated State (SPN 3552) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26919 | 1 | 326920 | 4 |  | Engine Ventilation Status (SPN 3554) Validity | BOOL | [5 empty] | X
EIC measurements validity | 26919 | 0 | 326920 | 4 |  | Rail pressure (Jichai) Validity | BOOL | [5 empty] | X
EIC measurements value | 26020 | 15 | 326021 | 4 |  | Engine Actual Exhaust 1 Oxygen (SPN 1119) Validity | INT16u | AB |  |  |  |  | X
PV monitoring area | 40000 |  | 340001 | 4 |  | DC voltage string 05 | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 40001 |  | 340002 | 4 |  | DC power string 05 | INT16s | AB | 1 | kW |  |  | X
PV monitoring area | 40002 |  | 340003 | 4 |  | DC voltage string 06 | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 40003 |  | 340004 | 4 |  | DC power string 06 | INT16s | AB | 1 | kW |  |  | X
PV monitoring area | 40004 |  | 340005 | 4 |  | DC voltage string 07 | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 40005 |  | 340006 | 4 |  | DC power string 07 | INT16s | AB | 1 | kW |  |  | X
PV monitoring area | 40006 |  | 340007 | 4 |  | DC voltage string 08 | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 40007 |  | 340008 | 4 |  | DC power string 08 | INT16s | AB | 1 | kW |  |  | X
PV monitoring area | 40008 |  | 340009 | 4 |  | DC voltage string 09 | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 40009 |  | 340010 | 4 |  | DC power string 09 | INT16s | AB | 1 | kW |  |  | X
PV monitoring area | 40010 |  | 340011 | 4 |  | DC voltage string 10 | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 40011 |  | 340012 | 4 |  | DC power string 10 | INT16s | AB | 1 | kW |  |  | X
PV monitoring area | 40012 |  | 340013 | 4 |  | DC voltage string 11 | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 40013 |  | 340014 | 4 |  | DC power string 11 | INT16s | AB | 1 | kW |  |  | X
PV monitoring area | 40014 |  | 340015 | 4 |  | DC voltage string 12 | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 40015 |  | 340016 | 4 |  | DC power string 12 | INT16s | AB | 1 | kW |  |  | X
PV monitoring area | 40016 |  | 340017 | 4 |  | DC current string 01 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40017 |  | 340018 | 4 |  | DC current string 02 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40018 |  | 340019 | 4 |  | DC current string 03 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40019 |  | 340020 | 4 |  | DC current string 04 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40020 |  | 340021 | 4 |  | DC current string 05 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40021 |  | 340022 | 4 |  | DC current string 06 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40022 |  | 340023 | 4 |  | DC current string 07 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40023 |  | 340024 | 4 |  | DC current string 08 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40024 |  | 340025 | 4 |  | DC current string 09 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40025 |  | 340026 | 4 |  | DC current string 10 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40026 |  | 340027 | 4 |  | DC current string 11 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40027 |  | 340028 | 4 |  | DC current string 12 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40028 |  | 340029 | 4 |  | DC current string 13 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40029 |  | 340030 | 4 |  | DC current string 14 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40030 |  | 340031 | 4 |  | DC current string 15 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40031 |  | 340032 | 4 |  | DC current string 16 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40032 |  | 340033 | 4 |  | DC current string 17 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40033 |  | 340034 | 4 |  | DC current string 18 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40034 |  | 340035 | 4 |  | DC current string 19 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40035 |  | 340036 | 4 |  | DC current string 20 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40036 |  | 340037 | 4 |  | DC current string 21 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40037 |  | 340038 | 4 |  | DC current string 22 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40038 |  | 340039 | 4 |  | DC current string 23 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 40039 |  | 340040 | 4 |  | DC current string 24 | INT16u | AB | 1 | A |  |  | X
PV monitoring area | 47000 |  | 347001 | 4 |  | Inverter serial number 01-02 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47001 |  | 347002 | 4 |  | Inverter serial number 03-04 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47002 |  | 347003 | 4 |  | Inverter serial number 05-06 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47003 |  | 347004 | 4 |  | Inverter serial number 07-08 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47004 |  | 347005 | 4 |  | Inverter serial number 09-10 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47005 |  | 347006 | 4 |  | Inverter serial number 11-12 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47006 |  | 347007 | 4 |  | Inverter serial number 13-14 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47007 |  | 347008 | 4 |  | Inverter serial number 15-16 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47008 |  | 347009 | 4 |  | Inverter serial number 17-18 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47009 |  | 347010 | 4 |  | Inverter serial number 19-20 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47010 |  | 347011 | 4 |  | Inverter serial number 21-22 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47011 |  | 347012 | 4 |  | Inverter serial number 23-24 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47012 |  | 347013 | 4 |  | Inverter serial number 25-26 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47013 |  | 347014 | 4 |  | Inverter serial number 27-28 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47014 |  | 347015 | 4 |  | Inverter serial number 19-30 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47015 |  | 347016 | 4 |  | Inverter serial number 31-32 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47016 |  | 347017 | 4 |  | Inverter model 01-02 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47017 |  | 347018 | 4 |  | Inverter model 03-04 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47018 |  | 347019 | 4 |  | Inverter model 05-06 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47019 |  | 347020 | 4 |  | Inverter model 07-08 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47020 |  | 347021 | 4 |  | Inverter model 09-10 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47021 |  | 347022 | 4 |  | Inverter model 11-12 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47022 |  | 347023 | 4 |  | Inverter model 13-14 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47023 |  | 347024 | 4 |  | Inverter model 15-16 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47024 |  | 347025 | 4 |  | Inverter model 17-18 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47025 |  | 347026 | 4 |  | Inverter model 19-20 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47026 |  | 347027 | 4 |  | Inverter model 21-22 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47027 |  | 347028 | 4 |  | Inverter model 23-24 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47028 |  | 347029 | 4 |  | Inverter model 25-26 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47029 |  | 347030 | 4 |  | Inverter model 27-28 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47030 |  | 347031 | 4 |  | Inverter model 19-30 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47031 |  | 347032 | 4 |  | Inverter model 31-32 (format maker-dependent) | string | AB | 0 |  |  |  | X
PV monitoring area | 47032 |  | 347033 | 4 |  | Rated active power size | INT16u | AB | 1 | kW |  |  | X
PV monitoring area | 47033 |  | 347034 | 4 |  | Rated reactive power size | INT16u | AB | 1 | kVAr |  |  | X
PV monitoring area | 47034 |  | 347035 | 4 |  | Country code (format maker-dependent) | INT16u | AB | 0 |  |  |  | X
PV monitoring area | 47035 |  | 347036 | 4 |  | DC voltage string 01 | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 47036 |  | 347037 | 4 |  | DC power string 01 | INT16s | AB | 1 | kW |  |  | X
PV monitoring area | 47037 |  | 347038 | 4 |  | DC voltage string 02 | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 47038 |  | 347039 | 4 |  | DC power string 02 | INT16s | AB | 1 | kW |  |  | X
PV monitoring area | 47039 |  | 347040 | 4 |  | DC voltage string 03 | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 47040 |  | 347041 | 4 |  | DC power string 03 | INT16s | AB | 1 | kW |  |  | X
PV monitoring area | 47041 |  | 347042 | 4 |  | DC voltage string 04 | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 47042 |  | 347043 | 4 |  | DC power string 04 | INT16s | AB | 1 | kW |  |  | X
PV monitoring area | 47043 |  | 347044 | 4 |  | AC active power | INT16s | AB | 1 | kW |  |  | X
PV monitoring area | 47044 |  | 347045 | 4 |  | AC reactive power | INT16s | AB | 1 | kVAr |  |  | X
PV monitoring area | 47045 |  | 347046 | 4 |  | AC apparent power | INT16s | AB | 1 | kVA |  |  | X
PV monitoring area | 47046 |  | 347047 | 4 |  | Energy produced | INT32u | ABCD | 0 | kWh |  |  | X
PV monitoring area | 47048 |  | 347049 | 4 |  | Energy produced today | INT32u | ABCD | 1 | kWh |  |  | X
PV monitoring area | 47050 |  | 347051 | 4 |  | Operating hours | INT32u | ABCD | 0 | hour |  |  | X
PV monitoring area | 47052 |  | 347053 | 4 |  | Operating minutes today | INT16u | AB | 0 | minute |  |  | X
PV monitoring area | 47053 |  | 347054 | 4 |  | Cabinet temperature | INT16s | AB | 1 | Deg C |  |  | X
PV monitoring area | 47054 |  | 347055 | 4 |  | Phase1 to neutral PV voltage | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 47055 |  | 347056 | 4 |  | Phase2 to neutral PV voltage | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 47056 |  | 347057 | 4 |  | Phase3 to neutral PV voltage | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 47057 |  | 347058 | 4 |  | Phase1 to phase2 PV voltage | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 47058 |  | 347059 | 4 |  | Phase2 to phase3 PV voltage | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 47059 |  | 347060 | 4 |  | Phase3 to phase1 PV voltage | INT16u | AB | 1 | V |  |  | X
PV monitoring area | 47060 |  | 347061 | 4 |  | Grid frequency | INT16u | AB | 1 | Hz |  |  | X
PV monitoring area | 47061 |  | 347062 | 4 |  | Active power reference (format maker-dependent) | INT16s | AB | 0 |  |  |  | X
PV monitoring area | 47062 |  | 347063 | 4 |  | Reactive power reference (format maker-dependent) | INT16s | AB | 0 |  |  |  | X
PV monitoring area | 47063 |  | 347064 | 4 |  | Inverter state (format maker-dependent) | INT16u | AB | 0 |  |  |  | X
PV monitoring area | 47064 |  | 347065 | 4 |  | Fault code (format maker-dependent) | INT16u | AB | 0 |  |  |  | X
PV monitoring area | 47069 |  | 347070 | 4 |  | 0: Inverter not alive on communication link. 1: Inverter alive on communication link. | INT16s | AB | 0 |  |  |  | X
PV monitoring area | 49940 |  | 349941 | 4 |  | PV monitoring version | INT16u | AB | 0 |  |  |  | X
PV monitoring area | 49941 |  | 349942 | 4 |  | PV protocol selection | INT16u | AB | 0 |  |  |  | X
PV monitoring area | 49942 |  | 349943 | 4 |  | PV protocol selection 01-02 (string access) | string | AB | 0 |  |  |  | X
PV monitoring area | 49943 |  | 349944 | 4 |  | PV protocol selection 03-04 (string access) | string | AB | 0 |  |  |  | X
PV monitoring area | 49944 |  | 349945 | 4 |  | PV protocol selection 05-06 (string access) | string | AB | 0 |  |  |  | X
PV monitoring area | 49945 |  | 349946 | 4 |  | PV protocol selection 07-08 (string access) | string | AB | 0 |  |  |  | X
PV monitoring area | 49946 |  | 349947 | 4 |  | PV protocol selection 09-10 (string access) | string | AB | 0 |  |  |  | X
PV monitoring area | 49947 |  | 349948 | 4 |  | PV protocol selection 11-12 (string access) | string | AB | 0 |  |  |  | X
PV monitoring area | 49948 |  | 349949 | 4 |  | PV protocol selection 13-14 (string access) | string | AB | 0 |  |  |  | X
PV monitoring area | 49949 |  | 349950 | 4 |  | PV protocol selection 15-16 (string access) | string | AB | 0 |  |  |  | X
PV monitoring area | 49950 |  | 349951 | 4 |  | PV protocol selection 17-18 (string access) | string | AB | 0 |  |  |  | X
PV monitoring area | 49951 |  | 349952 | 4 |  | PV protocol selection 19-20 (string access) | string | AB | 0 |  |  |  | X
PV monitoring area | 49952 |  | 349953 | 4 |  | Monitoring enabled: 0: Disabled. 1: Enabled | INT16u | AB | 0 |  |  |  | X
PV monitoring area | 49953 |  | 349954 | 4 |  | Number of inverter to monitor | INT16u | AB | 0 |  |  |  | X
PV monitoring area | 49954 |  | 349955 | 4 |  | Number of inverters missing | INT16u | AB | 0 |  |  |  | X
PV monitoring area | 49955 |  | 349956 | 4 |  | Lowest inverter ID missing | INT16u | AB | 0 |  |  |  | X
PV monitoring area | 49956 |  | 349957 | 4 |  | Highest inverter ID missing | INT16u | AB | 0 |  |  |  | X
PV monitoring area | 49957 |  | 349958 | 4 |  | P ref type: 0: Percentage. 1: kW | INT16u | AB | 0 |  |  |  | X
PV monitoring area | 49958 |  | 349959 | 4 |  | Q ref type: 0: Percentage. 1: kW. 2: Cos phi. 3: PF | INT16u | AB | 0 |  |  |  | X
PV monitoring area | 49959 |  | 349960 | 4 |  | P ref resolution: 0: zero decimals. 1: one decimal. 2: two decimals. 3: three decimals. | INT16u | AB | 0 |  |  |  | X
PV monitoring area | 49960 |  | 349961 | 4 |  | Q ref resolution: 0: zero decimals. 1: one decimal. 2: two decimals. 3: three decimals. | INT16u | AB | 0 |  |  |  | X
PV monitoring area | 49961 |  | 349962 | 4 |  | Lowest Modbus ID of the inverters | INT16u | AB | 0 |  |  |  | X
Note on A4: More information about each function group is available in the description sheet.
Note on C4: Bit location of the function in the associated Modbus address.
Note on E4: 04 - Read single or multiple
Note on F4: The parameter number of the function.
Note on G4: The controller function name shows the name of the parameter in the Utility Software. Some functions might contain additional information.
Note on I4: AB - Most significant byte first ABCD - Most significant byte first and most significant word first
Note on J4: Example: Scaling = 1 Read Data = 266 Actual value = 26,6
Note on K4: Unit of the associated function
Note on L4: Indicates if the address is available in the BUS TIE breaker controller.
Note on M4: Indicates if the address is available in the MAINS controller.
Note on N4: Indicates if the address is available in the GENSET controller.