## Modbus client
Solar Modbus client
These are the ASC-4 and ASC 150 Solar Modbus client tables (Revision G). They were last updated for ASC-4 software version 4.26 and AGC 150 software version 1.17.
See the ASC-4 Modbus client User manual for more information.
See the DEIF hybrid controller compatibility application note for details of the makers and inverter types supported by each PV protocol (ASC parameter 7561) selection.
PV protocol (ASC parameter 7561) | ABB PRO | ABB PVS800 | ABB TRIO | ABB Trio 50 | CPS (Chint Power) 14/36 kW | CPS (Chint Power) 50/60kW | CPS (Chint Power) Boost 100-250kW | DEIF Open | Delta RPI | Delta RPI M88H | Deye SUN 30-50k-G03 | EVVO | FIMER PVS980 | Fronius before 3.7.1-5 (1) | Gamesa E-series | Goodwe DT series | Goodwe HT series | Goodwe MT series | Growatt CP100-CP250 | Growatt CP500-CP2520 | Growatt MAC, MAX and MID series | Growatt UE-series | Havells 1-40kW | Havells 50-70kW | Havells 80-136kW | HiQ solar truestring | Huawei smartlogger | Huawei SUN2000 100-125M0-M2 | Huawei SUN2000 33-40KTL | Huawei SUN2000 50-60KTL | Huawei SUN2000 55-60KTL | Huawei SUN2000 8-28KTL | Huawei SUN2000 90-105KTL | Huawei V.3 | Ingeteam 3Play - ABI (2) | Ingeteam 3Play- ABS | INVT BG series | INVT XG series | Kehua SPI | KStar | Matter Energy SPI20k-160k | Polycab 50-60kW | PowerOne | Scheider Conext CL 20/25 | Scheider Conext CL 30/33/50/60 (3) | SMA cluster controller | SMA Data Manager | SMA FSC | SMA Solid-Q 50 | SMA Solid-Q PRO 60 | SMA SunSpec before v2.82 (4) | Sofar -G3 | Sofar Solar 1-40kW | Sofar Solar 50-70kW | Sofar Solar 80-136kW | SolarEdge | SolarEdge PPC | Solis Logger NISE | Solis (Ginlong) | Sungrow Logger 1000 | Sungrow SG series | SunSpec Generic | Thea | Vacon8000
Protocol number (address 49941) | 11 | 7 | 10 | 32 | 28 | 27 | 66 | 5 | 12 | 37 | 76 | 42 | 56 | 3 | 9 | 17 | 59 | 33 | 67 | 68 | 69 | 48 | 64 | 61 | 53 | 20 | 16 | 40 | 15 | 41 | 34 | 14 | 35 | 63 | 21 | 87 | 19 | 79 | 97 | 31 | 78 | 58 | 93 | 8 | 4 | 18 | 71 | 1 | 29 | 30 | 2 | 90 | 65 | 62 | 75 | 23 | 82 | 94 | 22 | 46 | 13 | 6 | 74 | 26
From ASC 150 SW version | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | - | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | - | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.16 | 1.15 | 1.15 | 1.17 | 1.15 | 1.15 | 1.15 | 1.17 | 1.15 | 1.15 | 1.15 | 1.15 | - | 1.15 | 1.15 |  | 1.16 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.17 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15
From ASC-4 SW version | 4.00 | 4.00 | 4.00 | 4.11 | 4.10 | 4.10 | 4.20 | - | 4.00 | 4.12 | 4.23 | 4.12 | 4.19 | 4.00 | - | 4.01 | 4.19 | 4.11 | 4.21 | 4.21 | 4.21 | 4.16 | 4.20 | 4.20 | 4.18 | 4.04 | - | 4.12 | 4.00 | 4.12 | 4.11 | 4.00 | 4.11 | 4.20 | 4.04 | 4.26 | 4.02 | 4.24 | 4.26 | 4.11 | 4.24 | 4.19 | 4.26 | 4.00 | 4.01 | 4.01 | 4.21 | - | 4.10 | 4.10 | 4.00/4.01 | 4.26 | 4.20 | 4.20 | 4.23 | 4.10 | 4.24 | 4.26 | 4.05 | 4.16 | 4.00 | 4.00 | 4.23 | 4.10
From AGC 150 Hybrid SW version | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.09 | - | 1.04 | 1.04 | 1.12 | 1.04 | 1.08 | 1.04 | - | 1.09 | 1.09 | 1.09 | 1.10 | 1.10 | 1.10 | 1.06 | 1.09 | 1.09 | 1.08 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.09 | 1.04 | 1.16 | 1.04 | 1.13 | 1.17 | 1.04 | 1.13 | 1.08 | 1.17 | 1.04 | 1.04 | 1.04 | 1.10 | - | 1.04 | 1.04 |  | 1.16 | 1.09 | 1.04 | 1.04 | 1.04 | 1.15 | 1.17 | 1.04 | 1.06 | 1.04 | 1.04 | 1.12 | 1.04
Inverter serial number | X |  | X | X |  |  |  |  | X | X | x | X | X | X |  | X | X | X |  |  | X | X | X | X | X | X |  |  |  | X |  |  | X | X |  |  | X | X | X |  | X | X | X | X | X | X |  |  | X | X | X | X | X | X | X | X | X |  | X | X | X | X | X
Inverter model | X |  | X | X | X | X | X |  |  | X |  |  |  | X |  | X | X | X | [11 empty] | X |  |  | X | X |  |  | X |  | X |  | X |  |  | X | [6 empty] | X |  |  |  |  | X |  |  |  | X |  | X | X
Rated power size | [37 empty] | X | [6 empty] | X | [11 empty] | X |  |  | X | X |  | X
Rated reactive power size | [44 empty] | X | [11 empty] | X |  |  | X | X
Country code | X |  | X | X | [5 empty] | X |  | X | [10 empty] | X | X | [17 empty] | X |  |  | X | [7 empty] | X | X |  |  |  |  | X |  | X
DC voltage string 01 | X | X | X | X | X | X | X |  | X | X | X | X |  | X |  | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  |  | X | X | X | X | X | X | X | X |  | X | X |  | X | X | X | X
DC power string 01 | X | X | X | X | X | X | X |  | X | X | X | X |  | X |  | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  |  | X | X | X | X | X | X | X | X |  | X | X |  | X | X | X
DC voltage string 02 |  |  | X |  | X | X | X |  | X |  | X | X |  |  |  | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X | X |  |  |  | X | X | X | X | X | X | X |  |  | X | X |  | X |  | X
DC power string 02 |  |  | X |  | X | X | X |  | X |  | X | X |  |  |  | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X | X |  |  |  | X | X | X | X | X | X | X |  |  | X | X |  | X |  | X
DC voltage string 03 |  |  |  |  | X | X | X |  |  |  | X | X |  |  |  |  | X |  |  |  | X | X | X | X | X | X |  | X | X | X | X | X | X | X |  |  |  | X | X | X | X | X | X |  | X |  |  |  | X | X |  | X | X | X | X |  |  | X | X |  | X |  | X
DC power string 03 |  |  |  |  | X | X | X |  |  |  | X | X |  |  |  |  | X |  |  |  | X | X | X | X | X | X |  | X | X | X | X | X | X | X |  |  |  | X | X | X | X | X | X |  | X |  |  |  | X | X |  | X | X | X | X |  |  | X | X |  | X |  | X
DC voltage string 04 | [6 empty] | X |  |  |  | X | X |  |  |  |  | X |  |  |  | X | X | X | X | X | X |  | X | X | X | X | X | X | X |  |  |  | X | X |  | X | X | X |  | X | [6 empty] | X | X | X | X |  |  | X | X |  | X |  | X
DC power string 04 | [6 empty] | X |  |  |  | X | X |  |  |  |  | X |  |  |  | X | X | X | X | X | X |  | X | X | X | X | X | X | X |  |  |  | X | X |  | X | X | X |  | X | [6 empty] | X | X | X | X |  |  | X | X |  | X |  | X
AC active power | X | X | X | X | X | X | X |  | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
AC reactive power | X | X | X | X | X | X | X |  | X | X | X | X | X | X |  |  |  |  | X | X |  | X | X | X | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
AC apparent power | X | X | X | X | X | X | X |  | X | X | X | X |  | X |  |  |  |  | X | X |  | X |  |  | X |  |  | X | X | X | X | X | X |  | X | X | X |  | X | X | X | X | X | X | X | X |  |  | X | X | X | X |  |  | X | X | X | X | X |  | X | X
Energy produced | X | X | X | X | X | X | X |  | X | X |  | X | X | X |  | X | X | X | X | X | X | X | X | X |  | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X |  |  | X | X | X |  | X | X |  | X | X | X | X | X | X | X | X | X
Energy produced today | X |  | X | X | X | X | X |  | X | X |  | X | X |  |  | X | X | X | X | X | X | X | X | X |  |  |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X |  |  | X | X |  |  | X | X |  |  | X | X | X | X | X |  | X | X
Operating hours | X | X | [6 empty] | X | X | X | X |  |  |  | X | X | X | X | X | X | X | X | X | [10 empty] | X | X | X | [5 empty] | X | X | X | X |  |  | X | X |  |  | X | X |  |  | X |  |  |  | X |  | X | X
Operating minutes today | [8 empty] | X |  | X | X | [6 empty] | X | X |  |  | X | X | [18 empty] | X |  | X | [7 empty] | X | X |  |  | X |  |  |  | X |  |  | X
Cabinet temperature | X | X | X | X | X | X | X |  | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X | X |  | X |  | X | X | X | X | X | X | X |  |  | X | X | X | X | X | X | X | X | X | X |  |  | X | X | X |  | X | X |  | X |  | X | X |  | X | X | X | X
Phase1 to neutral PV voltage | X | X | X | X | [5 empty] | X | X | X |  | X |  | X | X | X |  |  | X |  | X | X | X | X |  | X | X | X | X |  | X | X | X | X | X | X | X |  | X |  | X | X | X | X | X |  | X |  | X | X | X | X | X | X | X | X |  |  | X | X | X
Phase2 to neutral PV voltage | X | X | [7 empty] | X | X | X |  | X |  | X | X | X |  |  | X |  | X | X | X | X |  | X | X | X | X |  | X | X | X | X | X | X | X |  | X |  | X | X | X | X | X |  | X |  | X | X | X | X | X | X | X | X |  |  | X | X | X
Phase3 to neutral PV voltage | X | X | [7 empty] | X | X | X |  | X |  | X | X | X |  |  | X |  | X | X | X | X |  | X | X | X | X |  | X | X | X | X | X | X | X |  | X |  | X | X | X | X | X |  | X |  | X | X | X | X | X | X | X | X |  |  | X | X | X
Phase1 to phase2 PV voltage | X |  |  |  | X | X | X |  | X | X | X |  | X | X |  |  | X |  | X | X | X | X | [5 empty] | X | X | X | X | X | X | X |  |  |  | X |  | X |  | X | X | X | X | X | X |  |  | X | X |  |  |  |  | X | X |  | X |  | X | X |  | X
Phase2 to phase3 PV voltage | X |  |  |  | X | X | X |  |  | X | X |  | X | X |  |  | X |  | X | X | X | X | [5 empty] | X | X | X | X | X | X | X |  |  |  | X |  | X |  | X | X | X | X | X | X |  |  | X | X |  |  |  |  | X | X |  | X |  | X | X
Phase3 to phase1 PV voltage | X |  |  |  | X | X | X |  |  | X | X |  | X | X |  |  | X |  | X | X | X | X | [5 empty] | X | X | X | X | X | X | X |  |  |  | X |  | X |  | X | X | X | X | X | X |  |  | X | X |  |  |  |  | X | X |  | X |  | X | X
Grid frequency | X | X | X | X | X | X | X |  | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X | X |  | X |  | X | X | X | X
Active power reference | X | X | X | X | X | X | X |  | X | X | X | X | X | X |  | X | X | X | X | X | X |  | X | X | X | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X | X
Reactive power reference | X | X | X | X | X | X | X |  | X | X | X | X | X | X |  | X | X | X | X | X | X |  | X | X | X | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  |  | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X | X
Inverter state | X | X | X | X | X | X | X |  | X | X | X |  | X | X |  | X | X | X | X | X | X |  | X | X | X | X |  | X | X | X | X | X | X | X |  |  | X | X | X | X | X | X | X | X | X |  |  |  | X | X | X | X | X | X | X | X | X |  | X | X | X | X | X | X
Fault code | X | X | X | X | X | X | X |  |  | X | [5 empty] | X |  | X |  |  | X | X | X | X | [5 empty] | X |  |  | X | X |  |  | X | X |  | X |  |  |  | X | X |  |  |  | X | X |  |  | X | X |  |  | X |  |  |  | X |  | X | X
Inverter alive | X | X | X | X | X | X | X |  | X | X | X | X | X | X |  | X | X | X | X | X | X |  | X | X |  | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X | X
Notes
X marks supported data. If the data is not available, the ASC presents it as "Not available".
(1) Fronius before 3.7.1-5 is only for older Fronius systems. For more recent systems, use SunSpec Generic.
(2) Ingeteam 3Play - ABI was previously Ingeteam 3Play.
(3) Scheider Conext CL 30/33/50/60 was previously Scheider Conext CL 60.
(4) SMA SunSpec v2.82 is only for older SMA systems below version 2.82. For more recent systems, use SunSpec Generic.

## Modbus server addresses
Input register (04) - Modbus server
The ASC Modbus client can poll key data from the inverter(s) and place it in the designated Modbus server area for a monitoring system to read. PV monitoring can be used with unicast and broadcast topologies. The number of nodes determines the number of inverters the ASC should poll data from. A maximum of 42 nodes can be monitored. The ASC expects that the ModbusIDs of the inverters are consecutive in order starting from the selected ModbusID and forward. 70 registers are reserved for each inverter. The Modbus addresses are only for the first inverter. Registers for additional inverters are consecutive.
The ASC-4 Modbus server tables and ASC 150 Modbus server tables include the PV monitoring addresses for the first inverter. These are also given below.
Function group | Modbus address | Bit | PLC address | Modbus function code | Channel | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | SOLAR | BATT
PV monitoring area | 47000 |  | 347001 | 04 |  | Inverter serial number 01-02 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47001 |  | 347002 | 04 |  | Inverter serial number 03-04 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47002 |  | 347003 | 04 |  | Inverter serial number 05-06 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47003 |  | 347004 | 04 |  | Inverter serial number 07-08 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47004 |  | 347005 | 04 |  | Inverter serial number 09-10 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47005 |  | 347006 | 04 |  | Inverter serial number 11-12 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47006 |  | 347007 | 04 |  | Inverter serial number 13-14 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47007 |  | 347008 | 04 |  | Inverter serial number 15-16 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47008 |  | 347009 | 04 |  | Inverter serial number 17-18 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47009 |  | 347010 | 04 |  | Inverter serial number 19-20 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47010 |  | 347011 | 04 |  | Inverter serial number 21-22 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47011 |  | 347012 | 04 |  | Inverter serial number 23-24 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47012 |  | 347013 | 04 |  | Inverter serial number 25-26 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47013 |  | 347014 | 04 |  | Inverter serial number 27-18 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47014 |  | 347015 | 04 |  | Inverter serial number 19-30 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47015 |  | 347016 | 04 |  | Inverter serial number 31-32 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47016 |  | 347017 | 04 |  | Inverter model 01-02 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47017 |  | 347018 | 04 |  | Inverter model 03-04 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47018 |  | 347019 | 04 |  | Inverter model 05-06 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47019 |  | 347020 | 04 |  | Inverter model 07-08 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47020 |  | 347021 | 04 |  | Inverter model 09-10 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47021 |  | 347022 | 04 |  | Inverter model 11-12 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47022 |  | 347023 | 04 |  | Inverter model 13-14 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47023 |  | 347024 | 04 |  | Inverter model 15-16 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47024 |  | 347025 | 04 |  | Inverter model 17-18 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47025 |  | 347026 | 04 |  | Inverter model 19-20 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47026 |  | 347027 | 04 |  | Inverter model 21-22 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47027 |  | 347028 | 04 |  | Inverter model 23-24 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47028 |  | 347029 | 04 |  | Inverter model 25-26 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47029 |  | 347030 | 04 |  | Inverter model 27-18 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47030 |  | 347031 | 04 |  | Inverter model 19-30 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47031 |  | 347032 | 04 |  | Inverter model 31-32 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47032 |  | 347033 | 04 |  | Rated power size | INT16u | AB | 1 | kW | X | X
PV monitoring area | 47033 |  | 347034 | 04 |  | Rated reactive power size | INT16u | AB | 1 | kVAr | X | X
PV monitoring area | 47034 |  | 347035 | 04 |  | Country code (format maker-dependent) | INT16u | AB | 0 |  | X | X
PV monitoring area | 47035 |  | 347036 | 04 |  | DC voltage string 01 | INT16u | AB | 1 | V | X | X
PV monitoring area | 47036 |  | 347037 | 04 |  | DC power string 01 | INT16s | AB | 1 | kW | X | X
PV monitoring area | 47037 |  | 347038 | 04 |  | DC voltage string 02 | INT16u | AB | 1 | V | X | X
PV monitoring area | 47038 |  | 347039 | 04 |  | DC power string 02 | INT16s | AB | 1 | kW | X | X
PV monitoring area | 47039 |  | 347040 | 04 |  | DC voltage string 03 | INT16u | AB | 1 | V | X | X
PV monitoring area | 47040 |  | 347041 | 04 |  | DC power string 03 | INT16s | AB | 1 | kW | X | X
PV monitoring area | 47041 |  | 347042 | 04 |  | DC voltage string 04 | INT16u | AB | 1 | V | X | X
PV monitoring area | 47042 |  | 347043 | 04 |  | DC power string 04 | INT16s | AB | 1 | kW | X | X
PV monitoring area | 47043 |  | 347044 | 04 |  | AC active power | INT16s | AB | 1 | kW | X | X
PV monitoring area | 47044 |  | 347045 | 04 |  | AC reactive power | INT16s | AB | 1 | kVAr | X | X
PV monitoring area | 47045 |  | 347046 | 04 |  | AC apparent power | INT16s | AB | 1 | kVA | X | X
PV monitoring area | 47046 |  | 347047 | 04 |  | Energy produced | INT32u | ABCD | 0 | kWh | X | X
PV monitoring area | 47048 |  | 347049 | 04 |  | Energy produced today | INT32u | ABCD | 1 | kWh | X | X
PV monitoring area | 47050 |  | 347051 | 04 |  | Operating hours | INT32u | ABCD | 0 | hour | X | X
PV monitoring area | 47052 |  | 347053 | 04 |  | Operating minutes today | INT16u | AB | 0 | minute | X | X
PV monitoring area | 47053 |  | 347054 | 04 |  | Cabinet temperature | INT16s | AB | 1 | Deg C | X | X
PV monitoring area | 47054 |  | 347055 | 04 |  | Phase1 to neutral PV voltage | INT16u | AB | 1 | V | X | X
PV monitoring area | 47055 |  | 347056 | 04 |  | Phase2 to neutral PV voltage | INT16u | AB | 1 | V | X | X
PV monitoring area | 47056 |  | 347057 | 04 |  | Phase3 to neutral PV voltage | INT16u | AB | 1 | V | X | X
PV monitoring area | 47057 |  | 347058 | 04 |  | Phase1 to phase2 PV voltage | INT16u | AB | 1 | V | X | X
PV monitoring area | 47058 |  | 347059 | 04 |  | Phase2 to phase3 PV voltage | INT16u | AB | 1 | V | X | X
PV monitoring area | 47059 |  | 347060 | 04 |  | Phase3 to phase1 PV voltage | INT16u | AB | 1 | V | X | X
PV monitoring area | 47060 |  | 347061 | 04 |  | Grid frequency | INT16u | AB | 1 | Hz | X | X
PV monitoring area | 47061 |  | 347062 | 04 |  | Active power reference (format maker-dependent) | INT16s | AB | 0 |  | X | X
PV monitoring area | 47062 |  | 347063 | 04 |  | Reactive power reference (format maker-dependent) | INT16s | AB | 0 |  | X | X
PV monitoring area | 47063 |  | 347064 | 04 |  | Inverter state (format maker-dependent) | INT16u | AB | 0 |  | X | X
PV monitoring area | 47064 |  | 347065 | 04 |  | Fault code (format maker-dependent) | INT16u | AB | 0 |  | X | X
PV monitoring area | 47069 |  | 347070 | 04 |  | 0: Inverter not alive on communication link. 1: Inverter alive on communication link. | INT16s | AB | 0 |  | X | X