## Data Range
Turbo Control (TC) Steam ¦ Turbine controller
Modbus tables 4189341447-A
Product: TC Turbo Control - Steam ¦ Turbine
Software-Version: x.0.0.5
1 | 1000-1364 | Stop Condition
2 | 14000-14507 | Versions
3 | 15000-15036 | Electrical Data
4 | 16000-16035 | Counters
5 | 17000-17211 | Digital Input
6 | 17400-17847 | Temperature Input
7 | 18000-18013 | Digital Input Function
18817-19009
8 | 18200-18207 | Digital Output Function
19010-19203
9 | 18400-18816 | Temperature and Analog Input Function
19204-19820
10 | 50000-51000 | Write Function

## 01_Stop Condition
#VALUE! | 1000 - 1364 ¦ Stop Condition
Register | Bit | Text | Configuration | Resolution | Factor | Unit | Access
1000 |  | Level 1 stopcondition register 1
1000 | 0 | Software fault under boot | - | 1 | - | - | Read
1000 | 1 | Reboot necessary | - | 1 | - | - | Read
1000 | 2 | Wrong configuration (SERIAL) | - | 1 | - | - | Read
1000 | 3 | Wrong configuration (CAN) | - | 1 | - | - | Read
1000 | 4 | Timeout: Stopping | - | 1 | - | - | Read
1000 | 5 | Shutdown: Emergency stop button | - | 1 | - | - | Read
1000 | 6 | IO: Timeout data exchange | - | 1 | - | - | Read
1000 | 7 | Multiple IO assignment | - | 1 | - | - | Read
1000 | 8 | Watchdog relay does not work | - | 1 | - | - | Read
1000 | 9 | Safety chain does not rearm | - | 1 | - | - | Read
1000 | 10 | Safety chain does not trip | - | 1 | - | - | Read
1000 | 11 | Safety chain relay fallen off | - | 1 | - | - | Read
1000 | 12 | DI 'Emergency stop' is not assigned | - | 1 | - | - | Read
1000 | 13 | DI 'Watchdog' is not assigned | - | 1 | - | - | Read
1000 | 14 | DI 'Safety chain' is not assigned | - | 1 | - | - | Read
1000 | 15 | DO 'Trip safety chain' is not assigned | - | 1 | - | - | Read
1001 |  | Level 1 stopcondition register 2
1001 | 0 | DO 'Rearm safety chain' is not assigned | - | 1 | - | - | Read
1001 | 1 | DO 'GCB on' is not assigned | - | 1 | - | - | Read
1001 | 2 | DO 'GCB off' is not assigned | - | 1 | - | - | Read
1001 | 3 | DO 'GCB trip' is not assigned | - | 1 | - | - | Read
1001 | 4 | AO 'Steam valve' is not assigned | - | 1 | - | - | Read
1001 | 5 | AO 'Voltage regulator' is not assigned | - | 1 | - | - | Read
1001 | 6 | AI 'Generator power' is not assigned | - | 1 | - | - | Read
1001 | 7 | DO 'GCB Release' is not assigned | - | 1 | - | - | Read
2000 |  | Level 2 stopcondition register 1
2000 | 0 | File from different project | - | 1 | - | - | Read
2000 | 1 | File from test version | - | 1 | - | - | Read
2000 | 2 | File from older version (incompatible) | - | 1 | - | - | Read
2000 | 3 | Shutdown selected | - | 1 | - | - | Read
2000 | 4 | Test mode | - | 1 | - | - | Read
2000 | 5 | IO card uncalibrated | - | 1 | - | - | Read
2000 | 6 | IO card 3 outputs overloaded or voltage out of range | - | 1 | - | - | Read
2000 | 7 | IO card 4 outputs overloaded or voltage out of range | - | 1 | - | - | Read
2000 | 8 | IO card 5 outputs overloaded or voltage out of range | - | 1 | - | - | Read
2000 | 9 | IO card 6 outputs overloaded or voltage out of range | - | 1 | - | - | Read
2000 | 10 | IO card 7 outputs overloaded or voltage out of range | - | 1 | - | - | Read
2000 | 11 | IO card 8 outputs overloaded or voltage out of range | - | 1 | - | - | Read
2000 | 12 | IO card 9: outputs overloaded or voltage out of range | - | 1 | - | - | Read
2000 | 13 | IO card 10: outputs overloaded or voltage out of range | - | 1 | - | - | Read
2000 | 14 | IO card 11: outputs overloaded or voltage out of range | - | 1 | - | - | Read
2000 | 15 | IO card 12: outputs overloaded or voltage out of range | - | 1 | - | - | Read
2001 |  | Level 2 stopcondition register 2
2001 | 0 | IO card 13: outputs overloaded or voltage out of range | - | 1 | - | - | Read
2001 | 1 | IO card 14: outputs overloaded or voltage out of range | - | 1 | - | - | Read
2001 | 2 | Modbus master: initialization error | - | 1 | - | - | Read
2001 | 3 | Modbus master: timeout modbus master | - | 1 | - | - | Read
2001 | 4 | Timeout: Start preparation | - | 1 | - | - | Read
2001 | 5 | Timeout: Starting | - | 1 | - | - | Read
2001 | 6 | Timeout: Acceleration 1 | - | 1 | - | - | Read
2001 | 7 | Timeout: Acceleration 2 | - | 1 | - | - | Read
2001 | 8 | Timeout: Acceleration 3 | - | 1 | - | - | Read
2001 | 9 | Timeout: Deload | - | 1 | - | - | Read
2001 | 10 | Operation blocked on switchboard panel | - | 1 | - | - | Read
2001 | 11 | PickUp signals: faulty - Shutdown | - | 1 | - | - | Read
2001 | 12 | PickUp signals: faulty - Stopping | - | 1 | - | - | Read
2001 | 13 | Overspeed primary - Shutdown | - | 1 | - | - | Read
2001 | 14 | Overspeed secondary - Shutdown | - | 1 | - | - | Read
2001 | 15 | PickUp 1 config: Resulting max frequency > 20kHz | - | 1 | - | - | Read
2002 |  | Level 2 stopcondition register 3
2002 | 0 | PickUp 2 config: Resulting max frequency > 20kHz | - | 1 | - | - | Read
2002 | 2 | Turbine not running but voltage detected | - | 1 | - | - | Read
2002 | 3 | Stop due to time switch function | - | 1 | - | - | Read
2002 | 4 | Too long in critical speed 1 | - | 1 | - | - | Read
2002 | 5 | Too long in critical speed 2 | - | 1 | - | - | Read
2002 | 6 | Shutdown: Speed control deviation too high | - | 1 | - | - | Read
2002 | 7 | Shutdown: Power control deviation too high | - | 1 | - | - | Read
2002 | 8 | Stop: Speed control deviation too high | - | 1 | - | - | Read
2002 | 9 | Stop: Power control deviation too high | - | 1 | - | - | Read
2002 | 10 | Wrong sensor configuration cold junction A | - | 1 | - | - | Read
2002 | 11 | Wrong sensor configuration cold junction B | - | 1 | - | - | Read
2002 | 12 | Wire break generator power | - | 1 | - | - | Read
2002 | 13 | Analog power limitation input defective | - | 1 | - | - | Read
2002 | 14 | Grid protection: Too many mains failures | - | 1 | - | - | Read
2002 | 15 | Grid protection 2 Stop: Overvoltage delta | - | 1 | - | - | Read
2003 |  | Level 2 stopcondition register 4
2003 | 0 | Grid protection 2 Stop: Overvoltage star | - | 1 | - | - | Read
2003 | 1 | Grid protection 2 Stop: Undervoltage delta | - | 1 | - | - | Read
2003 | 2 | Grid protection 2 Stop: Undervoltage star | - | 1 | - | - | Read
2003 | 3 | Grid protection 2 Stop: Overfrequency | - | 1 | - | - | Read
2003 | 4 | Grid protection 2 Stop: Underfrequency | - | 1 | - | - | Read
2003 | 5 | Gen protection: Overvoltage delta | - | 1 | - | - | Read
2003 | 6 | Gen protection: Overvoltage star | - | 1 | - | - | Read
2003 | 7 | Gen protection: Undervoltage delta | - | 1 | - | - | Read
2003 | 8 | Gen protection: Undervoltage star | - | 1 | - | - | Read
2003 | 9 | Gen protection: Overfrequency | - | 1 | - | - | Read
2003 | 10 | Gen protection: Underfrequency | - | 1 | - | - | Read
2003 | 11 | Gen protection: Overcurrent 1 | - | 1 | - | - | Read
2003 | 12 | Gen protection: Overcurrent 2 | - | 1 | - | - | Read
2003 | 13 | Gen protection: Current asymmetry | - | 1 | - | - | Read
2003 | 14 | Gen protection: Continuously below min power | - | 1 | - | - | Read
2003 | 15 | Gen protection: Overload 1 | - | 1 | - | - | Read
2004 |  | Level 2 stopcondition register 5
2004 | 0 | Gen protection: Overload 2 | - | 1 | - | - | Read
2004 | 1 | Gen protection: Reverse power 1 | - | 1 | - | - | Read
2004 | 2 | Gen protection: Reverse power 2 | - | 1 | - | - | Read
2004 | 3 | Gen protection: Overexcitation (reactive power export too high) | - | 1 | - | - | Read
2004 | 4 | Gen protection: Underexcitation (reactive power import too high) | - | 1 | - | - | Read
2004 | 5 | Generator breaker has tripped | - | 1 | - | - | Read
2004 | 6 | Generator breaker does not disconnect | - | 1 | - | - | Read
2004 | 7 | Generator breaker close failure | - | 1 | - | - | Read
2004 | 8 | GCB: load too high when opening | - | 1 | - | - | Read
2004 | 9 | Generator breaker position failure | - | 1 | - | - | Read
2004 | 10 | Mains breaker position failure | - | 1 | - | - | Read
2004 | 11 | Generator breaker not released, but closed | - | 1 | - | - | Read
2004 | 12 | Mains breaker could not be tripped | - | 1 | - | - | Read
2004 | 13 | U/f failure | - | 1 | - | - | Read
2004 | 14 | Voltage control does not work | - | 1 | - | - | Read
2004 | 15 | Cos phi control does not work | - | 1 | - | - | Read
2005 |  | Level 2 stopcondition register 6
2005 | 0 | Maximum speed in Test exceeded | - | 1 | - | - | Read
3000 |  | Level 3 stopcondition register 1
3000 | 0 | Operation stopped - Wait for Startpreparation | - | 1 | - | - | Read
4000 |  | Level 4 stopcondition register 1
4000 | 0 | Operation stopped - Wait for Ready | - | 1 | - | - | Read
4000 | 1 | Minimum startpreparation time running | - | 1 | - | - | Read
5000 |  | Level 5 stopcondition register 1
5000 | 0 | Operation stopped - Wait for Start | - | 1 | - | - | Read
6000 |  | Level 6 stopcondition register 1
6000 | 0 | Operation started - Wait for Acceleration 2 | - | 1 | - | - | Read
6000 | 1 | Speed limit - Idle speed 1 | - | 1 | - | - | Read
7000 |  | Level 7 stopcondition register 1
7000 | 0 | Operation started - Wait for Acceleration 3 | - | 1 | - | - | Read
7000 | 1 | Speed limit - Idle speed 2 | - | 1 | - | - | Read
8000 |  | Level 8 stopcondition register 1
8000 | 0 | Operation started - Wait for Synchronizing | - | 1 | - | - | Read
8000 | 1 | Timeout: Synchronizing | - | 1 | - | - | Read
8000 | 2 | Timeout: Synchron connect | - | 1 | - | - | Read
8000 | 3 | Timeout: Black closing | - | 1 | - | - | Read
8000 | 4 | Grid protection: Delayed synchronizing after Trip | - | 1 | - | - | Read
8000 | 5 | Grid protection 1 Trip: Overvoltage delta | - | 1 | - | - | Read
8000 | 6 | Grid protection 1 Trip: Overvoltage delta (delayed) | - | 1 | - | - | Read
8000 | 7 | Grid protection 1 Trip: Overvoltage star | - | 1 | - | - | Read
8000 | 8 | Grid protection 1 Trip: Overvoltage star (delayed) | - | 1 | - | - | Read
8000 | 9 | Grid protection 1 Trip: Undervoltage delta | - | 1 | - | - | Read
8000 | 10 | Grid protection 1 Trip: Undervoltage delta (delayed) | - | 1 | - | - | Read
8000 | 11 | Grid protection 1 Trip: Undervoltage star | - | 1 | - | - | Read
8000 | 12 | Grid protection 1 Trip: Undervoltage star (delayed) | - | 1 | - | - | Read
8000 | 13 | Grid protection 1 Trip: Overfrequency 1 | - | 1 | - | - | Read
8000 | 14 | Grid protection 1 Trip: Overfrequency (delayed) | - | 1 | - | - | Read
8000 | 15 | Grid protection 1 Trip: Underfrequency 1 | - | 1 | - | - | Read
8001 |  | Level 8 stopcondition register 2
8001 | 0 | Grid protection 1 Trip: Underfrequency (delayed) | - | 1 | - | - | Read
8001 | 1 | Grid protection 1 Trip: Vector shift | - | 1 | - | - | Read
8001 | 2 | Grid protection 1 Trip: df/dt | - | 1 | - | - | Read
8001 | 3 | Grid protection 1 Trip: Overvoltage (average) | - | 1 | - | - | Read
8001 | 4 | Grid protection 1 Trip: Current asymmetry | - | 1 | - | - | Read
8001 | 5 | Generator breaker tried to close | - | 1 | - | - | Read
8001 | 6 | Overspeed test failed | - | 1 | - | - | Read
8001 | 7 | Overspeed test active | - | 1 | - | - | Read
8001 | 8 | Speed setpoint changed (critical speed 1) | - | 1 | - | - | Read
8001 | 9 | Speed setpoint changed (critical speed 2) | - | 1 | - | - | Read
8001 | 10 | Speed input defective or turbine still running | - | 1 | - | - | Read
9000 |  | Level 9 stopcondition register 1
9000 | 0 | Operation started - Wait for Closing GCB | - | 1 | - | - | Read
11000 |  | Level 11 stopcondition register 1
11000 | 0 | Power limitation | - | 1 | - | - | Read
12000 |  | Level 12 stopcondition register 1
12000 | 0 | Parameter file transfer failed | - | 1 | - | - | Read
12000 | 1 | FT: unknown return code | - | 1 | - | - | Read
12000 | 2 | FT: service not available | - | 1 | - | - | Read
12000 | 3 | FT: error (fewer bytes) | - | 1 | - | - | Read
12000 | 4 | FT: error (bytes which make no sense) | - | 1 | - | - | Read
12000 | 5 | FT: Grid protection not updated | - | 1 | - | - | Read
12000 | 6 | FT: error (access-level too low) | - | 1 | - | - | Read
12000 | 7 | FT: return code 6 | - | 1 | - | - | Read
12000 | 8 | FT: return code 7 | - | 1 | - | - | Read
12000 | 9 | FT: parameter ID does not exist | - | 1 | - | - | Read
12000 | 10 | FT: parameter not within limits | - | 1 | - | - | Read
12000 | 11 | FT: syntax error | - | 1 | - | - | Read
12000 | 12 | FT: not logged in | - | 1 | - | - | Read
12000 | 13 | FT: engine is running | - | 1 | - | - | Read
12000 | 14 | FT: error (file too big) | - | 1 | - | - | Read
12000 | 15 | FT: MES text too long | - | 1 | - | - | Read
12001 |  | Level 12 stopcondition register 2
12001 | 0 | FT: CNT text too long | - | 1 | - | - | Read
12001 | 1 | FT: CNT unit too long | - | 1 | - | - | Read
12001 | 2 | FT: CAI text too long | - | 1 | - | - | Read
12001 | 3 | FT: CAI unit too long | - | 1 | - | - | Read
12001 | 4 | FT: TMP text too long | - | 1 | - | - | Read
12001 | 5 | HMI: Start preparation blocked | - | 1 | - | - | Read
12001 | 6 | HMI: Start blocked | - | 1 | - | - | Read
12001 | 7 | HMI: GCB close command blocked | - | 1 | - | - | Read
12001 | 8 | PickUp signals: faulty - Warning | - | 1 | - | - | Read
12001 | 9 | PickUp signals: faulty | - | 1 | - | - | Read
12001 | 10 | PickUp signal 1: faulty | - | 1 | - | - | Read
12001 | 11 | PickUp signal 2: faulty | - | 1 | - | - | Read
12001 | 12 | PickUp signals: deviation too big | - | 1 | - | - | Read
12001 | 13 | PickUp signal 1: no pulses | - | 1 | - | - | Read
12001 | 14 | PickUp signal 2: no pulses | - | 1 | - | - | Read
12001 | 15 | PickUp signal 1: Gradient to big | - | 1 | - | - | Read
12002 |  | Level 12 stopcondition register 3
12002 | 0 | PickUp signal 2: Gradient to big | - | 1 | - | - | Read
12002 | 1 | Overspeed primary - Warning | - | 1 | - | - | Read
12002 | 2 | Overspeed secondary - Warning | - | 1 | - | - | Read
12002 | 3 | Warning: Speed control deviation too high | - | 1 | - | - | Read
12002 | 4 | Warning: Power control deviation too high | - | 1 | - | - | Read
12002 | 5 | Analog power demand input defective | - | 1 | - | - | Read
12002 | 6 | Wire break cold-junction A | - | 1 | - | - | Read
12002 | 7 | Wire break cold-junction B | - | 1 | - | - | Read
12002 | 8 | Wire break extraction pressure | - | 1 | - | - | Read
12002 | 9 | Overload extraction pressure | - | 1 | - | - | Read
12002 | 10 | Wire break extraction demand | - | 1 | - | - | Read
12002 | 11 | Overload extraction demand | - | 1 | - | - | Read
12002 | 12 | LP max limit | - | 1 | - | - | Read
12002 | 13 | LP min limit | - | 1 | - | - | Read
12002 | 14 | HP max limit | - | 1 | - | - | Read
12002 | 15 | HP & LP max limit | - | 1 | - | - | Read
12003 |  | Level 12 stopcondition register 4
12003 | 0 | Grid protection 1 Trip: Undervoltage delta | - | 1 | - | - | Read
12003 | 1 | Grid protection 1 Trip: Undervoltage delta (delayed) | - | 1 | - | - | Read
12003 | 2 | Grid protection 1 Trip: Undervoltage star | - | 1 | - | - | Read
12003 | 3 | Grid protection 1 Trip: Undervoltage star (delayed) | - | 1 | - | - | Read
12003 | 4 | Grid protection 1 Trip: Overfrequency 1 | - | 1 | - | - | Read
12003 | 5 | Grid protection 1 Trip: Overfrequency (delayed) | - | 1 | - | - | Read
12003 | 6 | Grid protection 1 Trip: Underfrequency 1 | - | 1 | - | - | Read
12003 | 7 | Grid protection 1 Trip: Underfrequency (delayed) | - | 1 | - | - | Read
12003 | 8 | Grid protection 1 Trip: Vector shift | - | 1 | - | - | Read
12003 | 9 | Grid protection 1 Trip: df/dt | - | 1 | - | - | Read
12003 | 10 | Grid protection 1 Trip: Overvoltage (average) | - | 1 | - | - | Read
12003 | 11 | Grid protection 1 Trip: Current asymmetry | - | 1 | - | - | Read
12003 | 12 | Mains breaker not released, but closed | - | 1 | - | - | Read
12003 | 13 | Set system time has failed | - | 1 | - | - | Read
12003 | 14 | GOV - Limitation | - | 1 | - | - | Read
12003 | 15 | EXT - LP Limitation | - | 1 | - | - | Read
12900 |  | AGC stopcondition register 1
12900 | 0 | AGC4: reverse power 1 | - | 1 | - | - | Read
12900 | 1 | AGC4: reverse power 2 | - | 1 | - | - | Read
12900 | 2 | AGC4: Reserve | - | 1 | - | - | Read
12900 | 3 | AGC4: generator overcurrent 1 | - | 1 | - | - | Read
12900 | 4 | AGC4: generator overcurrent 2 | - | 1 | - | - | Read
12900 | 5 | AGC4: generator overcurrent 3 | - | 1 | - | - | Read
12900 | 6 | AGC4: generator overcurrent 4 | - | 1 | - | - | Read
12900 | 7 | AGC4: inversed time overcurrent | - | 1 | - | - | Read
12900 | 8 | AGC4: voltage dependent overcurrent | - | 1 | - | - | Read
12900 | 9 | AGC4: generator overcurrent 1 (high) | - | 1 | - | - | Read
12900 | 10 | AGC4: generator overcurrent 2 (high) | - | 1 | - | - | Read
12900 | 11 | AGC4: generator overvoltage 1 | - | 1 | - | - | Read
12900 | 12 | AGC4: generator overvoltage 2 | - | 1 | - | - | Read
12900 | 13 | AGC4: generator undervoltage 1 | - | 1 | - | - | Read
12900 | 14 | AGC4: generator undervoltage 2 | - | 1 | - | - | Read
12900 | 15 | AGC4: generator undervoltage 3 | - | 1 | - | - | Read
12901 |  | AGC stopcondition register 2
12901 | 0 | AGC4: generator overfrequency 1 | - | 1 | - | - | Read
12901 | 1 | AGC4: generator overfrequency 2 | - | 1 | - | - | Read
12901 | 2 | AGC4: generator overfrequency 3 | - | 1 | - | - | Read
12901 | 3 | AGC4: generator underfrequency 1 | - | 1 | - | - | Read
12901 | 4 | AGC4: generator underfrequency 2 | - | 1 | - | - | Read
12901 | 5 | AGC4: generator underfrequency 3 | - | 1 | - | - | Read
12901 | 6 | AGC4: grid overvoltage 1 | - | 1 | - | - | Read
12901 | 7 | AGC4: grid overvoltage 2 | - | 1 | - | - | Read
12901 | 8 | AGC4: grid overvoltage 3 | - | 1 | - | - | Read
12901 | 9 | AGC4: grid undervoltage 1 | - | 1 | - | - | Read
12901 | 10 | AGC4: generator overfrequency 1 | - | 1 | - | - | Read
12901 | 11 | AGC4: grid undervoltage 3 | - | 1 | - | - | Read
12901 | 12 | AGC4: grid undervoltage 4 | - | 1 | - | - | Read
12901 | 13 | AGC4: grid overfrequency 1 | - | 1 | - | - | Read
12901 | 14 | AGC4: grid overfrequency 2 | - | 1 | - | - | Read
12901 | 15 | AGC4: grid overfrequency 3 | - | 1 | - | - | Read
12902 |  | AGC stopcondition register 3
12902 | 0 | AGC4: grid underfrequency 1 | - | 1 | - | - | Read
12902 | 1 | AGC4: grid underfrequency 2 | - | 1 | - | - | Read
12902 | 2 | AGC4: grid underfrequency 3 | - | 1 | - | - | Read
12902 | 3 | AGC4: grid underfrequency 4 | - | 1 | - | - | Read
12902 | 4 | AGC4: df/dt (ROCOF) | - | 1 | - | - | Read
12902 | 5 | AGC4: vector jump | - | 1 | - | - | Read
12902 | 6 | AGC4: grid undervoltage (positive sequence) | - | 1 | - | - | Read
12902 | 7 | AGC4: generator overload 1 | - | 1 | - | - | Read
12902 | 8 | AGC4: generator overload 2 | - | 1 | - | - | Read
12902 | 9 | AGC4: generator overload 3 | - | 1 | - | - | Read
12902 | 10 | AGC4: generator overload 4 | - | 1 | - | - | Read
12902 | 11 | AGC4: generator overload 5 | - | 1 | - | - | Read
12902 | 12 | AGC4: unbalance current 1 | - | 1 | - | - | Read
12902 | 13 | AGC4: unbalance voltage | - | 1 | - | - | Read
12902 | 14 | AGC4: generator underexcitation | - | 1 | - | - | Read
12902 | 15 | AGC4: generator overexcitation | - | 1 | - | - | Read
12903 |  | AGC stopcondition register 4
12903 | 0 | AGC4: Reserve | - | 1 | - | - | Read
12903 | 1 | AGC4: synchronizing failure GCB | - | 1 | - | - | Read
12903 | 2 | AGC4: synchronizing failure MCB | - | 1 | - | - | Read
12903 | 3 | AGC4: phase sequence failure | - | 1 | - | - | Read
12903 | 4 | AGC4: GCB open failure | - | 1 | - | - | Read
12903 | 5 | AGC4: GCB close failure | - | 1 | - | - | Read
12903 | 6 | AGC4: GCB position failure | - | 1 | - | - | Read
12903 | 7 | AGC4: MCB open failure | - | 1 | - | - | Read
12903 | 8 | AGC4: MCB close failure | - | 1 | - | - | Read
12903 | 9 | AGC4: MCB position failure | - | 1 | - | - | Read
12903 | 10 | AGC4: close excitation failure | - | 1 | - | - | Read
12903 | 11 | AGC4: Reserve | - | 1 | - | - | Read
12903 | 12 | AGC4: HVRT 1 active | - | 1 | - | - | Read
12903 | 13 | AGC4: HVRT 1 trip | - | 1 | - | - | Read
12903 | 14 | AGC4: Reserve | - | 1 | - | - | Read
12903 | 15 | AGC4: Reserve | - | 1 | - | - | Read
12904 |  | AGC stopcondition register 5
12904 | 0 | AGC4: Reserve | - | 1 | - | - | Read
12904 | 1 | AGC4: Reserve | - | 1 | - | - | Read
12904 | 2 | AGC4: Reserve | - | 1 | - | - | Read
12904 | 3 | AGC4: Reserve | - | 1 | - | - | Read
12904 | 4 | AGC4: Reserve | - | 1 | - | - | Read
12904 | 5 | AGC4: Reserve | - | 1 | - | - | Read
12904 | 6 | AGC4: undervoltage dependent reactive power 1 | - | 1 | - | - | Read
12904 | 7 | AGC4: undervoltage dependent reactive power 2 | - | 1 | - | - | Read
12904 | 8 | AGC4: GCB external trip | - | 1 | - | - | Read
12904 | 9 | AGC4: MCB external trip | - | 1 | - | - | Read
12904 | 10 | AGC4: LVRT 1 active | - | 1 | - | - | Read
12904 | 11 | AGC4: LVRT 1 trip | - | 1 | - | - | Read
12904 | 12 | AGC4: LVRT 2 active | - | 1 | - | - | Read
12904 | 13 | AGC4: LVRT 2 trip | - | 1 | - | - | Read
12904 | 14 | AGC4: active power dependent reactive power (underexcitation) | - | 1 | - | - | Read
12904 | 15 | AGC4: active power dependent reactive power (overexcitation) | - | 1 | - | - | Read
12905 |  | AGC stopcondition register 6
12905 | 0 | AGC4: stop failure | - | 1 | - | - | Read
12905 | 1 | AGC4: U< supply voltage terminal 1 | - | 1 | - | - | Read
12905 | 2 | AGC4: U> supply voltage terminal 1 | - | 1 | - | - | Read
12905 | 3 | AGC4: U< supply voltage terminal 98 | - | 1 | - | - | Read
12905 | 4 | AGC4: U> supply voltage terminal 98 | - | 1 | - | - | Read
12905 | 5 | AGC4: Reserve | - | 1 | - | - | Read
12905 | 6 | AGC4: Reserve | - | 1 | - | - | Read
12905 | 7 | AGC4: Reserve | - | 1 | - | - | Read
12905 | 8 | AGC4: Reserve | - | 1 | - | - | Read
12905 | 9 | AGC4: Reserve | - | 1 | - | - | Read
12905 | 10 | AGC4: Reserve | - | 1 | - | - | Read
12905 | 11 | AGC4: Reserve | - | 1 | - | - | Read
12905 | 12 | AGC4: Reserve | - | 1 | - | - | Read
12905 | 13 | AGC4: Reserve | - | 1 | - | - | Read
12905 | 14 | AGC4: Reserve | - | 1 | - | - | Read
12905 | 15 | AGC4: Reserve | - | 1 | - | - | Read
12906 |  | AGC stopcondition register 7
12906 | 0 | AGC4: Reserve | - | 1 | - | - | Read
12906 | 1 | AGC4: Reserve | - | 1 | - | - | Read
12906 | 2 | AGC4: Reserve | - | 1 | - | - | Read
12906 | 3 | AGC4: internal communication error | - | 1 | - | - | Read
12906 | 4 | AGC4: Reserve | - | 1 | - | - | Read
12906 | 5 | AGC4: Reserve | - | 1 | - | - | Read
12906 | 6 | AGC4: Reserve | - | 1 | - | - | Read
12906 | 7 | AGC4: Reserve | - | 1 | - | - | Read
12906 | 8 | AGC4: Reserve | - | 1 | - | - | Read
12906 | 9 | AGC4: Reserve | - | 1 | - | - | Read
12906 | 10 | AGC4: Reserve | - | 1 | - | - | Read
12906 | 11 | AGC4: Reserve | - | 1 | - | - | Read
12906 | 12 | AGC4: Reserve | - | 1 | - | - | Read
12906 | 13 | AGC4: Reserve | - | 1 | - | - | Read
12906 | 14 | AGC4: Reserve | - | 1 | - | - | Read
12906 | 15 | AGC4: Reserve | - | 1 | - | - | Read
12907 |  | AGC stopcondition register 8
12907 | 0 | AGC4: Reserve | - | 1 | - | - | Read
12907 | 1 | AGC4: Reserve | - | 1 | - | - | Read
12907 | 2 | AGC4: Reserve | - | 1 | - | - | Read
12907 | 3 | AGC4: Reserve | - | 1 | - | - | Read
12907 | 4 | AGC4: Reserve | - | 1 | - | - | Read
12907 | 5 | AGC4: Reserve | - | 1 | - | - | Read
12907 | 6 | AGC4: Reserve | - | 1 | - | - | Read
12907 | 7 | AGC4: Reserve | - | 1 | - | - | Read
12907 | 8 | AGC4: Reserve | - | 1 | - | - | Read
12907 | 9 | AGC4: Reserve | - | 1 | - | - | Read
12907 | 10 | AGC4: Reserve | - | 1 | - | - | Read
12907 | 11 | AGC4: crank failure | - | 1 | - | - | Read
12907 | 12 | AGC4: running feedback failure | - | 1 | - | - | Read
12907 | 13 | AGC4: Reserve | - | 1 | - | - | Read
12907 | 14 | AGC4: Hz/V failure | - | 1 | - | - | Read
12907 | 15 | AGC4: start failure | - | 1 | - | - | Read
12908 |  | AGC stopcondition register 9
12908 | 0 | AGC4: Reserve | - | 1 | - | - | Read
12908 | 1 | AGC4: Reserve | - | 1 | - | - | Read
12908 | 2 | AGC4: Reserve | - | 1 | - | - | Read
12908 | 3 | AGC4: Reserve | - | 1 | - | - | Read
12908 | 4 | AGC4: unbalance current 2 | - | 1 | - | - | Read
12908 | 5 | AGC4: grid overvoltage 1 (average) | - | 1 | - | - | Read
12908 | 6 | AGC4: grid overvoltage 2 (average) | - | 1 | - | - | Read
12908 | 7 | AGC4: Reserve | - | 1 | - | - | Read
12908 | 8 | AGC4: Reserve | - | 1 | - | - | Read
12908 | 9 | AGC4: Reserve | - | 1 | - | - | Read
12908 | 10 | AGC4: Reserve | - | 1 | - | - | Read
12908 | 11 | AGC4: grid overfrequency 4 | - | 1 | - | - | Read
12908 | 12 | AGC4: grid underfrequency 5 | - | 1 | - | - | Read
12908 | 13 | AGC4: grid overvoltage 4 | - | 1 | - | - | Read
12908 | 14 | AGC4: grid undervoltage 5 | - | 1 | - | - | Read
12908 | 15 | AGC4: Reserve | - | 1 | - | - | Read
12909 |  | AGC stopcondition register 10
12909 | 0 | AGC4: generator negative sequence I> | - | 1 | - | - | Read
12909 | 1 | AGC4: generator negative sequence U> | - | 1 | - | - | Read
12909 | 2 | AGC4: generator zero sequence I> | - | 1 | - | - | Read
12909 | 3 | AGC4: generator zero sequence U> | - | 1 | - | - | Read
12909 | 4 | AGC4: Reserve | - | 1 | - | - | Read
12909 | 5 | AGC4: Reserve | - | 1 | - | - | Read
12909 | 6 | AGC4: grid unbalance voltage | - | 1 | - | - | Read
12909 | 7 | AGC4: Reserve | - | 1 | - | - | Read
12909 | 8 | AGC4: Reserve | - | 1 | - | - | Read
12909 | 9 | AGC4: Reserve | - | 1 | - | - | Read
12909 | 10 | AGC4: Reserve | - | 1 | - | - | Read
12909 | 11 | AGC4: Reserve | - | 1 | - | - | Read
12909 | 12 | AGC4: Reserve | - | 1 | - | - | Read
12909 | 13 | AGC4: Reserve | - | 1 | - | - | Read
12909 | 14 | AGC4: Reserve | - | 1 | - | - | Read
12909 | 15 | AGC4: Reserve | - | 1 | - | - | Read
12910 |  | AGC stopcondition register 11
12910 | 0 | AGC4: generator overvoltage 1 L-L (RMS average) | - | 1 | - | - | Read
12910 | 1 | AGC4: generator overvoltage 2 L-L (RMS average) | - | 1 | - | - | Read
12910 | 2 | AGC4: generator undervoltage 1 L-L (RMS average) | - | 1 | - | - | Read
12910 | 3 | AGC4: generator undervoltage 2 L-L (RMS average) | - | 1 | - | - | Read
12910 | 4 | AGC4: generator overvoltage 1 L-N (RMS average) | - | 1 | - | - | Read
12910 | 5 | AGC4: generator overvoltage 2 L-N (RMS average) | - | 1 | - | - | Read
12910 | 6 | AGC4: generator undervoltage 1 L-N (RMS average) | - | 1 | - | - | Read
12910 | 7 | AGC4: generator undervoltage 2 L-N (RMS average) | - | 1 | - | - | Read
12910 | 8 | AGC4: generator overfrequency 1 (average) | - | 1 | - | - | Read
12910 | 9 | AGC4: generator overfrequency 2 (average) | - | 1 | - | - | Read
12910 | 10 | AGC4: generator underfrequency 1 (average) | - | 1 | - | - | Read
12910 | 11 | AGC4: generator underfrequency 2 (average) | - | 1 | - | - | Read
12910 | 12 | AGC4: generator overcurrent 1 (RMS average) | - | 1 | - | - | Read
12910 | 13 | AGC4: generator overcurrent 2 (RMS average) | - | 1 | - | - | Read
12910 | 14 | AGC4: Reserve | - | 1 | - | - | Read
12910 | 15 | AGC4: Reserve | - | 1 | - | - | Read
13000 |  | Conf. DI stopcondition 1 register 1
13000 | 0 | (1) Conf. DI 1 | - | 1 | - | - | Read
13000 | 1 | (1) Conf. DI 2 | - | 1 | - | - | Read
13000 | 2 | (1) Conf. DI 3 | - | 1 | - | - | Read
13000 | 3 | (1) Conf. DI 4 | - | 1 | - | - | Read
13000 | 4 | (1) Conf. DI 5 | - | 1 | - | - | Read
13000 | 5 | (1) Conf. DI 6 | - | 1 | - | - | Read
13000 | 6 | (1) Conf. DI 7 | - | 1 | - | - | Read
13000 | 7 | (1) Conf. DI 8 | - | 1 | - | - | Read
13000 | 8 | (1) Conf. DI 9 | - | 1 | - | - | Read
13000 | 9 | (1) Conf. DI 10 | - | 1 | - | - | Read
13000 | 10 | (1) Conf. DI 11 | - | 1 | - | - | Read
13000 | 11 | (1) Conf. DI 12 | - | 1 | - | - | Read
13000 | 12 | (1) Conf. DI 13 | - | 1 | - | - | Read
13000 | 13 | (1) Conf. DI 14 | - | 1 | - | - | Read
13000 | 14 | (1) Conf. DI 15 | - | 1 | - | - | Read
13000 | 15 | (1) Conf. DI 16 | - | 1 | - | - | Read
13001 |  | Conf. DI stopcondition 1 register 2
13001 | 0 | (1) Conf. DI 17 | - | 1 | - | - | Read
13001 | 1 | (1) Conf. DI 18 | - | 1 | - | - | Read
13001 | 2 | (1) Conf. DI 19 | - | 1 | - | - | Read
13001 | 3 | (1) Conf. DI 20 | - | 1 | - | - | Read
13001 | 4 | (1) Conf. DI 21 | - | 1 | - | - | Read
13001 | 5 | (1) Conf. DI 22 | - | 1 | - | - | Read
13001 | 6 | (1) Conf. DI 23 | - | 1 | - | - | Read
13001 | 7 | (1) Conf. DI 24 | - | 1 | - | - | Read
13001 | 8 | (1) Conf. DI 25 | - | 1 | - | - | Read
13001 | 9 | (1) Conf. DI 26 | - | 1 | - | - | Read
13001 | 10 | (1) Conf. DI 27 | - | 1 | - | - | Read
13001 | 11 | (1) Conf. DI 28 | - | 1 | - | - | Read
13001 | 12 | (1) Conf. DI 29 | - | 1 | - | - | Read
13001 | 13 | (1) Conf. DI 30 | - | 1 | - | - | Read
13001 | 14 | (1) Conf. DI 31 | - | 1 | - | - | Read
13001 | 15 | (1) Conf. DI 32 | - | 1 | - | - | Read
13002 |  | Conf. DI stopcondition 1 register 3
13002 | 0 | (1) Conf. DI 33 | - | 1 | - | - | Read
13002 | 1 | (1) Conf. DI 34 | - | 1 | - | - | Read
13002 | 2 | (1) Conf. DI 35 | - | 1 | - | - | Read
13002 | 3 | (1) Conf. DI 36 | - | 1 | - | - | Read
13002 | 4 | (1) Conf. DI 37 | - | 1 | - | - | Read
13002 | 5 | (1) Conf. DI 38 | - | 1 | - | - | Read
13002 | 6 | (1) Conf. DI 39 | - | 1 | - | - | Read
13002 | 7 | (1) Conf. DI 40 | - | 1 | - | - | Read
13002 | 8 | (1) Conf. DI 41 | - | 1 | - | - | Read
13002 | 9 | (1) Conf. DI 42 | - | 1 | - | - | Read
13002 | 10 | (1) Conf. DI 43 | - | 1 | - | - | Read
13002 | 11 | (1) Conf. DI 44 | - | 1 | - | - | Read
13002 | 12 | (1) Conf. DI 45 | - | 1 | - | - | Read
13002 | 13 | (1) Conf. DI 46 | - | 1 | - | - | Read
13002 | 14 | (1) Conf. DI 47 | - | 1 | - | - | Read
13002 | 15 | (1) Conf. DI 48 | - | 1 | - | - | Read
13003 |  | Conf. DI stopcondition 1 register 4
13003 | 0 | (1) Conf. DI 49 | - | 1 | - | - | Read
13003 | 1 | (1) Conf. DI 50 | - | 1 | - | - | Read
13003 | 2 | (1) Conf. DI 51 | - | 1 | - | - | Read
13003 | 3 | (1) Conf. DI 52 | - | 1 | - | - | Read
13003 | 4 | (1) Conf. DI 53 | - | 1 | - | - | Read
13003 | 5 | (1) Conf. DI 54 | - | 1 | - | - | Read
13003 | 6 | (1) Conf. DI 55 | - | 1 | - | - | Read
13003 | 7 | (1) Conf. DI 56 | - | 1 | - | - | Read
13003 | 8 | (1) Conf. DI 57 | - | 1 | - | - | Read
13003 | 9 | (1) Conf. DI 58 | - | 1 | - | - | Read
13003 | 10 | (1) Conf. DI 59 | - | 1 | - | - | Read
13003 | 11 | (1) Conf. DI 60 | - | 1 | - | - | Read
13003 | 12 | (1) Conf. DI 61 | - | 1 | - | - | Read
13003 | 13 | (1) Conf. DI 62 | - | 1 | - | - | Read
13003 | 14 | (1) Conf. DI 63 | - | 1 | - | - | Read
13003 | 15 | (1) Conf. DI 64 | - | 1 | - | - | Read
13004 |  | Conf. DI stopcondition 1 register 5
13004 | 0 | (1) Conf. DI 65 | - | 1 | - | - | Read
13004 | 1 | (1) Conf. DI 66 | - | 1 | - | - | Read
13004 | 2 | (1) Conf. DI 67 | - | 1 | - | - | Read
13004 | 3 | (1) Conf. DI 68 | - | 1 | - | - | Read
13004 | 4 | (1) Conf. DI 69 | - | 1 | - | - | Read
13004 | 5 | (1) Conf. DI 70 | - | 1 | - | - | Read
13004 | 6 | (1) Conf. DI 71 | - | 1 | - | - | Read
13004 | 7 | (1) Conf. DI 72 | - | 1 | - | - | Read
13004 | 8 | (1) Conf. DI 73 | - | 1 | - | - | Read
13004 | 9 | (1) Conf. DI 74 | - | 1 | - | - | Read
13004 | 10 | (1) Conf. DI 75 | - | 1 | - | - | Read
13004 | 11 | (1) Conf. DI 76 | - | 1 | - | - | Read
13004 | 12 | (1) Conf. DI 77 | - | 1 | - | - | Read
13004 | 13 | (1) Conf. DI 78 | - | 1 | - | - | Read
13004 | 14 | (1) Conf. DI 79 | - | 1 | - | - | Read
13004 | 15 | (1) Conf. DI 80 | - | 1 | - | - | Read
13005 |  | Conf. DI stopcondition 1 register 6
13005 | 0 | (1) Conf. DI 81 | - | 1 | - | - | Read
13005 | 1 | (1) Conf. DI 82 | - | 1 | - | - | Read
13005 | 2 | (1) Conf. DI 83 | - | 1 | - | - | Read
13005 | 3 | (1) Conf. DI 84 | - | 1 | - | - | Read
13005 | 4 | (1) Conf. DI 85 | - | 1 | - | - | Read
13005 | 5 | (1) Conf. DI 86 | - | 1 | - | - | Read
13005 | 6 | (1) Conf. DI 87 | - | 1 | - | - | Read
13005 | 7 | (1) Conf. DI 88 | - | 1 | - | - | Read
13005 | 8 | (1) Conf. DI 89 | - | 1 | - | - | Read
13005 | 9 | (1) Conf. DI 90 | - | 1 | - | - | Read
13005 | 10 | (1) Conf. DI 91 | - | 1 | - | - | Read
13005 | 11 | (1) Conf. DI 92 | - | 1 | - | - | Read
13005 | 12 | (1) Conf. DI 93 | - | 1 | - | - | Read
13005 | 13 | (1) Conf. DI 94 | - | 1 | - | - | Read
13005 | 14 | (1) Conf. DI 95 | - | 1 | - | - | Read
13005 | 15 | (1) Conf. DI 96 | - | 1 | - | - | Read
13006 |  | Conf. DI stopcondition 1 register 7
13006 | 0 | (1) Conf. DI 97 | - | 1 | - | - | Read
13006 | 1 | (1) Conf. DI 98 | - | 1 | - | - | Read
13006 | 2 | (1) Conf. DI 99 | - | 1 | - | - | Read
13006 | 3 | (1) Conf. DI 100 | - | 1 | - | - | Read
13006 | 4 | (1) Conf. DI 101 | - | 1 | - | - | Read
13006 | 5 | (1) Conf. DI 102 | - | 1 | - | - | Read
13006 | 6 | (1) Conf. DI 103 | - | 1 | - | - | Read
13006 | 7 | (1) Conf. DI 104 | - | 1 | - | - | Read
13006 | 8 | (1) Conf. DI 105 | - | 1 | - | - | Read
13006 | 9 | (1) Conf. DI 106 | - | 1 | - | - | Read
13006 | 10 | (1) Conf. DI 107 | - | 1 | - | - | Read
13006 | 11 | (1) Conf. DI 108 | - | 1 | - | - | Read
13006 | 12 | (1) Conf. DI 109 | - | 1 | - | - | Read
13006 | 13 | (1) Conf. DI 110 | - | 1 | - | - | Read
13006 | 14 | (1) Conf. DI 111 | - | 1 | - | - | Read
13006 | 15 | (1) Conf. DI 112 | - | 1 | - | - | Read
13007 |  | Conf. DI stopcondition 1 register 8
13007 | 0 | (1) Conf. DI 113 | - | 1 | - | - | Read
13007 | 1 | (1) Conf. DI 114 | - | 1 | - | - | Read
13007 | 2 | (1) Conf. DI 115 | - | 1 | - | - | Read
13007 | 3 | (1) Conf. DI 116 | - | 1 | - | - | Read
13007 | 4 | (1) Conf. DI 117 | - | 1 | - | - | Read
13007 | 5 | (1) Conf. DI 118 | - | 1 | - | - | Read
13007 | 6 | (1) Conf. DI 119 | - | 1 | - | - | Read
13007 | 7 | (1) Conf. DI 120 | - | 1 | - | - | Read
13010 |  | Conf. DI stopcondition 2 register 1
13010 | 0 | (2) Conf. DI 1 | - | 1 | - | - | Read
13010 | 1 | (2) Conf. DI 2 | - | 1 | - | - | Read
13010 | 2 | (2) Conf. DI 3 | - | 1 | - | - | Read
13010 | 3 | (2) Conf. DI 4 | - | 1 | - | - | Read
13010 | 4 | (2) Conf. DI 5 | - | 1 | - | - | Read
13010 | 5 | (2) Conf. DI 6 | - | 1 | - | - | Read
13010 | 6 | (2) Conf. DI 7 | - | 1 | - | - | Read
13010 | 7 | (2) Conf. DI 8 | - | 1 | - | - | Read
13010 | 8 | (2) Conf. DI 9 | - | 1 | - | - | Read
13010 | 9 | (2) Conf. DI 10 | - | 1 | - | - | Read
13010 | 10 | (2) Conf. DI 11 | - | 1 | - | - | Read
13010 | 11 | (2) Conf. DI 12 | - | 1 | - | - | Read
13010 | 12 | (2) Conf. DI 13 | - | 1 | - | - | Read
13010 | 13 | (2) Conf. DI 14 | - | 1 | - | - | Read
13010 | 14 | (2) Conf. DI 15 | - | 1 | - | - | Read
13010 | 15 | (2) Conf. DI 16 | - | 1 | - | - | Read
13011 |  | Conf. DI stopcondition 2 register 2
13011 | 0 | (2) Conf. DI 17 | - | 1 | - | - | Read
13011 | 1 | (2) Conf. DI 18 | - | 1 | - | - | Read
13011 | 2 | (2) Conf. DI 19 | - | 1 | - | - | Read
13011 | 3 | (2) Conf. DI 20 | - | 1 | - | - | Read
13011 | 4 | (2) Conf. DI 21 | - | 1 | - | - | Read
13011 | 5 | (2) Conf. DI 22 | - | 1 | - | - | Read
13011 | 6 | (2) Conf. DI 23 | - | 1 | - | - | Read
13011 | 7 | (2) Conf. DI 24 | - | 1 | - | - | Read
13011 | 8 | (2) Conf. DI 25 | - | 1 | - | - | Read
13011 | 9 | (2) Conf. DI 26 | - | 1 | - | - | Read
13011 | 10 | (2) Conf. DI 27 | - | 1 | - | - | Read
13011 | 11 | (2) Conf. DI 28 | - | 1 | - | - | Read
13011 | 12 | (2) Conf. DI 29 | - | 1 | - | - | Read
13011 | 13 | (2) Conf. DI 30 | - | 1 | - | - | Read
13011 | 14 | (2) Conf. DI 31 | - | 1 | - | - | Read
13011 | 15 | (2) Conf. DI 32 | - | 1 | - | - | Read
13012 |  | Conf. DI stopcondition 2 register 3
13012 | 0 | (2) Conf. DI 33 | - | 1 | - | - | Read
13012 | 1 | (2) Conf. DI 34 | - | 1 | - | - | Read
13012 | 2 | (2) Conf. DI 35 | - | 1 | - | - | Read
13012 | 3 | (2) Conf. DI 36 | - | 1 | - | - | Read
13012 | 4 | (2) Conf. DI 37 | - | 1 | - | - | Read
13012 | 5 | (2) Conf. DI 38 | - | 1 | - | - | Read
13012 | 6 | (2) Conf. DI 39 | - | 1 | - | - | Read
13012 | 7 | (2) Conf. DI 40 | - | 1 | - | - | Read
13012 | 8 | (2) Conf. DI 41 | - | 1 | - | - | Read
13012 | 9 | (2) Conf. DI 42 | - | 1 | - | - | Read
13012 | 10 | (2) Conf. DI 43 | - | 1 | - | - | Read
13012 | 11 | (2) Conf. DI 44 | - | 1 | - | - | Read
13012 | 12 | (2) Conf. DI 45 | - | 1 | - | - | Read
13012 | 13 | (2) Conf. DI 46 | - | 1 | - | - | Read
13012 | 14 | (2) Conf. DI 47 | - | 1 | - | - | Read
13012 | 15 | (2) Conf. DI 48 | - | 1 | - | - | Read
13013 |  | Conf. DI stopcondition 2 register 4
13013 | 0 | (2) Conf. DI 49 | - | 1 | - | - | Read
13013 | 1 | (2) Conf. DI 50 | - | 1 | - | - | Read
13013 | 2 | (2) Conf. DI 51 | - | 1 | - | - | Read
13013 | 3 | (2) Conf. DI 52 | - | 1 | - | - | Read
13013 | 4 | (2) Conf. DI 53 | - | 1 | - | - | Read
13013 | 5 | (2) Conf. DI 54 | - | 1 | - | - | Read
13013 | 6 | (2) Conf. DI 55 | - | 1 | - | - | Read
13013 | 7 | (2) Conf. DI 56 | - | 1 | - | - | Read
13013 | 8 | (2) Conf. DI 57 | - | 1 | - | - | Read
13013 | 9 | (2) Conf. DI 58 | - | 1 | - | - | Read
13013 | 10 | (2) Conf. DI 59 | - | 1 | - | - | Read
13013 | 11 | (2) Conf. DI 60 | - | 1 | - | - | Read
13013 | 12 | (2) Conf. DI 61 | - | 1 | - | - | Read
13013 | 13 | (2) Conf. DI 62 | - | 1 | - | - | Read
13013 | 14 | (2) Conf. DI 63 | - | 1 | - | - | Read
13013 | 15 | (2) Conf. DI 64 | - | 1 | - | - | Read
13014 |  | Conf. DI stopcondition 2 register 5
13014 | 0 | (2) Conf. DI 65 | - | 1 | - | - | Read
13014 | 1 | (2) Conf. DI 66 | - | 1 | - | - | Read
13014 | 2 | (2) Conf. DI 67 | - | 1 | - | - | Read
13014 | 3 | (2) Conf. DI 68 | - | 1 | - | - | Read
13014 | 4 | (2) Conf. DI 69 | - | 1 | - | - | Read
13014 | 5 | (2) Conf. DI 70 | - | 1 | - | - | Read
13014 | 6 | (2) Conf. DI 71 | - | 1 | - | - | Read
13014 | 7 | (2) Conf. DI 72 | - | 1 | - | - | Read
13014 | 8 | (2) Conf. DI 73 | - | 1 | - | - | Read
13014 | 9 | (2) Conf. DI 74 | - | 1 | - | - | Read
13014 | 10 | (2) Conf. DI 75 | - | 1 | - | - | Read
13014 | 11 | (2) Conf. DI 76 | - | 1 | - | - | Read
13014 | 12 | (2) Conf. DI 77 | - | 1 | - | - | Read
13014 | 13 | (2) Conf. DI 78 | - | 1 | - | - | Read
13014 | 14 | (2) Conf. DI 79 | - | 1 | - | - | Read
13014 | 15 | (2) Conf. DI 80 | - | 1 | - | - | Read
13015 |  | Conf. DI stopcondition 2 register 6
13015 | 0 | (2) Conf. DI 81 | - | 1 | - | - | Read
13015 | 1 | (2) Conf. DI 82 | - | 1 | - | - | Read
13015 | 2 | (2) Conf. DI 83 | - | 1 | - | - | Read
13015 | 3 | (2) Conf. DI 84 | - | 1 | - | - | Read
13015 | 4 | (2) Conf. DI 85 | - | 1 | - | - | Read
13015 | 5 | (2) Conf. DI 86 | - | 1 | - | - | Read
13015 | 6 | (2) Conf. DI 87 | - | 1 | - | - | Read
13015 | 7 | (2) Conf. DI 88 | - | 1 | - | - | Read
13015 | 8 | (2) Conf. DI 89 | - | 1 | - | - | Read
13015 | 9 | (2) Conf. DI 90 | - | 1 | - | - | Read
13015 | 10 | (2) Conf. DI 91 | - | 1 | - | - | Read
13015 | 11 | (2) Conf. DI 92 | - | 1 | - | - | Read
13015 | 12 | (2) Conf. DI 93 | - | 1 | - | - | Read
13015 | 13 | (2) Conf. DI 94 | - | 1 | - | - | Read
13015 | 14 | (2) Conf. DI 95 | - | 1 | - | - | Read
13015 | 15 | (2) Conf. DI 96 | - | 1 | - | - | Read
13016 |  | Conf. DI stopcondition 2 register 7
13016 | 0 | (2) Conf. DI 97 | - | 1 | - | - | Read
13016 | 1 | (2) Conf. DI 98 | - | 1 | - | - | Read
13016 | 2 | (2) Conf. DI 99 | - | 1 | - | - | Read
13016 | 3 | (2) Conf. DI 100 | - | 1 | - | - | Read
13016 | 4 | (2) Conf. DI 101 | - | 1 | - | - | Read
13016 | 5 | (2) Conf. DI 102 | - | 1 | - | - | Read
13016 | 6 | (2) Conf. DI 103 | - | 1 | - | - | Read
13016 | 7 | (2) Conf. DI 104 | - | 1 | - | - | Read
13016 | 8 | (2) Conf. DI 105 | - | 1 | - | - | Read
13016 | 9 | (2) Conf. DI 106 | - | 1 | - | - | Read
13016 | 10 | (2) Conf. DI 107 | - | 1 | - | - | Read
13016 | 11 | (2) Conf. DI 108 | - | 1 | - | - | Read
13016 | 12 | (2) Conf. DI 109 | - | 1 | - | - | Read
13016 | 13 | (2) Conf. DI 110 | - | 1 | - | - | Read
13016 | 14 | (2) Conf. DI 111 | - | 1 | - | - | Read
13016 | 15 | (2) Conf. DI 112 | - | 1 | - | - | Read
13017 |  | Conf. DI stopcondition 2 register 8
13017 | 0 | (2) Conf. DI 113 | - | 1 | - | - | Read
13017 | 1 | (2) Conf. DI 114 | - | 1 | - | - | Read
13017 | 2 | (2) Conf. DI 115 | - | 1 | - | - | Read
13017 | 3 | (2) Conf. DI 116 | - | 1 | - | - | Read
13017 | 4 | (2) Conf. DI 117 | - | 1 | - | - | Read
13017 | 5 | (2) Conf. DI 118 | - | 1 | - | - | Read
13017 | 6 | (2) Conf. DI 119 | - | 1 | - | - | Read
13017 | 7 | (2) Conf. DI 120 | - | 1 | - | - | Read
13100 |  | Conf. AI stopcondition 1 register 1
13100 | 0 | (1) abc < 0.0 Bar | - | 1 | - | - | Read
13100 | 1 | (1) Conf. AI 2 < 0.0 --- | - | 1 | - | - | Read
13100 | 2 | (1) Conf. AI 3 < 0.0 --- | - | 1 | - | - | Read
13100 | 3 | (1) Conf. AI 4 < 0.0 --- | - | 1 | - | - | Read
13100 | 4 | (1) Conf. AI 5 < 0.0 --- | - | 1 | - | - | Read
13100 | 5 | (1) Conf. AI 6 < 0.0 --- | - | 1 | - | - | Read
13100 | 6 | (1) Conf. AI 7 < 0.0 --- | - | 1 | - | - | Read
13100 | 7 | (1) Conf. AI 8 < 0.0 --- | - | 1 | - | - | Read
13100 | 8 | (1) Conf. AI 9 < 0.0 --- | - | 1 | - | - | Read
13100 | 9 | (1) Conf. AI 10 < 0.0 --- | - | 1 | - | - | Read
13100 | 10 | (1) Conf. AI 11 < 0.0 --- | - | 1 | - | - | Read
13100 | 11 | (1) Conf. AI 12 < 0.0 --- | - | 1 | - | - | Read
13100 | 12 | (1) Conf. AI 13 < 0.0 --- | - | 1 | - | - | Read
13100 | 13 | (1) Conf. AI 14 < 0.0 --- | - | 1 | - | - | Read
13100 | 14 | (1) Conf. AI 15 < 0.0 --- | - | 1 | - | - | Read
13100 | 15 | (1) Conf. AI 16 < 0.0 --- | - | 1 | - | - | Read
13101 |  | Conf. AI stopcondition 1 register 2
13101 | 0 | (1) Conf. AI 17 < 0.0 --- | - | 1 | - | - | Read
13101 | 1 | (1) Conf. AI 18 < 0.0 --- | - | 1 | - | - | Read
13101 | 2 | (1) Conf. AI 19 < 0.0 --- | - | 1 | - | - | Read
13101 | 3 | (1) Conf. AI 20 < 0.0 --- | - | 1 | - | - | Read
13101 | 4 | (1) Conf. AI 21 < 0.0 --- | - | 1 | - | - | Read
13101 | 5 | (1) Conf. AI 22 < 0.0 --- | - | 1 | - | - | Read
13101 | 6 | (1) Conf. AI 23 < 0.0 --- | - | 1 | - | - | Read
13101 | 7 | (1) Conf. AI 24 < 0.0 --- | - | 1 | - | - | Read
13101 | 8 | (1) Conf. AI 25 < 0.0 --- | - | 1 | - | - | Read
13101 | 9 | (1) Conf. AI 26 < 0.0 --- | - | 1 | - | - | Read
13101 | 10 | (1) Conf. AI 27 < 0.0 --- | - | 1 | - | - | Read
13101 | 11 | (1) Conf. AI 28 < 0.0 --- | - | 1 | - | - | Read
13101 | 12 | (1) Conf. AI 29 < 0.0 --- | - | 1 | - | - | Read
13101 | 13 | (1) Conf. AI 30 < 0.0 --- | - | 1 | - | - | Read
13101 | 14 | (1) Conf. AI 31 < 0.0 --- | - | 1 | - | - | Read
13101 | 15 | (1) Conf. AI 32 < 0.0 --- | - | 1 | - | - | Read
13102 |  | Conf. AI stopcondition 1 register 3
13102 | 0 | (1) Conf. AI 33 < 0.0 --- | - | 1 | - | - | Read
13102 | 1 | (1) Conf. AI 34 < 0.0 --- | - | 1 | - | - | Read
13102 | 2 | (1) Conf. AI 35 < 0.0 --- | - | 1 | - | - | Read
13102 | 3 | (1) Conf. AI 36 < 0.0 --- | - | 1 | - | - | Read
13102 | 4 | (1) Conf. AI 37 < 0.0 --- | - | 1 | - | - | Read
13102 | 5 | (1) Conf. AI 38 < 0.0 --- | - | 1 | - | - | Read
13102 | 6 | (1) Conf. AI 39 < 0.0 --- | - | 1 | - | - | Read
13102 | 7 | (1) Conf. AI 40 < 0.0 --- | - | 1 | - | - | Read
13102 | 8 | (1) Conf. AI 41 < 0.0 --- | - | 1 | - | - | Read
13102 | 9 | (1) Conf. AI 42 < 0.0 --- | - | 1 | - | - | Read
13102 | 10 | (1) Conf. AI 43 < 0.0 --- | - | 1 | - | - | Read
13102 | 11 | (1) Conf. AI 44 < 0.0 --- | - | 1 | - | - | Read
13102 | 12 | (1) Conf. AI 45 < 0.0 --- | - | 1 | - | - | Read
13102 | 13 | (1) Conf. AI 46 < 0.0 --- | - | 1 | - | - | Read
13102 | 14 | (1) Conf. AI 47 < 0.0 --- | - | 1 | - | - | Read
13102 | 15 | (1) Conf. AI 48 < 0.0 --- | - | 1 | - | - | Read
13110 |  | Conf. AI stopcondition 2 register 1
13110 | 0 | (2) abc < 0.0 Bar | - | 1 | - | - | Read
13110 | 1 | (2) Conf. AI 2 < 0.0 --- | - | 1 | - | - | Read
13110 | 2 | (2) Conf. AI 3 < 0.0 --- | - | 1 | - | - | Read
13110 | 3 | (2) Conf. AI 4 < 0.0 --- | - | 1 | - | - | Read
13110 | 4 | (2) Conf. AI 5 < 0.0 --- | - | 1 | - | - | Read
13110 | 5 | (2) Conf. AI 6 < 0.0 --- | - | 1 | - | - | Read
13110 | 6 | (2) Conf. AI 7 < 0.0 --- | - | 1 | - | - | Read
13110 | 7 | (2) Conf. AI 8 < 0.0 --- | - | 1 | - | - | Read
13110 | 8 | (2) Conf. AI 9 < 0.0 --- | - | 1 | - | - | Read
13110 | 9 | (2) Conf. AI 10 < 0.0 --- | - | 1 | - | - | Read
13110 | 10 | (2) Conf. AI 11 < 0.0 --- | - | 1 | - | - | Read
13110 | 11 | (2) Conf. AI 12 < 0.0 --- | - | 1 | - | - | Read
13110 | 12 | (2) Conf. AI 13 < 0.0 --- | - | 1 | - | - | Read
13110 | 13 | (2) Conf. AI 14 < 0.0 --- | - | 1 | - | - | Read
13110 | 14 | (2) Conf. AI 15 < 0.0 --- | - | 1 | - | - | Read
13110 | 15 | (2) Conf. AI 16 < 0.0 --- | - | 1 | - | - | Read
13111 |  | Conf. AI stopcondition 2 register 2
13111 | 0 | (2) Conf. AI 17 < 0.0 --- | - | 1 | - | - | Read
13111 | 1 | (2) Conf. AI 18 < 0.0 --- | - | 1 | - | - | Read
13111 | 2 | (2) Conf. AI 19 < 0.0 --- | - | 1 | - | - | Read
13111 | 3 | (2) Conf. AI 20 < 0.0 --- | - | 1 | - | - | Read
13111 | 4 | (2) Conf. AI 21 < 0.0 --- | - | 1 | - | - | Read
13111 | 5 | (2) Conf. AI 22 < 0.0 --- | - | 1 | - | - | Read
13111 | 6 | (2) Conf. AI 23 < 0.0 --- | - | 1 | - | - | Read
13111 | 7 | (2) Conf. AI 24 < 0.0 --- | - | 1 | - | - | Read
13111 | 8 | (2) Conf. AI 25 < 0.0 --- | - | 1 | - | - | Read
13111 | 9 | (2) Conf. AI 26 < 0.0 --- | - | 1 | - | - | Read
13111 | 10 | (2) Conf. AI 27 < 0.0 --- | - | 1 | - | - | Read
13111 | 11 | (2) Conf. AI 28 < 0.0 --- | - | 1 | - | - | Read
13111 | 12 | (2) Conf. AI 29 < 0.0 --- | - | 1 | - | - | Read
13111 | 13 | (2) Conf. AI 30 < 0.0 --- | - | 1 | - | - | Read
13111 | 14 | (2) Conf. AI 31 < 0.0 --- | - | 1 | - | - | Read
13111 | 15 | (2) Conf. AI 32 < 0.0 --- | - | 1 | - | - | Read
13112 |  | Conf. AI stopcondition 2 register 3
13112 | 0 | (2) Conf. AI 33 < 0.0 --- | - | 1 | - | - | Read
13112 | 1 | (2) Conf. AI 34 < 0.0 --- | - | 1 | - | - | Read
13112 | 2 | (2) Conf. AI 35 < 0.0 --- | - | 1 | - | - | Read
13112 | 3 | (2) Conf. AI 36 < 0.0 --- | - | 1 | - | - | Read
13112 | 4 | (2) Conf. AI 37 < 0.0 --- | - | 1 | - | - | Read
13112 | 5 | (2) Conf. AI 38 < 0.0 --- | - | 1 | - | - | Read
13112 | 6 | (2) Conf. AI 39 < 0.0 --- | - | 1 | - | - | Read
13112 | 7 | (2) Conf. AI 40 < 0.0 --- | - | 1 | - | - | Read
13112 | 8 | (2) Conf. AI 41 < 0.0 --- | - | 1 | - | - | Read
13112 | 9 | (2) Conf. AI 42 < 0.0 --- | - | 1 | - | - | Read
13112 | 10 | (2) Conf. AI 43 < 0.0 --- | - | 1 | - | - | Read
13112 | 11 | (2) Conf. AI 44 < 0.0 --- | - | 1 | - | - | Read
13112 | 12 | (2) Conf. AI 45 < 0.0 --- | - | 1 | - | - | Read
13112 | 13 | (2) Conf. AI 46 < 0.0 --- | - | 1 | - | - | Read
13112 | 14 | (2) Conf. AI 47 < 0.0 --- | - | 1 | - | - | Read
13112 | 15 | (2) Conf. AI 48 < 0.0 --- | - | 1 | - | - | Read
13120 |  | Conf. AI stopcondition 3 register 1
13120 | 0 | (3) abc < 0.0 Bar | - | 1 | - | - | Read
13120 | 1 | (3) Conf. AI 2 < 0.0 --- | - | 1 | - | - | Read
13120 | 2 | (3) Conf. AI 3 < 0.0 --- | - | 1 | - | - | Read
13120 | 3 | (3) Conf. AI 4 < 0.0 --- | - | 1 | - | - | Read
13120 | 4 | (3) Conf. AI 5 < 0.0 --- | - | 1 | - | - | Read
13120 | 5 | (3) Conf. AI 6 < 0.0 --- | - | 1 | - | - | Read
13120 | 6 | (3) Conf. AI 7 < 0.0 --- | - | 1 | - | - | Read
13120 | 7 | (3) Conf. AI 8 < 0.0 --- | - | 1 | - | - | Read
13120 | 8 | (3) Conf. AI 9 < 0.0 --- | - | 1 | - | - | Read
13120 | 9 | (3) Conf. AI 10 < 0.0 --- | - | 1 | - | - | Read
13120 | 10 | (3) Conf. AI 11 < 0.0 --- | - | 1 | - | - | Read
13120 | 11 | (3) Conf. AI 12 < 0.0 --- | - | 1 | - | - | Read
13120 | 12 | (3) Conf. AI 13 < 0.0 --- | - | 1 | - | - | Read
13120 | 13 | (3) Conf. AI 14 < 0.0 --- | - | 1 | - | - | Read
13120 | 14 | (3) Conf. AI 15 < 0.0 --- | - | 1 | - | - | Read
13120 | 15 | (3) Conf. AI 16 < 0.0 --- | - | 1 | - | - | Read
13121 |  | Conf. AI stopcondition 3 register 2
13121 | 0 | (3) Conf. AI 17 < 0.0 --- | - | 1 | - | - | Read
13121 | 1 | (3) Conf. AI 18 < 0.0 --- | - | 1 | - | - | Read
13121 | 2 | (3) Conf. AI 19 < 0.0 --- | - | 1 | - | - | Read
13121 | 3 | (3) Conf. AI 20 < 0.0 --- | - | 1 | - | - | Read
13121 | 4 | (3) Conf. AI 21 < 0.0 --- | - | 1 | - | - | Read
13121 | 5 | (3) Conf. AI 22 < 0.0 --- | - | 1 | - | - | Read
13121 | 6 | (3) Conf. AI 23 < 0.0 --- | - | 1 | - | - | Read
13121 | 7 | (3) Conf. AI 24 < 0.0 --- | - | 1 | - | - | Read
13121 | 8 | (3) Conf. AI 25 < 0.0 --- | - | 1 | - | - | Read
13121 | 9 | (3) Conf. AI 26 < 0.0 --- | - | 1 | - | - | Read
13121 | 10 | (3) Conf. AI 27 < 0.0 --- | - | 1 | - | - | Read
13121 | 11 | (3) Conf. AI 28 < 0.0 --- | - | 1 | - | - | Read
13121 | 12 | (3) Conf. AI 29 < 0.0 --- | - | 1 | - | - | Read
13121 | 13 | (3) Conf. AI 30 < 0.0 --- | - | 1 | - | - | Read
13121 | 14 | (3) Conf. AI 31 < 0.0 --- | - | 1 | - | - | Read
13121 | 15 | (3) Conf. AI 32 < 0.0 --- | - | 1 | - | - | Read
13122 |  | Conf. AI stopcondition 3 register 3
13122 | 0 | (3) Conf. AI 33 < 0.0 --- | - | 1 | - | - | Read
13122 | 1 | (3) Conf. AI 34 < 0.0 --- | - | 1 | - | - | Read
13122 | 2 | (3) Conf. AI 35 < 0.0 --- | - | 1 | - | - | Read
13122 | 3 | (3) Conf. AI 36 < 0.0 --- | - | 1 | - | - | Read
13122 | 4 | (3) Conf. AI 37 < 0.0 --- | - | 1 | - | - | Read
13122 | 5 | (3) Conf. AI 38 < 0.0 --- | - | 1 | - | - | Read
13122 | 6 | (3) Conf. AI 39 < 0.0 --- | - | 1 | - | - | Read
13122 | 7 | (3) Conf. AI 40 < 0.0 --- | - | 1 | - | - | Read
13122 | 8 | (3) Conf. AI 41 < 0.0 --- | - | 1 | - | - | Read
13122 | 9 | (3) Conf. AI 42 < 0.0 --- | - | 1 | - | - | Read
13122 | 10 | (3) Conf. AI 43 < 0.0 --- | - | 1 | - | - | Read
13122 | 11 | (3) Conf. AI 44 < 0.0 --- | - | 1 | - | - | Read
13122 | 12 | (3) Conf. AI 45 < 0.0 --- | - | 1 | - | - | Read
13122 | 13 | (3) Conf. AI 46 < 0.0 --- | - | 1 | - | - | Read
13122 | 14 | (3) Conf. AI 47 < 0.0 --- | - | 1 | - | - | Read
13122 | 15 | (3) Conf. AI 48 < 0.0 --- | - | 1 | - | - | Read
13130 |  | Conf. AI stopcondition 4 register 1
13130 | 0 | (4) abc < 0.0 Bar | - | 1 | - | - | Read
13130 | 1 | (4) Conf. AI 2 < 0.0 --- | - | 1 | - | - | Read
13130 | 2 | (4) Conf. AI 3 < 0.0 --- | - | 1 | - | - | Read
13130 | 3 | (4) Conf. AI 4 < 0.0 --- | - | 1 | - | - | Read
13130 | 4 | (4) Conf. AI 5 < 0.0 --- | - | 1 | - | - | Read
13130 | 5 | (4) Conf. AI 6 < 0.0 --- | - | 1 | - | - | Read
13130 | 6 | (4) Conf. AI 7 < 0.0 --- | - | 1 | - | - | Read
13130 | 7 | (4) Conf. AI 8 < 0.0 --- | - | 1 | - | - | Read
13130 | 8 | (4) Conf. AI 9 < 0.0 --- | - | 1 | - | - | Read
13130 | 9 | (4) Conf. AI 10 < 0.0 --- | - | 1 | - | - | Read
13130 | 10 | (4) Conf. AI 11 < 0.0 --- | - | 1 | - | - | Read
13130 | 11 | (4) Conf. AI 12 < 0.0 --- | - | 1 | - | - | Read
13130 | 12 | (4) Conf. AI 13 < 0.0 --- | - | 1 | - | - | Read
13130 | 13 | (4) Conf. AI 14 < 0.0 --- | - | 1 | - | - | Read
13130 | 14 | (4) Conf. AI 15 < 0.0 --- | - | 1 | - | - | Read
13130 | 15 | (4) Conf. AI 16 < 0.0 --- | - | 1 | - | - | Read
13131 |  | Conf. AI stopcondition 4 register 2
13131 | 0 | (4) Conf. AI 17 < 0.0 --- | - | 1 | - | - | Read
13131 | 1 | (4) Conf. AI 18 < 0.0 --- | - | 1 | - | - | Read
13131 | 2 | (4) Conf. AI 19 < 0.0 --- | - | 1 | - | - | Read
13131 | 3 | (4) Conf. AI 20 < 0.0 --- | - | 1 | - | - | Read
13131 | 4 | (4) Conf. AI 21 < 0.0 --- | - | 1 | - | - | Read
13131 | 5 | (4) Conf. AI 22 < 0.0 --- | - | 1 | - | - | Read
13131 | 6 | (4) Conf. AI 23 < 0.0 --- | - | 1 | - | - | Read
13131 | 7 | (4) Conf. AI 24 < 0.0 --- | - | 1 | - | - | Read
13131 | 8 | (4) Conf. AI 25 < 0.0 --- | - | 1 | - | - | Read
13131 | 9 | (4) Conf. AI 26 < 0.0 --- | - | 1 | - | - | Read
13131 | 10 | (4) Conf. AI 27 < 0.0 --- | - | 1 | - | - | Read
13131 | 11 | (4) Conf. AI 28 < 0.0 --- | - | 1 | - | - | Read
13131 | 12 | (4) Conf. AI 29 < 0.0 --- | - | 1 | - | - | Read
13131 | 13 | (4) Conf. AI 30 < 0.0 --- | - | 1 | - | - | Read
13131 | 14 | (4) Conf. AI 31 < 0.0 --- | - | 1 | - | - | Read
13131 | 15 | (4) Conf. AI 32 < 0.0 --- | - | 1 | - | - | Read
13132 |  | Conf. AI stopcondition 4 register 3
13132 | 0 | (4) Conf. AI 33 < 0.0 --- | - | 1 | - | - | Read
13132 | 1 | (4) Conf. AI 34 < 0.0 --- | - | 1 | - | - | Read
13132 | 2 | (4) Conf. AI 35 < 0.0 --- | - | 1 | - | - | Read
13132 | 3 | (4) Conf. AI 36 < 0.0 --- | - | 1 | - | - | Read
13132 | 4 | (4) Conf. AI 37 < 0.0 --- | - | 1 | - | - | Read
13132 | 5 | (4) Conf. AI 38 < 0.0 --- | - | 1 | - | - | Read
13132 | 6 | (4) Conf. AI 39 < 0.0 --- | - | 1 | - | - | Read
13132 | 7 | (4) Conf. AI 40 < 0.0 --- | - | 1 | - | - | Read
13132 | 8 | (4) Conf. AI 41 < 0.0 --- | - | 1 | - | - | Read
13132 | 9 | (4) Conf. AI 42 < 0.0 --- | - | 1 | - | - | Read
13132 | 10 | (4) Conf. AI 43 < 0.0 --- | - | 1 | - | - | Read
13132 | 11 | (4) Conf. AI 44 < 0.0 --- | - | 1 | - | - | Read
13132 | 12 | (4) Conf. AI 45 < 0.0 --- | - | 1 | - | - | Read
13132 | 13 | (4) Conf. AI 46 < 0.0 --- | - | 1 | - | - | Read
13132 | 14 | (4) Conf. AI 47 < 0.0 --- | - | 1 | - | - | Read
13132 | 15 | (4) Conf. AI 48 < 0.0 --- | - | 1 | - | - | Read
13140 |  | Conf. AI sensor defect register 1
13140 | 0 | Sensor defect: abc | - | 1 | - | - | Read
13140 | 1 | Sensor defect: Conf. AI 2 | - | 1 | - | - | Read
13140 | 2 | Sensor defect: Conf. AI 3 | - | 1 | - | - | Read
13140 | 3 | Sensor defect: Conf. AI 4 | - | 1 | - | - | Read
13140 | 4 | Sensor defect: Conf. AI 5 | - | 1 | - | - | Read
13140 | 5 | Sensor defect: Conf. AI 6 | - | 1 | - | - | Read
13140 | 6 | Sensor defect: Conf. AI 7 | - | 1 | - | - | Read
13140 | 7 | Sensor defect: Conf. AI 8 | - | 1 | - | - | Read
13140 | 8 | Sensor defect: Conf. AI 9 | - | 1 | - | - | Read
13140 | 9 | Sensor defect: Conf. AI 10 | - | 1 | - | - | Read
13140 | 10 | Sensor defect: Conf. AI 11 | - | 1 | - | - | Read
13140 | 11 | Sensor defect: Conf. AI 12 | - | 1 | - | - | Read
13140 | 12 | Sensor defect: Conf. AI 13 | - | 1 | - | - | Read
13140 | 13 | Sensor defect: Conf. AI 14 | - | 1 | - | - | Read
13140 | 14 | Sensor defect: Conf. AI 15 | - | 1 | - | - | Read
13140 | 15 | Sensor defect: Conf. AI 16 | - | 1 | - | - | Read
13141 |  | Conf. AI sensor defect register 2
13141 | 0 | Sensor defect: Conf. AI 17 | - | 1 | - | - | Read
13141 | 1 | Sensor defect: Conf. AI 18 | - | 1 | - | - | Read
13141 | 2 | Sensor defect: Conf. AI 19 | - | 1 | - | - | Read
13141 | 3 | Sensor defect: Conf. AI 20 | - | 1 | - | - | Read
13141 | 4 | Sensor defect: Conf. AI 21 | - | 1 | - | - | Read
13141 | 5 | Sensor defect: Conf. AI 22 | - | 1 | - | - | Read
13141 | 6 | Sensor defect: Conf. AI 23 | - | 1 | - | - | Read
13141 | 7 | Sensor defect: Conf. AI 24 | - | 1 | - | - | Read
13141 | 8 | Sensor defect: Conf. AI 25 | - | 1 | - | - | Read
13141 | 9 | Sensor defect: Conf. AI 26 | - | 1 | - | - | Read
13141 | 10 | Sensor defect: Conf. AI 27 | - | 1 | - | - | Read
13141 | 11 | Sensor defect: Conf. AI 28 | - | 1 | - | - | Read
13141 | 12 | Sensor defect: Conf. AI 29 | - | 1 | - | - | Read
13141 | 13 | Sensor defect: Conf. AI 30 | - | 1 | - | - | Read
13141 | 14 | Sensor defect: Conf. AI 31 | - | 1 | - | - | Read
13141 | 15 | Sensor defect: Conf. AI 32 | - | 1 | - | - | Read
13142 |  | Conf. AI sensor defect register 3
13142 | 0 | Sensor defect: Conf. AI 33 | - | 1 | - | - | Read
13142 | 1 | Sensor defect: Conf. AI 34 | - | 1 | - | - | Read
13142 | 2 | Sensor defect: Conf. AI 35 | - | 1 | - | - | Read
13142 | 3 | Sensor defect: Conf. AI 36 | - | 1 | - | - | Read
13142 | 4 | Sensor defect: Conf. AI 37 | - | 1 | - | - | Read
13142 | 5 | Sensor defect: Conf. AI 38 | - | 1 | - | - | Read
13142 | 6 | Sensor defect: Conf. AI 39 | - | 1 | - | - | Read
13142 | 7 | Sensor defect: Conf. AI 40 | - | 1 | - | - | Read
13142 | 8 | Sensor defect: Conf. AI 41 | - | 1 | - | - | Read
13142 | 9 | Sensor defect: Conf. AI 42 | - | 1 | - | - | Read
13142 | 10 | Sensor defect: Conf. AI 43 | - | 1 | - | - | Read
13142 | 11 | Sensor defect: Conf. AI 44 | - | 1 | - | - | Read
13142 | 12 | Sensor defect: Conf. AI 45 | - | 1 | - | - | Read
13142 | 13 | Sensor defect: Conf. AI 46 | - | 1 | - | - | Read
13142 | 14 | Sensor defect: Conf. AI 47 | - | 1 | - | - | Read
13142 | 15 | Sensor defect: Conf. AI 48 | - | 1 | - | - | Read
13150 |  | Conf. AI wirebreak register 1
13150 | 0 | Wire break: abc | - | 1 | - | - | Read
13150 | 1 | Wire break: Conf. AI 2 | - | 1 | - | - | Read
13150 | 2 | Wire break: Conf. AI 3 | - | 1 | - | - | Read
13150 | 3 | Wire break: Conf. AI 4 | - | 1 | - | - | Read
13150 | 4 | Wire break: Conf. AI 5 | - | 1 | - | - | Read
13150 | 5 | Wire break: Conf. AI 6 | - | 1 | - | - | Read
13150 | 6 | Wire break: Conf. AI 7 | - | 1 | - | - | Read
13150 | 7 | Wire break: Conf. AI 8 | - | 1 | - | - | Read
13150 | 8 | Wire break: Conf. AI 9 | - | 1 | - | - | Read
13150 | 9 | Wire break: Conf. AI 10 | - | 1 | - | - | Read
13150 | 10 | Wire break: Conf. AI 11 | - | 1 | - | - | Read
13150 | 11 | Wire break: Conf. AI 12 | - | 1 | - | - | Read
13150 | 12 | Wire break: Conf. AI 13 | - | 1 | - | - | Read
13150 | 13 | Wire break: Conf. AI 14 | - | 1 | - | - | Read
13150 | 14 | Wire break: Conf. AI 15 | - | 1 | - | - | Read
13150 | 15 | Wire break: Conf. AI 16 | - | 1 | - | - | Read
13151 |  | Conf. AI wirebreak register 2
13151 | 0 | Wire break: Conf. AI 17 | - | 1 | - | - | Read
13151 | 1 | Wire break: Conf. AI 18 | - | 1 | - | - | Read
13151 | 2 | Wire break: Conf. AI 19 | - | 1 | - | - | Read
13151 | 3 | Wire break: Conf. AI 20 | - | 1 | - | - | Read
13151 | 4 | Wire break: Conf. AI 21 | - | 1 | - | - | Read
13151 | 5 | Wire break: Conf. AI 22 | - | 1 | - | - | Read
13151 | 6 | Wire break: Conf. AI 23 | - | 1 | - | - | Read
13151 | 7 | Wire break: Conf. AI 24 | - | 1 | - | - | Read
13151 | 8 | Wire break: Conf. AI 25 | - | 1 | - | - | Read
13151 | 9 | Wire break: Conf. AI 26 | - | 1 | - | - | Read
13151 | 10 | Wire break: Conf. AI 27 | - | 1 | - | - | Read
13151 | 11 | Wire break: Conf. AI 28 | - | 1 | - | - | Read
13151 | 12 | Wire break: Conf. AI 29 | - | 1 | - | - | Read
13151 | 13 | Wire break: Conf. AI 30 | - | 1 | - | - | Read
13151 | 14 | Wire break: Conf. AI 31 | - | 1 | - | - | Read
13151 | 15 | Wire break: Conf. AI 32 | - | 1 | - | - | Read
13152 |  | Conf. AI wirebreak register 3
13152 | 0 | Wire break: Conf. AI 33 | - | 1 | - | - | Read
13152 | 1 | Wire break: Conf. AI 34 | - | 1 | - | - | Read
13152 | 2 | Wire break: Conf. AI 35 | - | 1 | - | - | Read
13152 | 3 | Wire break: Conf. AI 36 | - | 1 | - | - | Read
13152 | 4 | Wire break: Conf. AI 37 | - | 1 | - | - | Read
13152 | 5 | Wire break: Conf. AI 38 | - | 1 | - | - | Read
13152 | 6 | Wire break: Conf. AI 39 | - | 1 | - | - | Read
13152 | 7 | Wire break: Conf. AI 40 | - | 1 | - | - | Read
13152 | 8 | Wire break: Conf. AI 41 | - | 1 | - | - | Read
13152 | 9 | Wire break: Conf. AI 42 | - | 1 | - | - | Read
13152 | 10 | Wire break: Conf. AI 43 | - | 1 | - | - | Read
13152 | 11 | Wire break: Conf. AI 44 | - | 1 | - | - | Read
13152 | 12 | Wire break: Conf. AI 45 | - | 1 | - | - | Read
13152 | 13 | Wire break: Conf. AI 46 | - | 1 | - | - | Read
13152 | 14 | Wire break: Conf. AI 47 | - | 1 | - | - | Read
13152 | 15 | Wire break: Conf. AI 48 | - | 1 | - | - | Read
13160 |  | Conf. AI overload register 1
13160 | 0 | Overload: abc | - | 1 | - | - | Read
13160 | 1 | Overload: Conf. AI 2 | - | 1 | - | - | Read
13160 | 2 | Overload: Conf. AI 3 | - | 1 | - | - | Read
13160 | 3 | Overload: Conf. AI 4 | - | 1 | - | - | Read
13160 | 4 | Overload: Conf. AI 5 | - | 1 | - | - | Read
13160 | 5 | Overload: Conf. AI 6 | - | 1 | - | - | Read
13160 | 6 | Overload: Conf. AI 7 | - | 1 | - | - | Read
13160 | 7 | Overload: Conf. AI 8 | - | 1 | - | - | Read
13160 | 8 | Overload: Conf. AI 9 | - | 1 | - | - | Read
13160 | 9 | Overload: Conf. AI 10 | - | 1 | - | - | Read
13160 | 10 | Overload: Conf. AI 11 | - | 1 | - | - | Read
13160 | 11 | Overload: Conf. AI 12 | - | 1 | - | - | Read
13160 | 12 | Overload: Conf. AI 13 | - | 1 | - | - | Read
13160 | 13 | Overload: Conf. AI 14 | - | 1 | - | - | Read
13160 | 14 | Overload: Conf. AI 15 | - | 1 | - | - | Read
13160 | 15 | Overload: Conf. AI 16 | - | 1 | - | - | Read
13161 |  | Conf. AI overload register 2
13161 | 0 | Overload: Conf. AI 17 | - | 1 | - | - | Read
13161 | 1 | Overload: Conf. AI 18 | - | 1 | - | - | Read
13161 | 2 | Overload: Conf. AI 19 | - | 1 | - | - | Read
13161 | 3 | Overload: Conf. AI 20 | - | 1 | - | - | Read
13161 | 4 | Overload: Conf. AI 21 | - | 1 | - | - | Read
13161 | 5 | Overload: Conf. AI 22 | - | 1 | - | - | Read
13161 | 6 | Overload: Conf. AI 23 | - | 1 | - | - | Read
13161 | 7 | Overload: Conf. AI 24 | - | 1 | - | - | Read
13161 | 8 | Overload: Conf. AI 25 | - | 1 | - | - | Read
13161 | 9 | Overload: Conf. AI 26 | - | 1 | - | - | Read
13161 | 10 | Overload: Conf. AI 27 | - | 1 | - | - | Read
13161 | 11 | Overload: Conf. AI 28 | - | 1 | - | - | Read
13161 | 12 | Overload: Conf. AI 29 | - | 1 | - | - | Read
13161 | 13 | Overload: Conf. AI 30 | - | 1 | - | - | Read
13161 | 14 | Overload: Conf. AI 31 | - | 1 | - | - | Read
13161 | 15 | Overload: Conf. AI 32 | - | 1 | - | - | Read
13162 |  | Conf. AI overload register 3
13162 | 0 | Overload: Conf. AI 33 | - | 1 | - | - | Read
13162 | 1 | Overload: Conf. AI 34 | - | 1 | - | - | Read
13162 | 2 | Overload: Conf. AI 35 | - | 1 | - | - | Read
13162 | 3 | Overload: Conf. AI 36 | - | 1 | - | - | Read
13162 | 4 | Overload: Conf. AI 37 | - | 1 | - | - | Read
13162 | 5 | Overload: Conf. AI 38 | - | 1 | - | - | Read
13162 | 6 | Overload: Conf. AI 39 | - | 1 | - | - | Read
13162 | 7 | Overload: Conf. AI 40 | - | 1 | - | - | Read
13162 | 8 | Overload: Conf. AI 41 | - | 1 | - | - | Read
13162 | 9 | Overload: Conf. AI 42 | - | 1 | - | - | Read
13162 | 10 | Overload: Conf. AI 43 | - | 1 | - | - | Read
13162 | 11 | Overload: Conf. AI 44 | - | 1 | - | - | Read
13162 | 12 | Overload: Conf. AI 45 | - | 1 | - | - | Read
13162 | 13 | Overload: Conf. AI 46 | - | 1 | - | - | Read
13162 | 14 | Overload: Conf. AI 47 | - | 1 | - | - | Read
13162 | 15 | Overload: Conf. AI 48 | - | 1 | - | - | Read
13200 |  | Conf. TMP stopcondition 1 register 1
13200 | 0 | (1) Conf. TMP 1 < 0 Â°C | - | 1 | - | - | Read
13200 | 1 | (1) Conf. TMP 2 < 0 Â°C | - | 1 | - | - | Read
13200 | 2 | (1) Conf. TMP 3 < 0 Â°C | - | 1 | - | - | Read
13200 | 3 | (1) Conf. TMP 4 < 0 Â°C | - | 1 | - | - | Read
13200 | 4 | (1) Conf. TMP 5 < 0 Â°C | - | 1 | - | - | Read
13200 | 5 | (1) Conf. TMP 6 < 0 Â°C | - | 1 | - | - | Read
13200 | 6 | (1) Conf. TMP 7 < 0 Â°C | - | 1 | - | - | Read
13200 | 7 | (1) Conf. TMP 8 < 0 Â°C | - | 1 | - | - | Read
13200 | 8 | (1) Conf. TMP 9 < 0 Â°C | - | 1 | - | - | Read
13200 | 9 | (1) Conf. TMP 10 < 0 Â°C | - | 1 | - | - | Read
13200 | 10 | (1) Conf. TMP 11 < 0 Â°C | - | 1 | - | - | Read
13200 | 11 | (1) Conf. TMP 12 < 0 Â°C | - | 1 | - | - | Read
13200 | 12 | (1) Conf. TMP 13 < 0 Â°C | - | 1 | - | - | Read
13200 | 13 | (1) Conf. TMP 14 < 0 Â°C | - | 1 | - | - | Read
13200 | 14 | (1) Conf. TMP 15 < 0 Â°C | - | 1 | - | - | Read
13200 | 15 | (1) Conf. TMP 16 < 0 Â°C | - | 1 | - | - | Read
13201 |  | Conf. TMP stopcondition 1 register 2
13201 | 0 | (1) Conf. TMP 17 < 0 Â°C | - | 1 | - | - | Read
13201 | 1 | (1) Conf. TMP 18 < 0 Â°C | - | 1 | - | - | Read
13201 | 2 | (1) Conf. TMP 19 < 0 Â°C | - | 1 | - | - | Read
13201 | 3 | (1) Conf. TMP 20 < 0 Â°C | - | 1 | - | - | Read
13201 | 4 | (1) Conf. TMP 21 < 0 Â°C | - | 1 | - | - | Read
13201 | 5 | (1) Conf. TMP 22 < 0 Â°C | - | 1 | - | - | Read
13201 | 6 | (1) Conf. TMP 23 < 0 Â°C | - | 1 | - | - | Read
13201 | 7 | (1) Conf. TMP 24 < 0 Â°C | - | 1 | - | - | Read
13201 | 8 | (1) Conf. TMP 25 < 0 Â°C | - | 1 | - | - | Read
13201 | 9 | (1) Conf. TMP 26 < 0 Â°C | - | 1 | - | - | Read
13201 | 10 | (1) Conf. TMP 27 < 0 Â°C | - | 1 | - | - | Read
13201 | 11 | (1) Conf. TMP 28 < 0 Â°C | - | 1 | - | - | Read
13201 | 12 | (1) Conf. TMP 29 < 0 Â°C | - | 1 | - | - | Read
13201 | 13 | (1) Conf. TMP 30 < 0 Â°C | - | 1 | - | - | Read
13201 | 14 | (1) Conf. TMP 31 < 0 Â°C | - | 1 | - | - | Read
13201 | 15 | (1) Conf. TMP 32 < 0 Â°C | - | 1 | - | - | Read
13202 |  | Conf. TMP stopcondition 1 register 3
13202 | 0 | (1) Conf. TMP 33 < 0 Â°C | - | 1 | - | - | Read
13202 | 1 | (1) Conf. TMP 34 < 0 Â°C | - | 1 | - | - | Read
13202 | 2 | (1) Conf. TMP 35 < 0 Â°C | - | 1 | - | - | Read
13202 | 3 | (1) Conf. TMP 36 < 0 Â°C | - | 1 | - | - | Read
13202 | 4 | (1) Conf. TMP 37 < 0 Â°C | - | 1 | - | - | Read
13202 | 5 | (1) Conf. TMP 38 < 0 Â°C | - | 1 | - | - | Read
13202 | 6 | (1) Conf. TMP 39 < 0 Â°C | - | 1 | - | - | Read
13202 | 7 | (1) Conf. TMP 40 < 0 Â°C | - | 1 | - | - | Read
13202 | 8 | (1) Conf. TMP 41 < 0 Â°C | - | 1 | - | - | Read
13202 | 9 | (1) Conf. TMP 42 < 0 Â°C | - | 1 | - | - | Read
13202 | 10 | (1) Conf. TMP 43 < 0 Â°C | - | 1 | - | - | Read
13202 | 11 | (1) Conf. TMP 44 < 0 Â°C | - | 1 | - | - | Read
13202 | 12 | (1) Conf. TMP 45 < 0 Â°C | - | 1 | - | - | Read
13202 | 13 | (1) Conf. TMP 46 < 0 Â°C | - | 1 | - | - | Read
13202 | 14 | (1) Conf. TMP 47 < 0 Â°C | - | 1 | - | - | Read
13202 | 15 | (1) Conf. TMP 48 < 0 Â°C | - | 1 | - | - | Read
13203 |  | Conf. TMP stopcondition 1 register 4
13203 | 0 | (1) Conf. TMP 49 < 0 Â°C | - | 1 | - | - | Read
13203 | 1 | (1) Conf. TMP 50 < 0 Â°C | - | 1 | - | - | Read
13203 | 2 | (1) Conf. TMP 51 < 0 Â°C | - | 1 | - | - | Read
13203 | 3 | (1) Conf. TMP 52 < 0 Â°C | - | 1 | - | - | Read
13203 | 4 | (1) Conf. TMP 53 < 0 Â°C | - | 1 | - | - | Read
13203 | 5 | (1) Conf. TMP 54 < 0 Â°C | - | 1 | - | - | Read
13203 | 6 | (1) Conf. TMP 55 < 0 Â°C | - | 1 | - | - | Read
13203 | 7 | (1) Conf. TMP 56 < 0 Â°C | - | 1 | - | - | Read
13203 | 8 | (1) Conf. TMP 57 < 0 Â°C | - | 1 | - | - | Read
13203 | 9 | (1) Conf. TMP 58 < 0 Â°C | - | 1 | - | - | Read
13203 | 10 | (1) Conf. TMP 59 < 0 Â°C | - | 1 | - | - | Read
13203 | 11 | (1) Conf. TMP 60 < 0 Â°C | - | 1 | - | - | Read
13203 | 12 | (1) Conf. TMP 61 < 0 Â°C | - | 1 | - | - | Read
13203 | 13 | (1) Conf. TMP 62 < 0 Â°C | - | 1 | - | - | Read
13203 | 14 | (1) Conf. TMP 63 < 0 Â°C | - | 1 | - | - | Read
13203 | 15 | (1) Conf. TMP 64 < 0 Â°C | - | 1 | - | - | Read
13204 |  | Conf. TMP stopcondition 1 register 5
13204 | 0 | (1) Conf. TMP 65 < 0 Â°C | - | 1 | - | - | Read
13204 | 1 | (1) Conf. TMP 66 < 0 Â°C | - | 1 | - | - | Read
13204 | 2 | (1) Conf. TMP 67 < 0 Â°C | - | 1 | - | - | Read
13204 | 3 | (1) Conf. TMP 68 < 0 Â°C | - | 1 | - | - | Read
13204 | 4 | (1) Conf. TMP 69 < 0 Â°C | - | 1 | - | - | Read
13204 | 5 | (1) Conf. TMP 70 < 0 Â°C | - | 1 | - | - | Read
13204 | 6 | (1) Conf. TMP 71 < 0 Â°C | - | 1 | - | - | Read
13204 | 7 | (1) Conf. TMP 72 < 0 Â°C | - | 1 | - | - | Read
13210 |  | Conf. TMP stopcondition 2 register 1
13210 | 0 | (2) Conf. TMP 1 < 0 Â°C | - | 1 | - | - | Read
13210 | 1 | (2) Conf. TMP 2 < 0 Â°C | - | 1 | - | - | Read
13210 | 2 | (2) Conf. TMP 3 < 0 Â°C | - | 1 | - | - | Read
13210 | 3 | (2) Conf. TMP 4 < 0 Â°C | - | 1 | - | - | Read
13210 | 4 | (2) Conf. TMP 5 < 0 Â°C | - | 1 | - | - | Read
13210 | 5 | (2) Conf. TMP 6 < 0 Â°C | - | 1 | - | - | Read
13210 | 6 | (2) Conf. TMP 7 < 0 Â°C | - | 1 | - | - | Read
13210 | 7 | (2) Conf. TMP 8 < 0 Â°C | - | 1 | - | - | Read
13210 | 8 | (2) Conf. TMP 9 < 0 Â°C | - | 1 | - | - | Read
13210 | 9 | (2) Conf. TMP 10 < 0 Â°C | - | 1 | - | - | Read
13210 | 10 | (2) Conf. TMP 11 < 0 Â°C | - | 1 | - | - | Read
13210 | 11 | (2) Conf. TMP 12 < 0 Â°C | - | 1 | - | - | Read
13210 | 12 | (2) Conf. TMP 13 < 0 Â°C | - | 1 | - | - | Read
13210 | 13 | (2) Conf. TMP 14 < 0 Â°C | - | 1 | - | - | Read
13210 | 14 | (2) Conf. TMP 15 < 0 Â°C | - | 1 | - | - | Read
13210 | 15 | (2) Conf. TMP 16 < 0 Â°C | - | 1 | - | - | Read
13211 |  | Conf. TMP stopcondition 2 register 2
13211 | 0 | (2) Conf. TMP 17 < 0 Â°C | - | 1 | - | - | Read
13211 | 1 | (2) Conf. TMP 18 < 0 Â°C | - | 1 | - | - | Read
13211 | 2 | (2) Conf. TMP 19 < 0 Â°C | - | 1 | - | - | Read
13211 | 3 | (2) Conf. TMP 20 < 0 Â°C | - | 1 | - | - | Read
13211 | 4 | (2) Conf. TMP 21 < 0 Â°C | - | 1 | - | - | Read
13211 | 5 | (2) Conf. TMP 22 < 0 Â°C | - | 1 | - | - | Read
13211 | 6 | (2) Conf. TMP 23 < 0 Â°C | - | 1 | - | - | Read
13211 | 7 | (2) Conf. TMP 24 < 0 Â°C | - | 1 | - | - | Read
13211 | 8 | (2) Conf. TMP 25 < 0 Â°C | - | 1 | - | - | Read
13211 | 9 | (2) Conf. TMP 26 < 0 Â°C | - | 1 | - | - | Read
13211 | 10 | (2) Conf. TMP 27 < 0 Â°C | - | 1 | - | - | Read
13211 | 11 | (2) Conf. TMP 28 < 0 Â°C | - | 1 | - | - | Read
13211 | 12 | (2) Conf. TMP 29 < 0 Â°C | - | 1 | - | - | Read
13211 | 13 | (2) Conf. TMP 30 < 0 Â°C | - | 1 | - | - | Read
13211 | 14 | (2) Conf. TMP 31 < 0 Â°C | - | 1 | - | - | Read
13211 | 15 | (2) Conf. TMP 32 < 0 Â°C | - | 1 | - | - | Read
13212 |  | Conf. TMP stopcondition 2 register 3
13212 | 0 | (2) Conf. TMP 33 < 0 Â°C | - | 1 | - | - | Read
13212 | 1 | (2) Conf. TMP 34 < 0 Â°C | - | 1 | - | - | Read
13212 | 2 | (2) Conf. TMP 35 < 0 Â°C | - | 1 | - | - | Read
13212 | 3 | (2) Conf. TMP 36 < 0 Â°C | - | 1 | - | - | Read
13212 | 4 | (2) Conf. TMP 37 < 0 Â°C | - | 1 | - | - | Read
13212 | 5 | (2) Conf. TMP 38 < 0 Â°C | - | 1 | - | - | Read
13212 | 6 | (2) Conf. TMP 39 < 0 Â°C | - | 1 | - | - | Read
13212 | 7 | (2) Conf. TMP 40 < 0 Â°C | - | 1 | - | - | Read
13212 | 8 | (2) Conf. TMP 41 < 0 Â°C | - | 1 | - | - | Read
13212 | 9 | (2) Conf. TMP 42 < 0 Â°C | - | 1 | - | - | Read
13212 | 10 | (2) Conf. TMP 43 < 0 Â°C | - | 1 | - | - | Read
13212 | 11 | (2) Conf. TMP 44 < 0 Â°C | - | 1 | - | - | Read
13212 | 12 | (2) Conf. TMP 45 < 0 Â°C | - | 1 | - | - | Read
13212 | 13 | (2) Conf. TMP 46 < 0 Â°C | - | 1 | - | - | Read
13212 | 14 | (2) Conf. TMP 47 < 0 Â°C | - | 1 | - | - | Read
13212 | 15 | (2) Conf. TMP 48 < 0 Â°C | - | 1 | - | - | Read
13213 |  | Conf. TMP stopcondition 2 register 4
13213 | 0 | (2) Conf. TMP 49 < 0 Â°C | - | 1 | - | - | Read
13213 | 1 | (2) Conf. TMP 50 < 0 Â°C | - | 1 | - | - | Read
13213 | 2 | (2) Conf. TMP 51 < 0 Â°C | - | 1 | - | - | Read
13213 | 3 | (2) Conf. TMP 52 < 0 Â°C | - | 1 | - | - | Read
13213 | 4 | (2) Conf. TMP 53 < 0 Â°C | - | 1 | - | - | Read
13213 | 5 | (2) Conf. TMP 54 < 0 Â°C | - | 1 | - | - | Read
13213 | 6 | (2) Conf. TMP 55 < 0 Â°C | - | 1 | - | - | Read
13213 | 7 | (2) Conf. TMP 56 < 0 Â°C | - | 1 | - | - | Read
13213 | 8 | (2) Conf. TMP 57 < 0 Â°C | - | 1 | - | - | Read
13213 | 9 | (2) Conf. TMP 58 < 0 Â°C | - | 1 | - | - | Read
13213 | 10 | (2) Conf. TMP 59 < 0 Â°C | - | 1 | - | - | Read
13213 | 11 | (2) Conf. TMP 60 < 0 Â°C | - | 1 | - | - | Read
13213 | 12 | (2) Conf. TMP 61 < 0 Â°C | - | 1 | - | - | Read
13213 | 13 | (2) Conf. TMP 62 < 0 Â°C | - | 1 | - | - | Read
13213 | 14 | (2) Conf. TMP 63 < 0 Â°C | - | 1 | - | - | Read
13213 | 15 | (2) Conf. TMP 64 < 0 Â°C | - | 1 | - | - | Read
13214 |  | Conf. TMP stopcondition 2 register 5
13214 | 0 | (2) Conf. TMP 65 < 0 Â°C | - | 1 | - | - | Read
13214 | 1 | (2) Conf. TMP 66 < 0 Â°C | - | 1 | - | - | Read
13214 | 2 | (2) Conf. TMP 67 < 0 Â°C | - | 1 | - | - | Read
13214 | 3 | (2) Conf. TMP 68 < 0 Â°C | - | 1 | - | - | Read
13214 | 4 | (2) Conf. TMP 69 < 0 Â°C | - | 1 | - | - | Read
13214 | 5 | (2) Conf. TMP 70 < 0 Â°C | - | 1 | - | - | Read
13214 | 6 | (2) Conf. TMP 71 < 0 Â°C | - | 1 | - | - | Read
13214 | 7 | (2) Conf. TMP 72 < 0 Â°C | - | 1 | - | - | Read
13220 |  | Conf. TMP stopcondition 3 register 1
13220 | 0 | (3) Conf. TMP 1 < 0 Â°C | - | 1 | - | - | Read
13220 | 1 | (3) Conf. TMP 2 < 0 Â°C | - | 1 | - | - | Read
13220 | 2 | (3) Conf. TMP 3 < 0 Â°C | - | 1 | - | - | Read
13220 | 3 | (3) Conf. TMP 4 < 0 Â°C | - | 1 | - | - | Read
13220 | 4 | (3) Conf. TMP 5 < 0 Â°C | - | 1 | - | - | Read
13220 | 5 | (3) Conf. TMP 6 < 0 Â°C | - | 1 | - | - | Read
13220 | 6 | (3) Conf. TMP 7 < 0 Â°C | - | 1 | - | - | Read
13220 | 7 | (3) Conf. TMP 8 < 0 Â°C | - | 1 | - | - | Read
13220 | 8 | (3) Conf. TMP 9 < 0 Â°C | - | 1 | - | - | Read
13220 | 9 | (3) Conf. TMP 10 < 0 Â°C | - | 1 | - | - | Read
13220 | 10 | (3) Conf. TMP 11 < 0 Â°C | - | 1 | - | - | Read
13220 | 11 | (3) Conf. TMP 12 < 0 Â°C | - | 1 | - | - | Read
13220 | 12 | (3) Conf. TMP 13 < 0 Â°C | - | 1 | - | - | Read
13220 | 13 | (3) Conf. TMP 14 < 0 Â°C | - | 1 | - | - | Read
13220 | 14 | (3) Conf. TMP 15 < 0 Â°C | - | 1 | - | - | Read
13220 | 15 | (3) Conf. TMP 16 < 0 Â°C | - | 1 | - | - | Read
13221 |  | Conf. TMP stopcondition 3 register 2
13221 | 0 | (3) Conf. TMP 17 < 0 Â°C | - | 1 | - | - | Read
13221 | 1 | (3) Conf. TMP 18 < 0 Â°C | - | 1 | - | - | Read
13221 | 2 | (3) Conf. TMP 19 < 0 Â°C | - | 1 | - | - | Read
13221 | 3 | (3) Conf. TMP 20 < 0 Â°C | - | 1 | - | - | Read
13221 | 4 | (3) Conf. TMP 21 < 0 Â°C | - | 1 | - | - | Read
13221 | 5 | (3) Conf. TMP 22 < 0 Â°C | - | 1 | - | - | Read
13221 | 6 | (3) Conf. TMP 23 < 0 Â°C | - | 1 | - | - | Read
13221 | 7 | (3) Conf. TMP 24 < 0 Â°C | - | 1 | - | - | Read
13221 | 8 | (3) Conf. TMP 25 < 0 Â°C | - | 1 | - | - | Read
13221 | 9 | (3) Conf. TMP 26 < 0 Â°C | - | 1 | - | - | Read
13221 | 10 | (3) Conf. TMP 27 < 0 Â°C | - | 1 | - | - | Read
13221 | 11 | (3) Conf. TMP 28 < 0 Â°C | - | 1 | - | - | Read
13221 | 12 | (3) Conf. TMP 29 < 0 Â°C | - | 1 | - | - | Read
13221 | 13 | (3) Conf. TMP 30 < 0 Â°C | - | 1 | - | - | Read
13221 | 14 | (3) Conf. TMP 31 < 0 Â°C | - | 1 | - | - | Read
13221 | 15 | (3) Conf. TMP 32 < 0 Â°C | - | 1 | - | - | Read
13222 |  | Conf. TMP stopcondition 3 register 3
13222 | 0 | (3) Conf. TMP 33 < 0 Â°C | - | 1 | - | - | Read
13222 | 1 | (3) Conf. TMP 34 < 0 Â°C | - | 1 | - | - | Read
13222 | 2 | (3) Conf. TMP 35 < 0 Â°C | - | 1 | - | - | Read
13222 | 3 | (3) Conf. TMP 36 < 0 Â°C | - | 1 | - | - | Read
13222 | 4 | (3) Conf. TMP 37 < 0 Â°C | - | 1 | - | - | Read
13222 | 5 | (3) Conf. TMP 38 < 0 Â°C | - | 1 | - | - | Read
13222 | 6 | (3) Conf. TMP 39 < 0 Â°C | - | 1 | - | - | Read
13222 | 7 | (3) Conf. TMP 40 < 0 Â°C | - | 1 | - | - | Read
13222 | 8 | (3) Conf. TMP 41 < 0 Â°C | - | 1 | - | - | Read
13222 | 9 | (3) Conf. TMP 42 < 0 Â°C | - | 1 | - | - | Read
13222 | 10 | (3) Conf. TMP 43 < 0 Â°C | - | 1 | - | - | Read
13222 | 11 | (3) Conf. TMP 44 < 0 Â°C | - | 1 | - | - | Read
13222 | 12 | (3) Conf. TMP 45 < 0 Â°C | - | 1 | - | - | Read
13222 | 13 | (3) Conf. TMP 46 < 0 Â°C | - | 1 | - | - | Read
13222 | 14 | (3) Conf. TMP 47 < 0 Â°C | - | 1 | - | - | Read
13222 | 15 | (3) Conf. TMP 48 < 0 Â°C | - | 1 | - | - | Read
13223 |  | Conf. TMP stopcondition 3 register 4
13223 | 0 | (3) Conf. TMP 49 < 0 Â°C | - | 1 | - | - | Read
13223 | 1 | (3) Conf. TMP 50 < 0 Â°C | - | 1 | - | - | Read
13223 | 2 | (3) Conf. TMP 51 < 0 Â°C | - | 1 | - | - | Read
13223 | 3 | (3) Conf. TMP 52 < 0 Â°C | - | 1 | - | - | Read
13223 | 4 | (3) Conf. TMP 53 < 0 Â°C | - | 1 | - | - | Read
13223 | 5 | (3) Conf. TMP 54 < 0 Â°C | - | 1 | - | - | Read
13223 | 6 | (3) Conf. TMP 55 < 0 Â°C | - | 1 | - | - | Read
13223 | 7 | (3) Conf. TMP 56 < 0 Â°C | - | 1 | - | - | Read
13223 | 8 | (3) Conf. TMP 57 < 0 Â°C | - | 1 | - | - | Read
13223 | 9 | (3) Conf. TMP 58 < 0 Â°C | - | 1 | - | - | Read
13223 | 10 | (3) Conf. TMP 59 < 0 Â°C | - | 1 | - | - | Read
13223 | 11 | (3) Conf. TMP 60 < 0 Â°C | - | 1 | - | - | Read
13223 | 12 | (3) Conf. TMP 61 < 0 Â°C | - | 1 | - | - | Read
13223 | 13 | (3) Conf. TMP 62 < 0 Â°C | - | 1 | - | - | Read
13223 | 14 | (3) Conf. TMP 63 < 0 Â°C | - | 1 | - | - | Read
13223 | 15 | (3) Conf. TMP 64 < 0 Â°C | - | 1 | - | - | Read
13224 |  | Conf. TMP stopcondition 3 register 5
13224 | 0 | (3) Conf. TMP 65 < 0 Â°C | - | 1 | - | - | Read
13224 | 1 | (3) Conf. TMP 66 < 0 Â°C | - | 1 | - | - | Read
13224 | 2 | (3) Conf. TMP 67 < 0 Â°C | - | 1 | - | - | Read
13224 | 3 | (3) Conf. TMP 68 < 0 Â°C | - | 1 | - | - | Read
13224 | 4 | (3) Conf. TMP 69 < 0 Â°C | - | 1 | - | - | Read
13224 | 5 | (3) Conf. TMP 70 < 0 Â°C | - | 1 | - | - | Read
13224 | 6 | (3) Conf. TMP 71 < 0 Â°C | - | 1 | - | - | Read
13224 | 7 | (3) Conf. TMP 72 < 0 Â°C | - | 1 | - | - | Read
13230 |  | Conf. TMP stopcondition 4 register 1
13230 | 0 | (4) Conf. TMP 1 < 0 Â°C | - | 1 | - | - | Read
13230 | 1 | (4) Conf. TMP 2 < 0 Â°C | - | 1 | - | - | Read
13230 | 2 | (4) Conf. TMP 3 < 0 Â°C | - | 1 | - | - | Read
13230 | 3 | (4) Conf. TMP 4 < 0 Â°C | - | 1 | - | - | Read
13230 | 4 | (4) Conf. TMP 5 < 0 Â°C | - | 1 | - | - | Read
13230 | 5 | (4) Conf. TMP 6 < 0 Â°C | - | 1 | - | - | Read
13230 | 6 | (4) Conf. TMP 7 < 0 Â°C | - | 1 | - | - | Read
13230 | 7 | (4) Conf. TMP 8 < 0 Â°C | - | 1 | - | - | Read
13230 | 8 | (4) Conf. TMP 9 < 0 Â°C | - | 1 | - | - | Read
13230 | 9 | (4) Conf. TMP 10 < 0 Â°C | - | 1 | - | - | Read
13230 | 10 | (4) Conf. TMP 11 < 0 Â°C | - | 1 | - | - | Read
13230 | 11 | (4) Conf. TMP 12 < 0 Â°C | - | 1 | - | - | Read
13230 | 12 | (4) Conf. TMP 13 < 0 Â°C | - | 1 | - | - | Read
13230 | 13 | (4) Conf. TMP 14 < 0 Â°C | - | 1 | - | - | Read
13230 | 14 | (4) Conf. TMP 15 < 0 Â°C | - | 1 | - | - | Read
13230 | 15 | (4) Conf. TMP 16 < 0 Â°C | - | 1 | - | - | Read
13231 |  | Conf. TMP stopcondition 4 register 2
13231 | 0 | (4) Conf. TMP 17 < 0 Â°C | - | 1 | - | - | Read
13231 | 1 | (4) Conf. TMP 18 < 0 Â°C | - | 1 | - | - | Read
13231 | 2 | (4) Conf. TMP 19 < 0 Â°C | - | 1 | - | - | Read
13231 | 3 | (4) Conf. TMP 20 < 0 Â°C | - | 1 | - | - | Read
13231 | 4 | (4) Conf. TMP 21 < 0 Â°C | - | 1 | - | - | Read
13231 | 5 | (4) Conf. TMP 22 < 0 Â°C | - | 1 | - | - | Read
13231 | 6 | (4) Conf. TMP 23 < 0 Â°C | - | 1 | - | - | Read
13231 | 7 | (4) Conf. TMP 24 < 0 Â°C | - | 1 | - | - | Read
13231 | 8 | (4) Conf. TMP 25 < 0 Â°C | - | 1 | - | - | Read
13231 | 9 | (4) Conf. TMP 26 < 0 Â°C | - | 1 | - | - | Read
13231 | 10 | (4) Conf. TMP 27 < 0 Â°C | - | 1 | - | - | Read
13231 | 11 | (4) Conf. TMP 28 < 0 Â°C | - | 1 | - | - | Read
13231 | 12 | (4) Conf. TMP 29 < 0 Â°C | - | 1 | - | - | Read
13231 | 13 | (4) Conf. TMP 30 < 0 Â°C | - | 1 | - | - | Read
13231 | 14 | (4) Conf. TMP 31 < 0 Â°C | - | 1 | - | - | Read
13231 | 15 | (4) Conf. TMP 32 < 0 Â°C | - | 1 | - | - | Read
13232 |  | Conf. TMP stopcondition 4 register 3
13232 | 0 | (4) Conf. TMP 33 < 0 Â°C | - | 1 | - | - | Read
13232 | 1 | (4) Conf. TMP 34 < 0 Â°C | - | 1 | - | - | Read
13232 | 2 | (4) Conf. TMP 35 < 0 Â°C | - | 1 | - | - | Read
13232 | 3 | (4) Conf. TMP 36 < 0 Â°C | - | 1 | - | - | Read
13232 | 4 | (4) Conf. TMP 37 < 0 Â°C | - | 1 | - | - | Read
13232 | 5 | (4) Conf. TMP 38 < 0 Â°C | - | 1 | - | - | Read
13232 | 6 | (4) Conf. TMP 39 < 0 Â°C | - | 1 | - | - | Read
13232 | 7 | (4) Conf. TMP 40 < 0 Â°C | - | 1 | - | - | Read
13232 | 8 | (4) Conf. TMP 41 < 0 Â°C | - | 1 | - | - | Read
13232 | 9 | (4) Conf. TMP 42 < 0 Â°C | - | 1 | - | - | Read
13232 | 10 | (4) Conf. TMP 43 < 0 Â°C | - | 1 | - | - | Read
13232 | 11 | (4) Conf. TMP 44 < 0 Â°C | - | 1 | - | - | Read
13232 | 12 | (4) Conf. TMP 45 < 0 Â°C | - | 1 | - | - | Read
13232 | 13 | (4) Conf. TMP 46 < 0 Â°C | - | 1 | - | - | Read
13232 | 14 | (4) Conf. TMP 47 < 0 Â°C | - | 1 | - | - | Read
13232 | 15 | (4) Conf. TMP 48 < 0 Â°C | - | 1 | - | - | Read
13233 |  | Conf. TMP stopcondition 4 register 4
13233 | 0 | (4) Conf. TMP 49 < 0 Â°C | - | 1 | - | - | Read
13233 | 1 | (4) Conf. TMP 50 < 0 Â°C | - | 1 | - | - | Read
13233 | 2 | (4) Conf. TMP 51 < 0 Â°C | - | 1 | - | - | Read
13233 | 3 | (4) Conf. TMP 52 < 0 Â°C | - | 1 | - | - | Read
13233 | 4 | (4) Conf. TMP 53 < 0 Â°C | - | 1 | - | - | Read
13233 | 5 | (4) Conf. TMP 54 < 0 Â°C | - | 1 | - | - | Read
13233 | 6 | (4) Conf. TMP 55 < 0 Â°C | - | 1 | - | - | Read
13233 | 7 | (4) Conf. TMP 56 < 0 Â°C | - | 1 | - | - | Read
13233 | 8 | (4) Conf. TMP 57 < 0 Â°C | - | 1 | - | - | Read
13233 | 9 | (4) Conf. TMP 58 < 0 Â°C | - | 1 | - | - | Read
13233 | 10 | (4) Conf. TMP 59 < 0 Â°C | - | 1 | - | - | Read
13233 | 11 | (4) Conf. TMP 60 < 0 Â°C | - | 1 | - | - | Read
13233 | 12 | (4) Conf. TMP 61 < 0 Â°C | - | 1 | - | - | Read
13233 | 13 | (4) Conf. TMP 62 < 0 Â°C | - | 1 | - | - | Read
13233 | 14 | (4) Conf. TMP 63 < 0 Â°C | - | 1 | - | - | Read
13233 | 15 | (4) Conf. TMP 64 < 0 Â°C | - | 1 | - | - | Read
13234 |  | Conf. TMP stopcondition 4 register 5
13234 | 0 | (4) Conf. TMP 65 < 0 Â°C | - | 1 | - | - | Read
13234 | 1 | (4) Conf. TMP 66 < 0 Â°C | - | 1 | - | - | Read
13234 | 2 | (4) Conf. TMP 67 < 0 Â°C | - | 1 | - | - | Read
13234 | 3 | (4) Conf. TMP 68 < 0 Â°C | - | 1 | - | - | Read
13234 | 4 | (4) Conf. TMP 69 < 0 Â°C | - | 1 | - | - | Read
13234 | 5 | (4) Conf. TMP 70 < 0 Â°C | - | 1 | - | - | Read
13234 | 6 | (4) Conf. TMP 71 < 0 Â°C | - | 1 | - | - | Read
13234 | 7 | (4) Conf. TMP 72 < 0 Â°C | - | 1 | - | - | Read
13240 |  | Conf. TMP sensor defect register 1
13240 | 0 | Sensor defect: Conf. TMP 1 | - | 1 | - | - | Read
13240 | 1 | Sensor defect: Conf. TMP 2 | - | 1 | - | - | Read
13240 | 2 | Sensor defect: Conf. TMP 3 | - | 1 | - | - | Read
13240 | 3 | Sensor defect: Conf. TMP 4 | - | 1 | - | - | Read
13240 | 4 | Sensor defect: Conf. TMP 5 | - | 1 | - | - | Read
13240 | 5 | Sensor defect: Conf. TMP 6 | - | 1 | - | - | Read
13240 | 6 | Sensor defect: Conf. TMP 7 | - | 1 | - | - | Read
13240 | 7 | Sensor defect: Conf. TMP 8 | - | 1 | - | - | Read
13240 | 8 | Sensor defect: Conf. TMP 9 | - | 1 | - | - | Read
13240 | 9 | Sensor defect: Conf. TMP 10 | - | 1 | - | - | Read
13240 | 10 | Sensor defect: Conf. TMP 11 | - | 1 | - | - | Read
13240 | 11 | Sensor defect: Conf. TMP 12 | - | 1 | - | - | Read
13240 | 12 | Sensor defect: Conf. TMP 13 | - | 1 | - | - | Read
13240 | 13 | Sensor defect: Conf. TMP 14 | - | 1 | - | - | Read
13240 | 14 | Sensor defect: Conf. TMP 15 | - | 1 | - | - | Read
13240 | 15 | Sensor defect: Conf. TMP 16 | - | 1 | - | - | Read
13241 |  | Conf. TMP sensor defect register 2
13241 | 0 | Sensor defect: Conf. TMP 17 | - | 1 | - | - | Read
13241 | 1 | Sensor defect: Conf. TMP 18 | - | 1 | - | - | Read
13241 | 2 | Sensor defect: Conf. TMP 19 | - | 1 | - | - | Read
13241 | 3 | Sensor defect: Conf. TMP 20 | - | 1 | - | - | Read
13241 | 4 | Sensor defect: Conf. TMP 21 | - | 1 | - | - | Read
13241 | 5 | Sensor defect: Conf. TMP 22 | - | 1 | - | - | Read
13241 | 6 | Sensor defect: Conf. TMP 23 | - | 1 | - | - | Read
13241 | 7 | Sensor defect: Conf. TMP 24 | - | 1 | - | - | Read
13241 | 8 | Sensor defect: Conf. TMP 25 | - | 1 | - | - | Read
13241 | 9 | Sensor defect: Conf. TMP 26 | - | 1 | - | - | Read
13241 | 10 | Sensor defect: Conf. TMP 27 | - | 1 | - | - | Read
13241 | 11 | Sensor defect: Conf. TMP 28 | - | 1 | - | - | Read
13241 | 12 | Sensor defect: Conf. TMP 29 | - | 1 | - | - | Read
13241 | 13 | Sensor defect: Conf. TMP 30 | - | 1 | - | - | Read
13241 | 14 | Sensor defect: Conf. TMP 31 | - | 1 | - | - | Read
13241 | 15 | Sensor defect: Conf. TMP 32 | - | 1 | - | - | Read
13242 |  | Conf. TMP sensor defect register 3
13242 | 0 | Sensor defect: Conf. TMP 33 | - | 1 | - | - | Read
13242 | 1 | Sensor defect: Conf. TMP 34 | - | 1 | - | - | Read
13242 | 2 | Sensor defect: Conf. TMP 35 | - | 1 | - | - | Read
13242 | 3 | Sensor defect: Conf. TMP 36 | - | 1 | - | - | Read
13242 | 4 | Sensor defect: Conf. TMP 37 | - | 1 | - | - | Read
13242 | 5 | Sensor defect: Conf. TMP 38 | - | 1 | - | - | Read
13242 | 6 | Sensor defect: Conf. TMP 39 | - | 1 | - | - | Read
13242 | 7 | Sensor defect: Conf. TMP 40 | - | 1 | - | - | Read
13242 | 8 | Sensor defect: Conf. TMP 41 | - | 1 | - | - | Read
13242 | 9 | Sensor defect: Conf. TMP 42 | - | 1 | - | - | Read
13242 | 10 | Sensor defect: Conf. TMP 43 | - | 1 | - | - | Read
13242 | 11 | Sensor defect: Conf. TMP 44 | - | 1 | - | - | Read
13242 | 12 | Sensor defect: Conf. TMP 45 | - | 1 | - | - | Read
13242 | 13 | Sensor defect: Conf. TMP 46 | - | 1 | - | - | Read
13242 | 14 | Sensor defect: Conf. TMP 47 | - | 1 | - | - | Read
13242 | 15 | Sensor defect: Conf. TMP 48 | - | 1 | - | - | Read
13243 |  | Conf. TMP sensor defect register 4
13243 | 0 | Sensor defect: Conf. TMP 49 | - | 1 | - | - | Read
13243 | 1 | Sensor defect: Conf. TMP 50 | - | 1 | - | - | Read
13243 | 2 | Sensor defect: Conf. TMP 51 | - | 1 | - | - | Read
13243 | 3 | Sensor defect: Conf. TMP 52 | - | 1 | - | - | Read
13243 | 4 | Sensor defect: Conf. TMP 53 | - | 1 | - | - | Read
13243 | 5 | Sensor defect: Conf. TMP 54 | - | 1 | - | - | Read
13243 | 6 | Sensor defect: Conf. TMP 55 | - | 1 | - | - | Read
13243 | 7 | Sensor defect: Conf. TMP 56 | - | 1 | - | - | Read
13243 | 8 | Sensor defect: Conf. TMP 57 | - | 1 | - | - | Read
13243 | 9 | Sensor defect: Conf. TMP 58 | - | 1 | - | - | Read
13243 | 10 | Sensor defect: Conf. TMP 59 | - | 1 | - | - | Read
13243 | 11 | Sensor defect: Conf. TMP 60 | - | 1 | - | - | Read
13243 | 12 | Sensor defect: Conf. TMP 61 | - | 1 | - | - | Read
13243 | 13 | Sensor defect: Conf. TMP 62 | - | 1 | - | - | Read
13243 | 14 | Sensor defect: Conf. TMP 63 | - | 1 | - | - | Read
13243 | 15 | Sensor defect: Conf. TMP 64 | - | 1 | - | - | Read
13244 |  | Conf. TMP sensor defect register 5
13244 | 0 | Sensor defect: Conf. TMP 65 | - | 1 | - | - | Read
13244 | 1 | Sensor defect: Conf. TMP 66 | - | 1 | - | - | Read
13244 | 2 | Sensor defect: Conf. TMP 67 | - | 1 | - | - | Read
13244 | 3 | Sensor defect: Conf. TMP 68 | - | 1 | - | - | Read
13244 | 4 | Sensor defect: Conf. TMP 69 | - | 1 | - | - | Read
13244 | 5 | Sensor defect: Conf. TMP 70 | - | 1 | - | - | Read
13244 | 6 | Sensor defect: Conf. TMP 71 | - | 1 | - | - | Read
13244 | 7 | Sensor defect: Conf. TMP 72 | - | 1 | - | - | Read
13250 |  | Conf. TMP wirebreak register 1
13250 | 0 | Wire break: Conf. TMP 1 | - | 1 | - | - | Read
13250 | 1 | Wire break: Conf. TMP 2 | - | 1 | - | - | Read
13250 | 2 | Wire break: Conf. TMP 3 | - | 1 | - | - | Read
13250 | 3 | Wire break: Conf. TMP 4 | - | 1 | - | - | Read
13250 | 4 | Wire break: Conf. TMP 5 | - | 1 | - | - | Read
13250 | 5 | Wire break: Conf. TMP 6 | - | 1 | - | - | Read
13250 | 6 | Wire break: Conf. TMP 7 | - | 1 | - | - | Read
13250 | 7 | Wire break: Conf. TMP 8 | - | 1 | - | - | Read
13250 | 8 | Wire break: Conf. TMP 9 | - | 1 | - | - | Read
13250 | 9 | Wire break: Conf. TMP 10 | - | 1 | - | - | Read
13250 | 10 | Wire break: Conf. TMP 11 | - | 1 | - | - | Read
13250 | 11 | Wire break: Conf. TMP 12 | - | 1 | - | - | Read
13250 | 12 | Wire break: Conf. TMP 13 | - | 1 | - | - | Read
13250 | 13 | Wire break: Conf. TMP 14 | - | 1 | - | - | Read
13250 | 14 | Wire break: Conf. TMP 15 | - | 1 | - | - | Read
13250 | 15 | Wire break: Conf. TMP 16 | - | 1 | - | - | Read
13251 |  | Conf. TMP wirebreak register 2
13251 | 0 | Wire break: Conf. TMP 17 | - | 1 | - | - | Read
13251 | 1 | Wire break: Conf. TMP 18 | - | 1 | - | - | Read
13251 | 2 | Wire break: Conf. TMP 19 | - | 1 | - | - | Read
13251 | 3 | Wire break: Conf. TMP 20 | - | 1 | - | - | Read
13251 | 4 | Wire break: Conf. TMP 21 | - | 1 | - | - | Read
13251 | 5 | Wire break: Conf. TMP 22 | - | 1 | - | - | Read
13251 | 6 | Wire break: Conf. TMP 23 | - | 1 | - | - | Read
13251 | 7 | Wire break: Conf. TMP 24 | - | 1 | - | - | Read
13251 | 8 | Wire break: Conf. TMP 25 | - | 1 | - | - | Read
13251 | 9 | Wire break: Conf. TMP 26 | - | 1 | - | - | Read
13251 | 10 | Wire break: Conf. TMP 27 | - | 1 | - | - | Read
13251 | 11 | Wire break: Conf. TMP 28 | - | 1 | - | - | Read
13251 | 12 | Wire break: Conf. TMP 29 | - | 1 | - | - | Read
13251 | 13 | Wire break: Conf. TMP 30 | - | 1 | - | - | Read
13251 | 14 | Wire break: Conf. TMP 31 | - | 1 | - | - | Read
13251 | 15 | Wire break: Conf. TMP 32 | - | 1 | - | - | Read
13252 |  | Conf. TMP wirebreak register 3
13252 | 0 | Wire break: Conf. TMP 33 | - | 1 | - | - | Read
13252 | 1 | Wire break: Conf. TMP 34 | - | 1 | - | - | Read
13252 | 2 | Wire break: Conf. TMP 35 | - | 1 | - | - | Read
13252 | 3 | Wire break: Conf. TMP 36 | - | 1 | - | - | Read
13252 | 4 | Wire break: Conf. TMP 37 | - | 1 | - | - | Read
13252 | 5 | Wire break: Conf. TMP 38 | - | 1 | - | - | Read
13252 | 6 | Wire break: Conf. TMP 39 | - | 1 | - | - | Read
13252 | 7 | Wire break: Conf. TMP 40 | - | 1 | - | - | Read
13252 | 8 | Wire break: Conf. TMP 41 | - | 1 | - | - | Read
13252 | 9 | Wire break: Conf. TMP 42 | - | 1 | - | - | Read
13252 | 10 | Wire break: Conf. TMP 43 | - | 1 | - | - | Read
13252 | 11 | Wire break: Conf. TMP 44 | - | 1 | - | - | Read
13252 | 12 | Wire break: Conf. TMP 45 | - | 1 | - | - | Read
13252 | 13 | Wire break: Conf. TMP 46 | - | 1 | - | - | Read
13252 | 14 | Wire break: Conf. TMP 47 | - | 1 | - | - | Read
13252 | 15 | Wire break: Conf. TMP 48 | - | 1 | - | - | Read
13253 |  | Conf. TMP wirebreak register 4
13253 | 0 | Wire break: Conf. TMP 49 | - | 1 | - | - | Read
13253 | 1 | Wire break: Conf. TMP 50 | - | 1 | - | - | Read
13253 | 2 | Wire break: Conf. TMP 51 | - | 1 | - | - | Read
13253 | 3 | Wire break: Conf. TMP 52 | - | 1 | - | - | Read
13253 | 4 | Wire break: Conf. TMP 53 | - | 1 | - | - | Read
13253 | 5 | Wire break: Conf. TMP 54 | - | 1 | - | - | Read
13253 | 6 | Wire break: Conf. TMP 55 | - | 1 | - | - | Read
13253 | 7 | Wire break: Conf. TMP 56 | - | 1 | - | - | Read
13253 | 8 | Wire break: Conf. TMP 57 | - | 1 | - | - | Read
13253 | 9 | Wire break: Conf. TMP 58 | - | 1 | - | - | Read
13253 | 10 | Wire break: Conf. TMP 59 | - | 1 | - | - | Read
13253 | 11 | Wire break: Conf. TMP 60 | - | 1 | - | - | Read
13253 | 12 | Wire break: Conf. TMP 61 | - | 1 | - | - | Read
13253 | 13 | Wire break: Conf. TMP 62 | - | 1 | - | - | Read
13253 | 14 | Wire break: Conf. TMP 63 | - | 1 | - | - | Read
13253 | 15 | Wire break: Conf. TMP 64 | - | 1 | - | - | Read
13254 |  | Conf. TMP wirebreak register 5
13254 | 0 | Wire break: Conf. TMP 65 | - | 1 | - | - | Read
13254 | 1 | Wire break: Conf. TMP 66 | - | 1 | - | - | Read
13254 | 2 | Wire break: Conf. TMP 67 | - | 1 | - | - | Read
13254 | 3 | Wire break: Conf. TMP 68 | - | 1 | - | - | Read
13254 | 4 | Wire break: Conf. TMP 69 | - | 1 | - | - | Read
13254 | 5 | Wire break: Conf. TMP 70 | - | 1 | - | - | Read
13254 | 6 | Wire break: Conf. TMP 71 | - | 1 | - | - | Read
13254 | 7 | Wire break: Conf. TMP 72 | - | 1 | - | - | Read
13260 |  | Conf. TMP short circuit register 1
13260 | 0 | Short circuit: Conf. TMP 1 | - | 1 | - | - | Read
13260 | 1 | Short circuit: Conf. TMP 2 | - | 1 | - | - | Read
13260 | 2 | Short circuit: Conf. TMP 3 | - | 1 | - | - | Read
13260 | 3 | Short circuit: Conf. TMP 4 | - | 1 | - | - | Read
13260 | 4 | Short circuit: Conf. TMP 5 | - | 1 | - | - | Read
13260 | 5 | Short circuit: Conf. TMP 6 | - | 1 | - | - | Read
13260 | 6 | Short circuit: Conf. TMP 7 | - | 1 | - | - | Read
13260 | 7 | Short circuit: Conf. TMP 8 | - | 1 | - | - | Read
13260 | 8 | Short circuit: Conf. TMP 9 | - | 1 | - | - | Read
13260 | 9 | Short circuit: Conf. TMP 10 | - | 1 | - | - | Read
13260 | 10 | Short circuit: Conf. TMP 11 | - | 1 | - | - | Read
13260 | 11 | Short circuit: Conf. TMP 12 | - | 1 | - | - | Read
13260 | 12 | Short circuit: Conf. TMP 13 | - | 1 | - | - | Read
13260 | 13 | Short circuit: Conf. TMP 14 | - | 1 | - | - | Read
13260 | 14 | Short circuit: Conf. TMP 15 | - | 1 | - | - | Read
13260 | 15 | Short circuit: Conf. TMP 16 | - | 1 | - | - | Read
13261 |  | Conf. TMP short circuit register 2
13261 | 0 | Short circuit: Conf. TMP 17 | - | 1 | - | - | Read
13261 | 1 | Short circuit: Conf. TMP 18 | - | 1 | - | - | Read
13261 | 2 | Short circuit: Conf. TMP 19 | - | 1 | - | - | Read
13261 | 3 | Short circuit: Conf. TMP 20 | - | 1 | - | - | Read
13261 | 4 | Short circuit: Conf. TMP 21 | - | 1 | - | - | Read
13261 | 5 | Short circuit: Conf. TMP 22 | - | 1 | - | - | Read
13261 | 6 | Short circuit: Conf. TMP 23 | - | 1 | - | - | Read
13261 | 7 | Short circuit: Conf. TMP 24 | - | 1 | - | - | Read
13261 | 8 | Short circuit: Conf. TMP 25 | - | 1 | - | - | Read
13261 | 9 | Short circuit: Conf. TMP 26 | - | 1 | - | - | Read
13261 | 10 | Short circuit: Conf. TMP 27 | - | 1 | - | - | Read
13261 | 11 | Short circuit: Conf. TMP 28 | - | 1 | - | - | Read
13261 | 12 | Short circuit: Conf. TMP 29 | - | 1 | - | - | Read
13261 | 13 | Short circuit: Conf. TMP 30 | - | 1 | - | - | Read
13261 | 14 | Short circuit: Conf. TMP 31 | - | 1 | - | - | Read
13261 | 15 | Short circuit: Conf. TMP 32 | - | 1 | - | - | Read
13262 |  | Conf. TMP short circuit register 3
13262 | 0 | Short circuit: Conf. TMP 33 | - | 1 | - | - | Read
13262 | 1 | Short circuit: Conf. TMP 34 | - | 1 | - | - | Read
13262 | 2 | Short circuit: Conf. TMP 35 | - | 1 | - | - | Read
13262 | 3 | Short circuit: Conf. TMP 36 | - | 1 | - | - | Read
13262 | 4 | Short circuit: Conf. TMP 37 | - | 1 | - | - | Read
13262 | 5 | Short circuit: Conf. TMP 38 | - | 1 | - | - | Read
13262 | 6 | Short circuit: Conf. TMP 39 | - | 1 | - | - | Read
13262 | 7 | Short circuit: Conf. TMP 40 | - | 1 | - | - | Read
13262 | 8 | Short circuit: Conf. TMP 41 | - | 1 | - | - | Read
13262 | 9 | Short circuit: Conf. TMP 42 | - | 1 | - | - | Read
13262 | 10 | Short circuit: Conf. TMP 43 | - | 1 | - | - | Read
13262 | 11 | Short circuit: Conf. TMP 44 | - | 1 | - | - | Read
13262 | 12 | Short circuit: Conf. TMP 45 | - | 1 | - | - | Read
13262 | 13 | Short circuit: Conf. TMP 46 | - | 1 | - | - | Read
13262 | 14 | Short circuit: Conf. TMP 47 | - | 1 | - | - | Read
13262 | 15 | Short circuit: Conf. TMP 48 | - | 1 | - | - | Read
13263 |  | Conf. TMP short circuit register 4
13263 | 0 | Short circuit: Conf. TMP 49 | - | 1 | - | - | Read
13263 | 1 | Short circuit: Conf. TMP 50 | - | 1 | - | - | Read
13263 | 2 | Short circuit: Conf. TMP 51 | - | 1 | - | - | Read
13263 | 3 | Short circuit: Conf. TMP 52 | - | 1 | - | - | Read
13263 | 4 | Short circuit: Conf. TMP 53 | - | 1 | - | - | Read
13263 | 5 | Short circuit: Conf. TMP 54 | - | 1 | - | - | Read
13263 | 6 | Short circuit: Conf. TMP 55 | - | 1 | - | - | Read
13263 | 7 | Short circuit: Conf. TMP 56 | - | 1 | - | - | Read
13263 | 8 | Short circuit: Conf. TMP 57 | - | 1 | - | - | Read
13263 | 9 | Short circuit: Conf. TMP 58 | - | 1 | - | - | Read
13263 | 10 | Short circuit: Conf. TMP 59 | - | 1 | - | - | Read
13263 | 11 | Short circuit: Conf. TMP 60 | - | 1 | - | - | Read
13263 | 12 | Short circuit: Conf. TMP 61 | - | 1 | - | - | Read
13263 | 13 | Short circuit: Conf. TMP 62 | - | 1 | - | - | Read
13263 | 14 | Short circuit: Conf. TMP 63 | - | 1 | - | - | Read
13263 | 15 | Short circuit: Conf. TMP 64 | - | 1 | - | - | Read
13264 |  | Conf. TMP short circuit register 5
13264 | 0 | Short circuit: Conf. TMP 65 | - | 1 | - | - | Read
13264 | 1 | Short circuit: Conf. TMP 66 | - | 1 | - | - | Read
13264 | 2 | Short circuit: Conf. TMP 67 | - | 1 | - | - | Read
13264 | 3 | Short circuit: Conf. TMP 68 | - | 1 | - | - | Read
13264 | 4 | Short circuit: Conf. TMP 69 | - | 1 | - | - | Read
13264 | 5 | Short circuit: Conf. TMP 70 | - | 1 | - | - | Read
13264 | 6 | Short circuit: Conf. TMP 71 | - | 1 | - | - | Read
13264 | 7 |  | - | 1 | - | - | Read

## 02_Versions
#VALUE! | 14000-14507 ¦ Versions
Register | Bit | Text | Configuration | Resolution | Factor | Unit | Access
14000 |  | Module 1: Product code [Highbyte] | - | 32 | - | - | Read
14001 |  | Module 1: Product code [Lowbyte] | - | 32 | - | - | Read
14002 |  | Module 1: Revision [Highbyte] | - | 32 | - | - | Read
14003 |  | Module 1: Revision [Lowbyte] | - | 32 | - | - | Read
14004 |  | Module 1: Serial number [Highbyte] | - | 32 | - | - | Read
14005 |  | Module 1: Serial number [Lowbyte] | - | 32 | - | - | Read
14006 |  | Module 2: Product code [Highbyte] | - | 32 | - | - | Read
14007 |  | Module 2: Product code [Lowbyte] | - | 32 | - | - | Read
14008 |  | Module 2: Revision [Highbyte] | - | 32 | - | - | Read
14009 |  | Module 2: Revision [Lowbyte] | - | 32 | - | - | Read
14010 |  | Module 2: Serial number [Highbyte] | - | 32 | - | - | Read
14011 |  | Module 2: Serial number [Lowbyte] | - | 32 | - | - | Read
14012 |  | Module 3: Product code [Highbyte] | - | 32 | - | - | Read
14013 |  | Module 3: Product code [Lowbyte] | - | 32 | - | - | Read
14014 |  | Module 3: Revision [Highbyte] | - | 32 | - | - | Read
14015 |  | Module 3: Revision [Lowbyte] | - | 32 | - | - | Read
14016 |  | Module 3: Serial number [Highbyte] | - | 32 | - | - | Read
14017 |  | Module 3: Serial number [Lowbyte] | - | 32 | - | - | Read
14018 |  | Module 4: Product code [Highbyte] | - | 32 | - | - | Read
14019 |  | Module 4: Product code [Lowbyte] | - | 32 | - | - | Read
14020 |  | Module 4: Revision [Highbyte] | - | 32 | - | - | Read
14021 |  | Module 4: Revision [Lowbyte] | - | 32 | - | - | Read
14022 |  | Module 4: Serial number [Highbyte] | - | 32 | - | - | Read
14023 |  | Module 4: Serial number [Lowbyte] | - | 32 | - | - | Read
14024 |  | Module 5: Product code [Highbyte] | - | 32 | - | - | Read
14025 |  | Module 5: Product code [Lowbyte] | - | 32 | - | - | Read
14026 |  | Module 5: Revision [Highbyte] | - | 32 | - | - | Read
14027 |  | Module 5: Revision [Lowbyte] | - | 32 | - | - | Read
14028 |  | Module 5: Serial number [Highbyte] | - | 32 | - | - | Read
14029 |  | Module 5: Serial number [Lowbyte] | - | 32 | - | - | Read
14030 |  | Module 6: Product code [Highbyte] | - | 32 | - | - | Read
14031 |  | Module 6: Product code [Lowbyte] | - | 32 | - | - | Read
14032 |  | Module 6: Revision [Highbyte] | - | 32 | - | - | Read
14033 |  | Module 6: Revision [Lowbyte] | - | 32 | - | - | Read
14034 |  | Module 6: Serial number [Highbyte] | - | 32 | - | - | Read
14035 |  | Module 6: Serial number [Lowbyte] | - | 32 | - | - | Read
14036 |  | Module 7: Product code [Highbyte] | - | 32 | - | - | Read
14037 |  | Module 7: Product code [Lowbyte] | - | 32 | - | - | Read
14038 |  | Module 7: Revision [Highbyte] | - | 32 | - | - | Read
14039 |  | Module 7: Revision [Lowbyte] | - | 32 | - | - | Read
14040 |  | Module 7: Serial number [Highbyte] | - | 32 | - | - | Read
14041 |  | Module 7: Serial number [Lowbyte] | - | 32 | - | - | Read
14042 |  | Module 8: Product code [Highbyte] | - | 32 | - | - | Read
14043 |  | Module 8: Product code [Lowbyte] | - | 32 | - | - | Read
14044 |  | Module 8: Revision [Highbyte] | - | 32 | - | - | Read
14045 |  | Module 8: Revision [Lowbyte] | - | 32 | - | - | Read
14046 |  | Module 8: Serial number [Highbyte] | - | 32 | - | - | Read
14047 |  | Module 8: Serial number [Lowbyte] | - | 32 | - | - | Read
14048 |  | Module 9: Product code [Highbyte] | - | 32 | - | - | Read
14049 |  | Module 9: Product code [Lowbyte] | - | 32 | - | - | Read
14050 |  | Module 9: Revision [Highbyte] | - | 32 | - | - | Read
14051 |  | Module 9: Revision [Lowbyte] | - | 32 | - | - | Read
14052 |  | Module 9: Serial number [Highbyte] | - | 32 | - | - | Read
14053 |  | Module 9: Serial number [Lowbyte] | - | 32 | - | - | Read
14054 |  | Module 10: Product code [Highbyte] | - | 32 | - | - | Read
14055 |  | Module 10: Product code [Lowbyte] | - | 32 | - | - | Read
14056 |  | Module 10: Revision [Highbyte] | - | 32 | - | - | Read
14057 |  | Module 10: Revision [Lowbyte] | - | 32 | - | - | Read
14058 |  | Module 10: Serial number [Highbyte] | - | 32 | - | - | Read
14059 |  | Module 10: Serial number [Lowbyte] | - | 32 | - | - | Read
14060 |  | Module 11: Product code [Highbyte] | - | 32 | - | - | Read
14061 |  | Module 11: Product code [Lowbyte] | - | 32 | - | - | Read
14062 |  | Module 11: Revision [Highbyte] | - | 32 | - | - | Read
14063 |  | Module 11: Revision [Lowbyte] | - | 32 | - | - | Read
14064 |  | Module 11: Serial number [Highbyte] | - | 32 | - | - | Read
14065 |  | Module 11: Serial number [Lowbyte] | - | 32 | - | - | Read
14066 |  | Module 12: Product code [Highbyte] | - | 32 | - | - | Read
14067 |  | Module 12: Product code [Lowbyte] | - | 32 | - | - | Read
14068 |  | Module 12: Revision [Highbyte] | - | 32 | - | - | Read
14069 |  | Module 12: Revision [Lowbyte] | - | 32 | - | - | Read
14070 |  | Module 12: Serial number [Highbyte] | - | 32 | - | - | Read
14071 |  | Module 12: Serial number [Lowbyte] | - | 32 | - | - | Read
14072 |  | Module 13: Product code [Highbyte] | - | 32 | - | - | Read
14073 |  | Module 13: Product code [Lowbyte] | - | 32 | - | - | Read
14074 |  | Module 13: Revision [Highbyte] | - | 32 | - | - | Read
14075 |  | Module 13: Revision [Lowbyte] | - | 32 | - | - | Read
14076 |  | Module 13: Serial number [Highbyte] | - | 32 | - | - | Read
14077 |  | Module 13: Serial number [Lowbyte] | - | 32 | - | - | Read
14078 |  | Module 14: Product code [Highbyte] | - | 32 | - | - | Read
14079 |  | Module 14: Product code [Lowbyte] | - | 32 | - | - | Read
14080 |  | Module 14: Revision [Highbyte] | - | 32 | - | - | Read
14081 |  | Module 14: Revision [Lowbyte] | - | 32 | - | - | Read
14082 |  | Module 14: Serial number [Highbyte] | - | 32 | - | - | Read
14083 |  | Module 14: Serial number [Lowbyte] | - | 32 | - | - | Read
14084 |  | Module 15: Product code [Highbyte] | - | 32 | - | - | Read
14085 |  | Module 15: Product code [Lowbyte] | - | 32 | - | - | Read
14086 |  | Module 15: Revision [Highbyte] | - | 32 | - | - | Read
14087 |  | Module 15: Revision [Lowbyte] | - | 32 | - | - | Read
14088 |  | Module 15: Serial number [Highbyte] | - | 32 | - | - | Read
14089 |  | Module 15: Serial number [Lowbyte] | - | 32 | - | - | Read
14090 |  | Module 16: Product code [Highbyte] | - | 32 | - | - | Read
14091 |  | Module 16: Product code [Lowbyte] | - | 32 | - | - | Read
14092 |  | Module 16: Revision [Highbyte] | - | 32 | - | - | Read
14093 |  | Module 16: Revision [Lowbyte] | - | 32 | - | - | Read
14094 |  | Module 16: Serial number [Highbyte] | - | 32 | - | - | Read
14095 |  | Module 16: Serial number [Lowbyte] | - | 32 | - | - | Read
14096 |  | Module 17: Product code [Highbyte] | - | 32 | - | - | Read
14097 |  | Module 17: Product code [Lowbyte] | - | 32 | - | - | Read
14098 |  | Module 17: Revision [Highbyte] | - | 32 | - | - | Read
14099 |  | Module 17: Revision [Lowbyte] | - | 32 | - | - | Read
14100 |  | Module 17: Serial number [Highbyte] | - | 32 | - | - | Read
14101 |  | Module 17: Serial number [Lowbyte] | - | 32 | - | - | Read
14102 |  | Module 18: Product code [Highbyte] | - | 32 | - | - | Read
14103 |  | Module 18: Product code [Lowbyte] | - | 32 | - | - | Read
14104 |  | Module 18: Revision [Highbyte] | - | 32 | - | - | Read
14105 |  | Module 18: Revision [Lowbyte] | - | 32 | - | - | Read
14106 |  | Module 18: Serial number [Highbyte] | - | 32 | - | - | Read
14107 |  | Module 18: Serial number [Lowbyte] | - | 32 | - | - | Read
14500 |  | Project version [Highbyte] | - | 32 | - | - | Read
14501 |  | Project version [Lowbyte] | - | 32 | - | - | Read
14502 |  | Software revision [Highbyte] | - | 32 | - | - | Read
14503 |  | Software revision [Lowbyte] | - | 32 | - | - | Read
14504 |  | Software version xxx (xxx.yyy.zzz.vvv) | - | 16 | - | - | Read
14505 |  | Software version yyy (xxx.yyy.zzz.vvv) | - | 16 | - | - | Read
14506 |  | Software version zzz (xxx.yyy.zzz.vvv) | - | 16 | - | - | Read
14507 |  | Software version vvv (xxx.yyy.zzz.vvv) | - | 16 | - | - | Read

## 03_Electrical Data
#VALUE! | 15000-15036 ¦ Electrical Data
Register | Bit | Text | Configuration | Resolution | Factor | Unit | Access
15000 |  | Circuit breaker positions
15000 | 0 |  | - | 1 | - | - | Read
15000 | 1 |  | - | 1 | - | - | Read
15000 | 2 |  | - | 1 | - | - | Read
15000 | 3 |  | - | 1 | - | - | Read
15001 |  | Generator voltage L1-L2 | - | 16 | 1 | V | Read
15002 |  | Generator voltage L2-L3 | - | 16 | 1 | V | Read
15003 |  | Generator voltage L3-L1 | - | 16 | 1 | V | Read
15004 |  | Generator voltage L1-N | - | 16 | 1 | V | Read
15005 |  | Generator voltage L2-N | - | 16 | 1 | V | Read
15006 |  | Generator voltage L3-N | - | 16 | 1 | V | Read
15007 |  | Generator frequency | - | 16 | 2025-10-01 | Hz | Read
15008 |  | Generator current L1 | - | 16 | 1 | A | Read
15009 |  | Generator current L2 | - | 16 | 1 | A | Read
15010 |  | Generator current L3 | - | 16 | 1 | A | Read
15011 |  | Generator power | - | 16 | 1 | kW | Read
15012 |  | Generator reactive power | - | 16 | 1 | kvar | Read
15013 |  | Generator cosphi | - | 16 | 1/100 | - | Read
15014 |  | Mains voltage L1-L2 | - | 16 | 1 | V | Read
15015 |  | Mains voltage L2-L3 | - | 16 | 1 | V | Read
15016 |  | Mains voltage L3-L1 | - | 16 | 1 | V | Read
15017 |  | Mains voltage L1-N | - | 16 | 1 | V | Read
15018 |  | Mains voltage L2-N | - | 16 | 1 | V | Read
15019 |  | Mains voltage L3-N | - | 16 | 1 | V | Read
15020 |  | Mains frequency | - | 16 | 2025-10-01 | Hz | Read
15021 |  | Mains current L1 | - | 16 | 1 | A | Read
15022 |  | Mains current L2 | - | 16 | 1 | A | Read
15023 |  | Mains current L3 | - | 16 | 1 | A | Read
15024 |  | Mains cosphi | - | 16 | 1/100 | - | Read
15025 |  | Busbar voltage L1-L2 | - | 16 | 1 | V | Read
15026 |  | Busbar voltage L2-L3 | - | 16 | 1 | V | Read
15027 |  | Busbar voltage L3-L1 | - | 16 | 1 | V | Read
15028 |  | Busbar voltage L1-N | - | 16 | 1 | V | Read
15029 |  | Busbar voltage L2-N | - | 16 | 1 | V | Read
15030 |  | Busbar voltage L3-N | - | 16 | 1 | V | Read
15031 |  | Nominal frequency | - | 16 | 2025-10-01 | Hz | Read
15032 |  | Nominal voltage | - | 16 | 1 | V | Read
15033 |  | Frequency setpoint | - | 16 | 2025-10-01 | Hz | Read
15034 |  | Voltage setpoint | - | 16 | 1 | V | Read
15035 |  | Power setpoint | - | 16 | 1 | kW | Read
15036 |  | Reactive power setpoint | - | 16 | 1 | kvar | Read

## 04_Counter
#VALUE! | 16000-16035 ¦ Counters
Register | Bit | Text | Configuration | Resolution | Factor | Unit | Access
16000 |  | Conf. counter 1 value [Highbyte] | - | 32 | 1 | pulses | Read
16001 |  | Conf. counter 1 value [Lowbyte] | - | 32 | 1 | pulses | Read
16002 |  | Conf. counter 2 value [Highbyte] | - | 32 | 1 | pulses | Read
16003 |  | Conf. counter 2 value [Lowbyte] | - | 32 | 1 | pulses | Read
16004 |  | Conf. counter 3 value [Highbyte] | - | 32 | 1 | pulses | Read
16005 |  | Conf. counter 3 value [Lowbyte] | - | 32 | 1 | pulses | Read
16006 |  | Conf. counter 4 value [Highbyte] | - | 32 | 1 | pulses | Read
16007 |  | Conf. counter 4 value [Lowbyte] | - | 32 | 1 | pulses | Read
16008 |  | Day | - | 16 | 1 | d | Read
16009 |  | Month | - | 16 | 1 | m | Read
16010 |  | Year | - | 16 | 1 | a | Read
16011 |  | Hour | - | 16 | 1 | h | Read
16012 |  | Minute | - | 16 | 1 | min | Read
16013 |  | Second | - | 16 | 1 | s | Read
16014 |  | Running hours [Highbyte] | - | 32 | 1 | h | Read
16015 |  | Running hours [Lowbyte] | - | 32 | 1 | h | Read
16016 |  | Produced power [Highbyte] | - | 32 | 1 | kWh | Read
16017 |  | Produced power [Lowbyte] | - | 32 | 1 | kWh | Read
16018 |  | Consumed power [Highbyte] | - | 32 | 1 | kWh | Read
16019 |  | Consumed power [Lowbyte] | - | 32 | 1 | kWh | Read
16020 |  | Produced reactive power [Highbyte] | - | 32 | 1 | kvarh | Read
16021 |  | Produced reactive power [Lowbyte] | - | 32 | 1 | kvarh | Read
16022 |  | Consumed reactive power [Highbyte] | - | 32 | 1 | kvarh | Read
16023 |  | Consumed reactive power [Lowbyte] | - | 32 | 1 | kvarh | Read
16024 |  | Generator breaker operations [Highbyte] | - | 32 | 1 | - | Read
16025 |  | Generator breaker operations [Lowbyte] | - | 32 | 1 | - | Read
16026 |  | Mains breaker operations [Highbyte] | - | 32 | 1 | - | Read
16027 |  | Mains breaker operations [Lowbyte] | - | 32 | 1 | - | Read
16028 |  | Start attempt counter [Highbyte] | - | 32 | 1 | - | Read
16029 |  | Start attempt counter [Lowbyte] | - | 32 | 1 | - | Read
16030 |  | Service timer 1 [Highbyte] | - | 32 | 1 | h | Read
16031 |  | Service timer 1 [Lowbyte] | - | 32 | 1 | h | Read
16032 |  | Service timer 2 [Highbyte] | - | 32 | 1 | h | Read
16033 |  | Service timer 2 [Lowbyte] | - | 32 | 1 | h | Read
16034 |  | Service timer 3 [Highbyte] | - | 32 | 1 | h | Read
16035 |  | Service timer 3 [Lowbyte] | - | 32 | 1 | h | Read

## 05_Digital Input
#VALUE! | 17000-17211
Register | Bit | Text | Configuration | Resolution | Factor | Unit | Access
17000 |  | Digital input terminals IOM5.1 1
17000 | 0 | Terminal 23 | Not inverted | 1 | - | - | Read
17000 | 1 | Terminal 24 | Not inverted | 1 | - | - | Read
17000 | 2 | Terminal 25 | Not inverted | 1 | - | - | Read
17000 | 3 | Terminal 26 | Not inverted | 1 | - | - | Read
17000 | 4 | Terminal 27 | Not inverted | 1 | - | - | Read
17000 | 5 | Terminal 28 | Not inverted | 1 | - | - | Read
17000 | 6 | Terminal 30/31 | Not inverted | 1 | - | - | Read
17000 | 7 | Terminal 32/33 | Not inverted | 1 | - | - | Read
17000 | 8 | Terminal 63 | Not inverted | 1 | - | - | Read
17000 | 9 | Terminal 64 | Not inverted | 1 | - | - | Read
17000 | 10 | Terminal 65 | Not inverted | 1 | - | - | Read
17000 | 11 | Terminal 66 | Not inverted | 1 | - | - | Read
17000 | 12 | Terminal 67 | Not inverted | 1 | - | - | Read
17000 | 13 | Terminal 68 | Not inverted | 1 | - | - | Read
17000 | 14 | Terminal 70/71 | Not inverted | 1 | - | - | Read
17000 | 15 | Terminal 72/73 | Not inverted | 1 | - | - | Read
17001 |  | Digital input terminals IOM5.1 2
17001 | 0 | Terminal 23 | Not inverted | 1 | - | - | Read
17001 | 1 | Terminal 24 | Not inverted | 1 | - | - | Read
17001 | 2 | Terminal 25 | Not inverted | 1 | - | - | Read
17001 | 3 | Terminal 26 | Not inverted | 1 | - | - | Read
17001 | 4 | Terminal 27 | Not inverted | 1 | - | - | Read
17001 | 5 | Terminal 28 | Not inverted | 1 | - | - | Read
17001 | 6 | Terminal 30/31 | Not inverted | 1 | - | - | Read
17001 | 7 | Terminal 32/33 | Not inverted | 1 | - | - | Read
17001 | 8 | Terminal 63 | Not inverted | 1 | - | - | Read
17001 | 9 | Terminal 64 | Not inverted | 1 | - | - | Read
17001 | 10 | Terminal 65 | Not inverted | 1 | - | - | Read
17001 | 11 | Terminal 66 | Not inverted | 1 | - | - | Read
17001 | 12 | Terminal 67 | Not inverted | 1 | - | - | Read
17001 | 13 | Terminal 68 | Not inverted | 1 | - | - | Read
17001 | 14 | Terminal 70/71 | Not inverted | 1 | - | - | Read
17001 | 15 | Terminal 72/73 | Not inverted | 1 | - | - | Read
17002 |  | Digital input terminals IOM5.1 3
17002 | 0 | Terminal 23 | Not inverted | 1 | - | - | Read
17002 | 1 | Terminal 24 | Not inverted | 1 | - | - | Read
17002 | 2 | Terminal 25 | Not inverted | 1 | - | - | Read
17002 | 3 | Terminal 26 | Not inverted | 1 | - | - | Read
17002 | 4 | Terminal 27 | Not inverted | 1 | - | - | Read
17002 | 5 | Terminal 28 | Not inverted | 1 | - | - | Read
17002 | 6 | Terminal 30/31 | Not inverted | 1 | - | - | Read
17002 | 7 | Terminal 32/33 | Not inverted | 1 | - | - | Read
17002 | 8 | Terminal 63 | Not inverted | 1 | - | - | Read
17002 | 9 | Terminal 64 | Not inverted | 1 | - | - | Read
17002 | 10 | Terminal 65 | Not inverted | 1 | - | - | Read
17002 | 11 | Terminal 66 | Not inverted | 1 | - | - | Read
17002 | 12 | Terminal 67 | Not inverted | 1 | - | - | Read
17002 | 13 | Terminal 68 | Not inverted | 1 | - | - | Read
17002 | 14 | Terminal 70/71 | Not inverted | 1 | - | - | Read
17002 | 15 | Terminal 72/73 | Not inverted | 1 | - | - | Read
17003 |  | Digital input terminals IOM5.1 4
17003 | 0 | Terminal 23 | Not inverted | 1 | - | - | Read
17003 | 1 | Terminal 24 | Not inverted | 1 | - | - | Read
17003 | 2 | Terminal 25 | Not inverted | 1 | - | - | Read
17003 | 3 | Terminal 26 | Not inverted | 1 | - | - | Read
17003 | 4 | Terminal 27 | Not inverted | 1 | - | - | Read
17003 | 5 | Terminal 28 | Not inverted | 1 | - | - | Read
17003 | 6 | Terminal 30/31 | Not inverted | 1 | - | - | Read
17003 | 7 | Terminal 32/33 | Not inverted | 1 | - | - | Read
17003 | 8 | Terminal 63 | Not inverted | 1 | - | - | Read
17003 | 9 | Terminal 64 | Not inverted | 1 | - | - | Read
17003 | 10 | Terminal 65 | Not inverted | 1 | - | - | Read
17003 | 11 | Terminal 66 | Not inverted | 1 | - | - | Read
17003 | 12 | Terminal 67 | Not inverted | 1 | - | - | Read
17003 | 13 | Terminal 68 | Not inverted | 1 | - | - | Read
17003 | 14 | Terminal 70/71 | Not inverted | 1 | - | - | Read
17003 | 15 | Terminal 72/73 | Not inverted | 1 | - | - | Read
17004 |  | Digital input terminals IOM5.1 5
17004 | 0 | Terminal 23 | Not inverted | 1 | - | - | Read
17004 | 1 | Terminal 24 | Not inverted | 1 | - | - | Read
17004 | 2 | Terminal 25 | Not inverted | 1 | - | - | Read
17004 | 3 | Terminal 26 | Not inverted | 1 | - | - | Read
17004 | 4 | Terminal 27 | Not inverted | 1 | - | - | Read
17004 | 5 | Terminal 28 | Not inverted | 1 | - | - | Read
17004 | 6 | Terminal 30/31 | Not inverted | 1 | - | - | Read
17004 | 7 | Terminal 32/33 | Not inverted | 1 | - | - | Read
17004 | 8 | Terminal 63 | Not inverted | 1 | - | - | Read
17004 | 9 | Terminal 64 | Not inverted | 1 | - | - | Read
17004 | 10 | Terminal 65 | Not inverted | 1 | - | - | Read
17004 | 11 | Terminal 66 | Not inverted | 1 | - | - | Read
17004 | 12 | Terminal 67 | Not inverted | 1 | - | - | Read
17004 | 13 | Terminal 68 | Not inverted | 1 | - | - | Read
17004 | 14 | Terminal 70/71 | Not inverted | 1 | - | - | Read
17004 | 15 | Terminal 72/73 | Not inverted | 1 | - | - | Read
17005 |  | Digital input terminals IOM5.1 6
17005 | 0 | Terminal 23 | Not inverted | 1 | - | - | Read
17005 | 1 | Terminal 24 | Not inverted | 1 | - | - | Read
17005 | 2 | Terminal 25 | Not inverted | 1 | - | - | Read
17005 | 3 | Terminal 26 | Not inverted | 1 | - | - | Read
17005 | 4 | Terminal 27 | Not inverted | 1 | - | - | Read
17005 | 5 | Terminal 28 | Not inverted | 1 | - | - | Read
17005 | 6 | Terminal 30/31 | Not inverted | 1 | - | - | Read
17005 | 7 | Terminal 32/33 | Not inverted | 1 | - | - | Read
17005 | 8 | Terminal 63 | Not inverted | 1 | - | - | Read
17005 | 9 | Terminal 64 | Not inverted | 1 | - | - | Read
17005 | 10 | Terminal 65 | Not inverted | 1 | - | - | Read
17005 | 11 | Terminal 66 | Not inverted | 1 | - | - | Read
17005 | 12 | Terminal 67 | Not inverted | 1 | - | - | Read
17005 | 13 | Terminal 68 | Not inverted | 1 | - | - | Read
17005 | 14 | Terminal 70/71 | Not inverted | 1 | - | - | Read
17005 | 15 | Terminal 72/73 | Not inverted | 1 | - | - | Read
17006 |  | Digital input terminals IOM5.1 7
17006 | 0 | Terminal 23 | Not inverted | 1 | - | - | Read
17006 | 1 | Terminal 24 | Not inverted | 1 | - | - | Read
17006 | 2 | Terminal 25 | Not inverted | 1 | - | - | Read
17006 | 3 | Terminal 26 | Not inverted | 1 | - | - | Read
17006 | 4 | Terminal 27 | Not inverted | 1 | - | - | Read
17006 | 5 | Terminal 28 | Not inverted | 1 | - | - | Read
17006 | 6 | Terminal 30/31 | Not inverted | 1 | - | - | Read
17006 | 7 | Terminal 32/33 | Not inverted | 1 | - | - | Read
17006 | 8 | Terminal 63 | Not inverted | 1 | - | - | Read
17006 | 9 | Terminal 64 | Not inverted | 1 | - | - | Read
17006 | 10 | Terminal 65 | Not inverted | 1 | - | - | Read
17006 | 11 | Terminal 66 | Not inverted | 1 | - | - | Read
17006 | 12 | Terminal 67 | Not inverted | 1 | - | - | Read
17006 | 13 | Terminal 68 | Not inverted | 1 | - | - | Read
17006 | 14 | Terminal 70/71 | Not inverted | 1 | - | - | Read
17006 | 15 | Terminal 72/73 | Not inverted | 1 | - | - | Read
17007 |  | Digital input terminals IOM5.1 8
17007 | 0 | Terminal 23 | Not inverted | 1 | - | - | Read
17007 | 1 | Terminal 24 | Not inverted | 1 | - | - | Read
17007 | 2 | Terminal 25 | Not inverted | 1 | - | - | Read
17007 | 3 | Terminal 26 | Not inverted | 1 | - | - | Read
17007 | 4 | Terminal 27 | Not inverted | 1 | - | - | Read
17007 | 5 | Terminal 28 | Not inverted | 1 | - | - | Read
17007 | 6 | Terminal 30/31 | Not inverted | 1 | - | - | Read
17007 | 7 | Terminal 32/33 | Not inverted | 1 | - | - | Read
17007 | 8 | Terminal 63 | Not inverted | 1 | - | - | Read
17007 | 9 | Terminal 64 | Not inverted | 1 | - | - | Read
17007 | 10 | Terminal 65 | Not inverted | 1 | - | - | Read
17007 | 11 | Terminal 66 | Not inverted | 1 | - | - | Read
17007 | 12 | Terminal 67 | Not inverted | 1 | - | - | Read
17007 | 13 | Terminal 68 | Not inverted | 1 | - | - | Read
17007 | 14 | Terminal 70/71 | Not inverted | 1 | - | - | Read
17007 | 15 | Terminal 72/73 | Not inverted | 1 | - | - | Read
17008 |  | Digital input terminals IOM5.1 9
17008 | 0 | Terminal 23 | Not inverted | 1 | - | - | Read
17008 | 1 | Terminal 24 | Not inverted | 1 | - | - | Read
17008 | 2 | Terminal 25 | Not inverted | 1 | - | - | Read
17008 | 3 | Terminal 26 | Not inverted | 1 | - | - | Read
17008 | 4 | Terminal 27 | Not inverted | 1 | - | - | Read
17008 | 5 | Terminal 28 | Not inverted | 1 | - | - | Read
17008 | 6 | Terminal 30/31 | Not inverted | 1 | - | - | Read
17008 | 7 | Terminal 32/33 | Not inverted | 1 | - | - | Read
17008 | 8 | Terminal 63 | Not inverted | 1 | - | - | Read
17008 | 9 | Terminal 64 | Not inverted | 1 | - | - | Read
17008 | 10 | Terminal 65 | Not inverted | 1 | - | - | Read
17008 | 11 | Terminal 66 | Not inverted | 1 | - | - | Read
17008 | 12 | Terminal 67 | Not inverted | 1 | - | - | Read
17008 | 13 | Terminal 68 | Not inverted | 1 | - | - | Read
17008 | 14 | Terminal 70/71 | Not inverted | 1 | - | - | Read
17008 | 15 | Terminal 72/73 | Not inverted | 1 | - | - | Read
17009 |  | Digital input terminals IOM5.1 10
17009 | 0 | Terminal 23 | Not inverted | 1 | - | - | Read
17009 | 1 | Terminal 24 | Not inverted | 1 | - | - | Read
17009 | 2 | Terminal 25 | Not inverted | 1 | - | - | Read
17009 | 3 | Terminal 26 | Not inverted | 1 | - | - | Read
17009 | 4 | Terminal 27 | Not inverted | 1 | - | - | Read
17009 | 5 | Terminal 28 | Not inverted | 1 | - | - | Read
17009 | 6 | Terminal 30/31 | Not inverted | 1 | - | - | Read
17009 | 7 | Terminal 32/33 | Not inverted | 1 | - | - | Read
17009 | 8 | Terminal 63 | Not inverted | 1 | - | - | Read
17009 | 9 | Terminal 64 | Not inverted | 1 | - | - | Read
17009 | 10 | Terminal 65 | Not inverted | 1 | - | - | Read
17009 | 11 | Terminal 66 | Not inverted | 1 | - | - | Read
17009 | 12 | Terminal 67 | Not inverted | 1 | - | - | Read
17009 | 13 | Terminal 68 | Not inverted | 1 | - | - | Read
17009 | 14 | Terminal 70/71 | Not inverted | 1 | - | - | Read
17009 | 15 | Terminal 72/73 | Not inverted | 1 | - | - | Read
17010 |  | Digital input terminals IOM5.1 11
17010 | 0 | Terminal 23 | Not inverted | 1 | - | - | Read
17010 | 1 | Terminal 24 | Not inverted | 1 | - | - | Read
17010 | 2 | Terminal 25 | Not inverted | 1 | - | - | Read
17010 | 3 | Terminal 26 | Not inverted | 1 | - | - | Read
17010 | 4 | Terminal 27 | Not inverted | 1 | - | - | Read
17010 | 5 | Terminal 28 | Not inverted | 1 | - | - | Read
17010 | 6 | Terminal 30/31 | Not inverted | 1 | - | - | Read
17010 | 7 | Terminal 32/33 | Not inverted | 1 | - | - | Read
17010 | 8 | Terminal 63 | Not inverted | 1 | - | - | Read
17010 | 9 | Terminal 64 | Not inverted | 1 | - | - | Read
17010 | 10 | Terminal 65 | Not inverted | 1 | - | - | Read
17010 | 11 | Terminal 66 | Not inverted | 1 | - | - | Read
17010 | 12 | Terminal 67 | Not inverted | 1 | - | - | Read
17010 | 13 | Terminal 68 | Not inverted | 1 | - | - | Read
17010 | 14 | Terminal 70/71 | Not inverted | 1 | - | - | Read
17010 | 15 | Terminal 72/73 | Not inverted | 1 | - | - | Read
17011 |  | Digital input terminals IOM5.1 12
17011 | 0 | Terminal 23 | Not inverted | 1 | - | - | Read
17011 | 1 | Terminal 24 | Not inverted | 1 | - | - | Read
17011 | 2 | Terminal 25 | Not inverted | 1 | - | - | Read
17011 | 3 | Terminal 26 | Not inverted | 1 | - | - | Read
17011 | 4 | Terminal 27 | Not inverted | 1 | - | - | Read
17011 | 5 | Terminal 28 | Not inverted | 1 | - | - | Read
17011 | 6 | Terminal 30/31 | Not inverted | 1 | - | - | Read
17011 | 7 | Terminal 32/33 | Not inverted | 1 | - | - | Read
17011 | 8 | Terminal 63 | Not inverted | 1 | - | - | Read
17011 | 9 | Terminal 64 | Not inverted | 1 | - | - | Read
17011 | 10 | Terminal 65 | Not inverted | 1 | - | - | Read
17011 | 11 | Terminal 66 | Not inverted | 1 | - | - | Read
17011 | 12 | Terminal 67 | Not inverted | 1 | - | - | Read
17011 | 13 | Terminal 68 | Not inverted | 1 | - | - | Read
17011 | 14 | Terminal 70/71 | Not inverted | 1 | - | - | Read
17011 | 15 | Terminal 72/73 | Not inverted | 1 | - | - | Read
17200 |  | Digital output terminals IOM5.1 1
17200 | 0 | Terminal 35 | Not inverted | 1 | - | - | Read
17200 | 1 | Terminal 36 | Not inverted | 1 | - | - | Read
17200 | 2 | Terminal 37 | Not inverted | 1 | - | - | Read
17200 | 3 | Terminal 38 | Not inverted | 1 | - | - | Read
17200 | 4 | Terminal 39 | Not inverted | 1 | - | - | Read
17200 | 5 | Terminal 75 | Not inverted | 1 | - | - | Read
17200 | 6 | Terminal 76 | Not inverted | 1 | - | - | Read
17200 | 7 | Terminal 77 | Not inverted | 1 | - | - | Read
17200 | 8 | Terminal 78 | Not inverted | 1 | - | - | Read
17200 | 9 | Terminal 79 | Not inverted | 1 | - | - | Read
17201 |  | Digital output terminals IOM5.1 2
17201 | 0 | Terminal 35 | Not inverted | 1 | - | - | Read
17201 | 1 | Terminal 36 | Not inverted | 1 | - | - | Read
17201 | 2 | Terminal 37 | Not inverted | 1 | - | - | Read
17201 | 3 | Terminal 38 | Not inverted | 1 | - | - | Read
17201 | 4 | Terminal 39 | Not inverted | 1 | - | - | Read
17201 | 5 | Terminal 75 | Not inverted | 1 | - | - | Read
17201 | 6 | Terminal 76 | Not inverted | 1 | - | - | Read
17201 | 7 | Terminal 77 | Not inverted | 1 | - | - | Read
17201 | 8 | Terminal 78 | Not inverted | 1 | - | - | Read
17201 | 9 | Terminal 79 | Not inverted | 1 | - | - | Read
17202 |  | Digital output terminals IOM5.1 3
17202 | 0 | Terminal 35 | Not inverted | 1 | - | - | Read
17202 | 1 | Terminal 36 | Not inverted | 1 | - | - | Read
17202 | 2 | Terminal 37 | Not inverted | 1 | - | - | Read
17202 | 3 | Terminal 38 | Not inverted | 1 | - | - | Read
17202 | 4 | Terminal 39 | Not inverted | 1 | - | - | Read
17202 | 5 | Terminal 75 | Not inverted | 1 | - | - | Read
17202 | 6 | Terminal 76 | Not inverted | 1 | - | - | Read
17202 | 7 | Terminal 77 | Not inverted | 1 | - | - | Read
17202 | 8 | Terminal 78 | Not inverted | 1 | - | - | Read
17202 | 9 | Terminal 79 | Not inverted | 1 | - | - | Read
17203 |  | Digital output terminals IOM5.1 4
17203 | 0 | Terminal 35 | Not inverted | 1 | - | - | Read
17203 | 1 | Terminal 36 | Not inverted | 1 | - | - | Read
17203 | 2 | Terminal 37 | Not inverted | 1 | - | - | Read
17203 | 3 | Terminal 38 | Not inverted | 1 | - | - | Read
17203 | 4 | Terminal 39 | Not inverted | 1 | - | - | Read
17203 | 5 | Terminal 75 | Not inverted | 1 | - | - | Read
17203 | 6 | Terminal 76 | Not inverted | 1 | - | - | Read
17203 | 7 | Terminal 77 | Not inverted | 1 | - | - | Read
17203 | 8 | Terminal 78 | Not inverted | 1 | - | - | Read
17203 | 9 | Terminal 79 | Not inverted | 1 | - | - | Read
17204 |  | Digital output terminals IOM5.1 5
17204 | 0 | Terminal 35 | Not inverted | 1 | - | - | Read
17204 | 1 | Terminal 36 | Not inverted | 1 | - | - | Read
17204 | 2 | Terminal 37 | Not inverted | 1 | - | - | Read
17204 | 3 | Terminal 38 | Not inverted | 1 | - | - | Read
17204 | 4 | Terminal 39 | Not inverted | 1 | - | - | Read
17204 | 5 | Terminal 75 | Not inverted | 1 | - | - | Read
17204 | 6 | Terminal 76 | Not inverted | 1 | - | - | Read
17204 | 7 | Terminal 77 | Not inverted | 1 | - | - | Read
17204 | 8 | Terminal 78 | Not inverted | 1 | - | - | Read
17204 | 9 | Terminal 79 | Not inverted | 1 | - | - | Read
17205 |  | Digital output terminals IOM5.1 6
17205 | 0 | Terminal 35 | Not inverted | 1 | - | - | Read
17205 | 1 | Terminal 36 | Not inverted | 1 | - | - | Read
17205 | 2 | Terminal 37 | Not inverted | 1 | - | - | Read
17205 | 3 | Terminal 38 | Not inverted | 1 | - | - | Read
17205 | 4 | Terminal 39 | Not inverted | 1 | - | - | Read
17205 | 5 | Terminal 75 | Not inverted | 1 | - | - | Read
17205 | 6 | Terminal 76 | Not inverted | 1 | - | - | Read
17205 | 7 | Terminal 77 | Not inverted | 1 | - | - | Read
17205 | 8 | Terminal 78 | Not inverted | 1 | - | - | Read
17205 | 9 | Terminal 79 | Not inverted | 1 | - | - | Read
17206 |  | Digital output terminals IOM5.1 7
17206 | 0 | Terminal 35 | Not inverted | 1 | - | - | Read
17206 | 1 | Terminal 36 | Not inverted | 1 | - | - | Read
17206 | 2 | Terminal 37 | Not inverted | 1 | - | - | Read
17206 | 3 | Terminal 38 | Not inverted | 1 | - | - | Read
17206 | 4 | Terminal 39 | Not inverted | 1 | - | - | Read
17206 | 5 | Terminal 75 | Not inverted | 1 | - | - | Read
17206 | 6 | Terminal 76 | Not inverted | 1 | - | - | Read
17206 | 7 | Terminal 77 | Not inverted | 1 | - | - | Read
17206 | 8 | Terminal 78 | Not inverted | 1 | - | - | Read
17206 | 9 | Terminal 79 | Not inverted | 1 | - | - | Read
17207 |  | Digital output terminals IOM5.1 8
17207 | 0 | Terminal 35 | Not inverted | 1 | - | - | Read
17207 | 1 | Terminal 36 | Not inverted | 1 | - | - | Read
17207 | 2 | Terminal 37 | Not inverted | 1 | - | - | Read
17207 | 3 | Terminal 38 | Not inverted | 1 | - | - | Read
17207 | 4 | Terminal 39 | Not inverted | 1 | - | - | Read
17207 | 5 | Terminal 75 | Not inverted | 1 | - | - | Read
17207 | 6 | Terminal 76 | Not inverted | 1 | - | - | Read
17207 | 7 | Terminal 77 | Not inverted | 1 | - | - | Read
17207 | 8 | Terminal 78 | Not inverted | 1 | - | - | Read
17207 | 9 | Terminal 79 | Not inverted | 1 | - | - | Read
17208 |  | Digital output terminals IOM5.1 9
17208 | 0 | Terminal 35 | Not inverted | 1 | - | - | Read
17208 | 1 | Terminal 36 | Not inverted | 1 | - | - | Read
17208 | 2 | Terminal 37 | Not inverted | 1 | - | - | Read
17208 | 3 | Terminal 38 | Not inverted | 1 | - | - | Read
17208 | 4 | Terminal 39 | Not inverted | 1 | - | - | Read
17208 | 5 | Terminal 75 | Not inverted | 1 | - | - | Read
17208 | 6 | Terminal 76 | Not inverted | 1 | - | - | Read
17208 | 7 | Terminal 77 | Not inverted | 1 | - | - | Read
17208 | 8 | Terminal 78 | Not inverted | 1 | - | - | Read
17208 | 9 | Terminal 79 | Not inverted | 1 | - | - | Read
17209 |  | Digital output terminals IOM5.1 10
17209 | 0 | Terminal 35 | Not inverted | 1 | - | - | Read
17209 | 1 | Terminal 36 | Not inverted | 1 | - | - | Read
17209 | 2 | Terminal 37 | Not inverted | 1 | - | - | Read
17209 | 3 | Terminal 38 | Not inverted | 1 | - | - | Read
17209 | 4 | Terminal 39 | Not inverted | 1 | - | - | Read
17209 | 5 | Terminal 75 | Not inverted | 1 | - | - | Read
17209 | 6 | Terminal 76 | Not inverted | 1 | - | - | Read
17209 | 7 | Terminal 77 | Not inverted | 1 | - | - | Read
17209 | 8 | Terminal 78 | Not inverted | 1 | - | - | Read
17209 | 9 | Terminal 79 | Not inverted | 1 | - | - | Read
17210 |  | Digital output terminals IOM5.1 11
17210 | 0 | Terminal 35 | Not inverted | 1 | - | - | Read
17210 | 1 | Terminal 36 | Not inverted | 1 | - | - | Read
17210 | 2 | Terminal 37 | Not inverted | 1 | - | - | Read
17210 | 3 | Terminal 38 | Not inverted | 1 | - | - | Read
17210 | 4 | Terminal 39 | Not inverted | 1 | - | - | Read
17210 | 5 | Terminal 75 | Not inverted | 1 | - | - | Read
17210 | 6 | Terminal 76 | Not inverted | 1 | - | - | Read
17210 | 7 | Terminal 77 | Not inverted | 1 | - | - | Read
17210 | 8 | Terminal 78 | Not inverted | 1 | - | - | Read
17210 | 9 | Terminal 79 | Not inverted | 1 | - | - | Read
17211 |  | Digital output terminals IOM5.1 12
17211 | 0 | Terminal 35 | Not inverted | 1 | - | - | Read
17211 | 1 | Terminal 36 | Not inverted | 1 | - | - | Read
17211 | 2 | Terminal 37 | Not inverted | 1 | - | - | Read
17211 | 3 | Terminal 38 | Not inverted | 1 | - | - | Read
17211 | 4 | Terminal 39 | Not inverted | 1 | - | - | Read
17211 | 5 | Terminal 75 | Not inverted | 1 | - | - | Read
17211 | 6 | Terminal 76 | Not inverted | 1 | - | - | Read
17211 | 7 | Terminal 77 | Not inverted | 1 | - | - | Read
17211 | 8 | Terminal 78 | Not inverted | 1 | - | - | Read
17211 | 9 | Terminal 79 | Not inverted | 1 | - | - | Read

## 06_Temp. Input
#VALUE! | 17400-17847
Register | Bit | Text | Configuration | Resolution | Factor | Unit | Access
17400 |  | Temperature input terminal IOM5.1 301-304 | PT100 | 16 | 2025-10-01 | Â°C | Read
17401 |  | Temperature input terminal IOM5.1 305-308 | PT100 | 16 | 2025-10-01 | Â°C | Read
17402 |  | Temperature input terminal IOM5.1 309-312 | PT100 | 16 | 2025-10-01 | Â°C | Read
17403 |  | Temperature input terminal IOM5.1 341-344 | PT100 | 16 | 2025-10-01 | Â°C | Read
17404 |  | Temperature input terminal IOM5.1 345-348 | PT100 | 16 | 2025-10-01 | Â°C | Read
17405 |  | Temperature input terminal IOM5.1 349-352 | PT100 | 16 | 2025-10-01 | Â°C | Read
17406 |  | Temperature input terminal IOM5.1 401-404 | PT100 | 16 | 2025-10-01 | Â°C | Read
17407 |  | Temperature input terminal IOM5.1 405-408 | PT100 | 16 | 2025-10-01 | Â°C | Read
17408 |  | Temperature input terminal IOM5.1 409-412 | PT100 | 16 | 2025-10-01 | Â°C | Read
17409 |  | Temperature input terminal IOM5.1 441-444 | PT100 | 16 | 2025-10-01 | Â°C | Read
17410 |  | Temperature input terminal IOM5.1 445-448 | PT100 | 16 | 2025-10-01 | Â°C | Read
17411 |  | Temperature input terminal IOM5.1 449-452 | PT100 | 16 | 2025-10-01 | Â°C | Read
17412 |  | Temperature input terminal IOM5.1 501-504 | PT100 | 16 | 2025-10-01 | Â°C | Read
17413 |  | Temperature input terminal IOM5.1 505-508 | PT100 | 16 | 2025-10-01 | Â°C | Read
17414 |  | Temperature input terminal IOM5.1 509-512 | PT100 | 16 | 2025-10-01 | Â°C | Read
17415 |  | Temperature input terminal IOM5.1 541-544 | PT100 | 16 | 2025-10-01 | Â°C | Read
17416 |  | Temperature input terminal IOM5.1 545-548 | PT100 | 16 | 2025-10-01 | Â°C | Read
17417 |  | Temperature input terminal IOM5.1 549-552 | PT100 | 16 | 2025-10-01 | Â°C | Read
17418 |  | Temperature input terminal IOM5.1 601-604 | PT100 | 16 | 2025-10-01 | Â°C | Read
17419 |  | Temperature input terminal IOM5.1 605-608 | PT100 | 16 | 2025-10-01 | Â°C | Read
17420 |  | Temperature input terminal IOM5.1 609-612 | PT100 | 16 | 2025-10-01 | Â°C | Read
17421 |  | Temperature input terminal IOM5.1 641-644 | PT100 | 16 | 2025-10-01 | Â°C | Read
17422 |  | Temperature input terminal IOM5.1 645-648 | PT100 | 16 | 2025-10-01 | Â°C | Read
17423 |  | Temperature input terminal IOM5.1 649-652 | PT100 | 16 | 2025-10-01 | Â°C | Read
17424 |  | Temperature input terminal IOM5.1 701-704 | PT100 | 16 | 2025-10-01 | Â°C | Read
17425 |  | Temperature input terminal IOM5.1 705-708 | PT100 | 16 | 2025-10-01 | Â°C | Read
17426 |  | Temperature input terminal IOM5.1 709-712 | PT100 | 16 | 2025-10-01 | Â°C | Read
17427 |  | Temperature input terminal IOM5.1 741-744 | PT100 | 16 | 2025-10-01 | Â°C | Read
17428 |  | Temperature input terminal IOM5.1 745-748 | PT100 | 16 | 2025-10-01 | Â°C | Read
17429 |  | Temperature input terminal IOM5.1 749-752 | PT100 | 16 | 2025-10-01 | Â°C | Read
17430 |  | Temperature input terminal IOM5.1 801-804 | PT100 | 16 | 2025-10-01 | Â°C | Read
17431 |  | Temperature input terminal IOM5.1 805-808 | PT100 | 16 | 2025-10-01 | Â°C | Read
17432 |  | Temperature input terminal IOM5.1 809-812 | PT100 | 16 | 2025-10-01 | Â°C | Read
17433 |  | Temperature input terminal IOM5.1 841-844 | PT100 | 16 | 2025-10-01 | Â°C | Read
17434 |  | Temperature input terminal IOM5.1 845-848 | PT100 | 16 | 2025-10-01 | Â°C | Read
17435 |  | Temperature input terminal IOM5.1 849-852 | PT100 | 16 | 2025-10-01 | Â°C | Read
17436 |  | Temperature input terminal IOM5.1 901-904 | PT100 | 16 | 2025-10-01 | Â°C | Read
17437 |  | Temperature input terminal IOM5.1 905-908 | PT100 | 16 | 2025-10-01 | Â°C | Read
17438 |  | Temperature input terminal IOM5.1 909-912 | PT100 | 16 | 2025-10-01 | Â°C | Read
17439 |  | Temperature input terminal IOM5.1 941-944 | PT100 | 16 | 2025-10-01 | Â°C | Read
17440 |  | Temperature input terminal IOM5.1 945-948 | PT100 | 16 | 2025-10-01 | Â°C | Read
17441 |  | Temperature input terminal IOM5.1 949-952 | PT100 | 16 | 2025-10-01 | Â°C | Read
17442 |  | Temperature input terminal IOM5.1 1001-1004 | PT100 | 16 | 2025-10-01 | Â°C | Read
17443 |  | Temperature input terminal IOM5.1 1005-1008 | PT100 | 16 | 2025-10-01 | Â°C | Read
17444 |  | Temperature input terminal IOM5.1 1009-1012 | PT100 | 16 | 2025-10-01 | Â°C | Read
17445 |  | Temperature input terminal IOM5.1 1041-1044 | PT100 | 16 | 2025-10-01 | Â°C | Read
17446 |  | Temperature input terminal IOM5.1 1045-1048 | PT100 | 16 | 2025-10-01 | Â°C | Read
17447 |  | Temperature input terminal IOM5.1 1049-1052 | PT100 | 16 | 2025-10-01 | Â°C | Read
17448 |  | Temperature input terminal IOM5.1 1101-1104 | PT100 | 16 | 2025-10-01 | Â°C | Read
17449 |  | Temperature input terminal IOM5.1 1105-1108 | PT100 | 16 | 2025-10-01 | Â°C | Read
17450 |  | Temperature input terminal IOM5.1 1109-1112 | PT100 | 16 | 2025-10-01 | Â°C | Read
17451 |  | Temperature input terminal IOM5.1 1141-1144 | PT100 | 16 | 2025-10-01 | Â°C | Read
17452 |  | Temperature input terminal IOM5.1 1145-1148 | PT100 | 16 | 2025-10-01 | Â°C | Read
17453 |  | Temperature input terminal IOM5.1 1149-1152 | PT100 | 16 | 2025-10-01 | Â°C | Read
17454 |  | Temperature input terminal IOM5.1 1201-1204 | PT100 | 16 | 2025-10-01 | Â°C | Read
17455 |  | Temperature input terminal IOM5.1 1205-1208 | PT100 | 16 | 2025-10-01 | Â°C | Read
17456 |  | Temperature input terminal IOM5.1 1209-1212 | PT100 | 16 | 2025-10-01 | Â°C | Read
17457 |  | Temperature input terminal IOM5.1 1241-1244 | PT100 | 16 | 2025-10-01 | Â°C | Read
17458 |  | Temperature input terminal IOM5.1 1245-1248 | PT100 | 16 | 2025-10-01 | Â°C | Read
17459 |  | Temperature input terminal IOM5.1 1249-1252 | PT100 | 16 | 2025-10-01 | Â°C | Read
17460 |  | Temperature input terminal IOM5.1 1301-1304 | PT100 | 16 | 2025-10-01 | Â°C | Read
17461 |  | Temperature input terminal IOM5.1 1305-1308 | PT100 | 16 | 2025-10-01 | Â°C | Read
17462 |  | Temperature input terminal IOM5.1 1309-1312 | PT100 | 16 | 2025-10-01 | Â°C | Read
17463 |  | Temperature input terminal IOM5.1 1341-1344 | PT100 | 16 | 2025-10-01 | Â°C | Read
17464 |  | Temperature input terminal IOM5.1 1345-1348 | PT100 | 16 | 2025-10-01 | Â°C | Read
17465 |  | Temperature input terminal IOM5.1 1349-1352 | PT100 | 16 | 2025-10-01 | Â°C | Read
17466 |  | Temperature input terminal IOM5.1 1401-1404 | PT100 | 16 | 2025-10-01 | Â°C | Read
17467 |  | Temperature input terminal IOM5.1 1405-1408 | PT100 | 16 | 2025-10-01 | Â°C | Read
17468 |  | Temperature input terminal IOM5.1 1409-1412 | PT100 | 16 | 2025-10-01 | Â°C | Read
17469 |  | Temperature input terminal IOM5.1 1441-1444 | PT100 | 16 | 2025-10-01 | Â°C | Read
17470 |  | Temperature input terminal IOM5.1 1445-1448 | PT100 | 16 | 2025-10-01 | Â°C | Read
17471 |  | Temperature input terminal IOM5.1 1449-1452 | PT100 | 16 | 2025-10-01 | Â°C | Read
17600 |  | Analog input terminal IOM5.1 313-315 | mA | 16 | 1/1250 | mA | Read
17601 |  | Analog input terminal IOM5.1 316-318 | mA | 16 | 1/1250 | mA | Read
17602 |  | Analog input terminal IOM5.1 353-355 | mA | 16 | 1/1250 | mA | Read
17603 |  | Analog input terminal IOM5.1 356-358 | mA | 16 | 1/1250 | mA | Read
17604 |  | Analog input terminal IOM5.1 413-415 | mA | 16 | 1/1250 | mA | Read
17605 |  | Analog input terminal IOM5.1 416-418 | mA | 16 | 1/1250 | mA | Read
17606 |  | Analog input terminal IOM5.1 453-455 | mA | 16 | 1/1250 | mA | Read
17607 |  | Analog input terminal IOM5.1 456-458 | mA | 16 | 1/1250 | mA | Read
17608 |  | Analog input terminal IOM5.1 513-515 | mA | 16 | 1/1250 | mA | Read
17609 |  | Analog input terminal IOM5.1 516-518 | mA | 16 | 1/1250 | mA | Read
17610 |  | Analog input terminal IOM5.1 553-555 | mA | 16 | 1/1250 | mA | Read
17611 |  | Analog input terminal IOM5.1 556-558 | mA | 16 | 1/1250 | mA | Read
17612 |  | Analog input terminal IOM5.1 613-615 | mA | 16 | 1/1250 | mA | Read
17613 |  | Analog input terminal IOM5.1 616-618 | mA | 16 | 1/1250 | mA | Read
17614 |  | Analog input terminal IOM5.1 653-655 | mA | 16 | 1/1250 | mA | Read
17615 |  | Analog input terminal IOM5.1 656-658 | mA | 16 | 1/1250 | mA | Read
17616 |  | Analog input terminal IOM5.1 713-715 | mA | 16 | 1/1250 | mA | Read
17617 |  | Analog input terminal IOM5.1 716-718 | mA | 16 | 1/1250 | mA | Read
17618 |  | Analog input terminal IOM5.1 753-755 | mA | 16 | 1/1250 | mA | Read
17619 |  | Analog input terminal IOM5.1 756-758 | mA | 16 | 1/1250 | mA | Read
17620 |  | Analog input terminal IOM5.1 813-815 | mA | 16 | 1/1250 | mA | Read
17621 |  | Analog input terminal IOM5.1 816-818 | mA | 16 | 1/1250 | mA | Read
17622 |  | Analog input terminal IOM5.1 853-855 | mA | 16 | 1/1250 | mA | Read
17623 |  | Analog input terminal IOM5.1 856-858 | mA | 16 | 1/1250 | mA | Read
17624 |  | Analog input terminal IOM5.1 913-915 | mA | 16 | 1/1250 | mA | Read
17625 |  | Analog input terminal IOM5.1 916-918 | mA | 16 | 1/1250 | mA | Read
17626 |  | Analog input terminal IOM5.1 953-955 | mA | 16 | 1/1250 | mA | Read
17627 |  | Analog input terminal IOM5.1 956-958 | mA | 16 | 1/1250 | mA | Read
17628 |  | Analog input terminal IOM5.1 1013-1015 | mA | 16 | 1/1250 | mA | Read
17629 |  | Analog input terminal IOM5.1 1016-1018 | mA | 16 | 1/1250 | mA | Read
17630 |  | Analog input terminal IOM5.1 1053-1055 | mA | 16 | 1/1250 | mA | Read
17631 |  | Analog input terminal IOM5.1 1056-1058 | mA | 16 | 1/1250 | mA | Read
17632 |  | Analog input terminal IOM5.1 1113-1115 | mA | 16 | 1/1250 | mA | Read
17633 |  | Analog input terminal IOM5.1 1116-1118 | mA | 16 | 1/1250 | mA | Read
17634 |  | Analog input terminal IOM5.1 1153-1155 | mA | 16 | 1/1250 | mA | Read
17635 |  | Analog input terminal IOM5.1 1156-1158 | mA | 16 | 1/1250 | mA | Read
17636 |  | Analog input terminal IOM5.1 1213-1215 | mA | 16 | 1/1250 | mA | Read
17637 |  | Analog input terminal IOM5.1 1216-1218 | mA | 16 | 1/1250 | mA | Read
17638 |  | Analog input terminal IOM5.1 1253-1255 | mA | 16 | 1/1250 | mA | Read
17639 |  | Analog input terminal IOM5.1 1256-1258 | mA | 16 | 1/1250 | mA | Read
17640 |  | Analog input terminal IOM5.1 1313-1315 | mA | 16 | 1/1250 | mA | Read
17641 |  | Analog input terminal IOM5.1 1316-1318 | mA | 16 | 1/1250 | mA | Read
17642 |  | Analog input terminal IOM5.1 1353-1355 | mA | 16 | 1/1250 | mA | Read
17643 |  | Analog input terminal IOM5.1 1356-1358 | mA | 16 | 1/1250 | mA | Read
17644 |  | Analog input terminal IOM5.1 1413-1415 | mA | 16 | 1/1250 | mA | Read
17645 |  | Analog input terminal IOM5.1 1416-1418 | mA | 16 | 1/1250 | mA | Read
17646 |  | Analog input terminal IOM5.1 1453-1455 | mA | 16 | 1/1250 | mA | Read
17647 |  | Analog input terminal IOM5.1 1456-1458 | mA | 16 | 1/1250 | mA | Read
17800 |  | Analog output terminal IOM5.1 319/20 | - | 16 | 1/1250 | mA | Read
17801 |  | Analog output terminal IOM5.1 321/22 | - | 16 | 1/1250 | mA | Read
17802 |  | Analog output terminal IOM5.1 359/60 | - | 16 | 1/1250 | mA | Read
17803 |  | Analog output terminal IOM5.1 361/62 | - | 16 | 1/1250 | mA | Read
17804 |  | Analog output terminal IOM5.1 419/20 | - | 16 | 1/1250 | mA | Read
17805 |  | Analog output terminal IOM5.1 421/22 | - | 16 | 1/1250 | mA | Read
17806 |  | Analog output terminal IOM5.1 459/60 | - | 16 | 1/1250 | mA | Read
17807 |  | Analog output terminal IOM5.1 461/62 | - | 16 | 1/1250 | mA | Read
17808 |  | Analog output terminal IOM5.1 519/20 | - | 16 | 1/1250 | mA | Read
17809 |  | Analog output terminal IOM5.1 521/22 | - | 16 | 1/1250 | mA | Read
17810 |  | Analog output terminal IOM5.1 559/60 | - | 16 | 1/1250 | mA | Read
17811 |  | Analog output terminal IOM5.1 561/62 | - | 16 | 1/1250 | mA | Read
17812 |  | Analog output terminal IOM5.1 619/20 | - | 16 | 1/1250 | mA | Read
17813 |  | Analog output terminal IOM5.1 621/22 | - | 16 | 1/1250 | mA | Read
17814 |  | Analog output terminal IOM5.1 659/60 | - | 16 | 1/1250 | mA | Read
17815 |  | Analog output terminal IOM5.1 661/62 | - | 16 | 1/1250 | mA | Read
17816 |  | Analog output terminal IOM5.1 719/20 | - | 16 | 1/1250 | mA | Read
17817 |  | Analog output terminal IOM5.1 721/22 | - | 16 | 1/1250 | mA | Read
17818 |  | Analog output terminal IOM5.1 759/60 | - | 16 | 1/1250 | mA | Read
17819 |  | Analog output terminal IOM5.1 761/62 | - | 16 | 1/1250 | mA | Read
17820 |  | Analog output terminal IOM5.1 819/20 | - | 16 | 1/1250 | mA | Read
17821 |  | Analog output terminal IOM5.1 821/22 | - | 16 | 1/1250 | mA | Read
17822 |  | Analog output terminal IOM5.1 859/60 | - | 16 | 1/1250 | mA | Read
17823 |  | Analog output terminal IOM5.1 861/62 | - | 16 | 1/1250 | mA | Read
17824 |  | Analog output terminal IOM5.1 919/20 | - | 16 | 1/1250 | mA | Read
17825 |  | Analog output terminal IOM5.1 921/22 | - | 16 | 1/1250 | mA | Read
17826 |  | Analog output terminal IOM5.1 959/60 | - | 16 | 1/1250 | mA | Read
17827 |  | Analog output terminal IOM5.1 961/62 | - | 16 | 1/1250 | mA | Read
17828 |  | Analog output terminal IOM5.1 1019/20 | - | 16 | 1/1250 | mA | Read
17829 |  | Analog output terminal IOM5.1 1021/22 | - | 16 | 1/1250 | mA | Read
17830 |  | Analog output terminal IOM5.1 1059/60 | - | 16 | 1/1250 | mA | Read
17831 |  | Analog output terminal IOM5.1 1061/62 | - | 16 | 1/1250 | mA | Read
17832 |  | Analog output terminal IOM5.1 1119/20 | - | 16 | 1/1250 | mA | Read
17833 |  | Analog output terminal IOM5.1 1121/22 | - | 16 | 1/1250 | mA | Read
17834 |  | Analog output terminal IOM5.1 1159/60 | - | 16 | 1/1250 | mA | Read
17835 |  | Analog output terminal IOM5.1 1161/62 | - | 16 | 1/1250 | mA | Read
17836 |  | Analog output terminal IOM5.1 1219/20 | - | 16 | 1/1250 | mA | Read
17837 |  | Analog output terminal IOM5.1 1221/22 | - | 16 | 1/1250 | mA | Read
17838 |  | Analog output terminal IOM5.1 1259/60 | - | 16 | 1/1250 | mA | Read
17839 |  | Analog output terminal IOM5.1 1261/62 | - | 16 | 1/1250 | mA | Read
17840 |  | Analog output terminal IOM5.1 1319/20 | - | 16 | 1/1250 | mA | Read
17841 |  | Analog output terminal IOM5.1 1321/22 | - | 16 | 1/1250 | mA | Read
17842 |  | Analog output terminal IOM5.1 1359/60 | - | 16 | 1/1250 | mA | Read
17843 |  | Analog output terminal IOM5.1 1361/62 | - | 16 | 1/1250 | mA | Read
17844 |  | Analog output terminal IOM5.1 1419/20 | - | 16 | 1/1250 | mA | Read
17845 |  | Analog output terminal IOM5.1 1421/22 | - | 16 | 1/1250 | mA | Read
17846 |  | Analog output terminal IOM5.1 1459/60 | - | 16 | 1/1250 | mA | Read
17847 |  | Analog output terminal IOM5.1 1461/62 | - | 16 | 1/1250 | mA | Read

## 07_Digital Input Function
#VALUE! | 18000-18013
18817-19009
Register | Bit | Text | Configuration | Resolution | Factor | Unit | Access
18000 |  | Digital input function register 1
18000 | 0 | Conf. DI 1 | - | 1 | - | - | Read
18000 | 1 | Conf. DI 2 | - | 1 | - | - | Read
18000 | 2 | Conf. DI 3 | - | 1 | - | - | Read
18000 | 3 | Conf. DI 4 | - | 1 | - | - | Read
18000 | 4 | Conf. DI 5 | - | 1 | - | - | Read
18000 | 5 | Conf. DI 6 | - | 1 | - | - | Read
18000 | 6 | Conf. DI 7 | - | 1 | - | - | Read
18000 | 7 | Conf. DI 8 | - | 1 | - | - | Read
18000 | 8 | Conf. DI 9 | - | 1 | - | - | Read
18000 | 9 | Conf. DI 10 | - | 1 | - | - | Read
18000 | 10 | Conf. DI 11 | - | 1 | - | - | Read
18000 | 11 | Conf. DI 12 | - | 1 | - | - | Read
18000 | 12 | Conf. DI 13 | - | 1 | - | - | Read
18000 | 13 | Conf. DI 14 | - | 1 | - | - | Read
18000 | 14 | Conf. DI 15 | - | 1 | - | - | Read
18000 | 15 | Conf. DI 16 | - | 1 | - | - | Read
18001 |  | Digital input function register 2
18001 | 0 | Conf. DI 17 | - | 1 | - | - | Read
18001 | 1 | Conf. DI 18 | - | 1 | - | - | Read
18001 | 2 | Conf. DI 19 | - | 1 | - | - | Read
18001 | 3 | Conf. DI 20 | - | 1 | - | - | Read
18001 | 4 | Conf. DI 21 | - | 1 | - | - | Read
18001 | 5 | Conf. DI 22 | - | 1 | - | - | Read
18001 | 6 | Conf. DI 23 | - | 1 | - | - | Read
18001 | 7 | Conf. DI 24 | - | 1 | - | - | Read
18001 | 8 | Conf. DI 25 | - | 1 | - | - | Read
18001 | 9 | Conf. DI 26 | - | 1 | - | - | Read
18001 | 10 | Conf. DI 27 | - | 1 | - | - | Read
18001 | 11 | Conf. DI 28 | - | 1 | - | - | Read
18001 | 12 | Conf. DI 29 | - | 1 | - | - | Read
18001 | 13 | Conf. DI 30 | - | 1 | - | - | Read
18001 | 14 | Conf. DI 31 | - | 1 | - | - | Read
18001 | 15 | Conf. DI 32 | - | 1 | - | - | Read
18002 |  | Digital input function register 3
18002 | 0 | Conf. DI 33 | - | 1 | - | - | Read
18002 | 1 | Conf. DI 34 | - | 1 | - | - | Read
18002 | 2 | Conf. DI 35 | - | 1 | - | - | Read
18002 | 3 | Conf. DI 36 | - | 1 | - | - | Read
18002 | 4 | Conf. DI 37 | - | 1 | - | - | Read
18002 | 5 | Conf. DI 38 | - | 1 | - | - | Read
18002 | 6 | Conf. DI 39 | - | 1 | - | - | Read
18002 | 7 | Conf. DI 40 | - | 1 | - | - | Read
18002 | 8 | Conf. DI 41 | - | 1 | - | - | Read
18002 | 9 | Conf. DI 42 | - | 1 | - | - | Read
18002 | 10 | Conf. DI 43 | - | 1 | - | - | Read
18002 | 11 | Conf. DI 44 | - | 1 | - | - | Read
18002 | 12 | Conf. DI 45 | - | 1 | - | - | Read
18002 | 13 | Conf. DI 46 | - | 1 | - | - | Read
18002 | 14 | Conf. DI 47 | - | 1 | - | - | Read
18002 | 15 | Conf. DI 48 | - | 1 | - | - | Read
18003 |  | Digital input function register 4
18003 | 0 | Conf. DI 49 | - | 1 | - | - | Read
18003 | 1 | Conf. DI 50 | - | 1 | - | - | Read
18003 | 2 | Conf. DI 51 | - | 1 | - | - | Read
18003 | 3 | Conf. DI 52 | - | 1 | - | - | Read
18003 | 4 | Conf. DI 53 | - | 1 | - | - | Read
18003 | 5 | Conf. DI 54 | - | 1 | - | - | Read
18003 | 6 | Conf. DI 55 | - | 1 | - | - | Read
18003 | 7 | Conf. DI 56 | - | 1 | - | - | Read
18003 | 8 | Conf. DI 57 | - | 1 | - | - | Read
18003 | 9 | Conf. DI 58 | - | 1 | - | - | Read
18003 | 10 | Conf. DI 59 | - | 1 | - | - | Read
18003 | 11 | Conf. DI 60 | - | 1 | - | - | Read
18003 | 12 | Conf. DI 61 | - | 1 | - | - | Read
18003 | 13 | Conf. DI 62 | - | 1 | - | - | Read
18003 | 14 | Conf. DI 63 | - | 1 | - | - | Read
18003 | 15 | Conf. DI 64 | - | 1 | - | - | Read
18004 |  | Digital input function register 5
18004 | 0 | Conf. DI 65 | - | 1 | - | - | Read
18004 | 1 | Conf. DI 66 | - | 1 | - | - | Read
18004 | 2 | Conf. DI 67 | - | 1 | - | - | Read
18004 | 3 | Conf. DI 68 | - | 1 | - | - | Read
18004 | 4 | Conf. DI 69 | - | 1 | - | - | Read
18004 | 5 | Conf. DI 70 | - | 1 | - | - | Read
18004 | 6 | Conf. DI 71 | - | 1 | - | - | Read
18004 | 7 | Conf. DI 72 | - | 1 | - | - | Read
18004 | 8 | Conf. DI 73 | - | 1 | - | - | Read
18004 | 9 | Conf. DI 74 | - | 1 | - | - | Read
18004 | 10 | Conf. DI 75 | - | 1 | - | - | Read
18004 | 11 | Conf. DI 76 | - | 1 | - | - | Read
18004 | 12 | Conf. DI 77 | - | 1 | - | - | Read
18004 | 13 | Conf. DI 78 | - | 1 | - | - | Read
18004 | 14 | Conf. DI 79 | - | 1 | - | - | Read
18004 | 15 | Conf. DI 80 | - | 1 | - | - | Read
18005 |  | Digital input function register 6
18005 | 0 | Conf. DI 81 | - | 1 | - | - | Read
18005 | 1 | Conf. DI 82 | - | 1 | - | - | Read
18005 | 2 | Conf. DI 83 | - | 1 | - | - | Read
18005 | 3 | Conf. DI 84 | - | 1 | - | - | Read
18005 | 4 | Conf. DI 85 | - | 1 | - | - | Read
18005 | 5 | Conf. DI 86 | - | 1 | - | - | Read
18005 | 6 | Conf. DI 87 | - | 1 | - | - | Read
18005 | 7 | Conf. DI 88 | - | 1 | - | - | Read
18005 | 8 | Conf. DI 89 | - | 1 | - | - | Read
18005 | 9 | Conf. DI 90 | - | 1 | - | - | Read
18005 | 10 | Conf. DI 91 | - | 1 | - | - | Read
18005 | 11 | Conf. DI 92 | - | 1 | - | - | Read
18005 | 12 | Conf. DI 93 | - | 1 | - | - | Read
18005 | 13 | Conf. DI 94 | - | 1 | - | - | Read
18005 | 14 | Conf. DI 95 | - | 1 | - | - | Read
18005 | 15 | Conf. DI 96 | - | 1 | - | - | Read
18006 |  | Digital input function register 7
18006 | 0 | Conf. DI 97 | - | 1 | - | - | Read
18006 | 1 | Conf. DI 98 | - | 1 | - | - | Read
18006 | 2 | Conf. DI 99 | - | 1 | - | - | Read
18006 | 3 | Conf. DI 100 | - | 1 | - | - | Read
18006 | 4 | Conf. DI 101 | - | 1 | - | - | Read
18006 | 5 | Conf. DI 102 | - | 1 | - | - | Read
18006 | 6 | Conf. DI 103 | - | 1 | - | - | Read
18006 | 7 | Conf. DI 104 | - | 1 | - | - | Read
18006 | 8 | Conf. DI 105 | - | 1 | - | - | Read
18006 | 9 | Conf. DI 106 | - | 1 | - | - | Read
18006 | 10 | Conf. DI 107 | - | 1 | - | - | Read
18006 | 11 | Conf. DI 108 | - | 1 | - | - | Read
18006 | 12 | Conf. DI 109 | - | 1 | - | - | Read
18006 | 13 | Conf. DI 110 | - | 1 | - | - | Read
18006 | 14 | Conf. DI 111 | - | 1 | - | - | Read
18006 | 15 | Conf. DI 112 | - | 1 | - | - | Read
18007 |  | Digital input function register 8
18007 | 0 | Conf. DI 113 | - | 1 | - | - | Read
18007 | 1 | Conf. DI 114 | - | 1 | - | - | Read
18007 | 2 | Conf. DI 115 | - | 1 | - | - | Read
18007 | 3 | Conf. DI 116 | - | 1 | - | - | Read
18007 | 4 | Conf. DI 117 | - | 1 | - | - | Read
18007 | 5 | Conf. DI 118 | - | 1 | - | - | Read
18007 | 6 | Conf. DI 119 | - | 1 | - | - | Read
18007 | 7 | Conf. DI 120 | - | 1 | - | - | Read
18007 | 8 | Conf. counter 1 | - | 1 | - | - | Read
18007 | 9 | Conf. counter 2 | - | 1 | - | - | Read
18007 | 10 | Conf. counter 3 | - | 1 | - | - | Read
18007 | 11 | Conf. counter 4 | - | 1 | - | - | Read
18007 | 12 | Reset PID 1 | - | 1 | - | - | Read
18007 | 13 | Reset PID 2 | - | 1 | - | - | Read
18007 | 14 | Reset PID 3 | - | 1 | - | - | Read
18007 | 15 | Reset PID 4 | - | 1 | - | - | Read
18008 |  | Digital input function register 9
18008 | 0 | Reset PID 5 | - | 1 | - | - | Read
18008 | 1 | Alarm inhibit 1 | - | 1 | - | - | Read
18008 | 2 | Alarm inhibit 2 | - | 1 | - | - | Read
18008 | 3 | Alarm inhibit 3 | - | 1 | - | - | Read
18008 | 4 | Alarm inhibit 4 | - | 1 | - | - | Read
18008 | 5 | Alarm inhibit 5 | - | 1 | - | - | Read
18008 | 6 | Alarm inhibit 6 | - | 1 | - | - | Read
18008 | 7 | Alarm inhibit 7 | - | 1 | - | - | Read
18008 | 8 | Alarm inhibit 8 | - | 1 | - | - | Read
18008 | 9 | Alarm inhibit 9 | - | 1 | - | - | Read
18008 | 10 | Alarm inhibit 10 | - | 1 | - | - | Read
18008 | 11 | Alarm inhibit 11 | - | 1 | - | - | Read
18008 | 12 | Alarm inhibit 12 | - | 1 | - | - | Read
18008 | 13 | Alarm inhibit 13 | - | 1 | - | - | Read
18008 | 14 | Alarm inhibit 14 | - | 1 | - | - | Read
18008 | 15 | Alarm inhibit 15 | - | 1 | - | - | Read
18009 |  | Digital input function register 10
18009 | 0 | Alarm inhibit 16 | - | 1 | - | - | Read
18009 | 1 | Alarm inhibit 17 | - | 1 | - | - | Read
18009 | 2 | Alarm inhibit 18 | - | 1 | - | - | Read
18009 | 3 | Alarm inhibit 19 | - | 1 | - | - | Read
18009 | 4 | Alarm inhibit 20 | - | 1 | - | - | Read
18009 | 5 | Alarm inhibit 21 | - | 1 | - | - | Read
18009 | 6 | Alarm inhibit 22 | - | 1 | - | - | Read
18009 | 7 | Alarm inhibit 23 | - | 1 | - | - | Read
18009 | 8 | Alarm inhibit 24 | - | 1 | - | - | Read
18009 | 9 | Alarm inhibit 25 | - | 1 | - | - | Read
18009 | 10 | Alarm inhibit 26 | - | 1 | - | - | Read
18009 | 11 | Alarm inhibit 27 | - | 1 | - | - | Read
18009 | 12 | Alarm inhibit 28 | - | 1 | - | - | Read
18009 | 13 | Alarm inhibit 29 | - | 1 | - | - | Read
18009 | 14 | Alarm inhibit 30 | - | 1 | - | - | Read
18009 | 15 | Alarm inhibit 31 | - | 1 | - | - | Read
18010 |  | Digital input function register 11
18010 | 0 | Alarm inhibit 32 | - | 1 | - | - | Read
18010 | 1 | Emergency stop | - | 1 | - | - | Read
18010 | 2 | Watchdog | - | 1 | - | - | Read
18010 | 3 | Safety chain | - | 1 | - | - | Read
18010 | 4 | Pickup 1 | - | 1 | - | - | Read
18010 | 5 | Pickup 2 | - | 1 | - | - | Read
18010 | 6 | Acknowledge alarms | - | 1 | - | - | Read
18010 | 7 | Clear alarms | - | 1 | - | - | Read
18010 | 8 | Ack. / Clear alarms | - | 1 | - | - | Read
18010 | 9 | Select hot start | - | 1 | - | - | Read
18010 | 10 | Start preparation finished | - | 1 | - | - | Read
18010 | 11 | Start demand | - | 1 | - | - | Read
18010 | 12 | Stop demand | - | 1 | - | - | Read
18010 | 13 | Stop postrun | - | 1 | - | - | Read
18010 | 14 | Speed limit idle 1 | - | 1 | - | - | Read
18010 | 15 | Speed limit idle 2 | - | 1 | - | - | Read
18011 |  | Digital input function register 12
18011 | 0 | No speed limit | - | 1 | - | - | Read
18011 | 1 | Overspeed test | - | 1 | - | - | Read
18011 | 2 | GCB opened | - | 1 | - | - | Read
18011 | 3 | GCB closed | - | 1 | - | - | Read
18011 | 4 | MCB opened | - | 1 | - | - | Read
18011 | 5 | MCB closed | - | 1 | - | - | Read
18011 | 6 | Island parallel | - | 1 | - | - | Read
18011 | 7 | Busbar is black | - | 1 | - | - | Read
18011 | 8 | Wish black closing | - | 1 | - | - | Read
18011 | 9 | Release black closing | - | 1 | - | - | Read
18011 | 10 | Enable operation | - | 1 | - | - | Read
18011 | 11 | Manual mode | - | 1 | - | - | Read
18011 | 12 | Semi-Auto mode | - | 1 | - | - | Read
18011 | 13 | Automatic mode | - | 1 | - | - | Read
18011 | 14 | Local / Remote | - | 1 | - | - | Read
18011 | 15 | Demand island operation | - | 1 | - | - | Read
18012 |  | Digital input function register 13
18012 | 0 | Shutdown | - | 1 | - | - | Read
18012 | 1 | Power control (Load) | - | 1 | - | - | Read
18012 | 2 | Power control (Droop) | - | 1 | - | - | Read
18012 | 3 | Activate pressure control | - | 1 | - | - | Read
18012 | 4 | Remote pressure control | - | 1 | - | - | Read
18012 | 5 | Speed up | - | 1 | - | - | Read
18012 | 6 | Speed down | - | 1 | - | - | Read
18012 | 7 | Power up | - | 1 | - | - | Read
18012 | 8 | Power down | - | 1 | - | - | Read
18012 | 9 | Voltage up | - | 1 | - | - | Read
18012 | 10 | Voltage down | - | 1 | - | - | Read
18012 | 11 | Pressure up | - | 1 | - | - | Read
18012 | 12 | Pressure down | - | 1 | - | - | Read
18012 | 13 | Modbus write access | - | 1 | - | - | Read
18012 | 14 | Trending scope on | - | 1 | - | - | Read
18012 | 15 | Trending scope off | - | 1 | - | - | Read
18013 |  | Digital input function register 14
18013 | 0 | Valve limiter open | - | 1 | - | - | Read
18013 | 1 | Valve limiter close | - | 1 | - | - | Read
18013 | 2 | Clock synchronization | - | 1 | - | - | Read
18013 | 3 | Bearing lubrication | - | 1 | - | - | Read
18013 | 4 | Clear power limitation | - | 1 | - | - | Read
18013 | 5 | LP valve limiter open | - | 1 | - | - | Read
18013 | 6 | LP valve limiter close | - | 1 | - | - | Read
18013 | 7 | Extraction demand up | - | 1 | - | - | Read
18013 | 8 | Extraction demand down | - | 1 | - | - | Read
18817 |  | Digital input function assignment register 1 | - | 16 | 1/1250 | mA | Read
18818 |  | Digital input function assignment register 2 | - | 16 | 1/1250 | mA | Read
18819 |  | Digital input function assignment register 3 | - | 16 | 1/1250 | mA | Read
18820 |  | Digital input function assignment register 4 | - | 16 | 1/1250 | mA | Read
19000 |  | Digital input function assignment register 5
19000 | 0 | Conf. DI 1 | - | 1 | - | - | Read
19000 | 1 | Conf. DI 2 | - | 1 | - | - | Read
19000 | 2 | Conf. DI 3 | - | 1 | - | - | Read
19000 | 3 | Conf. DI 4 | - | 1 | - | - | Read
19000 | 4 | Conf. DI 5 | - | 1 | - | - | Read
19000 | 5 | Conf. DI 6 | - | 1 | - | - | Read
19000 | 6 | Conf. DI 7 | - | 1 | - | - | Read
19000 | 7 | Conf. DI 8 | - | 1 | - | - | Read
19000 | 8 | Conf. DI 9 | - | 1 | - | - | Read
19000 | 9 | Conf. DI 10 | - | 1 | - | - | Read
19000 | 10 | Conf. DI 11 | - | 1 | - | - | Read
19000 | 11 | Conf. DI 12 | - | 1 | - | - | Read
19000 | 12 | Conf. DI 13 | - | 1 | - | - | Read
19000 | 13 | Conf. DI 14 | - | 1 | - | - | Read
19000 | 14 | Conf. DI 15 | - | 1 | - | - | Read
19000 | 15 | Conf. DI 16 | - | 1 | - | - | Read
19001 |  | Digital input function assignment register 6
19001 | 0 | Conf. DI 17 | - | 1 | - | - | Read
19001 | 1 | Conf. DI 18 | - | 1 | - | - | Read
19001 | 2 | Conf. DI 19 | - | 1 | - | - | Read
19001 | 3 | Conf. DI 20 | - | 1 | - | - | Read
19001 | 4 | Conf. DI 21 | - | 1 | - | - | Read
19001 | 5 | Conf. DI 22 | - | 1 | - | - | Read
19001 | 6 | Conf. DI 23 | - | 1 | - | - | Read
19001 | 7 | Conf. DI 24 | - | 1 | - | - | Read
19001 | 8 | Conf. DI 25 | - | 1 | - | - | Read
19001 | 9 | Conf. DI 26 | - | 1 | - | - | Read
19001 | 10 | Conf. DI 27 | - | 1 | - | - | Read
19001 | 11 | Conf. DI 28 | - | 1 | - | - | Read
19001 | 12 | Conf. DI 29 | - | 1 | - | - | Read
19001 | 13 | Conf. DI 30 | - | 1 | - | - | Read
19001 | 14 | Conf. DI 31 | - | 1 | - | - | Read
19001 | 15 | Conf. DI 32 | - | 1 | - | - | Read
19002 |  | Digital input function assignment register 7
19002 | 0 | Conf. DI 33 | - | 1 | - | - | Read
19002 | 1 | Conf. DI 34 | - | 1 | - | - | Read
19002 | 2 | Conf. DI 35 | - | 1 | - | - | Read
19002 | 3 | Conf. DI 36 | - | 1 | - | - | Read
19002 | 4 | Conf. DI 37 | - | 1 | - | - | Read
19002 | 5 | Conf. DI 38 | - | 1 | - | - | Read
19002 | 6 | Conf. DI 39 | - | 1 | - | - | Read
19002 | 7 | Conf. DI 40 | - | 1 | - | - | Read
19002 | 8 | Conf. DI 41 | - | 1 | - | - | Read
19002 | 9 | Conf. DI 42 | - | 1 | - | - | Read
19002 | 10 | Conf. DI 43 | - | 1 | - | - | Read
19002 | 11 | Conf. DI 44 | - | 1 | - | - | Read
19002 | 12 | Conf. DI 45 | - | 1 | - | - | Read
19002 | 13 | Conf. DI 46 | - | 1 | - | - | Read
19002 | 14 | Conf. DI 47 | - | 1 | - | - | Read
19002 | 15 | Conf. DI 48 | - | 1 | - | - | Read
19003 |  | Digital input function assignment register 8
19003 | 0 | Conf. DI 49 | - | 1 | - | - | Read
19003 | 1 | Conf. DI 50 | - | 1 | - | - | Read
19003 | 2 | Conf. DI 51 | - | 1 | - | - | Read
19003 | 3 | Conf. DI 52 | - | 1 | - | - | Read
19003 | 4 | Conf. DI 53 | - | 1 | - | - | Read
19003 | 5 | Conf. DI 54 | - | 1 | - | - | Read
19003 | 6 | Conf. DI 55 | - | 1 | - | - | Read
19003 | 7 | Conf. DI 56 | - | 1 | - | - | Read
19003 | 8 | Conf. DI 57 | - | 1 | - | - | Read
19003 | 9 | Conf. DI 58 | - | 1 | - | - | Read
19003 | 10 | Conf. DI 59 | - | 1 | - | - | Read
19003 | 11 | Conf. DI 60 | - | 1 | - | - | Read
19003 | 12 | Conf. DI 61 | - | 1 | - | - | Read
19003 | 13 | Conf. DI 62 | - | 1 | - | - | Read
19003 | 14 | Conf. DI 63 | - | 1 | - | - | Read
19003 | 15 | Conf. DI 64 | - | 1 | - | - | Read
19004 |  | Digital input function assignment register 9
19004 | 0 | Conf. DI 65 | - | 1 | - | - | Read
19004 | 1 | Conf. DI 66 | - | 1 | - | - | Read
19004 | 2 | Conf. DI 67 | - | 1 | - | - | Read
19004 | 3 | Conf. DI 68 | - | 1 | - | - | Read
19004 | 4 | Conf. DI 69 | - | 1 | - | - | Read
19004 | 5 | Conf. DI 70 | - | 1 | - | - | Read
19004 | 6 | Conf. DI 71 | - | 1 | - | - | Read
19004 | 7 | Conf. DI 72 | - | 1 | - | - | Read
19004 | 8 | Conf. DI 73 | - | 1 | - | - | Read
19004 | 9 | Conf. DI 74 | - | 1 | - | - | Read
19004 | 10 | Conf. DI 75 | - | 1 | - | - | Read
19004 | 11 | Conf. DI 76 | - | 1 | - | - | Read
19004 | 12 | Conf. DI 77 | - | 1 | - | - | Read
19004 | 13 | Conf. DI 78 | - | 1 | - | - | Read
19004 | 14 | Conf. DI 79 | - | 1 | - | - | Read
19004 | 15 | Conf. DI 80 | - | 1 | - | - | Read
19005 |  | Digital input function assignment register 10
19005 | 0 | Conf. DI 81 | - | 1 | - | - | Read
19005 | 1 | Conf. DI 82 | - | 1 | - | - | Read
19005 | 2 | Conf. DI 83 | - | 1 | - | - | Read
19005 | 3 | Conf. DI 84 | - | 1 | - | - | Read
19005 | 4 | Conf. DI 85 | - | 1 | - | - | Read
19005 | 5 | Conf. DI 86 | - | 1 | - | - | Read
19005 | 6 | Conf. DI 87 | - | 1 | - | - | Read
19005 | 7 | Conf. DI 88 | - | 1 | - | - | Read
19005 | 8 | Conf. DI 89 | - | 1 | - | - | Read
19005 | 9 | Conf. DI 90 | - | 1 | - | - | Read
19005 | 10 | Conf. DI 91 | - | 1 | - | - | Read
19005 | 11 | Conf. DI 92 | - | 1 | - | - | Read
19005 | 12 | Conf. DI 93 | - | 1 | - | - | Read
19005 | 13 | Conf. DI 94 | - | 1 | - | - | Read
19005 | 14 | Conf. DI 95 | - | 1 | - | - | Read
19005 | 15 | Conf. DI 96 | - | 1 | - | - | Read
19006 |  | Digital input function assignment register 11
19006 | 0 | Conf. DI 97 | - | 1 | - | - | Read
19006 | 1 | Conf. DI 98 | - | 1 | - | - | Read
19006 | 2 | Conf. DI 99 | - | 1 | - | - | Read
19006 | 3 | Conf. DI 100 | - | 1 | - | - | Read
19006 | 4 | Conf. DI 101 | - | 1 | - | - | Read
19006 | 5 | Conf. DI 102 | - | 1 | - | - | Read
19006 | 6 | Conf. DI 103 | - | 1 | - | - | Read
19006 | 7 | Conf. DI 104 | - | 1 | - | - | Read
19006 | 8 | Conf. DI 105 | - | 1 | - | - | Read
19006 | 9 | Conf. DI 106 | - | 1 | - | - | Read
19006 | 10 | Conf. DI 107 | - | 1 | - | - | Read
19006 | 11 | Conf. DI 108 | - | 1 | - | - | Read
19006 | 12 | Conf. DI 109 | - | 1 | - | - | Read
19006 | 13 | Conf. DI 110 | - | 1 | - | - | Read
19006 | 14 | Conf. DI 111 | - | 1 | - | - | Read
19006 | 15 | Conf. DI 112 | - | 1 | - | - | Read
19007 |  | Digital input function assignment register 12
19007 | 0 | Conf. DI 113 | - | 1 | - | - | Read
19007 | 1 | Conf. DI 114 | - | 1 | - | - | Read
19007 | 2 | Conf. DI 115 | - | 1 | - | - | Read
19007 | 3 | Conf. DI 116 | - | 1 | - | - | Read
19007 | 4 | Conf. DI 117 | - | 1 | - | - | Read
19007 | 5 | Conf. DI 118 | - | 1 | - | - | Read
19007 | 6 | Conf. DI 119 | - | 1 | - | - | Read
19007 | 7 | Conf. DI 120 | - | 1 | - | - | Read
19007 | 8 | Conf. counter 1 | - | 1 | - | - | Read
19007 | 9 | Conf. counter 2 | - | 1 | - | - | Read
19007 | 10 | Conf. counter 3 | - | 1 | - | - | Read
19007 | 11 | Conf. counter 4 | - | 1 | - | - | Read
19007 | 12 | Reset PID 1 | - | 1 | - | - | Read
19007 | 13 | Reset PID 2 | - | 1 | - | - | Read
19007 | 14 | Reset PID 3 | - | 1 | - | - | Read
19007 | 15 | Reset PID 4 | - | 1 | - | - | Read
19008 |  | Digital input function assignment register 13
19008 | 0 | Reset PID 5 | - | 1 | - | - | Read
19008 | 1 | Alarm inhibit 1 | - | 1 | - | - | Read
19008 | 2 | Alarm inhibit 2 | - | 1 | - | - | Read
19008 | 3 | Alarm inhibit 3 | - | 1 | - | - | Read
19008 | 4 | Alarm inhibit 4 | - | 1 | - | - | Read
19008 | 5 | Alarm inhibit 5 | - | 1 | - | - | Read
19008 | 6 | Alarm inhibit 6 | - | 1 | - | - | Read
19008 | 7 | Alarm inhibit 7 | - | 1 | - | - | Read
19008 | 8 | Alarm inhibit 8 | - | 1 | - | - | Read
19008 | 9 | Alarm inhibit 9 | - | 1 | - | - | Read
19008 | 10 | Alarm inhibit 10 | - | 1 | - | - | Read
19008 | 11 | Alarm inhibit 11 | - | 1 | - | - | Read
19008 | 12 | Alarm inhibit 12 | - | 1 | - | - | Read
19008 | 13 | Alarm inhibit 13 | - | 1 | - | - | Read
19008 | 14 | Alarm inhibit 14 | - | 1 | - | - | Read
19008 | 15 | Alarm inhibit 15 | - | 1 | - | - | Read
19009 |  | Digital input function assignment register 14
19009 | 0 | Alarm inhibit 16 | - | 1 | - | - | Read
19009 | 1 | Alarm inhibit 17 | - | 1 | - | - | Read
19009 | 2 | Alarm inhibit 18 | - | 1 | - | - | Read
19009 | 3 | Alarm inhibit 19 | - | 1 | - | - | Read
19009 | 4 | Alarm inhibit 20 | - | 1 | - | - | Read
19009 | 5 | Alarm inhibit 21 | - | 1 | - | - | Read
19009 | 6 | Alarm inhibit 22 | - | 1 | - | - | Read
19009 | 7 | Alarm inhibit 23 | - | 1 | - | - | Read
19009 | 8 | Alarm inhibit 24 | - | 1 | - | - | Read
19009 | 9 | Alarm inhibit 25 | - | 1 | - | - | Read
19009 | 10 | Alarm inhibit 26 | - | 1 | - | - | Read
19009 | 11 | Alarm inhibit 27 | - | 1 | - | - | Read
19009 | 12 | Alarm inhibit 28 | - | 1 | - | - | Read
19009 | 13 | Alarm inhibit 29 | - | 1 | - | - | Read
19009 | 14 | Alarm inhibit 30 | - | 1 | - | - | Read
19009 | 15 | Alarm inhibit 31 | - | 1 | - | - | Read

## 08_Digital Output Function
#VALUE! | 18200-18207 & 19010-19203 - Digital Output Function
Register | Bit | Text | Configuration | Resolution | Factor | Unit | Access
18200 |  | Digital output function register 1
18200 | 0 | Alarm DO 1 | - | 1 | - | - | Read
18200 | 1 | Alarm DO 2 | - | 1 | - | - | Read
18200 | 2 | Alarm DO 3 | - | 1 | - | - | Read
18200 | 3 | Alarm DO 4 | - | 1 | - | - | Read
18200 | 4 | Alarm DO 5 | - | 1 | - | - | Read
18200 | 5 | Alarm DO 6 | - | 1 | - | - | Read
18200 | 6 | Alarm DO 7 | - | 1 | - | - | Read
18200 | 7 | Alarm DO 8 | - | 1 | - | - | Read
18200 | 8 | Alarm DO 9 | - | 1 | - | - | Read
18200 | 9 | Alarm DO 10 | - | 1 | - | - | Read
18200 | 10 | Alarm DO 11 | - | 1 | - | - | Read
18200 | 11 | Alarm DO 12 | - | 1 | - | - | Read
18200 | 12 | Alarm DO 13 | - | 1 | - | - | Read
18200 | 13 | Alarm DO 14 | - | 1 | - | - | Read
18200 | 14 | Alarm DO 15 | - | 1 | - | - | Read
18200 | 15 | Alarm DO 16 | - | 1 | - | - | Read
18201 |  | Digital output function register 2
18201 | 0 | Alarm DO 17 | - | 1 | - | - | Read
18201 | 1 | Alarm DO 18 | - | 1 | - | - | Read
18201 | 2 | Alarm DO 19 | - | 1 | - | - | Read
18201 | 3 | Alarm DO 20 | - | 1 | - | - | Read
18201 | 4 | Alarm DO 21 | - | 1 | - | - | Read
18201 | 5 | Alarm DO 22 | - | 1 | - | - | Read
18201 | 6 | Alarm DO 23 | - | 1 | - | - | Read
18201 | 7 | Alarm DO 24 | - | 1 | - | - | Read
18201 | 8 | Alarm DO 25 | - | 1 | - | - | Read
18201 | 9 | Alarm DO 26 | - | 1 | - | - | Read
18201 | 10 | Alarm DO 27 | - | 1 | - | - | Read
18201 | 11 | Alarm DO 28 | - | 1 | - | - | Read
18201 | 12 | Alarm DO 29 | - | 1 | - | - | Read
18201 | 13 | Alarm DO 30 | - | 1 | - | - | Read
18201 | 14 | Alarm DO 31 | - | 1 | - | - | Read
18201 | 15 | Alarm DO 32 | - | 1 | - | - | Read
18202 |  | Digital output function register 3
18202 | 0 | Alarm number DO 1 | - | 1 | - | - | Read
18202 | 1 | Alarm number DO 2 | - | 1 | - | - | Read
18202 | 2 | Alarm number DO 3 | - | 1 | - | - | Read
18202 | 3 | Alarm number DO 4 | - | 1 | - | - | Read
18202 | 4 | Alarm number DO 5 | - | 1 | - | - | Read
18202 | 5 | Alarm number DO 6 | - | 1 | - | - | Read
18202 | 6 | Alarm number DO 7 | - | 1 | - | - | Read
18202 | 7 | Alarm number DO 8 | - | 1 | - | - | Read
18202 | 8 | Alarm number DO 9 | - | 1 | - | - | Read
18202 | 9 | Alarm number DO 10 | - | 1 | - | - | Read
18202 | 10 | ON 1 | - | 1 | - | - | Read
18202 | 11 | ON 2 | - | 1 | - | - | Read
18202 | 12 | ON 3 | - | 1 | - | - | Read
18202 | 13 | ON 4 | - | 1 | - | - | Read
18202 | 14 | ON 5 | - | 1 | - | - | Read
18202 | 15 | ON 6 | - | 1 | - | - | Read
18203 |  | Digital output function register 4
18203 | 0 | ON 7 | - | 1 | - | - | Read
18203 | 1 | ON 8 | - | 1 | - | - | Read
18203 | 2 | ON 9 | - | 1 | - | - | Read
18203 | 3 | ON 10 | - | 1 | - | - | Read
18203 | 4 | Limit DO 1 | - | 1 | - | - | Read
18203 | 5 | Limit DO 2 | - | 1 | - | - | Read
18203 | 6 | Load Stage 1 | - | 1 | - | - | Read
18203 | 7 | Load Stage 2 | - | 1 | - | - | Read
18203 | 8 | Load Stage 3 | - | 1 | - | - | Read
18203 | 9 | Load stage 4 | - | 1 | - | - | Read
18203 | 10 | Load stage 5 | - | 1 | - | - | Read
18203 | 11 | Rearm safety chain | - | 1 | - | - | Read
18203 | 12 | Trip safety chain | - | 1 | - | - | Read
18203 | 13 | Reset ext. alarms | - | 1 | - | - | Read
18203 | 14 | AGC4: Reset grid protection | - | 1 | - | - | Read
18203 | 15 | Green lamp | - | 1 | - | - | Read
18204 |  | Digital output function register 5
18204 | 0 | Yellow lamp | - | 1 | - | - | Read
18204 | 1 | Red lamp | - | 1 | - | - | Read
18204 | 2 | Manual mode | - | 1 | - | - | Read
18204 | 3 | Semi-Auto mode | - | 1 | - | - | Read
18204 | 4 | Automatic mode | - | 1 | - | - | Read
18204 | 5 | State 'Available' | - | 1 | - | - | Read
18204 | 6 | State 'Ready to start' | - | 1 | - | - | Read
18204 | 7 | State 'Idle speed 1' | - | 1 | - | - | Read
18204 | 8 | State 'Idle speed 2' | - | 1 | - | - | Read
18204 | 9 | State 'Nominal speed' | - | 1 | - | - | Read
18204 | 10 | State 'Compressor' | - | 1 | - | - | Read
18204 | 11 | State 'Synchronizing' | - | 1 | - | - | Read
18204 | 12 | State 'Synchron connect' | - | 1 | - | - | Read
18204 | 13 | State 'Island' | - | 1 | - | - | Read
18204 | 14 | State 'Island parallel' | - | 1 | - | - | Read
18204 | 15 | State 'Grid parallel' | - | 1 | - | - | Read
18205 |  | Digital output function register 6
18205 | 0 | Turbine running | - | 1 | - | - | Read
18205 | 1 | Speed control active | - | 1 | - | - | Read
18205 | 2 | Frequency control active | - | 1 | - | - | Read
18205 | 3 | Position control active | - | 1 | - | - | Read
18205 | 4 | Power control active | - | 1 | - | - | Read
18205 | 5 | Live steam p control active | - | 1 | - | - | Read
18205 | 6 | Exh. steam p control active | - | 1 | - | - | Read
18205 | 7 | GCB On | - | 1 | - | - | Read
18205 | 8 | GCB Off | - | 1 | - | - | Read
18205 | 9 | GCB Trip | - | 1 | - | - | Read
18205 | 10 | GCB Release | - | 1 | - | - | Read
18205 | 11 | GCB Backup | - | 1 | - | - | Read
18205 | 12 | MCB Trip | - | 1 | - | - | Read
18205 | 13 | MCB Release | - | 1 | - | - | Read
18205 | 14 | Release AVR | - | 1 | - | - | Read
18205 | 15 | Release U=U | - | 1 | - | - | Read
18206 |  | Digital output function register 7
18206 | 0 | Release CosPhi control | - | 1 | - | - | Read
18206 | 1 | U/f Busbar is ok | - | 1 | - | - | Read
18206 | 2 | Overspeed tripped | - | 1 | - | - | Read
18206 | 3 | Island demand | - | 1 | - | - | Read
18206 | 4 | Wish black closing | - | 1 | - | - | Read
18206 | 5 | Release black closing | - | 1 | - | - | Read
18206 | 6 | Startprepare demand | - | 1 | - | - | Read
18206 | 7 | kWh pulse | - | 1 | - | - | Read
18206 | 8 | Time switch | - | 1 | - | - | Read
18206 | 9 | Limit switch speed < | - | 1 | - | - | Read
18206 | 10 | Limit switch speed > | - | 1 | - | - | Read
18206 | 11 | Limit switch power > | - | 1 | - | - | Read
18206 | 12 | Limit switch p live steam > | - | 1 | - | - | Read
18206 | 13 | Limit switch p exh. steam > | - | 1 | - | - | Read
18206 | 14 | Limit switch actuator output > | - | 1 | - | - | Read
18206 | 15 | Limit switch speed setpoint > | - | 1 | - | - | Read
18207 |  | Digital output function register 8
18207 | 0 | Cold start | - | 1 | - | - | Read
18207 | 1 | Hot start | - | 1 | - | - | Read
18207 | 2 | Warm start | - | 1 | - | - | Read
18207 | 3 | Bearing lubrication | - | 1 | - | - | Read
18207 | 4 | operation level > 1 | - | 1 | - | - | Read
18207 | 5 | turbine trip | - | 1 | - | - | Read
18207 | 6 | speed output 1 | - | 1 | - | - | Read
18207 | 7 | speed output 2 | - | 1 | - | - | Read
18207 | 8 | speed output 3 | - | 1 | - | - | Read
18207 | 9 | speed output 4 | - | 1 | - | - | Read
18207 | 10 | Extraction is allowed | - | 1 | - | - | Read
18207 | 11 | Extraction is active | - | 1 | - | - | Read
18207 | 12 | Extraction under regulation | - | 1 | - | - | Read
18207 | 13 | Extraction demand is analogue | - | 1 | - | - | Read
18207 | 14 | Ext. demand analogue is healthy | - | 1 | - | - | Read
19010 |  | Digital output function assignment register 1
19010 | 0 | Alarm inhibit 32 | - | 1 | - | - | Read
19010 | 1 | Emergency stop | - | 1 | - | - | Read
19010 | 2 | Watchdog | - | 1 | - | - | Read
19010 | 3 | Safety chain | - | 1 | - | - | Read
19010 | 4 | Pickup 1 | - | 1 | - | - | Read
19010 | 5 | Pickup 2 | - | 1 | - | - | Read
19010 | 6 | Acknowledge alarms | - | 1 | - | - | Read
19010 | 7 | Clear alarms | - | 1 | - | - | Read
19010 | 8 | Ack. / Clear alarms | - | 1 | - | - | Read
19010 | 9 | Select hot start | - | 1 | - | - | Read
19010 | 10 | Start preparation finished | - | 1 | - | - | Read
19010 | 11 | Start demand | - | 1 | - | - | Read
19010 | 12 | Stop demand | - | 1 | - | - | Read
19010 | 13 | Stop postrun | - | 1 | - | - | Read
19010 | 14 | Speed limit idle 1 | - | 1 | - | - | Read
19010 | 15 | Speed limit idle 2 | - | 1 | - | - | Read
19011 |  | Digital output function assignment register 2
19011 | 0 | No speed limit | - | 1 | - | - | Read
19011 | 1 | Overspeed test | - | 1 | - | - | Read
19011 | 2 | GCB opened | - | 1 | - | - | Read
19011 | 3 | GCB closed | - | 1 | - | - | Read
19011 | 4 | MCB opened | - | 1 | - | - | Read
19011 | 5 | MCB closed | - | 1 | - | - | Read
19011 | 6 | Island parallel | - | 1 | - | - | Read
19011 | 7 | Busbar is black | - | 1 | - | - | Read
19011 | 8 | Wish black closing | - | 1 | - | - | Read
19011 | 9 | Release black closing | - | 1 | - | - | Read
19011 | 10 | Enable operation | - | 1 | - | - | Read
19011 | 11 | Manual mode | - | 1 | - | - | Read
19011 | 12 | Semi-Auto mode | - | 1 | - | - | Read
19011 | 13 | Automatic mode | - | 1 | - | - | Read
19011 | 14 | Local / Remote | - | 1 | - | - | Read
19011 | 15 | Demand island operation | - | 1 | - | - | Read
19012 |  | Digital output function assignment register 3
19012 | 0 | Shutdown | - | 1 | - | - | Read
19012 | 1 | Power control (Load) | - | 1 | - | - | Read
19012 | 2 | Power control (Droop) | - | 1 | - | - | Read
19012 | 3 | Activate pressure control | - | 1 | - | - | Read
19012 | 4 | Remote pressure control | - | 1 | - | - | Read
19012 | 5 | Speed up | - | 1 | - | - | Read
19012 | 6 | Speed down | - | 1 | - | - | Read
19012 | 7 | Power up | - | 1 | - | - | Read
19012 | 8 | Power down | - | 1 | - | - | Read
19012 | 9 | Voltage up | - | 1 | - | - | Read
19012 | 10 | Voltage down | - | 1 | - | - | Read
19012 | 11 | Pressure up | - | 1 | - | - | Read
19012 | 12 | Pressure down | - | 1 | - | - | Read
19012 | 13 | Modbus write access | - | 1 | - | - | Read
19012 | 14 | Trending scope on | - | 1 | - | - | Read
19012 | 15 | Trending scope off | - | 1 | - | - | Read
19013 |  | Digital output function assignment register 4
19013 | 0 | Valve limiter open | - | 1 | - | - | Read
19013 | 1 | Valve limiter close | - | 1 | - | - | Read
19013 | 2 | Clock synchronization | - | 1 | - | - | Read
19013 | 3 | Bearing lubrication | - | 1 | - | - | Read
19013 | 4 | Clear power limitation | - | 1 | - | - | Read
19013 | 5 | LP valve limiter open | - | 1 | - | - | Read
19013 | 6 | LP valve limiter close | - | 1 | - | - | Read
19013 | 7 | Extraction demand up | - | 1 | - | - | Read
19013 | 8 | Extraction demand down | - | 1 | - | - | Read
19200 |  | Digital output function assignment register 5
19200 | 0 | Alarm DO 1 | - | 1 | - | - | Read
19200 | 1 | Alarm DO 2 | - | 1 | - | - | Read
19200 | 2 | Alarm DO 3 | - | 1 | - | - | Read
19200 | 3 | Alarm DO 4 | - | 1 | - | - | Read
19200 | 4 | Alarm DO 5 | - | 1 | - | - | Read
19200 | 5 | Alarm DO 6 | - | 1 | - | - | Read
19200 | 6 | Alarm DO 7 | - | 1 | - | - | Read
19200 | 7 | Alarm DO 8 | - | 1 | - | - | Read
19200 | 8 | Alarm DO 9 | - | 1 | - | - | Read
19200 | 9 | Alarm DO 10 | - | 1 | - | - | Read
19200 | 10 | Alarm DO 11 | - | 1 | - | - | Read
19200 | 11 | Alarm DO 12 | - | 1 | - | - | Read
19200 | 12 | Alarm DO 13 | - | 1 | - | - | Read
19200 | 13 | Alarm DO 14 | - | 1 | - | - | Read
19200 | 14 | Alarm DO 15 | - | 1 | - | - | Read
19200 | 15 | Alarm DO 16 | - | 1 | - | - | Read
19201 |  | Digital output function assignment register 6
19201 | 0 | Alarm DO 17 | - | 1 | - | - | Read
19201 | 1 | Alarm DO 18 | - | 1 | - | - | Read
19201 | 2 | Alarm DO 19 | - | 1 | - | - | Read
19201 | 3 | Alarm DO 20 | - | 1 | - | - | Read
19201 | 4 | Alarm DO 21 | - | 1 | - | - | Read
19201 | 5 | Alarm DO 22 | - | 1 | - | - | Read
19201 | 6 | Alarm DO 23 | - | 1 | - | - | Read
19201 | 7 | Alarm DO 24 | - | 1 | - | - | Read
19201 | 8 | Alarm DO 25 | - | 1 | - | - | Read
19201 | 9 | Alarm DO 26 | - | 1 | - | - | Read
19201 | 10 | Alarm DO 27 | - | 1 | - | - | Read
19201 | 11 | Alarm DO 28 | - | 1 | - | - | Read
19201 | 12 | Alarm DO 29 | - | 1 | - | - | Read
19201 | 13 | Alarm DO 30 | - | 1 | - | - | Read
19201 | 14 | Alarm DO 31 | - | 1 | - | - | Read
19201 | 15 | Alarm DO 32 | - | 1 | - | - | Read
19202 |  | Digital output function assignment register 7
19202 | 0 | Alarm number DO 1 | - | 1 | - | - | Read
19202 | 1 | Alarm number DO 2 | - | 1 | - | - | Read
19202 | 2 | Alarm number DO 3 | - | 1 | - | - | Read
19202 | 3 | Alarm number DO 4 | - | 1 | - | - | Read
19202 | 4 | Alarm number DO 5 | - | 1 | - | - | Read
19202 | 5 | Alarm number DO 6 | - | 1 | - | - | Read
19202 | 6 | Alarm number DO 7 | - | 1 | - | - | Read
19202 | 7 | Alarm number DO 8 | - | 1 | - | - | Read
19202 | 8 | Alarm number DO 9 | - | 1 | - | - | Read
19202 | 9 | Alarm number DO 10 | - | 1 | - | - | Read
19202 | 10 | ON 1 | - | 1 | - | - | Read
19202 | 11 | ON 2 | - | 1 | - | - | Read
19202 | 12 | ON 3 | - | 1 | - | - | Read
19202 | 13 | ON 4 | - | 1 | - | - | Read
19202 | 14 | ON 5 | - | 1 | - | - | Read
19202 | 15 | ON 6 | - | 1 | - | - | Read
19203 |  | Digital output function assignment register 8
19203 | 0 | ON 7 | - | 1 | - | - | Read
19203 | 1 | ON 8 | - | 1 | - | - | Read
19203 | 2 | ON 9 | - | 1 | - | - | Read
19203 | 3 | ON 10 | - | 1 | - | - | Read
19203 | 4 | Limit DO 1 | - | 1 | - | - | Read
19203 | 5 | Limit DO 2 | - | 1 | - | - | Read
19203 | 6 | Load Stage 1 | - | 1 | - | - | Read
19203 | 7 | Load Stage 2 | - | 1 | - | - | Read
19203 | 8 | Load Stage 3 | - | 1 | - | - | Read
19203 | 9 | Load stage 4 | - | 1 | - | - | Read
19203 | 10 | Load stage 5 | - | 1 | - | - | Read
19203 | 11 | Rearm safety chain | - | 1 | - | - | Read
19203 | 12 | Trip safety chain | - | 1 | - | - | Read
19203 | 13 | Reset ext. alarms | - | 1 | - | - | Read
19203 | 14 | AGC4: Reset grid protection | - | 1 | - | - | Read
19203 | 15 | Green lamp | - | 1 | - | - | Read

## 09_Temp. & AI Func.
#VALUE! | 18400-18816 & 19204-19820 - Temperature and Analog Input Function
Register | Bit | Text | Configuration | Resolution | Factor | Unit | Access
18400 |  | Temperature input function Conf. TMP 1 | - | 16 | 2025-10-01 | Â°C | Read
18401 |  | Temperature input function Conf. TMP 2 | - | 16 | 2025-10-01 | Â°C | Read
18402 |  | Temperature input function Conf. TMP 3 | - | 16 | 2025-10-01 | Â°C | Read
18403 |  | Temperature input function Conf. TMP 4 | - | 16 | 2025-10-01 | Â°C | Read
18404 |  | Temperature input function Conf. TMP 5 | - | 16 | 2025-10-01 | Â°C | Read
18405 |  | Temperature input function Conf. TMP 6 | - | 16 | 2025-10-01 | Â°C | Read
18406 |  | Temperature input function Conf. TMP 7 | - | 16 | 2025-10-01 | Â°C | Read
18407 |  | Temperature input function Conf. TMP 8 | - | 16 | 2025-10-01 | Â°C | Read
18408 |  | Temperature input function Conf. TMP 9 | - | 16 | 2025-10-01 | Â°C | Read
18409 |  | Temperature input function Conf. TMP 10 | - | 16 | 2025-10-01 | Â°C | Read
18410 |  | Temperature input function Conf. TMP 11 | - | 16 | 2025-10-01 | Â°C | Read
18411 |  | Temperature input function Conf. TMP 12 | - | 16 | 2025-10-01 | Â°C | Read
18412 |  | Temperature input function Conf. TMP 13 | - | 16 | 2025-10-01 | Â°C | Read
18413 |  | Temperature input function Conf. TMP 14 | - | 16 | 2025-10-01 | Â°C | Read
18414 |  | Temperature input function Conf. TMP 15 | - | 16 | 2025-10-01 | Â°C | Read
18415 |  | Temperature input function Conf. TMP 16 | - | 16 | 2025-10-01 | Â°C | Read
18416 |  | Temperature input function Conf. TMP 17 | - | 16 | 2025-10-01 | Â°C | Read
18417 |  | Temperature input function Conf. TMP 18 | - | 16 | 2025-10-01 | Â°C | Read
18418 |  | Temperature input function Conf. TMP 19 | - | 16 | 2025-10-01 | Â°C | Read
18419 |  | Temperature input function Conf. TMP 20 | - | 16 | 2025-10-01 | Â°C | Read
18420 |  | Temperature input function Conf. TMP 21 | - | 16 | 2025-10-01 | Â°C | Read
18421 |  | Temperature input function Conf. TMP 22 | - | 16 | 2025-10-01 | Â°C | Read
18422 |  | Temperature input function Conf. TMP 23 | - | 16 | 2025-10-01 | Â°C | Read
18423 |  | Temperature input function Conf. TMP 24 | - | 16 | 2025-10-01 | Â°C | Read
18424 |  | Temperature input function Conf. TMP 25 | - | 16 | 2025-10-01 | Â°C | Read
18425 |  | Temperature input function Conf. TMP 26 | - | 16 | 2025-10-01 | Â°C | Read
18426 |  | Temperature input function Conf. TMP 27 | - | 16 | 2025-10-01 | Â°C | Read
18427 |  | Temperature input function Conf. TMP 28 | - | 16 | 2025-10-01 | Â°C | Read
18428 |  | Temperature input function Conf. TMP 29 | - | 16 | 2025-10-01 | Â°C | Read
18429 |  | Temperature input function Conf. TMP 30 | - | 16 | 2025-10-01 | Â°C | Read
18430 |  | Temperature input function Conf. TMP 31 | - | 16 | 2025-10-01 | Â°C | Read
18431 |  | Temperature input function Conf. TMP 32 | - | 16 | 2025-10-01 | Â°C | Read
18432 |  | Temperature input function Conf. TMP 33 | - | 16 | 2025-10-01 | Â°C | Read
18433 |  | Temperature input function Conf. TMP 34 | - | 16 | 2025-10-01 | Â°C | Read
18434 |  | Temperature input function Conf. TMP 35 | - | 16 | 2025-10-01 | Â°C | Read
18435 |  | Temperature input function Conf. TMP 36 | - | 16 | 2025-10-01 | Â°C | Read
18436 |  | Temperature input function Conf. TMP 37 | - | 16 | 2025-10-01 | Â°C | Read
18437 |  | Temperature input function Conf. TMP 38 | - | 16 | 2025-10-01 | Â°C | Read
18438 |  | Temperature input function Conf. TMP 39 | - | 16 | 2025-10-01 | Â°C | Read
18439 |  | Temperature input function Conf. TMP 40 | - | 16 | 2025-10-01 | Â°C | Read
18440 |  | Temperature input function Conf. TMP 41 | - | 16 | 2025-10-01 | Â°C | Read
18441 |  | Temperature input function Conf. TMP 42 | - | 16 | 2025-10-01 | Â°C | Read
18442 |  | Temperature input function Conf. TMP 43 | - | 16 | 2025-10-01 | Â°C | Read
18443 |  | Temperature input function Conf. TMP 44 | - | 16 | 2025-10-01 | Â°C | Read
18444 |  | Temperature input function Conf. TMP 45 | - | 16 | 2025-10-01 | Â°C | Read
18445 |  | Temperature input function Conf. TMP 46 | - | 16 | 2025-10-01 | Â°C | Read
18446 |  | Temperature input function Conf. TMP 47 | - | 16 | 2025-10-01 | Â°C | Read
18447 |  | Temperature input function Conf. TMP 48 | - | 16 | 2025-10-01 | Â°C | Read
18448 |  | Temperature input function Conf. TMP 49 | - | 16 | 2025-10-01 | Â°C | Read
18449 |  | Temperature input function Conf. TMP 50 | - | 16 | 2025-10-01 | Â°C | Read
18450 |  | Temperature input function Conf. TMP 51 | - | 16 | 2025-10-01 | Â°C | Read
18451 |  | Temperature input function Conf. TMP 52 | - | 16 | 2025-10-01 | Â°C | Read
18452 |  | Temperature input function Conf. TMP 53 | - | 16 | 2025-10-01 | Â°C | Read
18453 |  | Temperature input function Conf. TMP 54 | - | 16 | 2025-10-01 | Â°C | Read
18454 |  | Temperature input function Conf. TMP 55 | - | 16 | 2025-10-01 | Â°C | Read
18455 |  | Temperature input function Conf. TMP 56 | - | 16 | 2025-10-01 | Â°C | Read
18456 |  | Temperature input function Conf. TMP 57 | - | 16 | 2025-10-01 | Â°C | Read
18457 |  | Temperature input function Conf. TMP 58 | - | 16 | 2025-10-01 | Â°C | Read
18458 |  | Temperature input function Conf. TMP 59 | - | 16 | 2025-10-01 | Â°C | Read
18459 |  | Temperature input function Conf. TMP 60 | - | 16 | 2025-10-01 | Â°C | Read
18460 |  | Temperature input function Conf. TMP 61 | - | 16 | 2025-10-01 | Â°C | Read
18461 |  | Temperature input function Conf. TMP 62 | - | 16 | 2025-10-01 | Â°C | Read
18462 |  | Temperature input function Conf. TMP 63 | - | 16 | 2025-10-01 | Â°C | Read
18463 |  | Temperature input function Conf. TMP 64 | - | 16 | 2025-10-01 | Â°C | Read
18464 |  | Temperature input function Conf. TMP 65 | - | 16 | 2025-10-01 | Â°C | Read
18465 |  | Temperature input function Conf. TMP 66 | - | 16 | 2025-10-01 | Â°C | Read
18466 |  | Temperature input function Conf. TMP 67 | - | 16 | 2025-10-01 | Â°C | Read
18467 |  | Temperature input function Conf. TMP 68 | - | 16 | 2025-10-01 | Â°C | Read
18468 |  | Temperature input function Conf. TMP 69 | - | 16 | 2025-10-01 | Â°C | Read
18469 |  | Temperature input function Conf. TMP 70 | - | 16 | 2025-10-01 | Â°C | Read
18470 |  | Temperature input function Conf. TMP 71 | - | 16 | 2025-10-01 | Â°C | Read
18471 |  | Temperature input function Conf. TMP 72 | - | 16 | 2025-10-01 | Â°C | Read
18472 |  | Temperature input function Cold junction A | - | 16 | 2025-10-01 | Â°C | Read
18473 |  | Temperature input function Cold junction B | - | 16 | 2025-10-01 | Â°C | Read
18600 |  | Analog input function Conf. AI 1 [Highbyte] | - | 32 | 1/100 | Bar | Read
18601 |  | Analog input function Conf. AI 1 [Lowbyte] | - | 32 | 1/100 | Bar | Read
18602 |  | Analog input function Conf. AI 2 [Highbyte] | - | 32 | 1/100 | --- | Read
18603 |  | Analog input function Conf. AI 2 [Lowbyte] | - | 32 | 1/100 | --- | Read
18604 |  | Analog input function Conf. AI 3 [Highbyte] | - | 32 | 1/100 | --- | Read
18605 |  | Analog input function Conf. AI 3 [Lowbyte] | - | 32 | 1/100 | --- | Read
18606 |  | Analog input function Conf. AI 4 [Highbyte] | - | 32 | 1/100 | --- | Read
18607 |  | Analog input function Conf. AI 4 [Lowbyte] | - | 32 | 1/100 | --- | Read
18608 |  | Analog input function Conf. AI 5 [Highbyte] | - | 32 | 1/100 | --- | Read
18609 |  | Analog input function Conf. AI 5 [Lowbyte] | - | 32 | 1/100 | --- | Read
18610 |  | Analog input function Conf. AI 6 [Highbyte] | - | 32 | 1/100 | --- | Read
18611 |  | Analog input function Conf. AI 6 [Lowbyte] | - | 32 | 1/100 | --- | Read
18612 |  | Analog input function Conf. AI 7 [Highbyte] | - | 32 | 1/100 | --- | Read
18613 |  | Analog input function Conf. AI 7 [Lowbyte] | - | 32 | 1/100 | --- | Read
18614 |  | Analog input function Conf. AI 8 [Highbyte] | - | 32 | 1/100 | --- | Read
18615 |  | Analog input function Conf. AI 8 [Lowbyte] | - | 32 | 1/100 | --- | Read
18616 |  | Analog input function Conf. AI 9 [Highbyte] | - | 32 | 1/100 | --- | Read
18617 |  | Analog input function Conf. AI 9 [Lowbyte] | - | 32 | 1/100 | --- | Read
18618 |  | Analog input function Conf. AI 10 [Highbyte] | - | 32 | 1/100 | --- | Read
18619 |  | Analog input function Conf. AI 10 [Lowbyte] | - | 32 | 1/100 | --- | Read
18620 |  | Analog input function Conf. AI 11 [Highbyte] | - | 32 | 1/100 | --- | Read
18621 |  | Analog input function Conf. AI 11 [Lowbyte] | - | 32 | 1/100 | --- | Read
18622 |  | Analog input function Conf. AI 12 [Highbyte] | - | 32 | 1/100 | --- | Read
18623 |  | Analog input function Conf. AI 12 [Lowbyte] | - | 32 | 1/100 | --- | Read
18624 |  | Analog input function Conf. AI 13 [Highbyte] | - | 32 | 1/100 | --- | Read
18625 |  | Analog input function Conf. AI 13 [Lowbyte] | - | 32 | 1/100 | --- | Read
18626 |  | Analog input function Conf. AI 14 [Highbyte] | - | 32 | 1/100 | --- | Read
18627 |  | Analog input function Conf. AI 14 [Lowbyte] | - | 32 | 1/100 | --- | Read
18628 |  | Analog input function Conf. AI 15 [Highbyte] | - | 32 | 1/100 | --- | Read
18629 |  | Analog input function Conf. AI 15 [Lowbyte] | - | 32 | 1/100 | --- | Read
18630 |  | Analog input function Conf. AI 16 [Highbyte] | - | 32 | 1/100 | --- | Read
18631 |  | Analog input function Conf. AI 16 [Lowbyte] | - | 32 | 1/100 | --- | Read
18632 |  | Analog input function Conf. AI 17 [Highbyte] | - | 32 | 1/100 | --- | Read
18633 |  | Analog input function Conf. AI 17 [Lowbyte] | - | 32 | 1/100 | --- | Read
18634 |  | Analog input function Conf. AI 18 [Highbyte] | - | 32 | 1/100 | --- | Read
18635 |  | Analog input function Conf. AI 18 [Lowbyte] | - | 32 | 1/100 | --- | Read
18636 |  | Analog input function Conf. AI 19 [Highbyte] | - | 32 | 1/100 | --- | Read
18637 |  | Analog input function Conf. AI 19 [Lowbyte] | - | 32 | 1/100 | --- | Read
18638 |  | Analog input function Conf. AI 20 [Highbyte] | - | 32 | 1/100 | --- | Read
18639 |  | Analog input function Conf. AI 20 [Lowbyte] | - | 32 | 1/100 | --- | Read
18640 |  | Analog input function Conf. AI 21 [Highbyte] | - | 32 | 1/100 | --- | Read
18641 |  | Analog input function Conf. AI 21 [Lowbyte] | - | 32 | 1/100 | --- | Read
18642 |  | Analog input function Conf. AI 22 [Highbyte] | - | 32 | 1/100 | --- | Read
18643 |  | Analog input function Conf. AI 22 [Lowbyte] | - | 32 | 1/100 | --- | Read
18644 |  | Analog input function Conf. AI 23 [Highbyte] | - | 32 | 1/100 | --- | Read
18645 |  | Analog input function Conf. AI 23 [Lowbyte] | - | 32 | 1/100 | --- | Read
18646 |  | Analog input function Conf. AI 24 [Highbyte] | - | 32 | 1/100 | --- | Read
18647 |  | Analog input function Conf. AI 24 [Lowbyte] | - | 32 | 1/100 | --- | Read
18648 |  | Analog input function Conf. AI 25 [Highbyte] | - | 32 | 1/100 | --- | Read
18649 |  | Analog input function Conf. AI 25 [Lowbyte] | - | 32 | 1/100 | --- | Read
18650 |  | Analog input function Conf. AI 26 [Highbyte] | - | 32 | 1/100 | --- | Read
18651 |  | Analog input function Conf. AI 26 [Lowbyte] | - | 32 | 1/100 | --- | Read
18652 |  | Analog input function Conf. AI 27 [Highbyte] | - | 32 | 1/100 | --- | Read
18653 |  | Analog input function Conf. AI 27 [Lowbyte] | - | 32 | 1/100 | --- | Read
18654 |  | Analog input function Conf. AI 28 [Highbyte] | - | 32 | 1/100 | --- | Read
18655 |  | Analog input function Conf. AI 28 [Lowbyte] | - | 32 | 1/100 | --- | Read
18656 |  | Analog input function Conf. AI 29 [Highbyte] | - | 32 | 1/100 | --- | Read
18657 |  | Analog input function Conf. AI 29 [Lowbyte] | - | 32 | 1/100 | --- | Read
18658 |  | Analog input function Conf. AI 30 [Highbyte] | - | 32 | 1/100 | --- | Read
18659 |  | Analog input function Conf. AI 30 [Lowbyte] | - | 32 | 1/100 | --- | Read
18660 |  | Analog input function Conf. AI 31 [Highbyte] | - | 32 | 1/100 | --- | Read
18661 |  | Analog input function Conf. AI 31 [Lowbyte] | - | 32 | 1/100 | --- | Read
18662 |  | Analog input function Conf. AI 32 [Highbyte] | - | 32 | 1/100 | --- | Read
18663 |  | Analog input function Conf. AI 32 [Lowbyte] | - | 32 | 1/100 | --- | Read
18664 |  | Analog input function Conf. AI 33 [Highbyte] | - | 32 | 1/100 | --- | Read
18665 |  | Analog input function Conf. AI 33 [Lowbyte] | - | 32 | 1/100 | --- | Read
18666 |  | Analog input function Conf. AI 34 [Highbyte] | - | 32 | 1/100 | --- | Read
18667 |  | Analog input function Conf. AI 34 [Lowbyte] | - | 32 | 1/100 | --- | Read
18668 |  | Analog input function Conf. AI 35 [Highbyte] | - | 32 | 1/100 | --- | Read
18669 |  | Analog input function Conf. AI 35 [Lowbyte] | - | 32 | 1/100 | --- | Read
18670 |  | Analog input function Conf. AI 36 [Highbyte] | - | 32 | 1/100 | --- | Read
18671 |  | Analog input function Conf. AI 36 [Lowbyte] | - | 32 | 1/100 | --- | Read
18672 |  | Analog input function Conf. AI 37 [Highbyte] | - | 32 | 1/100 | --- | Read
18673 |  | Analog input function Conf. AI 37 [Lowbyte] | - | 32 | 1/100 | --- | Read
18674 |  | Analog input function Conf. AI 38 [Highbyte] | - | 32 | 1/100 | --- | Read
18675 |  | Analog input function Conf. AI 38 [Lowbyte] | - | 32 | 1/100 | --- | Read
18676 |  | Analog input function Conf. AI 39 [Highbyte] | - | 32 | 1/100 | --- | Read
18677 |  | Analog input function Conf. AI 39 [Lowbyte] | - | 32 | 1/100 | --- | Read
18678 |  | Analog input function Conf. AI 40 [Highbyte] | - | 32 | 1/100 | --- | Read
18679 |  | Analog input function Conf. AI 40 [Lowbyte] | - | 32 | 1/100 | --- | Read
18680 |  | Analog input function Conf. AI 41 [Highbyte] | - | 32 | 1/100 | --- | Read
18681 |  | Analog input function Conf. AI 41 [Lowbyte] | - | 32 | 1/100 | --- | Read
18682 |  | Analog input function Conf. AI 42 [Highbyte] | - | 32 | 1/100 | --- | Read
18683 |  | Analog input function Conf. AI 42 [Lowbyte] | - | 32 | 1/100 | --- | Read
18684 |  | Analog input function Conf. AI 43 [Highbyte] | - | 32 | 1/100 | --- | Read
18685 |  | Analog input function Conf. AI 43 [Lowbyte] | - | 32 | 1/100 | --- | Read
18686 |  | Analog input function Conf. AI 44 [Highbyte] | - | 32 | 1/100 | --- | Read
18687 |  | Analog input function Conf. AI 44 [Lowbyte] | - | 32 | 1/100 | --- | Read
18688 |  | Analog input function Conf. AI 45 [Highbyte] | - | 32 | 1/100 | --- | Read
18689 |  | Analog input function Conf. AI 45 [Lowbyte] | - | 32 | 1/100 | --- | Read
18690 |  | Analog input function Conf. AI 46 [Highbyte] | - | 32 | 1/100 | --- | Read
18691 |  | Analog input function Conf. AI 46 [Lowbyte] | - | 32 | 1/100 | --- | Read
18692 |  | Analog input function Conf. AI 47 [Highbyte] | - | 32 | 1/100 | --- | Read
18693 |  | Analog input function Conf. AI 47 [Lowbyte] | - | 32 | 1/100 | --- | Read
18694 |  | Analog input function Conf. AI 48 [Highbyte] | - | 32 | 1/100 | --- | Read
18695 |  | Analog input function Conf. AI 48 [Lowbyte] | - | 32 | 1/100 | --- | Read
18696 |  | Analog input function Limit switch input (1) | - | 16 | 1/1250 | mA | Read
18697 |  | Analog input function Limit switch input (2) | - | 16 | 1/1250 | mA | Read
18698 |  | Analog input function Generator power [Highbyte] | - | 32 | - | W | Read
18699 |  | Analog input function Generator power [Lowbyte] | - | 32 | - | W | Read
18700 |  | Analog input function Demanded power [Highbyte] | - | 32 | - | W | Read
18701 |  | Analog input function Demanded power [Lowbyte] | - | 32 | - | W | Read
18702 |  | Analog input function Power limitation [Highbyte] | - | 32 | - | W | Read
18703 |  | Analog input function Power limitation [Lowbyte] | - | 32 | - | W | Read
18704 |  | Analog input function Speed adjustment [Highbyte] | - | 32 | - | - | Read
18705 |  | Analog input function Speed adjustment [Lowbyte] | - | 32 | - | - | Read
18706 |  | Analog output function PID output 1 | - |  |  |  | Read
18800 |  | Analog output function PID output 2 | - | 16 | 1/1250 | mA | Read
18801 |  | Analog output function PID output 3 | - | 16 | 1/1250 | mA | Read
18802 |  | Analog output function PID output 4 | - | 16 | 1/1250 | mA | Read
18803 |  | Analog output function PID output 5 | - | 16 | 1/1250 | mA | Read
18804 |  | Analog output function Steam valve | - | 16 | 1/1250 | mA | Read
18805 |  | Analog output function Voltage regulator | - | 16 | 1/1250 | mA | Read
18806 |  | Analog output function V instrument | - | 16 | 1/1250 | mA | Read
18807 |  | Analog output function kvar instrument | - | 16 | 1/1250 | mA | Read
18808 |  | Analog output function kW instrument | - | 16 | 1/1250 | mA | Read
18809 |  | Analog output function Maximum allowed load | - | 16 | 1/1250 | mA | Read
18810 |  | Analog output function Power setpoint | - | 16 | 1/1250 | mA | Read
18811 |  | Analog output function Speed | - | 16 | 1/1250 | mA | Read
18812 |  | Analog output function Speed setpoint | - | 16 | 1/1250 | mA | Read
18813 |  | Analog output function Live steam pressure | - | 16 | 1/1250 | mA | Read
18814 |  | Analog output function Live steam press. setp. | - | 16 | 1/1250 | mA | Read
18815 |  | Analog output function Exhaust steam pressure | - | 16 | 1/1250 | mA | Read
18816 |  | Analog output function Exh. steam press. setp. | - | 16 | 1/1250 | mA | Read
19204 |  | Temperature input info Conf. TMP 1
19204 | 0 | Yellow lamp | - | 1 | - | - | Read
19204 | 1 | Red lamp | - | 1 | - | - | Read
19204 | 2 | Manual mode | - | 1 | - | - | Read
19204 | 3 | Semi-Auto mode | - | 1 | - | - | Read
19204 | 4 | Automatic mode | - | 1 | - | - | Read
19204 | 5 | State 'Available' | - | 1 | - | - | Read
19204 | 6 | State 'Ready to start' | - | 1 | - | - | Read
19204 | 7 | State 'Idle speed 1' | - | 1 | - | - | Read
19204 | 8 | State 'Idle speed 2' | - | 1 | - | - | Read
19204 | 9 | State 'Nominal speed' | - | 1 | - | - | Read
19204 | 10 | State 'Compressor' | - | 1 | - | - | Read
19204 | 11 | State 'Synchronizing' | - | 1 | - | - | Read
19204 | 12 | State 'Synchron connect' | - | 1 | - | - | Read
19204 | 13 | State 'Island' | - | 1 | - | - | Read
19204 | 14 | State 'Island parallel' | - | 1 | - | - | Read
19204 | 15 | State 'Grid parallel' | - | 1 | - | - | Read
19205 |  | Temperature input info Conf. TMP 2
19205 | 0 | Turbine running | - | 1 | - | - | Read
19205 | 1 | Speed control active | - | 1 | - | - | Read
19205 | 2 | Frequency control active | - | 1 | - | - | Read
19205 | 3 | Position control active | - | 1 | - | - | Read
19205 | 4 | Power control active | - | 1 | - | - | Read
19205 | 5 | Live steam p control active | - | 1 | - | - | Read
19205 | 6 | Exh. steam p control active | - | 1 | - | - | Read
19205 | 7 | GCB On | - | 1 | - | - | Read
19205 | 8 | GCB Off | - | 1 | - | - | Read
19205 | 9 | GCB Trip | - | 1 | - | - | Read
19205 | 10 | GCB Release | - | 1 | - | - | Read
19205 | 11 | GCB Backup | - | 1 | - | - | Read
19205 | 12 | MCB Trip | - | 1 | - | - | Read
19205 | 13 | MCB Release | - | 1 | - | - | Read
19205 | 14 | Release AVR | - | 1 | - | - | Read
19205 | 15 | Release U=U | - | 1 | - | - | Read
19206 |  | Temperature input info Conf. TMP 3
19206 | 0 | Release CosPhi control | - | 1 | - | - | Read
19206 | 1 | U/f Busbar is ok | - | 1 | - | - | Read
19206 | 2 | Overspeed tripped | - | 1 | - | - | Read
19206 | 3 | Island demand | - | 1 | - | - | Read
19206 | 4 | Wish black closing | - | 1 | - | - | Read
19206 | 5 | Release black closing | - | 1 | - | - | Read
19206 | 6 | Startprepare demand | - | 1 | - | - | Read
19206 | 7 | kWh pulse | - | 1 | - | - | Read
19206 | 8 | Time switch | - | 1 | - | - | Read
19206 | 9 | Limit switch speed < | - | 1 | - | - | Read
19206 | 10 | Limit switch speed > | - | 1 | - | - | Read
19206 | 11 | Limit switch power > | - | 1 | - | - | Read
19206 | 12 | Limit switch p live steam > | - | 1 | - | - | Read
19206 | 13 | Limit switch p exh. steam > | - | 1 | - | - | Read
19206 | 14 | Limit switch actuator output > | - | 1 | - | - | Read
19206 | 15 | Limit switch speed setpoint > | - | 1 | - | - | Read
19207 |  | Temperature input info Conf. TMP 4
19207 | 0 | Cold start | - | 1 | - | - | Read
19207 | 1 | Hot start | - | 1 | - | - | Read
19207 | 2 | Warm start | - | 1 | - | - | Read
19207 | 3 | Bearing lubrication | - | 1 | - | - | Read
19207 | 4 | operation level > 1 | - | 1 | - | - | Read
19207 | 5 | turbine trip | - | 1 | - | - | Read
19207 | 6 | speed output 1 | - | 1 | - | - | Read
19207 | 7 | speed output 2 | - | 1 | - | - | Read
19207 | 8 | speed output 3 | - | 1 | - | - | Read
19207 | 9 | speed output 4 | - | 1 | - | - | Read
19207 | 10 | Extraction is allowed | - | 1 | - | - | Read
19207 | 11 | Extraction is active | - | 1 | - | - | Read
19207 | 12 | Extraction under regulation | - | 1 | - | - | Read
19207 | 13 | Extraction demand is analogue | - | 1 | - | - | Read
19207 | 14 | Ext. demand analogue is healthy | - | 1 | - | - | Read
19400 |  | Temperature input info Conf. TMP 5
19400 | 0 | Assigned | - | 1 | - | - | Read
19400 | 1 | Wirebreak | - | 1 | - | - | Read
19400 | 2 | Shortcircuit | - | 1 | - | - | Read
19401 |  | Temperature input info Conf. TMP 6
19401 | 0 | Assigned | - | 1 | - | - | Read
19401 | 1 | Wirebreak | - | 1 | - | - | Read
19401 | 2 | Shortcircuit | - | 1 | - | - | Read
19402 |  | Temperature input info Conf. TMP 7
19402 | 0 | Assigned | - | 1 | - | - | Read
19402 | 1 | Wirebreak | - | 1 | - | - | Read
19402 | 2 | Shortcircuit | - | 1 | - | - | Read
19403 |  | Temperature input info Conf. TMP 8
19403 | 0 | Assigned | - | 1 | - | - | Read
19403 | 1 | Wirebreak | - | 1 | - | - | Read
19403 | 2 | Shortcircuit | - | 1 | - | - | Read
19404 |  | Temperature input info Conf. TMP 9
19404 | 0 | Assigned | - | 1 | - | - | Read
19404 | 1 | Wirebreak | - | 1 | - | - | Read
19404 | 2 | Shortcircuit | - | 1 | - | - | Read
19405 |  | Temperature input info Conf. TMP 10
19405 | 0 | Assigned | - | 1 | - | - | Read
19405 | 1 | Wirebreak | - | 1 | - | - | Read
19405 | 2 | Shortcircuit | - | 1 | - | - | Read
19406 |  | Temperature input info Conf. TMP 11
19406 | 0 | Assigned | - | 1 | - | - | Read
19406 | 1 | Wirebreak | - | 1 | - | - | Read
19406 | 2 | Shortcircuit | - | 1 | - | - | Read
19407 |  | Temperature input info Conf. TMP 12
19407 | 0 | Assigned | - | 1 | - | - | Read
19407 | 1 | Wirebreak | - | 1 | - | - | Read
19407 | 2 | Shortcircuit | - | 1 | - | - | Read
19408 |  | Temperature input info Conf. TMP 13
19408 | 0 | Assigned | - | 1 | - | - | Read
19408 | 1 | Wirebreak | - | 1 | - | - | Read
19408 | 2 | Shortcircuit | - | 1 | - | - | Read
19409 |  | Temperature input info Conf. TMP 14
19409 | 0 | Assigned | - | 1 | - | - | Read
19409 | 1 | Wirebreak | - | 1 | - | - | Read
19409 | 2 | Shortcircuit | - | 1 | - | - | Read
19410 |  | Temperature input info Conf. TMP 15
19410 | 0 | Assigned | - | 1 | - | - | Read
19410 | 1 | Wirebreak | - | 1 | - | - | Read
19410 | 2 | Shortcircuit | - | 1 | - | - | Read
19411 |  | Temperature input info Conf. TMP 16
19411 | 0 | Assigned | - | 1 | - | - | Read
19411 | 1 | Wirebreak | - | 1 | - | - | Read
19411 | 2 | Shortcircuit | - | 1 | - | - | Read
19412 |  | Temperature input info Conf. TMP 17
19412 | 0 | Assigned | - | 1 | - | - | Read
19412 | 1 | Wirebreak | - | 1 | - | - | Read
19412 | 2 | Shortcircuit | - | 1 | - | - | Read
19413 |  | Temperature input info Conf. TMP 18
19413 | 0 | Assigned | - | 1 | - | - | Read
19413 | 1 | Wirebreak | - | 1 | - | - | Read
19413 | 2 | Shortcircuit | - | 1 | - | - | Read
19414 |  | Temperature input info Conf. TMP 19
19414 | 0 | Assigned | - | 1 | - | - | Read
19414 | 1 | Wirebreak | - | 1 | - | - | Read
19414 | 2 | Shortcircuit | - | 1 | - | - | Read
19415 |  | Temperature input info Conf. TMP 20
19415 | 0 | Assigned | - | 1 | - | - | Read
19415 | 1 | Wirebreak | - | 1 | - | - | Read
19415 | 2 | Shortcircuit | - | 1 | - | - | Read
19416 |  | Temperature input info Conf. TMP 21
19416 | 0 | Assigned | - | 1 | - | - | Read
19416 | 1 | Wirebreak | - | 1 | - | - | Read
19416 | 2 | Shortcircuit | - | 1 | - | - | Read
19417 |  | Temperature input info Conf. TMP 22
19417 | 0 | Assigned | - | 1 | - | - | Read
19417 | 1 | Wirebreak | - | 1 | - | - | Read
19417 | 2 | Shortcircuit | - | 1 | - | - | Read
19418 |  | Temperature input info Conf. TMP 23
19418 | 0 | Assigned | - | 1 | - | - | Read
19418 | 1 | Wirebreak | - | 1 | - | - | Read
19418 | 2 | Shortcircuit | - | 1 | - | - | Read
19419 |  | Temperature input info Conf. TMP 24
19419 | 0 | Assigned | - | 1 | - | - | Read
19419 | 1 | Wirebreak | - | 1 | - | - | Read
19419 | 2 | Shortcircuit | - | 1 | - | - | Read
19420 |  | Temperature input info Conf. TMP 25
19420 | 0 | Assigned | - | 1 | - | - | Read
19420 | 1 | Wirebreak | - | 1 | - | - | Read
19420 | 2 | Shortcircuit | - | 1 | - | - | Read
19421 |  | Temperature input info Conf. TMP 26
19421 | 0 | Assigned | - | 1 | - | - | Read
19421 | 1 | Wirebreak | - | 1 | - | - | Read
19421 | 2 | Shortcircuit | - | 1 | - | - | Read
19422 |  | Temperature input info Conf. TMP 27
19422 | 0 | Assigned | - | 1 | - | - | Read
19422 | 1 | Wirebreak | - | 1 | - | - | Read
19422 | 2 | Shortcircuit | - | 1 | - | - | Read
19423 |  | Temperature input info Conf. TMP 28
19423 | 0 | Assigned | - | 1 | - | - | Read
19423 | 1 | Wirebreak | - | 1 | - | - | Read
19423 | 2 | Shortcircuit | - | 1 | - | - | Read
19424 |  | Temperature input info Conf. TMP 29
19424 | 0 | Assigned | - | 1 | - | - | Read
19424 | 1 | Wirebreak | - | 1 | - | - | Read
19424 | 2 | Shortcircuit | - | 1 | - | - | Read
19425 |  | Temperature input info Conf. TMP 30
19425 | 0 | Assigned | - | 1 | - | - | Read
19425 | 1 | Wirebreak | - | 1 | - | - | Read
19425 | 2 | Shortcircuit | - | 1 | - | - | Read
19426 |  | Temperature input info Conf. TMP 31
19426 | 0 | Assigned | - | 1 | - | - | Read
19426 | 1 | Wirebreak | - | 1 | - | - | Read
19426 | 2 | Shortcircuit | - | 1 | - | - | Read
19427 |  | Temperature input info Conf. TMP 32
19427 | 0 | Assigned | - | 1 | - | - | Read
19427 | 1 | Wirebreak | - | 1 | - | - | Read
19427 | 2 | Shortcircuit | - | 1 | - | - | Read
19428 |  | Temperature input info Conf. TMP 33
19428 | 0 | Assigned | - | 1 | - | - | Read
19428 | 1 | Wirebreak | - | 1 | - | - | Read
19428 | 2 | Shortcircuit | - | 1 | - | - | Read
19429 |  | Temperature input info Conf. TMP 34
19429 | 0 | Assigned | - | 1 | - | - | Read
19429 | 1 | Wirebreak | - | 1 | - | - | Read
19429 | 2 | Shortcircuit | - | 1 | - | - | Read
19430 |  | Temperature input info Conf. TMP 35
19430 | 0 | Assigned | - | 1 | - | - | Read
19430 | 1 | Wirebreak | - | 1 | - | - | Read
19430 | 2 | Shortcircuit | - | 1 | - | - | Read
19431 |  | Temperature input info Conf. TMP 36
19431 | 0 | Assigned | - | 1 | - | - | Read
19431 | 1 | Wirebreak | - | 1 | - | - | Read
19431 | 2 | Shortcircuit | - | 1 | - | - | Read
19432 |  | Temperature input info Conf. TMP 37
19432 | 0 | Assigned | - | 1 | - | - | Read
19432 | 1 | Wirebreak | - | 1 | - | - | Read
19432 | 2 | Shortcircuit | - | 1 | - | - | Read
19433 |  | Temperature input info Conf. TMP 38
19433 | 0 | Assigned | - | 1 | - | - | Read
19433 | 1 | Wirebreak | - | 1 | - | - | Read
19433 | 2 | Shortcircuit | - | 1 | - | - | Read
19434 |  | Temperature input info Conf. TMP 39
19434 | 0 | Assigned | - | 1 | - | - | Read
19434 | 1 | Wirebreak | - | 1 | - | - | Read
19434 | 2 | Shortcircuit | - | 1 | - | - | Read
19435 |  | Temperature input info Conf. TMP 40
19435 | 0 | Assigned | - | 1 | - | - | Read
19435 | 1 | Wirebreak | - | 1 | - | - | Read
19435 | 2 | Shortcircuit | - | 1 | - | - | Read
19436 |  | Temperature input info Conf. TMP 41
19436 | 0 | Assigned | - | 1 | - | - | Read
19436 | 1 | Wirebreak | - | 1 | - | - | Read
19436 | 2 | Shortcircuit | - | 1 | - | - | Read
19437 |  | Temperature input info Conf. TMP 42
19437 | 0 | Assigned | - | 1 | - | - | Read
19437 | 1 | Wirebreak | - | 1 | - | - | Read
19437 | 2 | Shortcircuit | - | 1 | - | - | Read
19438 |  | Temperature input info Conf. TMP 43
19438 | 0 | Assigned | - | 1 | - | - | Read
19438 | 1 | Wirebreak | - | 1 | - | - | Read
19438 | 2 | Shortcircuit | - | 1 | - | - | Read
19439 |  | Temperature input info Conf. TMP 44
19439 | 0 | Assigned | - | 1 | - | - | Read
19439 | 1 | Wirebreak | - | 1 | - | - | Read
19439 | 2 | Shortcircuit | - | 1 | - | - | Read
19440 |  | Temperature input info Conf. TMP 45
19440 | 0 | Assigned | - | 1 | - | - | Read
19440 | 1 | Wirebreak | - | 1 | - | - | Read
19440 | 2 | Shortcircuit | - | 1 | - | - | Read
19441 |  | Temperature input info Conf. TMP 46
19441 | 0 | Assigned | - | 1 | - | - | Read
19441 | 1 | Wirebreak | - | 1 | - | - | Read
19441 | 2 | Shortcircuit | - | 1 | - | - | Read
19442 |  | Temperature input info Conf. TMP 47
19442 | 0 | Assigned | - | 1 | - | - | Read
19442 | 1 | Wirebreak | - | 1 | - | - | Read
19442 | 2 | Shortcircuit | - | 1 | - | - | Read
19443 |  | Temperature input info Conf. TMP 48
19443 | 0 | Assigned | - | 1 | - | - | Read
19443 | 1 | Wirebreak | - | 1 | - | - | Read
19443 | 2 | Shortcircuit | - | 1 | - | - | Read
19444 |  | Temperature input info Conf. TMP 49
19444 | 0 | Assigned | - | 1 | - | - | Read
19444 | 1 | Wirebreak | - | 1 | - | - | Read
19444 | 2 | Shortcircuit | - | 1 | - | - | Read
19445 |  | Temperature input info Conf. TMP 50
19445 | 0 | Assigned | - | 1 | - | - | Read
19445 | 1 | Wirebreak | - | 1 | - | - | Read
19445 | 2 | Shortcircuit | - | 1 | - | - | Read
19446 |  | Temperature input info Conf. TMP 51
19446 | 0 | Assigned | - | 1 | - | - | Read
19446 | 1 | Wirebreak | - | 1 | - | - | Read
19446 | 2 | Shortcircuit | - | 1 | - | - | Read
19447 |  | Temperature input info Conf. TMP 52
19447 | 0 | Assigned | - | 1 | - | - | Read
19447 | 1 | Wirebreak | - | 1 | - | - | Read
19447 | 2 | Shortcircuit | - | 1 | - | - | Read
19448 |  | Temperature input info Conf. TMP 53
19448 | 0 | Assigned | - | 1 | - | - | Read
19448 | 1 | Wirebreak | - | 1 | - | - | Read
19448 | 2 | Shortcircuit | - | 1 | - | - | Read
19449 |  | Temperature input info Conf. TMP 54
19449 | 0 | Assigned | - | 1 | - | - | Read
19449 | 1 | Wirebreak | - | 1 | - | - | Read
19449 | 2 | Shortcircuit | - | 1 | - | - | Read
19450 |  | Temperature input info Conf. TMP 55
19450 | 0 | Assigned | - | 1 | - | - | Read
19450 | 1 | Wirebreak | - | 1 | - | - | Read
19450 | 2 | Shortcircuit | - | 1 | - | - | Read
19451 |  | Temperature input info Conf. TMP 56
19451 | 0 | Assigned | - | 1 | - | - | Read
19451 | 1 | Wirebreak | - | 1 | - | - | Read
19451 | 2 | Shortcircuit | - | 1 | - | - | Read
19452 |  | Temperature input info Conf. TMP 57
19452 | 0 | Assigned | - | 1 | - | - | Read
19452 | 1 | Wirebreak | - | 1 | - | - | Read
19452 | 2 | Shortcircuit | - | 1 | - | - | Read
19453 |  | Temperature input info Conf. TMP 58
19453 | 0 | Assigned | - | 1 | - | - | Read
19453 | 1 | Wirebreak | - | 1 | - | - | Read
19453 | 2 | Shortcircuit | - | 1 | - | - | Read
19454 |  | Temperature input info Conf. TMP 59
19454 | 0 | Assigned | - | 1 | - | - | Read
19454 | 1 | Wirebreak | - | 1 | - | - | Read
19454 | 2 | Shortcircuit | - | 1 | - | - | Read
19455 |  | Temperature input info Conf. TMP 60
19455 | 0 | Assigned | - | 1 | - | - | Read
19455 | 1 | Wirebreak | - | 1 | - | - | Read
19455 | 2 | Shortcircuit | - | 1 | - | - | Read
19456 |  | Temperature input info Conf. TMP 61
19456 | 0 | Assigned | - | 1 | - | - | Read
19456 | 1 | Wirebreak | - | 1 | - | - | Read
19456 | 2 | Shortcircuit | - | 1 | - | - | Read
19457 |  | Temperature input info Conf. TMP 62
19457 | 0 | Assigned | - | 1 | - | - | Read
19457 | 1 | Wirebreak | - | 1 | - | - | Read
19457 | 2 | Shortcircuit | - | 1 | - | - | Read
19458 |  | Temperature input info Conf. TMP 63
19458 | 0 | Assigned | - | 1 | - | - | Read
19458 | 1 | Wirebreak | - | 1 | - | - | Read
19458 | 2 | Shortcircuit | - | 1 | - | - | Read
19459 |  | Temperature input info Conf. TMP 64
19459 | 0 | Assigned | - | 1 | - | - | Read
19459 | 1 | Wirebreak | - | 1 | - | - | Read
19459 | 2 | Shortcircuit | - | 1 | - | - | Read
19460 |  | Temperature input info Conf. TMP 65
19460 | 0 | Assigned | - | 1 | - | - | Read
19460 | 1 | Wirebreak | - | 1 | - | - | Read
19460 | 2 | Shortcircuit | - | 1 | - | - | Read
19461 |  | Temperature input info Conf. TMP 66
19461 | 0 | Assigned | - | 1 | - | - | Read
19461 | 1 | Wirebreak | - | 1 | - | - | Read
19461 | 2 | Shortcircuit | - | 1 | - | - | Read
19462 |  | Temperature input info Conf. TMP 67
19462 | 0 | Assigned | - | 1 | - | - | Read
19462 | 1 | Wirebreak | - | 1 | - | - | Read
19462 | 2 | Shortcircuit | - | 1 | - | - | Read
19463 |  | Temperature input info Conf. TMP 68
19463 | 0 | Assigned | - | 1 | - | - | Read
19463 | 1 | Wirebreak | - | 1 | - | - | Read
19463 | 2 | Shortcircuit | - | 1 | - | - | Read
19464 |  | Temperature input info Conf. TMP 69
19464 | 0 | Assigned | - | 1 | - | - | Read
19464 | 1 | Wirebreak | - | 1 | - | - | Read
19464 | 2 | Shortcircuit | - | 1 | - | - | Read
19465 |  | Temperature input info Conf. TMP 70
19465 | 0 | Assigned | - | 1 | - | - | Read
19465 | 1 | Wirebreak | - | 1 | - | - | Read
19465 | 2 | Shortcircuit | - | 1 | - | - | Read
19466 |  | Temperature input info Conf. TMP 71
19466 | 0 | Assigned | - | 1 | - | - | Read
19466 | 1 | Wirebreak | - | 1 | - | - | Read
19466 | 2 | Shortcircuit | - | 1 | - | - | Read
19467 |  | Temperature input info Conf. TMP 72
19467 | 0 | Assigned | - | 1 | - | - | Read
19467 | 1 | Wirebreak | - | 1 | - | - | Read
19467 | 2 | Shortcircuit | - | 1 | - | - | Read
19468 |  | Temperature input info Cold junction A
19468 | 0 | Assigned | - | 1 | - | - | Read
19468 | 1 | Wirebreak | - | 1 | - | - | Read
19468 | 2 | Shortcircuit | - | 1 | - | - | Read
19469 |  | Temperature input info Cold junction B
19469 | 0 | Assigned | - | 1 | - | - | Read
19469 | 1 | Wirebreak | - | 1 | - | - | Read
19469 | 2 | Shortcircuit | - | 1 | - | - | Read
19470 |  | Analog input info Conf. AI 1
19470 | 0 | Assigned | - | 1 | - | - | Read
19470 | 1 | Wirebreak | - | 1 | - | - | Read
19470 | 2 | Shortcircuit | - | 1 | - | - | Read
19471 |  | Analog input info Conf. AI 2
19471 | 0 | Assigned | - | 1 | - | - | Read
19471 | 1 | Wirebreak | - | 1 | - | - | Read
19471 | 2 | Shortcircuit | - | 1 | - | - | Read
19472 |  | Analog input info Conf. AI 3
19472 | 0 | Assigned | - | 1 | - | - | Read
19472 | 1 | Wirebreak | - | 1 | - | - | Read
19472 | 2 | Shortcircuit | - | 1 | - | - | Read
19473 |  | Analog input info Conf. AI 4
19473 | 0 | Assigned | - | 1 | - | - | Read
19473 | 1 | Wirebreak | - | 1 | - | - | Read
19473 | 2 | Shortcircuit | - | 1 | - | - | Read
19600 |  | Analog input info Conf. AI 5
19600 | 0 | Assigned | - | 1 | - | - | Read
19600 | 1 | Wirebreak | - | 1 | - | - | Read
19600 | 2 | Overload | - | 1 | - | - | Read
19602 |  | Analog input info Conf. AI 6
19602 | 0 | Assigned | - | 1 | - | - | Read
19602 | 1 | Wirebreak | - | 1 | - | - | Read
19602 | 2 | Overload | - | 1 | - | - | Read
19604 |  | Analog input info Conf. AI 7
19604 | 0 | Assigned | - | 1 | - | - | Read
19604 | 1 | Wirebreak | - | 1 | - | - | Read
19604 | 2 | Overload | - | 1 | - | - | Read
19606 |  | Analog input info Conf. AI 8
19606 | 0 | Assigned | - | 1 | - | - | Read
19606 | 1 | Wirebreak | - | 1 | - | - | Read
19606 | 2 | Overload | - | 1 | - | - | Read
19608 |  | Analog input info Conf. AI 9
19608 | 0 | Assigned | - | 1 | - | - | Read
19608 | 1 | Wirebreak | - | 1 | - | - | Read
19608 | 2 | Overload | - | 1 | - | - | Read
19610 |  | Analog input info Conf. AI 10
19610 | 0 | Assigned | - | 1 | - | - | Read
19610 | 1 | Wirebreak | - | 1 | - | - | Read
19610 | 2 | Overload | - | 1 | - | - | Read
19612 |  | Analog input info Conf. AI 11
19612 | 0 | Assigned | - | 1 | - | - | Read
19612 | 1 | Wirebreak | - | 1 | - | - | Read
19612 | 2 | Overload | - | 1 | - | - | Read
19614 |  | Analog input info Conf. AI 12
19614 | 0 | Assigned | - | 1 | - | - | Read
19614 | 1 | Wirebreak | - | 1 | - | - | Read
19614 | 2 | Overload | - | 1 | - | - | Read
19616 |  | Analog input info Conf. AI 13
19616 | 0 | Assigned | - | 1 | - | - | Read
19616 | 1 | Wirebreak | - | 1 | - | - | Read
19616 | 2 | Overload | - | 1 | - | - | Read
19618 |  | Analog input info Conf. AI 14
19618 | 0 | Assigned | - | 1 | - | - | Read
19618 | 1 | Wirebreak | - | 1 | - | - | Read
19618 | 2 | Overload | - | 1 | - | - | Read
19620 |  | Analog input info Conf. AI 15
19620 | 0 | Assigned | - | 1 | - | - | Read
19620 | 1 | Wirebreak | - | 1 | - | - | Read
19620 | 2 | Overload | - | 1 | - | - | Read
19622 |  | Analog input info Conf. AI 16
19622 | 0 | Assigned | - | 1 | - | - | Read
19622 | 1 | Wirebreak | - | 1 | - | - | Read
19622 | 2 | Overload | - | 1 | - | - | Read
19624 |  | Analog input info Conf. AI 17
19624 | 0 | Assigned | - | 1 | - | - | Read
19624 | 1 | Wirebreak | - | 1 | - | - | Read
19624 | 2 | Overload | - | 1 | - | - | Read
19626 |  | Analog input info Conf. AI 18
19626 | 0 | Assigned | - | 1 | - | - | Read
19626 | 1 | Wirebreak | - | 1 | - | - | Read
19626 | 2 | Overload | - | 1 | - | - | Read
19628 |  | Analog input info Conf. AI 19
19628 | 0 | Assigned | - | 1 | - | - | Read
19628 | 1 | Wirebreak | - | 1 | - | - | Read
19628 | 2 | Overload | - | 1 | - | - | Read
19630 |  | Analog input info Conf. AI 20
19630 | 0 | Assigned | - | 1 | - | - | Read
19630 | 1 | Wirebreak | - | 1 | - | - | Read
19630 | 2 | Overload | - | 1 | - | - | Read
19632 |  | Analog input info Conf. AI 21
19632 | 0 | Assigned | - | 1 | - | - | Read
19632 | 1 | Wirebreak | - | 1 | - | - | Read
19632 | 2 | Overload | - | 1 | - | - | Read
19634 |  | Analog input info Conf. AI 22
19634 | 0 | Assigned | - | 1 | - | - | Read
19634 | 1 | Wirebreak | - | 1 | - | - | Read
19634 | 2 | Overload | - | 1 | - | - | Read
19636 |  | Analog input info Conf. AI 23
19636 | 0 | Assigned | - | 1 | - | - | Read
19636 | 1 | Wirebreak | - | 1 | - | - | Read
19636 | 2 | Overload | - | 1 | - | - | Read
19638 |  | Analog input info Conf. AI 24
19638 | 0 | Assigned | - | 1 | - | - | Read
19638 | 1 | Wirebreak | - | 1 | - | - | Read
19638 | 2 | Overload | - | 1 | - | - | Read
19640 |  | Analog input info Conf. AI 25
19640 | 0 | Assigned | - | 1 | - | - | Read
19640 | 1 | Wirebreak | - | 1 | - | - | Read
19640 | 2 | Overload | - | 1 | - | - | Read
19642 |  | Analog input info Conf. AI 26
19642 | 0 | Assigned | - | 1 | - | - | Read
19642 | 1 | Wirebreak | - | 1 | - | - | Read
19642 | 2 | Overload | - | 1 | - | - | Read
19644 |  | Analog input info Conf. AI 27
19644 | 0 | Assigned | - | 1 | - | - | Read
19644 | 1 | Wirebreak | - | 1 | - | - | Read
19644 | 2 | Overload | - | 1 | - | - | Read
19646 |  | Analog input info Conf. AI 28
19646 | 0 | Assigned | - | 1 | - | - | Read
19646 | 1 | Wirebreak | - | 1 | - | - | Read
19646 | 2 | Overload | - | 1 | - | - | Read
19648 |  | Analog input info Conf. AI 29
19648 | 0 | Assigned | - | 1 | - | - | Read
19648 | 1 | Wirebreak | - | 1 | - | - | Read
19648 | 2 | Overload | - | 1 | - | - | Read
19650 |  | Analog input info Conf. AI 30
19650 | 0 | Assigned | - | 1 | - | - | Read
19650 | 1 | Wirebreak | - | 1 | - | - | Read
19650 | 2 | Overload | - | 1 | - | - | Read
19652 |  | Analog input info Conf. AI 31
19652 | 0 | Assigned | - | 1 | - | - | Read
19652 | 1 | Wirebreak | - | 1 | - | - | Read
19652 | 2 | Overload | - | 1 | - | - | Read
19654 |  | Analog input info Conf. AI 32
19654 | 0 | Assigned | - | 1 | - | - | Read
19654 | 1 | Wirebreak | - | 1 | - | - | Read
19654 | 2 | Overload | - | 1 | - | - | Read
19656 |  | Analog input info Conf. AI 33
19656 | 0 | Assigned | - | 1 | - | - | Read
19656 | 1 | Wirebreak | - | 1 | - | - | Read
19656 | 2 | Overload | - | 1 | - | - | Read
19658 |  | Analog input info Conf. AI 34
19658 | 0 | Assigned | - | 1 | - | - | Read
19658 | 1 | Wirebreak | - | 1 | - | - | Read
19658 | 2 | Overload | - | 1 | - | - | Read
19660 |  | Analog input info Conf. AI 35
19660 | 0 | Assigned | - | 1 | - | - | Read
19660 | 1 | Wirebreak | - | 1 | - | - | Read
19660 | 2 | Overload | - | 1 | - | - | Read
19662 |  | Analog input info Conf. AI 36
19662 | 0 | Assigned | - | 1 | - | - | Read
19662 | 1 | Wirebreak | - | 1 | - | - | Read
19662 | 2 | Overload | - | 1 | - | - | Read
19664 |  | Analog input info Conf. AI 37
19664 | 0 | Assigned | - | 1 | - | - | Read
19664 | 1 | Wirebreak | - | 1 | - | - | Read
19664 | 2 | Overload | - | 1 | - | - | Read
19666 |  | Analog input info Conf. AI 38
19666 | 0 | Assigned | - | 1 | - | - | Read
19666 | 1 | Wirebreak | - | 1 | - | - | Read
19666 | 2 | Overload | - | 1 | - | - | Read
19668 |  | Analog input info Conf. AI 39
19668 | 0 | Assigned | - | 1 | - | - | Read
19668 | 1 | Wirebreak | - | 1 | - | - | Read
19668 | 2 | Overload | - | 1 | - | - | Read
19670 |  | Analog input info Conf. AI 40
19670 | 0 | Assigned | - | 1 | - | - | Read
19670 | 1 | Wirebreak | - | 1 | - | - | Read
19670 | 2 | Overload | - | 1 | - | - | Read
19672 |  | Analog input info Conf. AI 41
19672 | 0 | Assigned | - | 1 | - | - | Read
19672 | 1 | Wirebreak | - | 1 | - | - | Read
19672 | 2 | Overload | - | 1 | - | - | Read
19674 |  | Analog input info Conf. AI 42
19674 | 0 | Assigned | - | 1 | - | - | Read
19674 | 1 | Wirebreak | - | 1 | - | - | Read
19674 | 2 | Overload | - | 1 | - | - | Read
19676 |  | Analog input info Conf. AI 43
19676 | 0 | Assigned | - | 1 | - | - | Read
19676 | 1 | Wirebreak | - | 1 | - | - | Read
19676 | 2 | Overload | - | 1 | - | - | Read
19678 |  | Analog input info Conf. AI 44
19678 | 0 | Assigned | - | 1 | - | - | Read
19678 | 1 | Wirebreak | - | 1 | - | - | Read
19678 | 2 | Overload | - | 1 | - | - | Read
19680 |  | Analog input info Conf. AI 45
19680 | 0 | Assigned | - | 1 | - | - | Read
19680 | 1 | Wirebreak | - | 1 | - | - | Read
19680 | 2 | Overload | - | 1 | - | - | Read
19682 |  | Analog input info Conf. AI 46
19682 | 0 | Assigned | - | 1 | - | - | Read
19682 | 1 | Wirebreak | - | 1 | - | - | Read
19682 | 2 | Overload | - | 1 | - | - | Read
19684 |  | Analog input info Conf. AI 47
19684 | 0 | Assigned | - | 1 | - | - | Read
19684 | 1 | Wirebreak | - | 1 | - | - | Read
19684 | 2 | Overload | - | 1 | - | - | Read
19686 |  | Analog input info Conf. AI 48
19686 | 0 | Assigned | - | 1 | - | - | Read
19686 | 1 | Wirebreak | - | 1 | - | - | Read
19686 | 2 | Overload | - | 1 | - | - | Read
19688 |  | Analog input info Limit switch input (1)
19688 | 0 | Assigned | - | 1 | - | - | Read
19688 | 1 | Wirebreak | - | 1 | - | - | Read
19688 | 2 | Overload | - | 1 | - | - | Read
19690 |  | Analog input info Limit switch input (1)
19690 | 0 | Assigned | - | 1 | - | - | Read
19690 | 1 | Wirebreak | - | 1 | - | - | Read
19690 | 2 | Overload | - | 1 | - | - | Read
19692 |  | Analog input info Generator power
19692 | 0 | Assigned | - | 1 | - | - | Read
19692 | 1 | Wirebreak | - | 1 | - | - | Read
19692 | 2 | Overload | - | 1 | - | - | Read
19694 |  | Analog input info Demanded power
19694 | 0 | Assigned | - | 1 | - | - | Read
19694 | 1 | Wirebreak | - | 1 | - | - | Read
19694 | 2 | Overload | - | 1 | - | - | Read
19696 |  | Analog input info Power limitation
19696 | 0 | Assigned | - | 1 | - | - | Read
19696 | 1 | Wirebreak | - | 1 | - | - | Read
19696 | 2 | Overload | - | 1 | - | - | Read
19697 |  | Analog output info PID output 1
19697 | 0 | Assigned | - | 1 | - | - | Read
19697 | 1 | Wirebreak | - | 1 | - | - | Read
19697 | 2 | Overload | - | 1 | - | - | Read
19698 |  | Analog output info PID output 2
19698 | 0 | Assigned | - | 1 | - | - | Read
19698 | 1 | Wirebreak | - | 1 | - | - | Read
19698 | 2 | Overload | - | 1 | - | - | Read
19700 |  | Analog output info PID output 3
19700 | 0 | Assigned | - | 1 | - | - | Read
19700 | 1 | Wirebreak | - | 1 | - | - | Read
19700 | 2 | Overload | - | 1 | - | - | Read
19702 |  | Analog output info PID output 4
19702 | 0 | Assigned | - | 1 | - | - | Read
19702 | 1 | Wirebreak | - | 1 | - | - | Read
19702 | 2 | Overload | - | 1 | - | - | Read
19704 |  | Analog output info PID output 5
19704 | 0 | Assigned | - | 1 | - | - | Read
19704 | 1 | Wirebreak | - | 1 | - | - | Read
19704 | 2 | Overload | - | 1 | - | - | Read
19706 |  | Analog output info Steam valve
19706 | 0 | Assigned | - | 1 | - | - | Read
19706 | 1 | Wirebreak | - | 1 | - | - | Read
19706 | 2 | Overload | - | 1 | - | - | Read
19707 |  | Analog output info Voltage regulator
19707 | 0 | Assigned | - | 1 | - | - | Read
19707 | 1 | Wirebreak | - | 1 | - | - | Read
19707 | 2 | Overload | - | 1 | - | - | Read
19800 |  | Analog output info V instrument
19800 | 0 | Assigned | - | 1 | - | - | Read
19801 |  | Analog output info kvar instrument
19801 | 0 | Assigned | - | 1 | - | - | Read
19802 |  | Analog output info kW instrument
19802 | 0 | Assigned | - | 1 | - | - | Read
19803 |  | Analog output info Maximum allowed load
19803 | 0 | Assigned | - | 1 | - | - | Read
19804 |  | Analog output info Power setpoint
19804 | 0 | Assigned | - | 1 | - | - | Read
19805 |  | Analog output info Speed
19805 | 0 | Assigned | - | 1 | - | - | Read
19806 |  | Analog output info Speed setpoint
19806 | 0 | Assigned | - | 1 | - | - | Read
19807 |  | Analog output info Live steam pressure
19807 | 0 | Assigned | - | 1 | - | - | Read
19808 |  | Analog output info Live steam press. setp.
19808 | 0 | Assigned | - | 1 | - | - | Read
19809 |  | Analog output info Exhaust steam pressure
19809 | 0 | Assigned | - | 1 | - | - | Read
19810 |  | Analog output info Exh. steam press. setp.
19810 | 0 | Assigned | - | 1 | - | - | Read
19811 |  | Analog write: PID 1 setpoint
19811 | 0 | Assigned | - | 1 | - | - | Read
19812 |  | Analog write: PID 2 setpoint
19812 | 0 | Assigned | - | 1 | - | - | Read
19813 |  | Analog write: PID 3 setpoint
19813 | 0 | Assigned | - | 1 | - | - | Read
19814 |  | Analog write: PID 4 setpoint
19814 | 0 | Assigned | - | 1 | - | - | Read
19815 |  | Analog write: PID 5 setpoint
19815 | 0 | Assigned | - | 1 | - | - | Read
19816 |  | Analog write: PID 1 input
19816 | 0 | Assigned | - | 1 | - | - | Read
19817 |  | Analog write: PID 2 input
19817 | 0 | Assigned | - | 1 | - | - | Read
19818 |  | Analog write: PID 3 input
19818 | 0 | Assigned | - | 1 | - | - | Read
19819 |  | Analog write: PID 4 input
19819 | 0 | Assigned | - | 1 | - | - | Read
19820 |  | Analog write: PID 5 input
19820 | 0 | Assigned | - | 1 | - | - | Read

## 10_Write Function
#VALUE! | 50000-51000
Register | Bit | Text | Configuration | Resolution | Factor | Unit | Access
50000 |  | Analog write: Power setpoint | - | 16 | 2025-10-01 |  | Write
50001 |  | Analog write: Power limitation | - | 16 | 2025-10-01 |  | Write
50002 |  | Analog write: Live steam pressure setpoint | - | 16 | 2025-10-01 |  | Write
50003 |  | Analog write: Exhaust steam pressure setpoint | - | 16 | 2025-10-01 |  | Write
50004 |  | Boolean write register 1 | - | 16 | 2025-10-01 |  | Write
50005 |  | Reserve | - | 16 | 2025-10-01 |  | Write
50006 |  | Reserve | - | 16 | 2025-10-01 |  | Write
50007 |  | Reserve | - | 16 | 2025-10-01 |  | Write
50008 |  | Reserve | - | 16 | 2025-10-01 |  | Write
50009 |  | Reserve | - | 16 | 2025-10-01 |  | Write
50010 |  | Reserve | - | 16 | 2025-10-01 | % | Write
50011 |  | Reserve | - | 16 | 2025-10-01 | % | Write
50012 |  | Reserve | - | 16 | 1/100 | bar | Write
50013 |  | Reserve | - | 16 | 1/100 | bar | Write
51000 |  | Reserve
51000 | 0 | Reset PID 1 | - | 1 | - | - | Write
51000 | 1 | Reset PID 2 | - | 1 | - | - | Write
51000 | 2 | Reset PID 3 | - | 1 | - | - | Write
51000 | 3 | Reset PID 4 | - | 1 | - | - | Write
51000 | 4 | Reset PID 5 | - | 1 | - | - | Write
51000 | 5 | Start demand | - | 1 | - | - | Write
51000 | 6 | Stop demand | - | 1 | - | - | Write
51000 | 7 | Shutdown | - | 1 | - | - | Write
51000 | 8 | Ack. / Clear alarms | - | 1 | - | - | Write
51000 | 9 | Demand island operation | - | 1 | - | - | Write
51000 | 10 | Activate pressure control | - | 1 | - | - | Write
51000 | 11 | Remote pressure control | - | 1 | - | - | Write