## About
iE 250 Marine Core Parameter lists
Software version
The information contained in these parameter lists (Revision A) are applicable to software version 2.0.18.x of the iE 250 Marine Core.
Controller types
This document includes the parameter and I/O function lists for these controller types:
GENSET controller
HYBRID controller
SHAFT generator controller
SHORE connection controller
BUS TIE breaker controller
See the iE 250 Marine Core Designer's handbook for more information.
Parameters
The parameter lists are based on the parameters shown in the display or in PICUS, under Configure > Parameters.
If you cannot find a parameter in the display or PICUS, it is probably Hidden. To see Hidden parameters you need to configure the application, configure an I/O function, and/or change a specific parameter selection. By only showing relevant parameters, the Hidden function ensures that the configuration is consistent.
Column names
Parameter path = The location of the parameter.
Parameter name = The name of the parameter.
Data type = The data type for the parameter value.*
Default = The default value or selection for the parameter.
Unit = The unit of measurement for the parameter value.*
Minimum = The minimum value of the parameter range.*
Maximum = The maximum value of the parameter range.*
Decimals = The number of decimal places for the value.*
Selections = The drop-down choices for the parameter.*
Hidden = To see this parameter, you need to configure the application, an I/O function, and/or change a related parameter selection.*
Notes
* Only included where relevant.
Inhibits are only included in the parameter list when they are selected in the default controller configuration.
Some advanced parameters (for example, Auto acknowledge and Latch) are not included in the parameter list.
[User defined] is used where part of the parameter path is configurable.
Custom parameters and Custom alarm are not included in the parameter list.
In addition to the parameters, the controllers also have a variety of other configurable settings. Examples include Fieldbus and Communication settings. These are not included in the parameter lists.
Input/output functions
The input/output function lists are based on the functions that can be selected in PICUS, under Configure > Input/ouput.
If you cannot find an input/output function in PICUS, it is probably Hidden. To see Hidden parameters you need to configure the application, configure an I/O function, and/or change a specific parameter selection. By only showing relevant parameters, the Hidden function ensures that the configuration is consistent.
Column names
Path = The location of the input/output function.
Name = The name of the input/output function.
IO type = The type of the input/output function.
DI = Digital input function DO = Digital output function AI = Analogue input function AO = Analogue output function
Unit = The default unit of measurement for the input/output function.*
Data type = The data type for the input/output function.
Minimum = The default minimum value of the input/output function.*
Maximum = The default maximum value of the input/output function.*
Decimals = The number of decimal places for the value.*
Hidden = To see this input/output function, you need to configure the application, an I/O function, and/or change a related parameter selection.*
Notes
* Only included where relevant.
[User defined] is used where part of the path is configurable.

## GENSET parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Engine > Nominal settings > Nominal settings 1 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 2 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 3 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 4 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
Engine > Emergency stop > Emergency stop | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Running detection > Feedback type | Primary running feedback | INT32 | Frequency |  |  |  |  | 2: Frequency, 1: Engine speed
Engine > Running detection > Engine ready | Delay | FLOAT | 2 | s | 1 | 300 | 1
Engine > Running detection > Frequency running detection | Frequency | FLOAT | 32 | Hz | 10 | 100 | 1
Engine > Running detection > RPM running detection | RPM | FLOAT | 1000 | RPM | 0 | 50000 | 1
Engine > Running detection > RPM running detection | Use engine speed | INT32 | 1 |  | 0 | 1 | 0
Engine > Running detection > MPU setup | Number of MPU teeth | FLOAT | 1 |  | 1 | 10000 | 0
Engine > Running detection > Oil pressure running detection | Oil pressure | FLOAT | 3 | bar | 0 | 10 | 1 |  | X
Engine > Running detection > Oil pressure running detection | Use oil pressure | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Running detection > Primary running feedback failure | Delay | FLOAT | 2 | s | 0 | 180 | 1
Engine > Running detection > Primary running feedback failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Running detection > Magnetic pickup wire break | Delay | FLOAT | 10 | s | 1 | 3600 | 0
Engine > Running detection > Magnetic pickup wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Running detection > Magnetic pickup wire break | Inhibit |  | Engine not running
Engine > Start sequence > Start prepare | Start prepare | FLOAT | 5 | s | 0 | 600 | 1 |  | X
Engine > Start sequence > Start prepare | Extended start prepare | FLOAT | 0 | s | 0 | 20 | 1 |  | X
Engine > Start sequence > Run coil | Run coil before crank | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Engine > Start sequence > Run coil | During start attempts | INT32 | Follow crank |  |  |  |  | 0: Follow crank, 1: Always on | X
Engine > Start sequence > Crank | Crank on | FLOAT | 5 | s | 1 | 180 | 1
Engine > Start sequence > Crank | Crank off | FLOAT | 5 | s | 1 | 180 | 1
Engine > Start sequence > Crank | Disengage crank | FLOAT | 400 | RPM | 1 | 2000 | 0
Engine > Start sequence > Stop coil | During crank off | INT32 | Activated |  |  |  |  | 0: Activated, 1: Not activated
Engine > Start sequence > Start attempts | Normal | INT32 | 3 |  | 1 | 10 | 0
Engine > Start sequence > Start attempts | Suppress alarm action | INT32 | 5 |  | 1 | 10 | 0
Engine > Start sequence > Start failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Start sequence > Crank failure | Set point | FLOAT | 50 | RPM | 1 | 400 | 1 |  | X
Engine > Start sequence > Crank failure | Delay | FLOAT | 20 | s | 0 | 180 | 1 |  | X
Engine > Start sequence > Crank failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Start sequence > Externally started | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Start sequence > Start enable removed during start | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Idle run start > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Idle run | Extended inhibit | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Engine > Idle run start > Minimum | Delay | FLOAT | 5 | s | 0 | 7200 | 1 |  | X
Engine > Idle run start > Coolant temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Coolant temperature | Set point | FLOAT | 50 | °C | -50 | 200 | 0 |  | X
Engine > Idle run start > Oil temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Oil temperature | Set point | FLOAT | 40 | °C | -50 | 200 | 0 |  | X
Engine > Idle run start > External condition | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Maximum | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Maximum | Delay | FLOAT | 60 | s | 1 | 7200 | 1 |  | X
Engine > Stop sequence > Cooldown | Cooldown time | FLOAT | 240 | s | 1 | 10800 | 0
Engine > Stop sequence > Cooldown | Suppress alarm action | FLOAT | 480 | s | 1 | 10800 | 0
Engine > Stop sequence > Cooldown | Temperature threshold | FLOAT | 0 | °C | 0 | 150 | 0 |  | X
Engine > Stop sequence > Extended stop | Extended stop | FLOAT | 5 | s | 1 | 180 | 1
Engine > Stop sequence > Stop failure | Delay | FLOAT | 30 | s | 0 | 300 | 0
Engine > Stop sequence > Stop failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Stop sequence > Externally stopped | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Idle run stop > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Minimum | Delay | FLOAT | 5 | s | 0 | 7200 | 1 |  | X
Engine > Idle run stop > Coolant temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Coolant temperature | Set point | FLOAT | 90 | °C | -50 | 200 | 0 |  | X
Engine > Idle run stop > Oil temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Oil temperature | Set point | FLOAT | 60 | °C | -50 | 200 | 0 |  | X
Engine > Idle run stop > External condition | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Maximum | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Maximum | Delay | FLOAT | 60 | s | 1 | 7200 | 1 |  | X
Engine > Protections > Speed > Overspeed 1 | Set point | FLOAT | 110 | % | 10 | 150 | 1
Engine > Protections > Speed > Overspeed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
Engine > Protections > Speed > Overspeed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
Engine > Protections > Speed > Overspeed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Protections > Speed > Overspeed 2 | Set point | FLOAT | 120 | % | 10 | 150 | 1
Engine > Protections > Speed > Overspeed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
Engine > Protections > Speed > Overspeed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
Engine > Protections > Speed > Overspeed 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Protections > Speed > Under-speed 1 | Set point | FLOAT | 90 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
Engine > Protections > Speed > Under-speed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Protections > Speed > Under-speed 1 | Inhibit |  | Engine not running, Idle run active
Engine > Protections > Speed > Under-speed 2 | Set point | FLOAT | 80 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
Engine > Protections > Speed > Under-speed 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Protections > Speed > Under-speed 2 | Inhibit |  | Engine not running, Idle run active
Engine > Protections > Pressure > Oil pressure 1 | Set point | FLOAT | 2 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Pressure > Oil pressure 1 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Pressure > Oil pressure 2 | Set point | FLOAT | 1 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Delay | FLOAT | 0.8 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Pressure > Oil pressure 2 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Temperature > Oil temperature 1 | Set point | FLOAT | 120 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Temperature > Oil temperature 2 | Set point | FLOAT | 140 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Temperature > Coolant temperature 1 | Set point | FLOAT | 100 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Temperature > Coolant temperature 2 | Set point | FLOAT | 110 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Temperature > Coolant temperature 3 | Set point | FLOAT | 115 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Level > Coolant level 1 | Set point | FLOAT | 20 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Level > Coolant level 2 | Set point | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Level > Coolant level 3 | Set point | FLOAT | 5 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Maintenance > Priming | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Maintenance > Priming | ON timer | FLOAT | 5 | s | 0 | 3600 | 1 |  | X
Engine > Maintenance > Priming | OFF timer | FLOAT | 30 | s | 0 | 3600 | 1 |  | X
Engine > Maintenance > Running hours total | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > Running hours total | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > ECU > Controls > Reset | Power off timer | FLOAT | 5 | s | 1 | 300 | 0 |  | X
Engine > Safety shutdown > Safety shutdown | Enable | INT32 | 0 |  | 0 | 1 | 0
Engine > Safety shutdown > Safety shutdown | Keep stop coil active | INT32 | 0 |  | 0 | 1 | 0
Engine > Safety shutdown > Safety shutdown | Use magnetic pickup | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Enable | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Use timer | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Time to enable function | FLOAT | 30 | s | 1 | 600 | 0
Engine > ECU diagnostic > ECU diagnostic | Mode | INT32 | Disable at start |  |  |  |  | 0: Disable at start, 1: Always on
Engine > Engine heater > Engine heater | Source selector | INT32 | Custom analogue input |  |  |  |  | 0: Custom analogue input, 1: Oil temperature, 2: Coolant temperature
Engine > Engine heater > Engine heater | Set point | FLOAT | 30 |  | 0 | 100 | 1
Engine > Engine heater > Engine heater | Hysteresis | FLOAT | 5 |  | 0 | 50 | 1
Engine > Engine heater > Engine heater | Enable | INT32 | 0 |  | 0 | 1 | 0
Generator > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Generator > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Generator > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Generator > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Generator > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
Generator > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Generator > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Generator > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Generator > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Generator > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
Generator > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
Generator > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 94 | % | 70 | 100 | 2
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2
Generator > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Generator > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Generator > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Generator > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Generator > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Generator > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Over-voltage 1 | Inhibit |  | Generator breaker closed
Generator > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Over-voltage 2 | Inhibit |  | Generator breaker closed
Generator > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Over-voltage 3 | Inhibit |  | Generator breaker closed
Generator > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Under-voltage 1 | Inhibit |  | Engine not running, Generator breaker closed, Idle run active
Generator > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Under-voltage 2 | Inhibit |  | Engine not running, Generator breaker closed, Idle run active
Generator > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Under-voltage 3 | Inhibit |  | Engine not running, Generator breaker closed, Idle run active
Generator > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Generator > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Generator > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Generator > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Generator > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Generator > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Generator > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Generator > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Generator > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
Generator > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
Generator > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
Generator > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
Generator > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
Generator > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
Generator > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Generator > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Generator > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Generator > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Generator > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Generator > Current protections > Inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Generator > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Generator > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Frequency protections > Over-frequency 1 | Inhibit |  | Generator breaker closed
Generator > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Frequency protections > Over-frequency 2 | Inhibit |  | Generator breaker closed
Generator > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Frequency protections > Under-frequency 1 | Inhibit |  | Engine not running, Generator breaker closed, Idle run active
Generator > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Frequency protections > Under-frequency 2 | Inhibit |  | Engine not running, Generator breaker closed, Idle run active
Generator > Power protections > Overload 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Generator > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Power protections > Overload 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Generator > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Power protections > Overload 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Generator > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Power protections > Reverse power 1 | Set point | FLOAT | 8 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Power protections > Reverse power 2 | Set point | FLOAT | 15 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Generator > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Generator > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Generator > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Busbar > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Over-voltage 1 | Inhibit |  | Generator breaker open
Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Over-voltage 2 | Inhibit |  | Generator breaker open
Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Over-voltage 3 | Inhibit |  | Generator breaker open
Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Under-voltage 1 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Under-voltage 2 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Under-voltage 3 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Frequency protections > Over-frequency 1 | Inhibit |  | Generator breaker open
Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Frequency protections > Over-frequency 2 | Inhibit |  | Generator breaker open
Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Frequency protections > Under-frequency 1 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Frequency protections > Under-frequency 2 | Inhibit |  | Generator breaker open, ACM wire break
Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 1 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 2 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 3 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 4 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Regulators > GOV > General configuration > Regulator output | Output type | INT32 | Relay |  |  |  |  | 0: Off, 2: Relay
Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1
Regulators > GOV > General configuration > Stand-alone configuration | GOV stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
Regulators > GOV > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
Regulators > GOV > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Regulators > GOV > Regulation set points > Fixed power | Set point of nominal | FLOAT | 0 | % | -100 | 100 | 0
Regulators > GOV > Regulation set points > Fixed power offset | Offset 1 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Regulation set points > Fixed power offset | Offset 2 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Regulation set points > Fixed power offset | Offset 3 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Regulation set points > Fixed power limit | Limit 1 | FLOAT | 2 | % | -300 | 300 | 2
Regulators > GOV > Regulation set points > Fixed power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2
Regulators > GOV > Analogue > Offset | GOV output offset 1 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 2 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 3 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 4 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Frequency regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > GOV > Analogue > Power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Phase synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Phase synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Phase synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1 |  | X
Regulators > GOV > Analogue > Manual slope | Manual GOV slope | FLOAT | 10 | %/s | 0 | 200 | 1 |  | X
Regulators > GOV > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0
Regulators > GOV > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0
Regulators > GOV > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2
Regulators > GOV > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0
Regulators > GOV > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0
Regulators > GOV > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2
Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Frequency synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Phase synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
Regulators > GOV > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
Regulators > GOV > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0
Regulators > GOV > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Regulators > GOV > Monitoring > Regulation mode not selected | Delay | FLOAT | 2 | s | 0 | 3600 | 0
Regulators > GOV > Monitoring > Regulation mode not selected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Regulators > GOV > Monitoring > P load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1
Regulators > GOV > Monitoring > P load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
Regulators > GOV > Monitoring > P load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Regulators > AVR > General configuration > Regulator output | Output type | INT32 | Off |  |  |  |  | 0: Off | X
Regulators > AVR > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Regulators > AVR > General configuration > Stand-alone configuration | AVR stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
Regulators > AVR > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
Regulators > AVR > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Regulators > AVR > Regulation set points > Fixed cos phi | Set point direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 1 | FLOAT | 0 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 2 | FLOAT | 0 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 3 | FLOAT | 0 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 3 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 | FLOAT | 0.97 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 | FLOAT | 0.8 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed reactive power | Set point | FLOAT | 0 | % | -100 | 100 | 0 |  | X
Regulators > AVR > Regulation set points > Fixed reactive power | Set point direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed reactive power | Set point adjustment | INT32 | Preferred |  |  |  |  | 0: Preferred, 1: Locked | X
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 1 | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 2 | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 3 | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 3 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 1 | FLOAT | -10 | % | -300 | 300 | 2 |  | X
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2 |  | X
Regulators > AVR > Regulation set points > Reactive power ramp down | Cos phi reset point | FLOAT | 5 | % | 0 | 100 | 0 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 1 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 2 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 3 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 4 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Voltage regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Voltage regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Voltage regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Analogue > Reactive power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Analogue > Manual slope | Manual AVR slope | FLOAT | 10 | %/s | 0 | 200 | 1 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > AVR > Relay configuration > Voltage regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Voltage regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | V deadband | FLOAT | 1 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1 |  | X
Regulators > AVR > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0 |  | X
Regulators > AVR > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Regulators > AVR > Monitoring > Regulation mode not selected | Delay | FLOAT | 2 | s | 0 | 3600 | 0 |  | X
Regulators > AVR > Monitoring > Regulation mode not selected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Regulators > AVR > Monitoring > Q load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1 |  | X
Regulators > AVR > Monitoring > Q load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0 |  | X
Regulators > AVR > Monitoring > Q load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > Generator breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Generator breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Generator breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Generator breaker configuration > Blackout close | Blackout close | INT32 | Generator OK, busbar is dead |  |  |  |  | 0: Blackout close is OFF, 1: Generator is dead, busbar OK, 2: Generator OK, busbar is dead, 3: One busbar is alive, 4: On
Breakers > Generator breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Generator breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Generator breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Generator breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Generator breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Generator breaker monitoring > Synchronisation failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Generator breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Generator breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Generator breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Generator breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Generator breaker monitoring > Closing failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Generator breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Generator breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > Generator breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker monitoring > Short circuit | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Auxiliary > Pump logic 1 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 1 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 1 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Auxiliary > Pump logic 1 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 2 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 2 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Auxiliary > Pump logic 2 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 3 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 3 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Auxiliary > Pump logic 3 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > Fieldbus > CAN bus > ECU > ECU Power configuration | ECU Power configuration | INT32 | Auto |  |  |  |  | 0: Auto, 1: Always ON | X
Communication > Fieldbus > CAN bus > ECU > ECU powerup time | ECU powerup time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Delay | FLOAT | 1 | s | 0 | 120 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > Fieldbus > CAN bus > Digital AVR > Power-up time | Power-up time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Delay | FLOAT | 0 | s | 0 | 120 | 1 |  | X
Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Mode > Command mode | Selected mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control
Local > Mode > Command mode | Boot mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > Blackout detection mismatch | Delay | FLOAT | 1 | s | 0 | 3600 | 1
System > Monitoring > Blackout detection mismatch | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Application selector | Application selector | INT32 | MS |  |  |  |  | 800000: LF, 800001: LC, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine

## GENSET IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
90130000 | Engine > Command | Start engine | DI |  | BOOL_NUM | 0 | 1 | 0
90130001 | Engine > Command | Stop engine | DI |  | BOOL_NUM | 0 | 1 | 0
90130002 | Engine > Command | Block engine start | DI |  | BOOL_NUM | 0 | 1 | 0
90230002 | Engine > Command | Start engine and close generator breaker | DI |  | BOOL_NUM | 0 | 1 | 0
90230003 | Engine > Command | Open generator breaker and stop engine | DI |  | BOOL_NUM | 0 | 1 | 0
11280002 | Engine > Feedback | Digital running detection | DI |  | BOOL_NUM | 0 | 1 | 0
11280003 | Engine > Function | Remove start (release crank relay) | DI |  | BOOL_NUM | 0 | 1 | 0
12080001 | Engine > Function | Start enable | DI |  | BOOL_NUM | 0 | 1 | 0
170000900 | Engine > ECU | Measurement list filter - available | DI |  | BOOL_NUM | 0 | 1 | 0 | X
170000901 | Engine > ECU | Measurement list filter - clear | DI |  | BOOL_NUM | 0 | 1 | 0 | X
170000930 | Engine > ECU | ECU reset input | DI |  | BOOL_NUM | 0 | 1 | 0
11180002 | Engine > Idle run | End idle start | DI |  | BOOL_NUM | 0 | 1 | 0
11180003 | Engine > Idle run | End idle stop | DI |  | BOOL_NUM | 0 | 1 | 0
11080100 | Engine > Safety shutdown | Manual reset | DI |  | BOOL_NUM | 0 | 1 | 0
11080054 | Engine > ECU diagnostic | ECU diagnostic on | DI |  | BOOL_NUM | 0 | 1 | 0
11080055 | Engine > ECU diagnostic | ECU diagnostic off | DI |  | BOOL_NUM | 0 | 1 | 0
70100053 | Regulators > GOV > Command | Pause ramping | DI |  | BOOL_NUM | 0 | 1 | 0
70100063 | Regulators > GOV > Command | Activate ramp 1 | DI |  | BOOL_NUM | 0 | 1 | 0
70100064 | Regulators > GOV > Command | Activate ramp 2 | DI |  | BOOL_NUM | 0 | 1 | 0
90230011 | Regulators > GOV > Command | Reset GOV to offset | DI |  | BOOL_NUM | 0 | 1 | 0
70100055 | Regulators > GOV > Modes | Deactivate regulation | DI |  | BOOL_NUM | 0 | 1 | 0
70100200 | Regulators > GOV > Modes | Activate fixed frequency | DI |  | BOOL_NUM | 0 | 1 | 0
70100201 | Regulators > GOV > Modes | Activate fixed power | DI |  | BOOL_NUM | 0 | 1 | 0
70100202 | Regulators > GOV > Modes | Activate frequency droop | DI |  | BOOL_NUM | 0 | 1 | 0
70100203 | Regulators > GOV > Modes | Activate power load sharing | DI |  | BOOL_NUM | 0 | 1 | 0
70100207 | Regulators > GOV > Modes | Activate manual regulation | DI |  | BOOL_NUM | 0 | 1 | 0
80100000 | Regulators > GOV > Modes | Stand-alone mode | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230006 | Regulators > GOV > Manual | Manual GOV increase | DI |  | BOOL_NUM | 0 | 1 | 0
90230007 | Regulators > GOV > Manual | Manual GOV decrease | DI |  | BOOL_NUM | 0 | 1 | 0
70100204 | Regulators > GOV > External set points | Activate external set point (network) | DI |  | BOOL_NUM | 0 | 1 | 0
70100205 | Regulators > GOV > External set points | Activate external set point | DI |  | BOOL_NUM | 0 | 1 | 0
70100214 | Regulators > GOV > External set points | Deactivate external set point (network) | DI |  | BOOL_NUM | 0 | 1 | 0
70100215 | Regulators > GOV > External set points | Deactivate external set point | DI |  | BOOL_NUM | 0 | 1 | 0
70100057 | Regulators > GOV > Active power offset | Active power offset 1 | DI |  | BOOL_NUM | 0 | 1 | 0
70100058 | Regulators > GOV > Active power offset | Active power offset 2 | DI |  | BOOL_NUM | 0 | 1 | 0
70100059 | Regulators > GOV > Active power offset | Active power offset 3 | DI |  | BOOL_NUM | 0 | 1 | 0
70100054 | Regulators > AVR > Command | Pause ramping | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230010 | Regulators > AVR > Command | Reset AVR to offset | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100056 | Regulators > AVR > Modes | Deactivate regulation | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100500 | Regulators > AVR > Modes | Activate fixed voltage | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100501 | Regulators > AVR > Modes | Activate fixed reactive power | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100502 | Regulators > AVR > Modes | Activate fixed cos phi | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100503 | Regulators > AVR > Modes | Activate voltage droop | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100504 | Regulators > AVR > Modes | Activate reactive power load sharing | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100508 | Regulators > AVR > Modes | Activate manual regulation | DI |  | BOOL_NUM | 0 | 1 | 0 | X
80100001 | Regulators > AVR > Modes | Stand-alone mode | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230008 | Regulators > AVR > Manual | Manual AVR increase | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230009 | Regulators > AVR > Manual | Manual AVR decrease | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100505 | Regulators > AVR > External set points | Activate external set point (network) | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100506 | Regulators > AVR > External set points | Activate external set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100515 | Regulators > AVR > External set points | Deactivate external set point (network) | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100516 | Regulators > AVR > External set points | Deactivate external set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100060 | Regulators > AVR > Cos phi/reactive power offset | Cos phi/Reactive power offset 1 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100061 | Regulators > AVR > Cos phi/reactive power offset | Cos phi/Reactive power offset 2 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100062 | Regulators > AVR > Cos phi/reactive power offset | Cos phi/Reactive power offset 3 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100052 | Regulators > Common | Freeze regulator | DI |  | BOOL_NUM | 0 | 1 | 0
3306001 | Breakers > Generator breaker > Command | GB static synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
3306002 | Breakers > Generator breaker > Command | GB dynamic synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
20180028 | Breakers > Generator breaker > Command | GB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Generator breaker > Command | GB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180030 | Breakers > Generator breaker > Command | GB open without de-loading | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Generator breaker > Command | Block GB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Generator breaker > Feedback | GB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Generator breaker > Feedback | GB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Generator breaker > Feedback | GB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Generator breaker > Feedback | GB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
110705000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110705001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
11580002 | Auxiliary > Pump logic | Activate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11580003 | Auxiliary > Pump logic | Deactivate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11680002 | Auxiliary > Pump logic | Activate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11680003 | Auxiliary > Pump logic | Deactivate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11780002 | Auxiliary > Pump logic | Activate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
11780003 | Auxiliary > Pump logic | Deactivate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
100001100 | Alarm system > Additional functions | Emergency stop | DI |  | BOOL_NUM | 0 | 1 | 0
60000505 | Local > Mode | Local control | DI |  | BOOL_NUM | 0 | 1 | 0
60000506 | Local > Mode | Remote control | DI |  | BOOL_NUM | 0 | 1 | 0
90020000 | Local > Mode | Switchboard control | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
11080000 | Engine > Controls | Run coil | DO |  | BOOL_NUM | 0 | 1 | 0
11080001 | Engine > Controls | Stop coil | DO |  | BOOL_NUM | 0 | 1 | 0
11080002 | Engine > Controls | Start prepare | DO |  | BOOL_NUM | 0 | 1 | 0
11080003 | Engine > Controls | Crank | DO |  | BOOL_NUM | 0 | 1 | 0
11480000 | Engine > Controls | Priming | DO |  | BOOL_NUM | 0 | 1 | 0
170000902 | Engine > Controls | ECU power | DO |  | BOOL_NUM | 0 | 1 | 0
11180001 | Engine > Controls | Idle run | DO |  | BOOL_NUM | 0 | 1 | 0
11080021 | Engine > State | Not ready to start | DO |  | BOOL_NUM | 0 | 1 | 0
11080022 | Engine > State | Ready to start | DO |  | BOOL_NUM | 0 | 1 | 0
11080023 | Engine > State | Starting | DO |  | BOOL_NUM | 0 | 1 | 0
11080024 | Engine > State | Cooldown | DO |  | BOOL_NUM | 0 | 1 | 0
11080027 | Engine > State | Stopping | DO |  | BOOL_NUM | 0 | 1 | 0
11080028 | Engine > State | Extended stop | DO |  | BOOL_NUM | 0 | 1 | 0
11080041 | Engine > State | Start prepare completed | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11280005 | Engine > State | Running | DO |  | BOOL_NUM | 0 | 1 | 0
11280006 | Engine > State | Not running | DO |  | BOOL_NUM | 0 | 1 | 0
11880000 | Engine > State | Engine heater | DO |  | BOOL_NUM | 0 | 1 | 0
11180000 | Engine > State | Idling | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11080101 | Engine > Safety shutdown | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
40219000 | Generator > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Generator > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40418002 | Generator > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Generator > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
90120018 | Generator > AVR | Trip AVR | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
70100004 | Regulators > GOV > Controls | GOV increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100005 | Regulators > GOV > Controls | GOV decrease | DO |  | BOOL_NUM | 0 | 1 | 0
70100220 | Regulators > GOV > State | Fixed frequency regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100221 | Regulators > GOV > State | Fixed power regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100222 | Regulators > GOV > State | Frequency droop regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100223 | Regulators > GOV > State | Power load sharing is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100224 | Regulators > GOV > State | Manual GOV regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100225 | Regulators > GOV > State | External set point (network) is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100226 | Regulators > GOV > State | External set point is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100235 | Regulators > GOV > State | External set point (network) is selected | DO |  | BOOL_NUM | 0 | 1 | 0
70100236 | Regulators > GOV > State | External set point is selected | DO |  | BOOL_NUM | 0 | 1 | 0
80100002 | Regulators > GOV > State | Stand-alone is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100002 | Regulators > AVR > Controls | AVR increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100003 | Regulators > AVR > Controls | AVR decrease | DO |  | BOOL_NUM | 0 | 1 | 0
70100520 | Regulators > AVR > State | Fixed voltage is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100521 | Regulators > AVR > State | Fixed reactive power is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100522 | Regulators > AVR > State | Fixed cos phi is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100523 | Regulators > AVR > State | Reactive power load sharing is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100524 | Regulators > AVR > State | Voltage droop is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100525 | Regulators > AVR > State | Manual AVR regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100526 | Regulators > AVR > State | External set point (network) is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100527 | Regulators > AVR > State | External set point is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100536 | Regulators > AVR > State | External set point (network) is selected | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100537 | Regulators > AVR > State | External set point is selected | DO |  | BOOL_NUM | 0 | 1 | 0 | X
80100003 | Regulators > AVR > State | Stand-alone is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
20180002 | Breakers > Generator breaker > Controls | GB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Generator breaker > Controls | GB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180027 | Breakers > Generator breaker > Controls | GB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Generator breaker > State | GB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Generator breaker > State | GB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Generator breaker > State | GB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Generator breaker > State | GB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Generator breaker > State | GB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
110705002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110705003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11580000 | Auxiliary > Pump logic | Activate pump 1 | DO |  | BOOL_NUM | 0 | 1 | 0
11680000 | Auxiliary > Pump logic | Activate pump 2 | DO |  | BOOL_NUM | 0 | 1 | 0
11780000 | Auxiliary > Pump logic | Activate pump 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035008 | Alarm system > State | Any GB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035009 | Alarm system > State | Any GB trip and stop alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035010 | Alarm system > State | Any GB trip and shutdown alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035023 | Alarm system > State | Any AVR trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035024 | Alarm system > State | Any GB + AVR alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035025 | Alarm system > State | Any GB + AVR + stop engine alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
90120012 | Local > System OK | GAM3.2 1 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120013 | Local > System OK | GAM3.2 2 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120014 | Local > System OK | GAM3.2 3 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60000507 | Local > Mode | Under local control | DO |  | BOOL_NUM | 0 | 1 | 0
60000508 | Local > Mode | Under remote control | DO |  | BOOL_NUM | 0 | 1 | 0
90020005 | Local > Mode | Under switchboard control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
125019000 | Non-essential load trip | Non-essential load trip 1 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125029000 | Non-essential load trip | Non-essential load trip 2 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125039000 | Non-essential load trip | Non-essential load trip 3 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11080004 | Engine > Measurements > Coolant | Engine coolant water | AI | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant | Engine coolant level | AI | % | FLOAT | 0 | 100 | 1
11080031 | Engine > Measurements > Lube oil | Engine oil temperature | AI | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil | Engine oil level | AI | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil | Engine oil pressure | AI | bar | FLOAT | 0 | 10 | 1
11080052 | Engine > Measurements > Fuel | Engine fuel level | AI | % | FLOAT | 0 | 100 | 1
11880001 | Engine > Engine heater | Custom analogue engine heater input | AI | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AI | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AI | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AI | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AI | % | FLOAT | 0 | 100 | 0
70100034 | Regulators > GOV | Frequency offset | AI | % | FLOAT | -10 | 10 | 1
70100035 | Regulators > GOV | Power set point | AI | % | FLOAT | -100 | 100 | 0
70100036 | Regulators > AVR | Voltage offset | AI | % | FLOAT | -10 | 10 | 1 | X
70100037 | Regulators > AVR | Reactive power set point | AI | % | FLOAT | -100 | 100 | 0 | X
70100038 | Regulators > AVR | Cos phi set point | AI |  | FLOAT | 0.6 | 1 | 4 | X
11580004 | Auxiliary > Pump logic | Custom analogue input 1 | AI | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic | Custom analogue input 2 | AI | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic | Custom analogue input 3 | AI | % | FLOAT | 0 | 100 | 1
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
11080044 | Engine > Measurements > Coolant | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080045 | Engine > Measurements > Coolant | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080004 | Engine > Measurements > Coolant > Analogue input | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant > Analogue input | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080042 | Engine > Measurements > Lube oil | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080043 | Engine > Measurements > Lube oil | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080058 | Engine > Measurements > Lube oil | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11080031 | Engine > Measurements > Lube oil > Analogue input | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil > Analogue input | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil > Analogue input | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080046 | Engine > Measurements > Speed | Engine speed | AO | RPM | FLOAT | 0 | 2000 | 0
11280001 | Engine > Measurements > Speed > Analogue input | Engine MPU | AO | RPM | FLOAT | 0 | 2000 | 0
11080053 | Engine > Measurements > Fuel | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
11080052 | Engine > Measurements > Fuel > Analogue input | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AO | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AO | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AO | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AO | % | FLOAT | 0 | 100 | 0
11380002 | Engine > Service timers | Hours until total running hours notification | AO | h | FLOAT | -1000000 | 1000000 | 0
11380003 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
40110000 | Generator > Voltage (V) | Generator ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Generator > Voltage (V) | Generator ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Generator > Voltage (V) | Generator ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Generator > Voltage (V) | Generator ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Generator > Voltage (V) | Generator ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Generator > Voltage (V) | Generator ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Generator > Voltage (V) | Generator ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Generator > Voltage (V) | Generator ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Generator > Voltage (V) | Generator ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Generator > Voltage (V) | Generator ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Generator > Voltage (V) | Generator ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Generator > Voltage (V) | Generator ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Generator > Voltage (V) | Generator ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Generator > Voltage (V) | Generator ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Generator > Voltage (V) | Generator ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Generator > Voltage (V) | Generator ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Generator > Frequency (f) (from voltage) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Generator > Frequency (f) (from voltage) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Generator > Frequency (f) (from voltage) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Generator > Frequency (f) (from voltage) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Generator > Frequency (f) (from voltage) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Generator > Frequency (f) (from voltage) | Generator ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Generator > Frequency (f) (from current) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Generator > Frequency (f) (from current) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Generator > Frequency (f) (from current) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Generator > Frequency (f) (from current) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Generator > Frequency (f) (from current) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Generator > Current (I) | Generator ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Generator > Current (I) | Generator ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Generator > Current (I) | Generator ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Generator > Current (I) | Generator ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Generator > Current (I) | Generator ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Generator > Current (I) | Generator ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Generator > Current (I) | Generator ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Generator > Current (I) | Generator ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Generator > Current (I) | Generator ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Generator > Current (I) | Generator ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Generator > Current (I) | Generator ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Generator > Power (P) | Generator ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Generator > Power (P) | Generator ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Generator > Power (P) | Generator ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Generator > Power (P) | Generator ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Generator > Power (P) | Generator ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Generator > Power (P) | Generator ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Generator > Power (P) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Generator > Power (P) | Generator ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Generator > Power (P) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Generator > Reactive power (Q) | Generator ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Generator > Reactive power (Q) | Generator ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Generator > Reactive power (Q) | Generator ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Generator > Reactive power (Q) | Generator ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Generator > Reactive power (Q) | Generator ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Generator > Reactive power (Q) | Generator ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Generator > Reactive power (Q) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Generator > Reactive power (Q) | Generator ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Generator > Reactive power (Q) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Generator > Apparent power (S) | Generator ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Generator > Apparent power (S) | Generator ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Generator > Apparent power (S) | Generator ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Generator > Apparent power (S) | Generator ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Generator > Apparent power (S) | Generator ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Generator > Apparent power (S) | Generator ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Generator > Apparent power (S) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Generator > Apparent power (S) | Generator ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Generator > Apparent power (S) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Generator > Power factor (PF) | Generator ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Generator > Power factor (PF) | Generator ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Generator > Phase angle | Generator ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Generator > Phase angle | Generator ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Generator > Phase angle | Generator ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Generator > Phase angle | Generator ¦ A-B phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Generator > Phase angle | Generator ¦ A-B phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Generator > Phase angle | Generator ¦ A-B phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar > Voltage (V) | Busbar ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar > Voltage (V) | Busbar ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar > Voltage (V) | Busbar ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar > Voltage (V) | Busbar ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar > Voltage (V) | Busbar ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar > Voltage (V) | Busbar ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar > Voltage (V) | Busbar ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar > Voltage (V) | Busbar ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar > Voltage (V) | Busbar ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar > Voltage (V) | Busbar ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar > Voltage (V) | Busbar ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar > Voltage (V) | Busbar ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar > Voltage (V) | Busbar ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar > Voltage (V) | Busbar ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar > Voltage (V) | Busbar ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar > Voltage (V) | Busbar ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar > Frequency (f) | Busbar ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar > Frequency (f) | Busbar ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar > Frequency (f) | Busbar ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar > Frequency (f) | Busbar ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar > Frequency (f) | Busbar ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar > Frequency (f) | Busbar ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100018 | Busbar > Phase angle | Busbar ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar > Phase angle | Busbar ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar > Phase angle | Busbar ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
70100001 | Regulators > GOV | GOV output | AO | % | FLOAT | -100 | 100 | 0
70100000 | Regulators > AVR | AVR output | AO | % | FLOAT | -100 | 100 | 0
11580004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 1 | AO | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 2 | AO | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 3 | AO | % | FLOAT | 0 | 100 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
100097000 | Hardware > Power supply > PCM2.1 | PCM2.1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1

## HYBRID parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Inverter > Start sequence > Restrictions | Allow start when | INT32 | Breaker is open |  |  |  |  | 0: Breaker is open, 1: Breaker is closed, 2: Breaker in any state
Inverter > Start sequence > Start | Start on | FLOAT | 5 | s | 1 | 180 | 1
Inverter > Start sequence > Start failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Start sequence > Externally started | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Stop sequence > Restrictions | Allow stop when | INT32 | Breaker is open |  |  |  |  | 0: Breaker is open, 1: Breaker is closed, 2: Breaker in any state
Inverter > Stop sequence > Stop failure | Delay | FLOAT | 5 | s | 0 | 300 | 0
Inverter > Stop sequence > Stop failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Stop sequence > Externally stopped | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Inverter > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Inverter > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Inverter > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Inverter > Maintenance > Running hours total | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Inverter > Maintenance > Running hours total | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Inverter > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Inverter > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Inverter > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Inverter > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Inverter > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
Inverter > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Inverter > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Inverter > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Inverter > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Inverter > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
Inverter > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
Inverter > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Inverter > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Inverter > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0
Inverter > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 94 | % | 70 | 100 | 2
Inverter > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2
Inverter > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Inverter > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Inverter > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Inverter > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Inverter > AC setup > Phase sequence error | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Inverter > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Inverter > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Inverter > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Inverter > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Inverter > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Inverter > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
Inverter > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Inverter > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Inverter > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Inverter > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
Inverter > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
Inverter > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Inverter > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Inverter > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Inverter > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Inverter > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Inverter > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Inverter > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Inverter > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Inverter > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Inverter > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Inverter > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Inverter > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Inverter > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Inverter > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Inverter > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Inverter > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Inverter > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Inverter > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Inverter > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Inverter > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Inverter > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Inverter > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Inverter > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Inverter > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Inverter > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Inverter > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
Inverter > Emergency stop > Emergency stop | Action | INT32 | Trip breaker and stop inverter |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Inverter > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Inverter > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Inverter > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Voltage protections > Over-voltage 1 | Inhibit |  | Breaker closed
Inverter > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Inverter > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Inverter > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Inverter > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Voltage protections > Over-voltage 2 | Inhibit |  | Breaker closed
Inverter > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Inverter > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Inverter > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Inverter > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Voltage protections > Over-voltage 3 | Inhibit |  | Breaker closed
Inverter > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Inverter > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Inverter > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Inverter > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Voltage protections > Under-voltage 1 | Inhibit |  | Inverter not running, Breaker closed
Inverter > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Inverter > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Inverter > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Inverter > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Voltage protections > Under-voltage 2 | Inhibit |  | Inverter not running, Breaker closed
Inverter > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Inverter > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Inverter > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Inverter > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Voltage protections > Under-voltage 3 | Inhibit |  | Inverter not running, Breaker closed
Inverter > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Inverter > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Inverter > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Inverter > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Inverter > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Inverter > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Inverter > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Inverter > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Inverter > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Inverter > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Inverter > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Inverter > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
Inverter > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Inverter > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
Inverter > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
Inverter > Current protections > Over-current 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
Inverter > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Inverter > Current protections > Fast over-current 1 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
Inverter > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Inverter > Current protections > Fast over-current 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Inverter > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Inverter > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Inverter > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Inverter > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
Inverter > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Inverter > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
Inverter > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Inverter > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Inverter > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Inverter > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Inverter > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Inverter > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Inverter > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Inverter > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Inverter > Current protections > Inverse time over-current | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Inverter > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Inverter > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Inverter > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Inverter > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Inverter > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Inverter > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Frequency protections > Over-frequency 1 | Inhibit |  | Breaker closed
Inverter > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
Inverter > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Inverter > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Frequency protections > Over-frequency 2 | Inhibit |  | Breaker closed
Inverter > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Inverter > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Inverter > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Frequency protections > Under-frequency 1 | Inhibit |  | Inverter not running, Breaker closed
Inverter > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Inverter > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Inverter > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Frequency protections > Under-frequency 2 | Inhibit |  | Inverter not running, Breaker closed
Inverter > Power protections > Overload 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Inverter > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Inverter > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Power protections > Overload 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Inverter > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Power protections > Overload 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Inverter > Power protections > Overload 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Power protections > Overload 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Inverter > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Power protections > Overload 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Inverter > Power protections > Overload 3 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Power protections > Reverse power 1 | Set point | FLOAT | 8 | % | 0 | 200 | 1
Inverter > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Power protections > Reverse power 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Inverter > Power protections > Reverse power 1 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Power protections > Reverse power 1 | Inhibit |  | Operating mode PTI (power take in), Operating mode standby
Inverter > Power protections > Reverse power 2 | Set point | FLOAT | 15 | % | 0 | 200 | 1
Inverter > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Power protections > Reverse power 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Inverter > Power protections > Reverse power 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Power protections > Reverse power 2 | Inhibit |  | Operating mode PTI (power take in), Operating mode standby
Inverter > Power protections > Overload reverse power 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Inverter > Power protections > Overload reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Power protections > Overload reverse power 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Inverter > Power protections > Overload reverse power 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Power protections > Overload reverse power 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Inverter > Power protections > Overload reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Power protections > Overload reverse power 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Inverter > Power protections > Overload reverse power 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Inverter > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Inverter > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Inverter > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Inverter > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 300 | 1
Inverter > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Inverter > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 300 | 1
Inverter > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Inverter > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Inverter > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Inverter > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Inverter > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Inverter > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Inverter > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Inverter > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Inverter > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Inverter > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar > AC setup > Phase sequence error | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Busbar > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > Voltage protections > Over-voltage 1 | Inhibit |  | Breaker open
Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > Voltage protections > Over-voltage 2 | Inhibit |  | Breaker open
Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > Voltage protections > Over-voltage 3 | Inhibit |  | Breaker open
Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > Voltage protections > Under-voltage 1 | Inhibit |  | Breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > Voltage protections > Under-voltage 2 | Inhibit |  | Breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > Voltage protections > Under-voltage 3 | Inhibit |  | Breaker open, ACM wire break
Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > Frequency protections > Over-frequency 1 | Inhibit |  | Breaker open
Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > Frequency protections > Over-frequency 2 | Inhibit |  | Breaker open
Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > Frequency protections > Under-frequency 1 | Inhibit |  | Breaker open, ACM wire break
Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Busbar > Frequency protections > Under-frequency 2 | Inhibit |  | Breaker open, ACM wire break
Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 1 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Inverter side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 2 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Inverter side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 3 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Inverter side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 4 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Inverter side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Regulators > GOV > General configuration > Regulator output | Output type | INT32 | Relay |  |  |  |  | 0: Off, 2: Relay
Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1
Regulators > GOV > General configuration > Stand-alone configuration | GOV stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
Regulators > GOV > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
Regulators > GOV > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Regulators > GOV > Regulation set points > Fixed power | Set point of nominal | FLOAT | 0 | % | -100 | 100 | 0
Regulators > GOV > Regulation set points > Fixed power offset | Offset 1 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Regulation set points > Fixed power offset | Offset 2 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Regulation set points > Fixed power offset | Offset 3 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Regulation set points > Fixed power limit | Limit 1 | FLOAT | 2 | % | -300 | 300 | 2
Regulators > GOV > Regulation set points > Fixed power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2
Regulators > GOV > Analogue > Offset | GOV output offset 1 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 2 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 3 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 4 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Frequency regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > GOV > Analogue > Power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Phase synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Phase synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Phase synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1 |  | X
Regulators > GOV > Analogue > Manual slope | Manual GOV slope | FLOAT | 10 | %/s | 0 | 200 | 1 |  | X
Regulators > GOV > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0
Regulators > GOV > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0
Regulators > GOV > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2
Regulators > GOV > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0
Regulators > GOV > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0
Regulators > GOV > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2
Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Frequency synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Phase synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
Regulators > GOV > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
Regulators > GOV > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0
Regulators > GOV > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Regulators > GOV > Monitoring > Regulation mode not selected | Delay | FLOAT | 2 | s | 0 | 3600 | 0
Regulators > GOV > Monitoring > Regulation mode not selected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Regulators > GOV > Monitoring > P load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1
Regulators > GOV > Monitoring > P load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
Regulators > GOV > Monitoring > P load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Regulators > AVR > General configuration > Regulator output | Output type | INT32 | Off |  |  |  |  | 0: Off | X
Regulators > AVR > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Regulators > AVR > General configuration > Stand-alone configuration | AVR stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
Regulators > AVR > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
Regulators > AVR > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Regulators > AVR > Regulation set points > Fixed cos phi | Set point direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 1 | FLOAT | 0 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 2 | FLOAT | 0 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 3 | FLOAT | 0 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 3 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 | FLOAT | 0.97 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 | FLOAT | 0.8 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed reactive power | Set point | FLOAT | 0 | % | -100 | 100 | 0 |  | X
Regulators > AVR > Regulation set points > Fixed reactive power | Set point direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed reactive power | Set point adjustment | INT32 | Preferred |  |  |  |  | 0: Preferred, 1: Locked | X
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 1 | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 2 | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 3 | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 3 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 1 | FLOAT | -10 | % | -300 | 300 | 2 |  | X
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2 |  | X
Regulators > AVR > Regulation set points > Reactive power ramp down | Cos phi reset point | FLOAT | 5 | % | 0 | 100 | 0 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 1 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 2 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 3 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 4 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Voltage regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Voltage regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Voltage regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Analogue > Reactive power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Analogue > Manual slope | Manual AVR slope | FLOAT | 10 | %/s | 0 | 200 | 1 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > AVR > Relay configuration > Voltage regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Voltage regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | V deadband | FLOAT | 1 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1 |  | X
Regulators > AVR > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0 |  | X
Regulators > AVR > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Regulators > AVR > Monitoring > Regulation mode not selected | Delay | FLOAT | 2 | s | 0 | 3600 | 0 |  | X
Regulators > AVR > Monitoring > Regulation mode not selected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Regulators > AVR > Monitoring > Q load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1 |  | X
Regulators > AVR > Monitoring > Q load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0 |  | X
Regulators > AVR > Monitoring > Q load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > Inverter breaker configuration > Configuration | Type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Inverter breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Inverter breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Inverter breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Inverter breaker configuration > Configuration | Breaker open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Inverter breaker configuration > Configuration | Allow breaker close when | INT32 | Inverter is started |  |  |  |  | 0: Inverter is started, 1: Inverter is stopped, 2: Inverter in any state
Breakers > Inverter breaker configuration > Configuration | Allow breaker open when | INT32 | Inverter in any state |  |  |  |  | 0: Inverter is started, 1: Inverter is stopped, 2: Inverter in any state
Breakers > Inverter breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Inverter breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Inverter breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Inverter breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Inverter breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Inverter breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Inverter breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Inverter breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Inverter breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Inverter breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Inverter breaker monitoring > Synchronisation failure | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Breakers > Inverter breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Inverter breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Breakers > Inverter breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Inverter breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Inverter breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Breakers > Inverter breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Inverter breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Breakers > Inverter breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Inverter breaker monitoring > Closing failure | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Breakers > Inverter breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Inverter breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Breakers > Inverter breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Inverter breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > Inverter breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Breakers > Inverter breaker monitoring > Short circuit | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Mode > Command mode | Selected mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control
Local > Mode > Command mode | Boot mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
System > Monitoring > Blackout detection mismatch | Delay | FLOAT | 1 | s | 0 | 3600 | 1
System > Monitoring > Blackout detection mismatch | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Application selector | Application selector | INT32 | MS |  |  |  |  | 800000: LF, 800001: LC, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter

## Hybrid IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
90130000 | Inverter > Command | Start inverter | DI |  | BOOL_NUM | 0 | 1 | 0
90130001 | Inverter > Command | Stop inverter | DI |  | BOOL_NUM | 0 | 1 | 0
90130002 | Inverter > Command | Block inverter start | DI |  | BOOL_NUM | 0 | 1 | 0
90230002 | Inverter > Command | Connect (inverter/breaker) | DI |  | BOOL_NUM | 0 | 1 | 0
90230003 | Inverter > Command | Disconnect (inverter/breaker) | DI |  | BOOL_NUM | 0 | 1 | 0
11280002 | Inverter > Feedback | Digital running detection | DI |  | BOOL_NUM | 0 | 1 | 0
70100053 | Regulators > GOV > Command | Pause ramping | DI |  | BOOL_NUM | 0 | 1 | 0
70100063 | Regulators > GOV > Command | Activate ramp 1 | DI |  | BOOL_NUM | 0 | 1 | 0
70100064 | Regulators > GOV > Command | Activate ramp 2 | DI |  | BOOL_NUM | 0 | 1 | 0
90230011 | Regulators > GOV > Command | Reset GOV to offset | DI |  | BOOL_NUM | 0 | 1 | 0
70100055 | Regulators > GOV > Modes | Deactivate regulation | DI |  | BOOL_NUM | 0 | 1 | 0
70100200 | Regulators > GOV > Modes | Activate fixed frequency | DI |  | BOOL_NUM | 0 | 1 | 0
70100201 | Regulators > GOV > Modes | Activate fixed power | DI |  | BOOL_NUM | 0 | 1 | 0
70100202 | Regulators > GOV > Modes | Activate frequency droop | DI |  | BOOL_NUM | 0 | 1 | 0
70100203 | Regulators > GOV > Modes | Activate power load sharing | DI |  | BOOL_NUM | 0 | 1 | 0
70100207 | Regulators > GOV > Modes | Activate manual regulation | DI |  | BOOL_NUM | 0 | 1 | 0
80100000 | Regulators > GOV > Modes | Stand-alone mode | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230006 | Regulators > GOV > Manual | Manual GOV increase | DI |  | BOOL_NUM | 0 | 1 | 0
90230007 | Regulators > GOV > Manual | Manual GOV decrease | DI |  | BOOL_NUM | 0 | 1 | 0
70100204 | Regulators > GOV > External set points | Activate external set point (network) | DI |  | BOOL_NUM | 0 | 1 | 0
70100205 | Regulators > GOV > External set points | Activate external set point | DI |  | BOOL_NUM | 0 | 1 | 0
70100214 | Regulators > GOV > External set points | Deactivate external set point (network) | DI |  | BOOL_NUM | 0 | 1 | 0
70100215 | Regulators > GOV > External set points | Deactivate external set point | DI |  | BOOL_NUM | 0 | 1 | 0
70100057 | Regulators > GOV > Active power offset | Active power offset 1 | DI |  | BOOL_NUM | 0 | 1 | 0
70100058 | Regulators > GOV > Active power offset | Active power offset 2 | DI |  | BOOL_NUM | 0 | 1 | 0
70100059 | Regulators > GOV > Active power offset | Active power offset 3 | DI |  | BOOL_NUM | 0 | 1 | 0
70100054 | Regulators > AVR > Command | Pause ramping | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230010 | Regulators > AVR > Command | Reset AVR to offset | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100056 | Regulators > AVR > Modes | Deactivate regulation | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100500 | Regulators > AVR > Modes | Activate fixed voltage | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100501 | Regulators > AVR > Modes | Activate fixed reactive power | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100502 | Regulators > AVR > Modes | Activate fixed cos phi | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100503 | Regulators > AVR > Modes | Activate voltage droop | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100504 | Regulators > AVR > Modes | Activate reactive power load sharing | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100508 | Regulators > AVR > Modes | Activate manual regulation | DI |  | BOOL_NUM | 0 | 1 | 0 | X
80100001 | Regulators > AVR > Modes | Stand-alone mode | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230008 | Regulators > AVR > Manual | Manual AVR increase | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230009 | Regulators > AVR > Manual | Manual AVR decrease | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100505 | Regulators > AVR > External set points | Activate external set point (network) | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100506 | Regulators > AVR > External set points | Activate external set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100515 | Regulators > AVR > External set points | Deactivate external set point (network) | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100516 | Regulators > AVR > External set points | Deactivate external set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100060 | Regulators > AVR > Cos phi/reactive power offset | Cos phi/Reactive power offset 1 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100061 | Regulators > AVR > Cos phi/reactive power offset | Cos phi/Reactive power offset 2 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100062 | Regulators > AVR > Cos phi/reactive power offset | Cos phi/Reactive power offset 3 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100052 | Regulators > Common | Freeze regulator | DI |  | BOOL_NUM | 0 | 1 | 0
3306001 | Breakers > Inverter breaker > Command | Breaker static synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
3306002 | Breakers > Inverter breaker > Command | Breaker dynamic synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
20180028 | Breakers > Inverter breaker > Command | Breaker close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Inverter breaker > Command | Breaker open | DI |  | BOOL_NUM | 0 | 1 | 0
20180030 | Breakers > Inverter breaker > Command | Breaker open without de-loading | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Inverter breaker > Command | Block breaker close | DI |  | BOOL_NUM | 0 | 1 | 0
90930000 | Breakers > Inverter breaker > Command | Block breaker open | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Inverter breaker > Feedback | Breaker open feedback | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Inverter breaker > Feedback | Breaker closed feedback | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Inverter breaker > Feedback | Breaker spring-loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Inverter breaker > Feedback | Breaker short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
110705000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110705001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
90920152 | Alarm system > Inhibits | Standby running (Hybrid) | DI |  | BOOL_NUM | 0 | 1 | 0
90920202 | Alarm system > Inhibits | PTI running | DI |  | BOOL_NUM | 0 | 1 | 0
90920252 | Alarm system > Inhibits | PTO running | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
100001100 | Alarm system > Additional functions | Emergency stop | DI |  | BOOL_NUM | 0 | 1 | 0
60000505 | Local > Mode | Local control | DI |  | BOOL_NUM | 0 | 1 | 0
60000506 | Local > Mode | Remote control | DI |  | BOOL_NUM | 0 | 1 | 0
90020000 | Local > Mode | Switchboard control | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
11080000 | Inverter > Controls | Run | DO |  | BOOL_NUM | 0 | 1 | 0
11080001 | Inverter > Controls | Stop | DO |  | BOOL_NUM | 0 | 1 | 0
11080003 | Inverter > Controls | Start | DO |  | BOOL_NUM | 0 | 1 | 0
11080022 | Inverter > State | Ready to start | DO |  | BOOL_NUM | 0 | 1 | 0
11080023 | Inverter > State | Starting | DO |  | BOOL_NUM | 0 | 1 | 0
11080027 | Inverter > State | Stopping | DO |  | BOOL_NUM | 0 | 1 | 0
11280005 | Inverter > State | Running | DO |  | BOOL_NUM | 0 | 1 | 0
40418002 | Inverter > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Inverter > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
40219000 | Inverter > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Inverter > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219020 | Inverter > Production counters | Active energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219030 | Inverter > Production counters | Reactive energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219040 | Inverter > Production counters | Active energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40219050 | Inverter > Production counters | Reactive energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120018 | Inverter > AVR | Trip AVR | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
70100004 | Regulators > GOV > Controls | GOV increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100005 | Regulators > GOV > Controls | GOV decrease | DO |  | BOOL_NUM | 0 | 1 | 0
70100220 | Regulators > GOV > State | Fixed frequency regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100221 | Regulators > GOV > State | Fixed power regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100222 | Regulators > GOV > State | Frequency droop regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100223 | Regulators > GOV > State | Power load sharing is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100224 | Regulators > GOV > State | Manual GOV regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100225 | Regulators > GOV > State | External set point (network) is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100226 | Regulators > GOV > State | External set point is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100235 | Regulators > GOV > State | External set point (network) is selected | DO |  | BOOL_NUM | 0 | 1 | 0
70100236 | Regulators > GOV > State | External set point is selected | DO |  | BOOL_NUM | 0 | 1 | 0
80100002 | Regulators > GOV > State | Stand-alone is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100002 | Regulators > AVR > Controls | AVR increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100003 | Regulators > AVR > Controls | AVR decrease | DO |  | BOOL_NUM | 0 | 1 | 0
70100520 | Regulators > AVR > State | Fixed voltage is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100521 | Regulators > AVR > State | Fixed reactive power is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100522 | Regulators > AVR > State | Fixed cos phi is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100523 | Regulators > AVR > State | Reactive power load sharing is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100524 | Regulators > AVR > State | Voltage droop is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100525 | Regulators > AVR > State | Manual AVR regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100526 | Regulators > AVR > State | External set point (network) is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100527 | Regulators > AVR > State | External set point is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100536 | Regulators > AVR > State | External set point (network) is selected | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100537 | Regulators > AVR > State | External set point is selected | DO |  | BOOL_NUM | 0 | 1 | 0 | X
80100003 | Regulators > AVR > State | Stand-alone is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
20180002 | Breakers > Inverter breaker > Controls | Breaker open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Inverter breaker > Controls | Breaker close | DO |  | BOOL_NUM | 0 | 1 | 0
20180027 | Breakers > Inverter breaker > Controls | Breaker trip | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Inverter breaker > State | Breaker is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Inverter breaker > State | Breaker is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Inverter breaker > State | Breaker is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Inverter breaker > State | Breaker is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Inverter breaker > State | Breaker is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
110705002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110705003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035008 | Alarm system > State | Any breaker trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035009 | Alarm system > State | Any breaker trip and stop inverter alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035013 | Alarm system > State | Any stop inverter alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035023 | Alarm system > State | Any AVR trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035024 | Alarm system > State | Any breaker + AVR alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035025 | Alarm system > State | Any breaker + AVR + stop inverter alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
90120012 | Local > System OK | GAM3.2 1 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120013 | Local > System OK | GAM3.2 2 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120014 | Local > System OK | GAM3.2 3 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60000507 | Local > Mode | Under local control | DO |  | BOOL_NUM | 0 | 1 | 0
60000508 | Local > Mode | Under remote control | DO |  | BOOL_NUM | 0 | 1 | 0
90020005 | Local > Mode | Under switchboard control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
125019000 | Non-essential load trip | Non-essential load trip 1 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125029000 | Non-essential load trip | Non-essential load trip 2 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125039000 | Non-essential load trip | Non-essential load trip 3 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40600510 | Inverter > Power derate > Temperature | Derate 1 temperature | AI | °C | FLOAT | -50 | 200 | 1
40610510 | Inverter > Power derate > Temperature | Derate 2 temperature | AI | °C | FLOAT | -50 | 200 | 1
40620510 | Inverter > Power derate > Temperature | Derate 3 temperature | AI | °C | FLOAT | -50 | 200 | 1
40640010 | Inverter > Power derate > Percentage | Derate percentage | AI | % | FLOAT | 0 | 100 | 0
70100034 | Regulators > GOV | Frequency offset | AI | % | FLOAT | -10 | 10 | 1
70100035 | Regulators > GOV | Power set point | AI | % | FLOAT | -100 | 100 | 0
70100036 | Regulators > AVR | Voltage offset | AI | % | FLOAT | -10 | 10 | 1 | X
70100037 | Regulators > AVR | Reactive power set point | AI | % | FLOAT | -100 | 100 | 0 | X
70100038 | Regulators > AVR | Cos phi set point | AI |  | FLOAT | 0.6 | 1 | 4 | X
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
40600510 | Inverter > Power derate > Temperature | Derate 1 temperature | AO | °C | FLOAT | -50 | 200 | 1
40610510 | Inverter > Power derate > Temperature | Derate 2 temperature | AO | °C | FLOAT | -50 | 200 | 1
40620510 | Inverter > Power derate > Temperature | Derate 3 temperature | AO | °C | FLOAT | -50 | 200 | 1
40640010 | Inverter > Power derate > Percentage | Derate percentage | AO | % | FLOAT | 0 | 100 | 0
11380002 | Inverter > Service timers | Hours until total running hours notification | AO | h | FLOAT | -1000000 | 1000000 | 0
11380003 | Inverter > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
40110000 | Inverter > Voltage (V) | Inverter ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Inverter > Voltage (V) | Inverter ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Inverter > Voltage (V) | Inverter ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Inverter > Voltage (V) | Inverter ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Inverter > Voltage (V) | Inverter ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Inverter > Voltage (V) | Inverter ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Inverter > Voltage (V) | Inverter ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Inverter > Voltage (V) | Inverter ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Inverter > Voltage (V) | Inverter ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Inverter > Voltage (V) | Inverter ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Inverter > Voltage (V) | Inverter ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Inverter > Voltage (V) | Inverter ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Inverter > Voltage (V) | Inverter ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Inverter > Voltage (V) | Inverter ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Inverter > Voltage (V) | Inverter ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Inverter > Voltage (V) | Inverter ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Inverter > Frequency (f) (from voltage) | Inverter ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Inverter > Frequency (f) (from voltage) | Inverter ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Inverter > Frequency (f) (from voltage) | Inverter ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Inverter > Frequency (f) (from voltage) | Inverter ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Inverter > Frequency (f) (from voltage) | Inverter ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Inverter > Frequency (f) (from voltage) | Inverter ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Inverter > Frequency (f) (from current) | Inverter ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Inverter > Frequency (f) (from current) | Inverter ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Inverter > Frequency (f) (from current) | Inverter ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Inverter > Frequency (f) (from current) | Inverter ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Inverter > Frequency (f) (from current) | Inverter ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Inverter > Current (I) | Inverter ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Inverter > Current (I) | Inverter ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Inverter > Current (I) | Inverter ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Inverter > Current (I) | Inverter ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Inverter > Current (I) | Inverter ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Inverter > Current (I) | Inverter ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Inverter > Current (I) | Inverter ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Inverter > Current (I) | Inverter ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Inverter > Current (I) | Inverter ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Inverter > Current (I) | Inverter ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Inverter > Current (I) | Inverter ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Inverter > Power (P) | Inverter ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Inverter > Power (P) | Inverter ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Inverter > Power (P) | Inverter ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Inverter > Power (P) | Inverter ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Inverter > Power (P) | Inverter ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Inverter > Power (P) | Inverter ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Inverter > Power (P) | Inverter ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Inverter > Power (P) | Inverter ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Inverter > Power (P) | Inverter ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Inverter > Reactive power (Q) | Inverter ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Inverter > Reactive power (Q) | Inverter ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Inverter > Reactive power (Q) | Inverter ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Inverter > Reactive power (Q) | Inverter ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Inverter > Reactive power (Q) | Inverter ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Inverter > Reactive power (Q) | Inverter ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Inverter > Reactive power (Q) | Inverter ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Inverter > Reactive power (Q) | Inverter ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Inverter > Reactive power (Q) | Inverter ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Inverter > Apparent power (S) | Inverter ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Inverter > Apparent power (S) | Inverter ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Inverter > Apparent power (S) | Inverter ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Inverter > Apparent power (S) | Inverter ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Inverter > Apparent power (S) | Inverter ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Inverter > Apparent power (S) | Inverter ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Inverter > Apparent power (S) | Inverter ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Inverter > Apparent power (S) | Inverter ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Inverter > Apparent power (S) | Inverter ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Inverter > Power factor (PF) | Inverter ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Inverter > Power factor (PF) | Inverter ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Inverter > Phase angle | Inverter ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Inverter > Phase angle | Inverter ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Inverter > Phase angle | Inverter ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Inverter > Phase angle | Inverter ¦ A-B phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Inverter > Phase angle | Inverter ¦ A-B phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Inverter > Phase angle | Inverter ¦ A-B phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar > Voltage (V) | Busbar ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar > Voltage (V) | Busbar ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar > Voltage (V) | Busbar ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar > Voltage (V) | Busbar ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar > Voltage (V) | Busbar ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar > Voltage (V) | Busbar ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar > Voltage (V) | Busbar ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar > Voltage (V) | Busbar ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar > Voltage (V) | Busbar ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar > Voltage (V) | Busbar ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar > Voltage (V) | Busbar ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar > Voltage (V) | Busbar ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar > Voltage (V) | Busbar ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar > Voltage (V) | Busbar ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar > Voltage (V) | Busbar ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar > Voltage (V) | Busbar ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar > Frequency (f) | Busbar ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar > Frequency (f) | Busbar ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar > Frequency (f) | Busbar ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar > Frequency (f) | Busbar ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar > Frequency (f) | Busbar ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar > Frequency (f) | Busbar ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100018 | Busbar > Phase angle | Busbar ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar > Phase angle | Busbar ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar > Phase angle | Busbar ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
70100001 | Regulators > GOV | GOV output | AO | % | FLOAT | -100 | 100 | 0
70100000 | Regulators > AVR | AVR output | AO | % | FLOAT | -100 | 100 | 0
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
100097000 | Hardware > Power supply > PCM2.1 | PCM2.1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1

## SHAFT generator parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Busbar A > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar A > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar A > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Busbar A > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Busbar A > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
Busbar A > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Busbar A > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar A > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar A > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar A > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar A > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar A > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar A > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar A > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar A > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Busbar A > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Busbar A > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar A > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar A > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar A > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar A > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar A > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar A > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar A > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Busbar A > Current protections > Fast over-current 1 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Busbar A > Current protections > Fast over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Busbar A > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Busbar A > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 3 | Set point | FLOAT | -110 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 3 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 4 | Set point | FLOAT | -130 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 4 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Busbar A > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Busbar A > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Busbar A > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Busbar A > Current protections > Inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Busbar A > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Busbar A > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Busbar A > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
Busbar A > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Busbar A > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar A > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Busbar A > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Busbar A > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 150 | 1
Busbar A > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 150 | 1
Busbar A > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Active energy difference | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy difference | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar B > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar B > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar B > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar B > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar B > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar B > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar B > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar B > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar B > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar B > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar B > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Busbar B > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 1 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 2 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 3 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar B > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar B > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar B > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar B > Voltage protections > Positive sequence under-voltage | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar B > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar B > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar B > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar B > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 1 | Inhibit |  | ACM wire break
Busbar B > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 2 | Inhibit |  | ACM wire break
Breakers > Bus tie breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Bus tie breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Bus tie breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Bus tie breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Bus tie breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Bus tie breaker configuration > Blackout close | Blackout close | INT32 | Blackout close is OFF |  |  |  |  | 0: Blackout close is OFF, 1: Busbar A is dead, busbar B OK, 2: Busbar A OK, busbar B is dead, 3: One busbar is alive, 4: On
Breakers > Bus tie breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Bus tie breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Bus tie breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Bus tie breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Bus tie breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Bus tie breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Bus tie breaker monitoring > Synchronisation failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Bus tie breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Bus tie breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Bus tie breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Bus tie breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Bus tie breaker monitoring > Closing failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Bus tie breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Bus tie breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > Bus tie breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Short circuit | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Mode > Command mode | Selected mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control
Local > Mode > Command mode | Boot mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Application selector | Application selector | INT32 | MS |  |  |  |  | 800000: LF, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PSM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Hardware > PSM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PSM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Hardware > EIM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Hardware > EIM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > EIM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Hardware > EIM3.1 1 > Relay 4 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Relay 4 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker

## SHAFT generator IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
3306001 | Breakers > Bus tie breaker > Command | BTB static synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
3306002 | Breakers > Bus tie breaker > Command | BTB dynamic synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
20180028 | Breakers > Bus tie breaker > Command | BTB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Bus tie breaker > Command | BTB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180030 | Breakers > Bus tie breaker > Command | BTB open without de-loading | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Bus tie breaker > Command | Block BTB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Bus tie breaker > Feedback | BTB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Bus tie breaker > Feedback | BTB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Bus tie breaker > Feedback | BTB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Bus tie breaker > Feedback | BTB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
110705000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110705001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
60000505 | Local > Mode | Local control | DI |  | BOOL_NUM | 0 | 1 | 0
60000506 | Local > Mode | Remote control | DI |  | BOOL_NUM | 0 | 1 | 0
90020000 | Local > Mode | Switchboard control | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
40219000 | Busbar A > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Busbar A > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219020 | Busbar A > Production counters | Active energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219030 | Busbar A > Production counters | Reactive energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219040 | Busbar A > Production counters | Active energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40219050 | Busbar A > Production counters | Reactive energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40418002 | Busbar A > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Busbar A > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar B > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar B > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
20180002 | Breakers > Bus tie breaker > Controls | BTB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Bus tie breaker > Controls | BTB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180027 | Breakers > Bus tie breaker > Controls | BTB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Bus tie breaker > State | BTB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Bus tie breaker > State | BTB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Bus tie breaker > State | BTB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Bus tie breaker > State | BTB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Bus tie breaker > State | BTB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
110705002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110705003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035012 | Alarm system > State | Any BTB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
60000507 | Local > Mode | Under local control | DO |  | BOOL_NUM | 0 | 1 | 0
60000508 | Local > Mode | Under remote control | DO |  | BOOL_NUM | 0 | 1 | 0
90020005 | Local > Mode | Under switchboard control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
40110000 | Busbar A > Voltage (V) | Busbar A ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Busbar A > Voltage (V) | Busbar A ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Busbar A > Voltage (V) | Busbar A ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Busbar A > Voltage (V) | Busbar A ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Busbar A > Voltage (V) | Busbar A ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Busbar A > Voltage (V) | Busbar A ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Busbar A > Voltage (V) | Busbar A ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Busbar A > Voltage (V) | Busbar A ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Busbar A > Voltage (V) | Busbar A ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Busbar A > Voltage (V) | Busbar A ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Busbar A > Voltage (V) | Busbar A ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Busbar A > Voltage (V) | Busbar A ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Busbar A > Voltage (V) | Busbar A ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Busbar A > Voltage (V) | Busbar A ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Busbar A > Voltage (V) | Busbar A ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Busbar A > Voltage (V) | Busbar A ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Busbar A > Frequency (f) (from current) | Busbar A ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Busbar A > Frequency (f) (from current) | Busbar A ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Busbar A > Current (I) | Busbar A ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Busbar A > Current (I) | Busbar A ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Busbar A > Current (I) | Busbar A ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Busbar A > Current (I) | Busbar A ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Busbar A > Current (I) | Busbar A ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Busbar A > Current (I) | Busbar A ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Busbar A > Current (I) | Busbar A ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Busbar A > Current (I) | Busbar A ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Busbar A > Current (I) | Busbar A ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Busbar A > Current (I) | Busbar A ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Busbar A > Current (I) | Busbar A ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Busbar A > Power (P) | Busbar A ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Busbar A > Power (P) | Busbar A ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Busbar A > Power (P) | Busbar A ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Busbar A > Power (P) | Busbar A ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Busbar A > Power (P) | Busbar A ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Busbar A > Power (P) | Busbar A ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Busbar A > Power (P) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Busbar A > Power (P) | Busbar A ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Busbar A > Power (P) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Busbar A > Reactive power (Q) | Busbar A ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Busbar A > Reactive power (Q) | Busbar A ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Busbar A > Reactive power (Q) | Busbar A ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Busbar A > Reactive power (Q) | Busbar A ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Busbar A > Reactive power (Q) | Busbar A ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Busbar A > Reactive power (Q) | Busbar A ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Busbar A > Reactive power (Q) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Busbar A > Reactive power (Q) | Busbar A ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Busbar A > Reactive power (Q) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Busbar A > Apparent power (S) | Busbar A ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Busbar A > Apparent power (S) | Busbar A ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Busbar A > Apparent power (S) | Busbar A ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Busbar A > Apparent power (S) | Busbar A ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Busbar A > Apparent power (S) | Busbar A ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Busbar A > Apparent power (S) | Busbar A ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Busbar A > Apparent power (S) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Busbar A > Apparent power (S) | Busbar A ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Busbar A > Apparent power (S) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Busbar A > Power factor (PF) | Busbar A ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Busbar A > Power factor (PF) | Busbar A ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Busbar A > Phase angle | Busbar A ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Busbar A > Phase angle | Busbar A ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Busbar A > Phase angle | Busbar A ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Busbar A > Phase angle | Busbar A ¦ Phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Busbar A > Phase angle | Busbar A ¦ Phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Busbar A > Phase angle | Busbar A ¦ Phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar B > Voltage (V) | Busbar B ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar B > Voltage (V) | Busbar B ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar B > Voltage (V) | Busbar B ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar B > Voltage (V) | Busbar B ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar B > Voltage (V) | Busbar B ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar B > Voltage (V) | Busbar B ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar B > Voltage (V) | Busbar B ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar B > Voltage (V) | Busbar B ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar B > Voltage (V) | Busbar B ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar B > Voltage (V) | Busbar B ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar B > Voltage (V) | Busbar B ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar B > Voltage (V) | Busbar B ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar B > Voltage (V) | Busbar B ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar B > Voltage (V) | Busbar B ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar B > Voltage (V) | Busbar B ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar B > Voltage (V) | Busbar B ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar B > Frequency (f) | Busbar B ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar B > Frequency (f) | Busbar B ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar B > Frequency (f) | Busbar B ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar B > Frequency (f) | Busbar B ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar B > Frequency (f) | Busbar B ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar B > Frequency (f) | Busbar B ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100018 | Busbar B > Phase angle | Busbar B ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar B > Phase angle | Busbar B ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar B > Phase angle | Busbar B ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
100041000 | Hardware > Power supply > PSM3.1 1 | PSM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
100049000 | Hardware > Power supply > EIM3.1 1 | EIM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1

## SHORE connection parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Busbar A > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar A > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar A > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Busbar A > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Busbar A > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
Busbar A > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Busbar A > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar A > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar A > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar A > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar A > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar A > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar A > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar A > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar A > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Busbar A > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Busbar A > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar A > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar A > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar A > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar A > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar A > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar A > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar A > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Busbar A > Current protections > Fast over-current 1 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Busbar A > Current protections > Fast over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Busbar A > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Busbar A > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 3 | Set point | FLOAT | -110 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 3 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 4 | Set point | FLOAT | -130 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 4 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Busbar A > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Busbar A > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Busbar A > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Busbar A > Current protections > Inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Busbar A > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Busbar A > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Busbar A > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
Busbar A > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Busbar A > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar A > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Busbar A > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Busbar A > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 150 | 1
Busbar A > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 150 | 1
Busbar A > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Active energy difference | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy difference | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar B > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar B > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar B > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar B > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar B > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar B > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar B > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar B > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar B > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar B > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar B > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Busbar B > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 1 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 2 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 3 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar B > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar B > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar B > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar B > Voltage protections > Positive sequence under-voltage | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar B > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar B > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar B > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar B > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 1 | Inhibit |  | ACM wire break
Busbar B > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 2 | Inhibit |  | ACM wire break
Breakers > Bus tie breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Bus tie breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Bus tie breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Bus tie breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Bus tie breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Bus tie breaker configuration > Blackout close | Blackout close | INT32 | Blackout close is OFF |  |  |  |  | 0: Blackout close is OFF, 1: Busbar A is dead, busbar B OK, 2: Busbar A OK, busbar B is dead, 3: One busbar is alive, 4: On
Breakers > Bus tie breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Bus tie breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Bus tie breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Bus tie breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Bus tie breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Bus tie breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Bus tie breaker monitoring > Synchronisation failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Bus tie breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Bus tie breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Bus tie breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Bus tie breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Bus tie breaker monitoring > Closing failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Bus tie breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Bus tie breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > Bus tie breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Short circuit | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Mode > Command mode | Selected mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control
Local > Mode > Command mode | Boot mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Application selector | Application selector | INT32 | MS |  |  |  |  | 800000: LF, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PSM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Hardware > PSM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PSM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Hardware > EIM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Hardware > EIM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > EIM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Hardware > EIM3.1 1 > Relay 4 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Relay 4 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker

## SHORE connection IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
3306001 | Breakers > Bus tie breaker > Command | BTB static synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
3306002 | Breakers > Bus tie breaker > Command | BTB dynamic synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
20180028 | Breakers > Bus tie breaker > Command | BTB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Bus tie breaker > Command | BTB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180030 | Breakers > Bus tie breaker > Command | BTB open without de-loading | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Bus tie breaker > Command | Block BTB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Bus tie breaker > Feedback | BTB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Bus tie breaker > Feedback | BTB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Bus tie breaker > Feedback | BTB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Bus tie breaker > Feedback | BTB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
110705000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110705001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
60000505 | Local > Mode | Local control | DI |  | BOOL_NUM | 0 | 1 | 0
60000506 | Local > Mode | Remote control | DI |  | BOOL_NUM | 0 | 1 | 0
90020000 | Local > Mode | Switchboard control | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
40219000 | Busbar A > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Busbar A > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219020 | Busbar A > Production counters | Active energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219030 | Busbar A > Production counters | Reactive energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219040 | Busbar A > Production counters | Active energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40219050 | Busbar A > Production counters | Reactive energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40418002 | Busbar A > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Busbar A > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar B > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar B > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
20180002 | Breakers > Bus tie breaker > Controls | BTB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Bus tie breaker > Controls | BTB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180027 | Breakers > Bus tie breaker > Controls | BTB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Bus tie breaker > State | BTB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Bus tie breaker > State | BTB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Bus tie breaker > State | BTB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Bus tie breaker > State | BTB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Bus tie breaker > State | BTB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
110705002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110705003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035012 | Alarm system > State | Any BTB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
60000507 | Local > Mode | Under local control | DO |  | BOOL_NUM | 0 | 1 | 0
60000508 | Local > Mode | Under remote control | DO |  | BOOL_NUM | 0 | 1 | 0
90020005 | Local > Mode | Under switchboard control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
40110000 | Busbar A > Voltage (V) | Busbar A ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Busbar A > Voltage (V) | Busbar A ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Busbar A > Voltage (V) | Busbar A ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Busbar A > Voltage (V) | Busbar A ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Busbar A > Voltage (V) | Busbar A ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Busbar A > Voltage (V) | Busbar A ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Busbar A > Voltage (V) | Busbar A ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Busbar A > Voltage (V) | Busbar A ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Busbar A > Voltage (V) | Busbar A ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Busbar A > Voltage (V) | Busbar A ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Busbar A > Voltage (V) | Busbar A ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Busbar A > Voltage (V) | Busbar A ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Busbar A > Voltage (V) | Busbar A ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Busbar A > Voltage (V) | Busbar A ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Busbar A > Voltage (V) | Busbar A ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Busbar A > Voltage (V) | Busbar A ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Busbar A > Frequency (f) (from current) | Busbar A ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Busbar A > Frequency (f) (from current) | Busbar A ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Busbar A > Current (I) | Busbar A ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Busbar A > Current (I) | Busbar A ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Busbar A > Current (I) | Busbar A ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Busbar A > Current (I) | Busbar A ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Busbar A > Current (I) | Busbar A ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Busbar A > Current (I) | Busbar A ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Busbar A > Current (I) | Busbar A ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Busbar A > Current (I) | Busbar A ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Busbar A > Current (I) | Busbar A ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Busbar A > Current (I) | Busbar A ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Busbar A > Current (I) | Busbar A ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Busbar A > Power (P) | Busbar A ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Busbar A > Power (P) | Busbar A ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Busbar A > Power (P) | Busbar A ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Busbar A > Power (P) | Busbar A ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Busbar A > Power (P) | Busbar A ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Busbar A > Power (P) | Busbar A ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Busbar A > Power (P) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Busbar A > Power (P) | Busbar A ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Busbar A > Power (P) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Busbar A > Reactive power (Q) | Busbar A ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Busbar A > Reactive power (Q) | Busbar A ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Busbar A > Reactive power (Q) | Busbar A ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Busbar A > Reactive power (Q) | Busbar A ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Busbar A > Reactive power (Q) | Busbar A ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Busbar A > Reactive power (Q) | Busbar A ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Busbar A > Reactive power (Q) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Busbar A > Reactive power (Q) | Busbar A ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Busbar A > Reactive power (Q) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Busbar A > Apparent power (S) | Busbar A ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Busbar A > Apparent power (S) | Busbar A ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Busbar A > Apparent power (S) | Busbar A ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Busbar A > Apparent power (S) | Busbar A ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Busbar A > Apparent power (S) | Busbar A ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Busbar A > Apparent power (S) | Busbar A ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Busbar A > Apparent power (S) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Busbar A > Apparent power (S) | Busbar A ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Busbar A > Apparent power (S) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Busbar A > Power factor (PF) | Busbar A ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Busbar A > Power factor (PF) | Busbar A ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Busbar A > Phase angle | Busbar A ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Busbar A > Phase angle | Busbar A ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Busbar A > Phase angle | Busbar A ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Busbar A > Phase angle | Busbar A ¦ Phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Busbar A > Phase angle | Busbar A ¦ Phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Busbar A > Phase angle | Busbar A ¦ Phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar B > Voltage (V) | Busbar B ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar B > Voltage (V) | Busbar B ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar B > Voltage (V) | Busbar B ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar B > Voltage (V) | Busbar B ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar B > Voltage (V) | Busbar B ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar B > Voltage (V) | Busbar B ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar B > Voltage (V) | Busbar B ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar B > Voltage (V) | Busbar B ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar B > Voltage (V) | Busbar B ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar B > Voltage (V) | Busbar B ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar B > Voltage (V) | Busbar B ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar B > Voltage (V) | Busbar B ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar B > Voltage (V) | Busbar B ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar B > Voltage (V) | Busbar B ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar B > Voltage (V) | Busbar B ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar B > Voltage (V) | Busbar B ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar B > Frequency (f) | Busbar B ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar B > Frequency (f) | Busbar B ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar B > Frequency (f) | Busbar B ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar B > Frequency (f) | Busbar B ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar B > Frequency (f) | Busbar B ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar B > Frequency (f) | Busbar B ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100018 | Busbar B > Phase angle | Busbar B ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar B > Phase angle | Busbar B ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar B > Phase angle | Busbar B ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
100041000 | Hardware > Power supply > PSM3.1 1 | PSM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
100049000 | Hardware > Power supply > EIM3.1 1 | EIM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1

## BUS TIE breaker parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Busbar A > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar A > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar A > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Busbar A > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Busbar A > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
Busbar A > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Busbar A > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar A > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar A > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar A > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar A > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar A > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar A > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar A > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar A > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Busbar A > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Busbar A > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar A > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar A > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar A > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar A > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar A > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar A > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar A > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Busbar A > Current protections > Fast over-current 1 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Busbar A > Current protections > Fast over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Busbar A > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Busbar A > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 3 | Set point | FLOAT | -110 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 3 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 4 | Set point | FLOAT | -130 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 4 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Busbar A > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Busbar A > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Busbar A > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Busbar A > Current protections > Inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Busbar A > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Busbar A > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Busbar A > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
Busbar A > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Busbar A > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar A > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Busbar A > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Busbar A > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 150 | 1
Busbar A > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 150 | 1
Busbar A > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar A > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Active energy difference | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy difference | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar B > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar B > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar B > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar B > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar B > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar B > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar B > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar B > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar B > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar B > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar B > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Busbar B > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 1 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 2 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 3 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar B > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar B > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar B > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar B > Voltage protections > Positive sequence under-voltage | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar B > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar B > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar B > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar B > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 1 | Inhibit |  | ACM wire break
Busbar B > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 2 | Inhibit |  | ACM wire break
Breakers > Bus tie breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Bus tie breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Bus tie breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Bus tie breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Bus tie breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Bus tie breaker configuration > Blackout close | Blackout close | INT32 | Blackout close is OFF |  |  |  |  | 0: Blackout close is OFF, 1: Busbar A is dead, busbar B OK, 2: Busbar A OK, busbar B is dead, 3: One busbar is alive, 4: On
Breakers > Bus tie breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Bus tie breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Bus tie breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Bus tie breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Bus tie breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Bus tie breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Bus tie breaker monitoring > Synchronisation failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Bus tie breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Bus tie breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Bus tie breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Bus tie breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Bus tie breaker monitoring > Closing failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Bus tie breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Bus tie breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > Bus tie breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Short circuit | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Mode > Command mode | Selected mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control
Local > Mode > Command mode | Boot mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Application selector | Application selector | INT32 | MS |  |  |  |  | 800000: LF, 800001: LC, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker | X
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip bus tie breaker

## BUS TIE breaker IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
3306001 | Breakers > Bus tie breaker > Command | BTB static synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
3306002 | Breakers > Bus tie breaker > Command | BTB dynamic synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
20180028 | Breakers > Bus tie breaker > Command | BTB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Bus tie breaker > Command | BTB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180030 | Breakers > Bus tie breaker > Command | BTB open without de-loading | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Bus tie breaker > Command | Block BTB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Bus tie breaker > Feedback | BTB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Bus tie breaker > Feedback | BTB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Bus tie breaker > Feedback | BTB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Bus tie breaker > Feedback | BTB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
110705000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110705001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
60000505 | Local > Mode | Local control | DI |  | BOOL_NUM | 0 | 1 | 0
60000506 | Local > Mode | Remote control | DI |  | BOOL_NUM | 0 | 1 | 0
90020000 | Local > Mode | Switchboard control | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
40219000 | Busbar A > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Busbar A > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219020 | Busbar A > Production counters | Active energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219030 | Busbar A > Production counters | Reactive energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219040 | Busbar A > Production counters | Active energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40219050 | Busbar A > Production counters | Reactive energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40418002 | Busbar A > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Busbar A > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar B > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar B > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
20180002 | Breakers > Bus tie breaker > Controls | BTB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Bus tie breaker > Controls | BTB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180027 | Breakers > Bus tie breaker > Controls | BTB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Bus tie breaker > State | BTB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Bus tie breaker > State | BTB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Bus tie breaker > State | BTB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Bus tie breaker > State | BTB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Bus tie breaker > State | BTB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
110705002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110705003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035012 | Alarm system > State | Any BTB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
60000507 | Local > Mode | Under local control | DO |  | BOOL_NUM | 0 | 1 | 0
60000508 | Local > Mode | Under remote control | DO |  | BOOL_NUM | 0 | 1 | 0
90020005 | Local > Mode | Under switchboard control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
40110000 | Busbar A > Voltage (V) | Busbar A ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Busbar A > Voltage (V) | Busbar A ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Busbar A > Voltage (V) | Busbar A ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Busbar A > Voltage (V) | Busbar A ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Busbar A > Voltage (V) | Busbar A ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Busbar A > Voltage (V) | Busbar A ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Busbar A > Voltage (V) | Busbar A ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Busbar A > Voltage (V) | Busbar A ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Busbar A > Voltage (V) | Busbar A ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Busbar A > Voltage (V) | Busbar A ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Busbar A > Voltage (V) | Busbar A ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Busbar A > Voltage (V) | Busbar A ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Busbar A > Voltage (V) | Busbar A ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Busbar A > Voltage (V) | Busbar A ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Busbar A > Voltage (V) | Busbar A ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Busbar A > Voltage (V) | Busbar A ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Busbar A > Frequency (f) (from current) | Busbar A ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Busbar A > Frequency (f) (from current) | Busbar A ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Busbar A > Current (I) | Busbar A ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Busbar A > Current (I) | Busbar A ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Busbar A > Current (I) | Busbar A ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Busbar A > Current (I) | Busbar A ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Busbar A > Current (I) | Busbar A ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Busbar A > Current (I) | Busbar A ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Busbar A > Current (I) | Busbar A ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Busbar A > Current (I) | Busbar A ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Busbar A > Current (I) | Busbar A ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Busbar A > Current (I) | Busbar A ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Busbar A > Current (I) | Busbar A ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Busbar A > Power (P) | Busbar A ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Busbar A > Power (P) | Busbar A ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Busbar A > Power (P) | Busbar A ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Busbar A > Power (P) | Busbar A ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Busbar A > Power (P) | Busbar A ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Busbar A > Power (P) | Busbar A ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Busbar A > Power (P) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Busbar A > Power (P) | Busbar A ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Busbar A > Power (P) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Busbar A > Reactive power (Q) | Busbar A ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Busbar A > Reactive power (Q) | Busbar A ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Busbar A > Reactive power (Q) | Busbar A ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Busbar A > Reactive power (Q) | Busbar A ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Busbar A > Reactive power (Q) | Busbar A ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Busbar A > Reactive power (Q) | Busbar A ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Busbar A > Reactive power (Q) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Busbar A > Reactive power (Q) | Busbar A ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Busbar A > Reactive power (Q) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Busbar A > Apparent power (S) | Busbar A ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Busbar A > Apparent power (S) | Busbar A ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Busbar A > Apparent power (S) | Busbar A ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Busbar A > Apparent power (S) | Busbar A ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Busbar A > Apparent power (S) | Busbar A ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Busbar A > Apparent power (S) | Busbar A ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Busbar A > Apparent power (S) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Busbar A > Apparent power (S) | Busbar A ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Busbar A > Apparent power (S) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Busbar A > Power factor (PF) | Busbar A ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Busbar A > Power factor (PF) | Busbar A ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Busbar A > Phase angle | Busbar A ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Busbar A > Phase angle | Busbar A ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Busbar A > Phase angle | Busbar A ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Busbar A > Phase angle | Busbar A ¦ Phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Busbar A > Phase angle | Busbar A ¦ Phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Busbar A > Phase angle | Busbar A ¦ Phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar B > Voltage (V) | Busbar B ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar B > Voltage (V) | Busbar B ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar B > Voltage (V) | Busbar B ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar B > Voltage (V) | Busbar B ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar B > Voltage (V) | Busbar B ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar B > Voltage (V) | Busbar B ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar B > Voltage (V) | Busbar B ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar B > Voltage (V) | Busbar B ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar B > Voltage (V) | Busbar B ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar B > Voltage (V) | Busbar B ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar B > Voltage (V) | Busbar B ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar B > Voltage (V) | Busbar B ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar B > Voltage (V) | Busbar B ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar B > Voltage (V) | Busbar B ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar B > Voltage (V) | Busbar B ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar B > Voltage (V) | Busbar B ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar B > Frequency (f) | Busbar B ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar B > Frequency (f) | Busbar B ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar B > Frequency (f) | Busbar B ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar B > Frequency (f) | Busbar B ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar B > Frequency (f) | Busbar B ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar B > Frequency (f) | Busbar B ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100018 | Busbar B > Phase angle | Busbar B ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar B > Phase angle | Busbar B ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar B > Phase angle | Busbar B ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
100097000 | Hardware > Power supply > PCM2.1 | PCM2.1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1