## Descriptions
AGC 200 Modbus descriptions
Software version
The information contained in these tables is applicable to software version 4.68.2.x of the AGC 200 product.
Row | Hyperlink index
13 | Modbus function codes
24 | Discrete output coil
32 | Discrete input contact
41 | Output holding register
50 | Input register
Back to index | Modbus function codes
| Function code | Description
| 01 | Read a single or multiple discrete output coils.
| 02 | Read a single or multiple discrete input contacts.
| 03 | Read a single or multiple output holding registers.
| 04 | Read a single or multiple input registers.
| 05 | Write a value to a single discrete output coil.
| 06 | Write a value to a single output holding register.
| 15 | Write a value to multiple consecutive discrete output coils.
| 16 | Write a value to multiple consecutive output holding registers.
Back to index | Discrete output coil
| Function code | Effect
| 01 | Read
| 05 or 15 | Write
| Function group | Description
| Command Flags | Activate a command in the controller. Read: The controller always returns 0 (false). Write: The controller executes the command if you write 1 (true).
Back to index | Discrete input contact
| Function code | Effect
| 02 | Read
| Function group | Description
| Status Flag | Read whether a status flag is activated. The controller returns 0 (false) when the status flag is not activated. The controller returns 1 (true) when the status flag is activated.
| Digital Input | Read the state of a digital input on the controller. The controller returns 0 (false) when the digital input is inactive. The controller returns 1 (true) when the digital input is active.
| Digital Output | Read the state of a digital output on the controller. The controller returns 0 (false) when the digital output is inactive. The controller returns 1 (true) when the digital output is active.
Back to index | Output holding register
| Function code | Effect
| 03 | Read
| 06 or 16 | Write
| Function group | Description
| Control Command | Activate a command in the controller. Read: The controller always returns 0 (false) from the bits. Write: The controller executes the command if you write 1 (true) to the address bit.
| Control Time Command | Read and write the time and date values of the controller. Read: The controller returns the value of the associated function. Write: The controller changes the value of the associated function if a valid value is entered.
Back to index | Input register
| Function code | Effect
| 04 | Read
| Function group | Description
| AC Measurement | Read the operating value of the associated AC measurement.
| Alarm | Read one bit to see whether the alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| PM AC Measurement | Read the operating value of the associated Power Management measurements and settings.
| PM Alarm | Read one bit to see whether the Power Management status or alarm is activated. The controller returns 0 (false) when the status/alarm is not activated. The controller returns 1 (true) when the status/alarm is activated.

## Discrete output coil (01;05;15)
Discrete output coil (01;05;15)
Function group | Modbus address | PLC address | Modbus function code | Controller function name | BTB | MAINS | DG
Command Flags | 0 | 1 | 01; 05; 15 | Remote start |  |  | X
Command Flags | 1 | 2 | 01; 05; 15 | Remote GB ON |  |  | X
Command Flags | 1 | 2 | 01; 05; 15 | Remote BTB ON | X
Command Flags | 1 | 2 | 01; 05; 15 | Remote TB ON |  | X
Command Flags | 2 | 3 | 01; 05; 15 | Remote GB OFF |  |  | X
Command Flags | 2 | 3 | 01; 05; 15 | Remote BTB OFF | X
Command Flags | 2 | 3 | 01; 05; 15 | Remote TB OFF |  | X
Command Flags | 3 | 4 | 01; 05; 15 | Remote stop |  |  | X
Command Flags | 4 | 5 | 01; 05; 15 | Alarm inhibit 1 | X | X | X
Command Flags | 5 | 6 | 01; 05; 15 | Alarm inhibit 2 | X | X | X
Command Flags | 6 | 7 | 01; 05; 15 | Alarm inhibit 3 | X | X | X
Command Flags | 7 | 8 | 01; 05; 15 | Reset GOV/AVR regulation output to offset |  |  | X
Command Flags | 9 | 10 | 01; 05; 15 | Alarm ack. | X | X | X
Command Flags | 10 | 11 | 01; 05; 15 | Nominal setting 1 | X | X | X
Command Flags | 11 | 12 | 01; 05; 15 | Nominal setting 2 | X | X | X
Command Flags | 12 | 13 | 01; 05; 15 | Nominal setting 3 | X | X | X
Command Flags | 13 | 14 | 01; 05; 15 | Nominal setting 4 | X | X | X
Command Flags | 14 | 15 | 01; 05; 15 | Start+sync. (semi) |  |  | X
Command Flags | 15 | 16 | 01; 05; 15 | Deload/stop (semi) |  |  | X
Command Flags | 16 | 17 | 01; 05; 15 | Island |  | X | X
Command Flags | 17 | 18 | 01; 05; 15 | Automatic mains failure (AMF) |  | X | X
Command Flags | 18 | 19 | 01; 05; 15 | Peak shaving |  | X | X
Command Flags | 19 | 20 | 01; 05; 15 | Fixed power |  | X | X
Command Flags | 20 | 21 | 01; 05; 15 | Mains power export (MPE) |  | X | X
Command Flags | 21 | 22 | 01; 05; 15 | Load takeover (LTO) |  | X | X
Command Flags | 24 | 25 | 01; 05; 15 | MB ON |  | X | X
Command Flags | 25 | 26 | 01; 05; 15 | MB OFF |  | X | X
Command Flags | 26 | 27 | 01; 05; 15 | Auto start/stop |  | X | X
Command Flags | 27 | 28 | 01; 05; 15 | Manual mode |  |  | X
Command Flags | 28 | 29 | 01; 05; 15 | Semi-auto mode | X | X | X
Command Flags | 29 | 30 | 01; 05; 15 | Auto mode | X | X | X
Command Flags | 30 | 31 | 01; 05; 15 | Test mode |  | X | X
Command Flags | 31 | 32 | 01; 05; 15 | External frequency control |  |  | X
Command Flags | 32 | 33 | 01; 05; 15 | External voltage control |  |  | X
Command Flags | 33 | 34 | 01; 05; 15 | External power control |  | X | X
Command Flags | 34 | 35 | 01; 05; 15 | External reactive power control |  |  | X
Command Flags | 35 | 36 | 01; 05; 15 | External power factor control |  |  | X
Command Flags | 36 | 37 | 01; 05; 15 | Capacitive PF |  |  | X
Command Flags | 37 | 38 | 01; 05; 15 | Base load |  |  | X
Command Flags | 38 | 39 | 01; 05; 15 | 1. priority |  |  | X
Command Flags | 40 | 41 | 01; 05; 15 | Application 1 | X | X | X
Command Flags | 41 | 42 | 01; 05; 15 | Application 2 | X | X | X
Command Flags | 42 | 43 | 01; 05; 15 | Application 3 | X | X | X
Command Flags | 43 | 44 | 01; 05; 15 | Application 4 | X | X | X
Command Flags | 44 | 45 | 01; 05; 15 | Battery test |  |  | X
Command Flags | 46 | 47 | 01; 05; 15 | Synchronise clock to 4:00 a.m. | X | X | X
Command Flags | 48 | 49 | 01; 05; 15 | Virtual event 1 | X | X | X
Command Flags | 49 | 50 | 01; 05; 15 | Virtual event 2 | X | X | X
Command Flags | 50 | 51 | 01; 05; 15 | Virtual event 3 | X | X | X
Command Flags | 51 | 52 | 01; 05; 15 | Virtual event 4 | X | X | X
Command Flags | 52 | 53 | 01; 05; 15 | Virtual event 5 | X | X | X
Command Flags | 53 | 54 | 01; 05; 15 | Virtual event 6 | X | X | X
Command Flags | 54 | 55 | 01; 05; 15 | Virtual event 7 | X | X | X
Command Flags | 55 | 56 | 01; 05; 15 | Virtual event 8 | X | X | X
Command Flags | 56 | 57 | 01; 05; 15 | Virtual event 9 | X | X | X
Command Flags | 57 | 58 | 01; 05; 15 | Virtual event 10 | X | X | X
Command Flags | 58 | 59 | 01; 05; 15 | Virtual event 11 | X | X | X
Command Flags | 59 | 60 | 01; 05; 15 | Virtual event 12 | X | X | X
Command Flags | 60 | 61 | 01; 05; 15 | Virtual event 13 | X | X | X
Command Flags | 61 | 62 | 01; 05; 15 | Virtual event 14 | X | X | X
Command Flags | 62 | 63 | 01; 05; 15 | Virtual event 15 | X | X | X
Command Flags | 63 | 64 | 01; 05; 15 | Virtual event 16 | X | X | X
Command Flags | 64 | 65 | 01; 05; 15 | Virtual event 17 | X | X | X
Command Flags | 65 | 66 | 01; 05; 15 | Virtual event 18 | X | X | X
Command Flags | 66 | 67 | 01; 05; 15 | Virtual event 19 | X | X | X
Command Flags | 67 | 68 | 01; 05; 15 | Virtual event 20 | X | X | X
Command Flags | 68 | 69 | 01; 05; 15 | Virtual event 21 | X | X | X
Command Flags | 69 | 70 | 01; 05; 15 | Virtual event 22 | X | X | X
Command Flags | 70 | 71 | 01; 05; 15 | Virtual event 23 | X | X | X
Command Flags | 71 | 72 | 01; 05; 15 | Virtual event 24 | X | X | X
Command Flags | 72 | 73 | 01; 05; 15 | Virtual event 25 | X | X | X
Command Flags | 73 | 74 | 01; 05; 15 | Virtual event 26 | X | X | X
Command Flags | 74 | 75 | 01; 05; 15 | Virtual event 27 | X | X | X
Command Flags | 75 | 76 | 01; 05; 15 | Virtual event 28 | X | X | X
Command Flags | 76 | 77 | 01; 05; 15 | Virtual event 29 | X | X | X
Command Flags | 77 | 78 | 01; 05; 15 | Virtual event 30 | X | X | X
Command Flags | 78 | 79 | 01; 05; 15 | Virtual event 31 | X | X | X
Command Flags | 79 | 80 | 01; 05; 15 | Virtual event 32 | X | X | X
Command Flags | 121 | 122 | 01; 05; 15 | Clear log | X | X | X
Command Flags | 122 | 123 | 01; 05; 15 | Clear Parameter edits | X | X | X
Command Flags | 123 | 124 | 01; 05; 15 | Enable external frequency control |  |  | X
Command Flags | 124 | 125 | 01; 05; 15 | Disable external frequency control |  |  | X
Command Flags | 125 | 126 | 01; 05; 15 | Enable external voltage control |  |  | X
Command Flags | 126 | 127 | 01; 05; 15 | Disable external voltage control |  |  | X
Command Flags | 127 | 128 | 01; 05; 15 | Enable external power control |  | X | X
Command Flags | 128 | 129 | 01; 05; 15 | Disable external power control |  | X | X
Command Flags | 129 | 130 | 01; 05; 15 | Enable external VAr control |  |  | X
Command Flags | 130 | 131 | 01; 05; 15 | Disable external VAr control |  |  | X
Command Flags | 131 | 132 | 01; 05; 15 | Enable external CosPhi control |  |  | X
Command Flags | 132 | 133 | 01; 05; 15 | Disable external CosPhi control |  |  | X
Command Flags | 133 | 134 | 01; 05; 15 | Enable PM base load |  |  | X
Command Flags | 134 | 135 | 01; 05; 15 | Disable PM base load |  |  | X
Command Flags | 135 | 136 | 01; 05; 15 | Reset horn | X | X | X
Command Flags | 137 | 138 | 01; 05; 15 | DVC 310/510: Reset Alarms |  |  | X
Command Flags | 138 | 139 | 01; 05; 15 | EIC: Change DM1 buffer |  |  | X
Command Flags | 139 | 140 | 01; 05; 15 | EIC: Request DM2 |  |  | X
Command Flags | 140 | 141 | 01; 05; 15 | EIC: Change secondary DM1 buffer |  |  | X
Command Flags | 141 | 142 | 01; 05; 15 | EIC: Request KWP2000 |  |  | X
Note on A4: More information about each function group is available in the description sheet.
Note on D4: 01 - Read single or multiple 05 - Write single 15 - Write multiple
Note on E4: The controller function name shows the name of the parameter in the Utility Software. Some functions might contain additional information.
Note on F4: Indicates if the address is available in the BUS TIE breaker controller.
Note on G4: Indicates if the address is available in the MAINS controller.
Note on H4: Indicates if the address is available in the GENSET controller.

## Discrete input contact (02)
Discrete input contact (02)
Function group | Modbus address | PLC address | Modbus function code | Controller function name | BTB | MAINS | DG
Status Flag | 1 | 100002 | 2 | MB position ON |  | X | X
Status Flag | 3 | 100004 | 2 | Running |  |  | X
Status Flag | 4 | 100005 | 2 | Generator voltage/frequency OK |  |  | X
Status Flag | 4 | 100005 | 2 | Busbar voltage/frequency OK |  | X
Status Flag | 4 | 100005 | 2 | Busbar B voltage/frequency OK | X
Status Flag | 5 | 100006 | 2 | Mains failure |  | X | X
Status Flag | 6 | 100007 | 2 | Block mode |  |  | X
Status Flag | 7 | 100008 | 2 | Manual mode |  |  | X
Status Flag | 8 | 100009 | 2 | Semi-auto mode | X | X | X
Status Flag | 9 | 100010 | 2 | Auto mode | X | X | X
Status Flag | 10 | 100011 | 2 | Test mode |  | X | X
Status Flag | 13 | 100014 | 2 | Island |  | X | X
Status Flag | 14 | 100015 | 2 | Automatic mains failure (AMF) |  | X | X
Status Flag | 15 | 100016 | 2 | Peak shaving |  | X | X
Status Flag | 16 | 100017 | 2 | Fixed power |  | X | X
Status Flag | 17 | 100018 | 2 | Mains power export (MPE) |  | X | X
Status Flag | 18 | 100019 | 2 | Load takeover (LTO) |  | X | X
Status Flag | 19 | 100020 | 2 | Power management |  |  | X
Status Flag | 20 | 100021 | 2 | Any alarm on PMS ID1 | X | X | X
Status Flag | 21 | 100022 | 2 | Any alarm on PMS ID2 | X | X | X
Status Flag | 22 | 100023 | 2 | Any alarm on PMS ID3 | X | X | X
Status Flag | 23 | 100024 | 2 | Any alarm on PMS ID4 | X | X | X
Status Flag | 24 | 100025 | 2 | Any alarm on PMS ID5 | X | X | X
Status Flag | 25 | 100026 | 2 | Any alarm on PMS ID6 | X | X | X
Status Flag | 26 | 100027 | 2 | Any alarm on PMS ID7 | X | X | X
Status Flag | 27 | 100028 | 2 | Any alarm on PMS ID8 | X | X | X
Status Flag | 28 | 100029 | 2 | Any alarm mains (Mains Command Unit) | X | X | X
Status Flag | 29 | 100030 | 2 | Battery test |  |  | X
Status Flag | 31 | 100032 | 2 | Ready auto-start DG1 | X | X | X
Status Flag | 32 | 100033 | 2 | Ready auto-start DG2 | X | X | X
Status Flag | 33 | 100034 | 2 | Ready auto-start DG3 | X | X | X
Status Flag | 34 | 100035 | 2 | Ready auto-start DG4 | X | X | X
Status Flag | 35 | 100036 | 2 | Ready auto-start DG5 | X | X | X
Status Flag | 36 | 100037 | 2 | Ready auto-start DG6 | X | X | X
Status Flag | 37 | 100038 | 2 | Ready auto-start DG7 | X | X | X
Status Flag | 38 | 100039 | 2 | Ready auto-start DG8 | X | X | X
Status Flag | 53 | 100054 | 2 | Mains sync. inhibit |  | X | X
Status Flag | 54 | 100055 | 2 | Any mains sync. inhibit | X | X | X
Status Flag | 518 | 100519 | 2 | TB Pos On |  | X
Status Flag | 518 | 100519 | 2 | GB position ON |  |  | X
Status Flag | 518 | 100519 | 2 | BTB Pos ON | X
Digital Input | 22500 | 122501 | 2 | Digital input 77 | X | X | X
Digital Input | 22501 | 122502 | 2 | Digital input 78 | X | X | X
Digital Input | 22502 | 122503 | 2 | Digital input 79 | X | X | X
Digital Input | 22503 | 122504 | 2 | Digital input 80 | X | X | X
Digital Input | 22504 | 122505 | 2 | Digital input 81 | X | X | X
Digital Input | 22505 | 122506 | 2 | Digital input 82 | X | X | X
Digital Input | 22506 | 122507 | 2 | Digital input 83 | X | X | X
Digital Input | 22507 | 122508 | 2 | Digital input 84 | X | X | X
Digital Input | 22508 | 122509 | 2 | Digital input 85 | X | X | X
Digital Input | 22509 | 122510 | 2 | Digital input 86 | X | X | X
Digital Input | 22515 | 122516 | 2 | Stop coil wirebreak |  |  | X
Digital Input | 22516 | 122517 | 2 | Emergency stop | X | X | X
Digital Input | 22591 | 122592 | 2 | Binary in 48 | X | X | X
Digital Input | 22592 | 122593 | 2 | Binary in 47 | X | X | X
Digital Input | 22593 | 122594 | 2 | Binary in 46 | X | X | X
Digital Input | 22594 | 122595 | 2 | External digital input/CIO 116 no. 1. Input 10 | X | X | X
Digital Input | 22595 | 122596 | 2 | External digital input/CIO 116 no. 1. Input 11 | X | X | X
Digital Input | 22596 | 122597 | 2 | External digital input/CIO 116 no. 1. Input 12 | X | X | X
Digital Input | 22597 | 122598 | 2 | External digital input/CIO 116 no. 1. Input 13 | X | X | X
Digital Input | 22598 | 122599 | 2 | External digital input/CIO 116 no. 1. Input 14 | X | X | X
Digital Input | 22599 | 122600 | 2 | External digital input/CIO 116 no. 1. Input 15 | X | X | X
Digital Input | 22600 | 122601 | 2 | External digital input/CIO 116 no. 1. Input 16 | X | X | X
Digital Input | 22601 | 122602 | 2 | External digital input/CIO 116 no. 1. Input 17 | X | X | X
Digital Input | 22602 | 122603 | 2 | External digital input/CIO 116 no. 1. Input 19 | X | X | X
Digital Input | 22603 | 122604 | 2 | External digital input/CIO 116 no. 1. Input 20 | X | X | X
Digital Input | 22604 | 122605 | 2 | External digital input/CIO 116 no. 1. Input 21 | X | X | X
Digital Input | 22605 | 122606 | 2 | External digital input/CIO 116 no. 1. Input 22 | X | X | X
Digital Input | 22606 | 122607 | 2 | External digital input/CIO 116 no. 1. Input 23 | X | X | X
Digital Input | 22607 | 122608 | 2 | External digital input/CIO 116 no. 1. Input 24 | X | X | X
Digital Input | 22608 | 122609 | 2 | External digital input/CIO 116 no. 1. Input 25 | X | X | X
Digital Input | 22609 | 122610 | 2 | External digital input/CIO 116 no. 1. Input 26 | X | X | X
Digital Input | 22610 | 122611 | 2 | CIO 116 no. 2. Input 10 | X | X | X
Digital Input | 22611 | 122612 | 2 | CIO 116 no. 2. Input 11 | X | X | X
Digital Input | 22612 | 122613 | 2 | CIO 116 no. 2. Input 12 | X | X | X
Digital Input | 22613 | 122614 | 2 | CIO 116 no. 2. Input 13 | X | X | X
Digital Input | 22614 | 122615 | 2 | CIO 116 no. 2. Input 14 | X | X | X
Digital Input | 22615 | 122616 | 2 | CIO 116 no. 2. Input 15 | X | X | X
Digital Input | 22616 | 122617 | 2 | CIO 116 no. 2. Input 16 | X | X | X
Digital Input | 22617 | 122618 | 2 | CIO 116 no. 2. Input 17 | X | X | X
Digital Input | 22618 | 122619 | 2 | CIO 116 no. 2. Input 19 | X | X | X
Digital Input | 22619 | 122620 | 2 | CIO 116 no. 2. Input 20 | X | X | X
Digital Input | 22620 | 122621 | 2 | CIO 116 no. 2. Input 21 | X | X | X
Digital Input | 22621 | 122622 | 2 | CIO 116 no. 2. Input 22 | X | X | X
Digital Input | 22622 | 122623 | 2 | CIO 116 no. 2. Input 23 | X | X | X
Digital Input | 22623 | 122624 | 2 | CIO 116 no. 2. Input 24 | X | X | X
Digital Input | 22624 | 122625 | 2 | CIO 116 no. 2. Input 25 | X | X | X
Digital Input | 22625 | 122626 | 2 | CIO 116 no. 2. Input 26 | X | X | X
Digital Input | 22626 | 122627 | 2 | CIO 116 no. 3. Input 10 | X | X | X
Digital Input | 22627 | 122628 | 2 | CIO 116 no. 3. Input 11 | X | X | X
Digital Input | 22628 | 122629 | 2 | CIO 116 no. 3. Input 12 | X | X | X
Digital Input | 22629 | 122630 | 2 | CIO 116 no. 3. Input 13 | X | X | X
Digital Input | 22630 | 122631 | 2 | CIO 116 no. 3. Input 14 | X | X | X
Digital Input | 22631 | 122632 | 2 | CIO 116 no. 3. Input 15 | X | X | X
Digital Input | 22632 | 122633 | 2 | CIO 116 no. 3. Input 16 | X | X | X
Digital Input | 22633 | 122634 | 2 | CIO 116 no. 3. Input 17 | X | X | X
Digital Input | 22634 | 122635 | 2 | CIO 116 no. 3. Input 19 | X | X | X
Digital Input | 22635 | 122636 | 2 | CIO 116 no. 3. Input 20 | X | X | X
Digital Input | 22636 | 122637 | 2 | CIO 116 no. 3. Input 21 | X | X | X
Digital Input | 22637 | 122638 | 2 | CIO 116 no. 3. Input 22 | X | X | X
Digital Input | 22638 | 122639 | 2 | CIO 116 no. 3. Input 23 | X | X | X
Digital Input | 22639 | 122640 | 2 | CIO 116 no. 3. Input 24 | X | X | X
Digital Input | 22640 | 122641 | 2 | CIO 116 no. 3. Input 25 | X | X | X
Digital Input | 22641 | 122642 | 2 | CIO 116 no. 3. Input 26 | X | X | X
Digital Output | 23001 | 123002 | 2 | Relay 16 | X | X | X
Digital Output | 23002 | 123003 | 2 | Relay 18 | X | X | X
Digital Output | 23003 | 123004 | 2 | Relay 20 | X | X | X
Digital Output | 23004 | 123005 | 2 | Relay 23 | X | X | X
Digital Output | 23005 | 123006 | 2 | Relay 26 | X | X | X
Digital Output | 23006 | 123007 | 2 | Relay 27 | X | X | X
Digital Output | 23007 | 123008 | 2 | Relay 28 | X | X | X
Digital Output | 23008 | 123009 | 2 | Relay 30 | X | X | X
Digital Output | 23009 | 123010 | 2 | Relay 32 | X | X | X
Digital Output | 23010 | 123011 | 2 | Relay 34 | X | X | X
Digital Output | 23011 | 123012 | 2 | Relay 36 | X | X | X
Digital Output | 23012 | 123013 | 2 | Relay 39 | X | X | X
Digital Output | 23013 | 123014 | 2 | Relay 41 | X | X | X
Digital Output | 23014 | 123015 | 2 | Relay 43 | X | X | X
Digital Output | 23056 | 123057 | 2 | External digital output/CIO 208 no. 1. Output 9 | X | X | X
Digital Output | 23057 | 123058 | 2 | External digital output/CIO 208 no. 1. Output 11 | X | X | X
Digital Output | 23058 | 123059 | 2 | External digital output/CIO 208 no. 1. Output 13 | X | X | X
Digital Output | 23059 | 123060 | 2 | External digital output/CIO 208 no. 1. Output 15 | X | X | X
Digital Output | 23060 | 123061 | 2 | External digital output/CIO 208 no. 1. Output 18 | X | X | X
Digital Output | 23061 | 123062 | 2 | External digital output/CIO 208 no. 1. Output 21 | X | X | X
Digital Output | 23062 | 123063 | 2 | External digital output/CIO 208 no. 1. Output 24 | X | X | X
Digital Output | 23063 | 123064 | 2 | External digital output/CIO 208 no. 1. Output 27 | X | X | X
Digital Output | 23064 | 123065 | 2 | External digital output/CIO 208 no. 2. Output 9 | X | X | X
Digital Output | 23065 | 123066 | 2 | External digital output/CIO 208 no. 2. Output 11 | X | X | X
Digital Output | 23066 | 123067 | 2 | External digital output/CIO 208 no. 2. Output 13 | X | X | X
Digital Output | 23067 | 123068 | 2 | External digital output/CIO 208 no. 2. Output 15 | X | X | X
Digital Output | 23068 | 123069 | 2 | External digital output/CIO 208 no. 2. Output 18 | X | X | X
Digital Output | 23069 | 123070 | 2 | External digital output/CIO 208 no. 2. Output 21 | X | X | X
Digital Output | 23070 | 123071 | 2 | External digital output/CIO 208 no. 2. Output 24 | X | X | X
Digital Output | 23071 | 123072 | 2 | External digital output/CIO 208 no. 2. Output 27 | X | X | X
Digital Output | 23072 | 123073 | 2 | CIO 208 no. 3. Output 9 | X | X | X
Digital Output | 23073 | 123074 | 2 | CIO 208 no. 3. Output 11 | X | X | X
Digital Output | 23074 | 123075 | 2 | CIO 208 no. 3. Output 13 | X | X | X
Digital Output | 23075 | 123076 | 2 | CIO 208 no. 3. Output 15 | X | X | X
Digital Output | 23076 | 123077 | 2 | CIO 208 no. 3. Output 18 | X | X | X
Digital Output | 23077 | 123078 | 2 | CIO 208 no. 3. Output 21 | X | X | X
Digital Output | 23078 | 123079 | 2 | CIO 208 no. 3. Output 24 | X | X | X
Digital Output | 23079 | 123080 | 2 | CIO 208 no. 3. Output 27 | X | X | X
Digital Output | 23080 | 123081 | 2 | CIO 116 no. 1 conf. status out | X | X | X
Digital Output | 23081 | 123082 | 2 | CIO 116 no. 2 conf. status out | X | X | X
Digital Output | 23082 | 123083 | 2 | CIO 116 no. 3 conf. status out | X | X | X
Digital Output | 23083 | 123084 | 2 | CIO 208 no. 1 conf. status out | X | X | X
Digital Output | 23084 | 123085 | 2 | CIO 208 no. 2 conf. status out | X | X | X
Digital Output | 23085 | 123086 | 2 | CIO 208 no. 3 conf. status out | X | X | X
Digital Output | 23086 | 123087 | 2 | CIO 308 no. 1 conf. status out | X | X | X
Digital Output | 23087 | 123088 | 2 | CIO 308 no. 2 conf. status out | X | X | X
Digital Output | 23088 | 123089 | 2 | CIO 308 no. 3 conf. status out | X | X | X
Note on A4: More information about each function group is available in the description sheet.
Note on D4: 02 - Read single or multiple
Note on E4: The controller function name shows the name of the parameter in the Utility Software. Some functions might contain additional information.
Note on F4: Indicates if the address is available in the BUS TIE breaker controller.
Note on G4: Indicates if the address is available in the MAINS controller.
Note on H4: Indicates if the address is available in the GENSET controller.

## Holding register (03;06;16)
Holding register (03;06;16)
Function group | Modbus address | Bit | PLC address | Modbus function code | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | BTB | MAINS | DG
Control Command | 0 |  | 400001 | 03; 06; 16 | Power regulator setpoint - 0...100% of nominal power. Activated in menu 7501 | INT16s | AB | 0 |  |  | X | X
Control Command | 1 |  | 400002 | 03; 06; 16 | cosPhi regulator setpoint - 60...100 stated as cosPhi value/100. The value 100 means cosPhi = 1.00 Activated in menu 7504 | INT16s | AB | 0 |  |  |  | X
Control Command | 2 |  | 400003 | 03; 06; 16 | Reactive power regulator setpoint - +/-100% of nominal power. A negative value means capacitive reactive power, and a positive value means inductive reactive power. Activated in menu 7505 | INT16s | AB | 0 |  |  |  | X
Control Command | 3 |  | 400004 | 03; 06; 16 | Frequency regulator setpoint - +/-100% corresponding to +/10.0% of nominal frequency. Activated in menu 7502 | INT16s | AB | 0 |  |  |  | X
Control Command | 4 |  | 400005 | 03; 06; 16 | Voltage regulator setpoint - +/-100% corresponding to +/10.0% of nominal voltage. Activated in menu 7503 | INT16s | AB | 0 |  |  |  | X
Control Command | 5 | 0 | 400006 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X
Control Command | 5 | 1 | 400006 | 03; 06; 16 | Remote start | BOOL | [5 empty] | X
Control Command | 5 | 2 | 400006 | 03; 06; 16 | Remote GB ON | BOOL | [5 empty] | X
Control Command | 5 | 2 | 400006 | 03; 06; 16 | Remote BTB ON | BOOL |  |  |  | X
Control Command | 5 | 2 | 400006 | 03; 06; 16 | Remote TB ON | BOOL |  |  |  |  | X
Control Command | 5 | 3 | 400006 | 03; 06; 16 | Remote GB OFF | BOOL | [5 empty] | X
Control Command | 5 | 3 | 400006 | 03; 06; 16 | Remote BTB OFF | BOOL |  |  |  | X
Control Command | 5 | 3 | 400006 | 03; 06; 16 | Remote TB OFF | BOOL |  |  |  |  | X
Control Command | 5 | 4 | 400006 | 03; 06; 16 | Remote stop | BOOL | [5 empty] | X
Control Command | 5 | 5 | 400006 | 03; 06; 16 | Reset GOV/AVR regulation output to offset | BOOL | [5 empty] | X
Control Command | 5 | 6 | 400006 | 03; 06; 16 | Start+sync. (semi) | BOOL | [5 empty] | X
Control Command | 5 | 7 | 400006 | 03; 06; 16 | Alarm inhibit 1 | BOOL |  |  |  | X | X | X
Control Command | 5 | 8 | 400006 | 03; 06; 16 | Alarm inhibit 2 | BOOL |  |  |  | X | X | X
Control Command | 5 | 9 | 400006 | 03; 06; 16 | Alarm inhibit 3 | BOOL |  |  |  | X | X | X
Control Command | 5 | 10 | 400006 | 03; 06; 16 | Alarm ack. | BOOL |  |  |  | X | X | X
Control Command | 5 | 11 | 400006 | 03; 06; 16 | Nominal setting 1 | BOOL |  |  |  | X | X | X
Control Command | 5 | 12 | 400006 | 03; 06; 16 | Nominal setting 2 | BOOL |  |  |  | X | X | X
Control Command | 5 | 13 | 400006 | 03; 06; 16 | Nominal setting 3 | BOOL |  |  |  | X | X | X
Control Command | 5 | 14 | 400006 | 03; 06; 16 | Nominal setting 4 | BOOL |  |  |  | X | X | X
Control Command | 5 | 15 | 400006 | 03; 06; 16 | Deload/stop (semi) | BOOL | [5 empty] | X
Control Command | 6 | 0 | 400007 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X
Control Command | 6 | 1 | 400007 | 03; 06; 16 | Island | BOOL |  |  |  |  | X | X
Control Command | 6 | 2 | 400007 | 03; 06; 16 | Automatic mains failure (AMF) | BOOL |  |  |  |  | X | X
Control Command | 6 | 3 | 400007 | 03; 06; 16 | Peak shaving | BOOL |  |  |  |  | X | X
Control Command | 6 | 4 | 400007 | 03; 06; 16 | Fixed power | BOOL |  |  |  |  | X | X
Control Command | 6 | 5 | 400007 | 03; 06; 16 | Mains power export (MPE) | BOOL |  |  |  |  | X | X
Control Command | 6 | 6 | 400007 | 03; 06; 16 | Load takeover (LTO) | BOOL |  |  |  |  | X | X
Control Command | 6 | 9 | 400007 | 03; 06; 16 | MB ON (Single DG) | BOOL | [5 empty] | X
Control Command | 6 | 9 | 400007 | 03; 06; 16 | MB ON | BOOL |  |  |  |  | X
Control Command | 6 | 10 | 400007 | 03; 06; 16 | MB OFF (Single DG) | BOOL | [5 empty] | X
Control Command | 6 | 10 | 400007 | 03; 06; 16 | MB OFF | BOOL |  |  |  |  | X
Control Command | 6 | 11 | 400007 | 03; 06; 16 | Auto start/stop | BOOL |  |  |  |  | X | X
Control Command | 6 | 12 | 400007 | 03; 06; 16 | Manual mode | BOOL | [5 empty] | X
Control Command | 6 | 13 | 400007 | 03; 06; 16 | Auto mode | BOOL |  |  |  | X | X | X
Control Command | 6 | 14 | 400007 | 03; 06; 16 | Semi-Auto mode | BOOL |  |  |  | X | X | X
Control Command | 6 | 15 | 400007 | 03; 06; 16 | Test mode | BOOL |  |  |  |  | X | X
Control Command | 7 | 0 | 400008 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X
Control Command | 7 | 1 | 400008 | 03; 06; 16 | External frequency control | BOOL | [5 empty] | X
Control Command | 7 | 2 | 400008 | 03; 06; 16 | External voltage control | BOOL | [5 empty] | X
Control Command | 7 | 3 | 400008 | 03; 06; 16 | External power control | BOOL |  |  |  |  | X | X
Control Command | 7 | 4 | 400008 | 03; 06; 16 | External reactive power control | BOOL | [5 empty] | X
Control Command | 7 | 5 | 400008 | 03; 06; 16 | External power factor control | BOOL | [5 empty] | X
Control Command | 7 | 6 | 400008 | 03; 06; 16 | Capacitive PF | BOOL | [5 empty] | X
Control Command | 7 | 7 | 400008 | 03; 06; 16 | Base load | BOOL | [5 empty] | X
Control Command | 7 | 8 | 400008 | 03; 06; 16 | 1. priority | BOOL | [5 empty] | X
Control Command | 7 | 9 | 400008 | 03; 06; 16 | Application 1 | BOOL |  |  |  | X | X | X
Control Command | 7 | 10 | 400008 | 03; 06; 16 | Application 2 | BOOL |  |  |  | X | X | X
Control Command | 7 | 11 | 400008 | 03; 06; 16 | Application 3 | BOOL |  |  |  | X | X | X
Control Command | 7 | 12 | 400008 | 03; 06; 16 | Application 4 | BOOL |  |  |  | X | X | X
Control Command | 7 | 13 | 400008 | 03; 06; 16 | Battery test | BOOL | [5 empty] | X
Control Command | 7 | 15 | 400008 | 03; 06; 16 | Synchronise clock to 4:00 a.m. | BOOL |  |  |  | X | X | X
Control Command | 8 | 0 | 400009 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X
Control Command | 8 | 1 | 400009 | 03; 06; 16 | Virtual event 1 | BOOL |  |  |  | X | X | X
Control Command | 8 | 2 | 400009 | 03; 06; 16 | Virtual event 2 | BOOL |  |  |  | X | X | X
Control Command | 8 | 3 | 400009 | 03; 06; 16 | Virtual event 3 | BOOL |  |  |  | X | X | X
Control Command | 8 | 4 | 400009 | 03; 06; 16 | Virtual event 4 | BOOL |  |  |  | X | X | X
Control Command | 8 | 5 | 400009 | 03; 06; 16 | Virtual event 5 | BOOL |  |  |  | X | X | X
Control Command | 8 | 6 | 400009 | 03; 06; 16 | Virtual event 6 | BOOL |  |  |  | X | X | X
Control Command | 8 | 7 | 400009 | 03; 06; 16 | Virtual event 7 | BOOL |  |  |  | X | X | X
Control Command | 8 | 8 | 400009 | 03; 06; 16 | Virtual event 8 | BOOL |  |  |  | X | X | X
Control Command | 8 | 9 | 400009 | 03; 06; 16 | Virtual event 9 | BOOL |  |  |  | X | X | X
Control Command | 8 | 10 | 400009 | 03; 06; 16 | Virtual event 10 | BOOL |  |  |  | X | X | X
Control Command | 8 | 11 | 400009 | 03; 06; 16 | Virtual event 11 | BOOL |  |  |  | X | X | X
Control Command | 8 | 12 | 400009 | 03; 06; 16 | Virtual event 12 | BOOL |  |  |  | X | X | X
Control Command | 8 | 13 | 400009 | 03; 06; 16 | Virtual event 13 | BOOL |  |  |  | X | X | X
Control Command | 8 | 14 | 400009 | 03; 06; 16 | Virtual event 14 | BOOL |  |  |  | X | X | X
Control Command | 8 | 15 | 400009 | 03; 06; 16 | Virtual event 15 | BOOL |  |  |  | X | X | X
Control Command | 9 | 0 | 400010 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X
Control Command | 9 | 1 | 400010 | 03; 06; 16 | Virtual event 16 | BOOL |  |  |  | X | X | X
Control Command | 9 | 2 | 400010 | 03; 06; 16 | Virtual event 17 | BOOL |  |  |  | X | X | X
Control Command | 9 | 3 | 400010 | 03; 06; 16 | Virtual event 18 | BOOL |  |  |  | X | X | X
Control Command | 9 | 4 | 400010 | 03; 06; 16 | Virtual event 19 | BOOL |  |  |  | X | X | X
Control Command | 9 | 5 | 400010 | 03; 06; 16 | Virtual event 20 | BOOL |  |  |  | X | X | X
Control Command | 9 | 6 | 400010 | 03; 06; 16 | Virtual event 21 | BOOL |  |  |  | X | X | X
Control Command | 9 | 7 | 400010 | 03; 06; 16 | Virtual event 22 | BOOL |  |  |  | X | X | X
Control Command | 9 | 8 | 400010 | 03; 06; 16 | Virtual event 23 | BOOL |  |  |  | X | X | X
Control Command | 9 | 9 | 400010 | 03; 06; 16 | Virtual event 24 | BOOL |  |  |  | X | X | X
Control Command | 9 | 10 | 400010 | 03; 06; 16 | Virtual event 25 | BOOL |  |  |  | X | X | X
Control Command | 9 | 11 | 400010 | 03; 06; 16 | Virtual event 26 | BOOL |  |  |  | X | X | X
Control Command | 9 | 12 | 400010 | 03; 06; 16 | Virtual event 27 | BOOL |  |  |  | X | X | X
Control Command | 9 | 13 | 400010 | 03; 06; 16 | Virtual event 28 | BOOL |  |  |  | X | X | X
Control Command | 9 | 14 | 400010 | 03; 06; 16 | Virtual event 29 | BOOL |  |  |  | X | X | X
Control Command | 9 | 15 | 400010 | 03; 06; 16 | Virtual event 30 | BOOL |  |  |  | X | X | X
Control Command | 10 | 0 | 400011 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X
Control Command | 10 | 1 | 400011 | 03; 06; 16 | Virtual event 31 | BOOL |  |  |  | X | X | X
Control Command | 10 | 2 | 400011 | 03; 06; 16 | Virtual event 32 | BOOL |  |  |  | X | X | X
Control Command | 10 | 4 | 400011 | 03; 06; 16 | Clear log | BOOL |  |  |  | X | X | X
Control Command | 10 | 5 | 400011 | 03; 06; 16 | Clear Parameter edits | BOOL |  |  |  | X | X | X
Control Command | 13 | 0 | 400014 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X
Control Command | 13 | 1 | 400014 | 03; 06; 16 | Enable external frequency control | BOOL | [5 empty] | X
Control Command | 13 | 2 | 400014 | 03; 06; 16 | Disable external frequency control | BOOL | [5 empty] | X
Control Command | 13 | 3 | 400014 | 03; 06; 16 | Enable external voltage control | BOOL | [5 empty] | X
Control Command | 13 | 4 | 400014 | 03; 06; 16 | Disable external voltage control | BOOL | [5 empty] | X
Control Command | 13 | 5 | 400014 | 03; 06; 16 | Enable external power control | BOOL |  |  |  |  | X | X
Control Command | 13 | 6 | 400014 | 03; 06; 16 | Disable external power control | BOOL |  |  |  |  | X | X
Control Command | 13 | 7 | 400014 | 03; 06; 16 | Enable external VAr control | BOOL | [5 empty] | X
Control Command | 13 | 8 | 400014 | 03; 06; 16 | Disable external VAr control | BOOL | [5 empty] | X
Control Command | 13 | 9 | 400014 | 03; 06; 16 | Enable external CosPhi control | BOOL | [5 empty] | X
Control Command | 13 | 10 | 400014 | 03; 06; 16 | Disable external CosPhi control | BOOL | [5 empty] | X
Control Command | 13 | 11 | 400014 | 03; 06; 16 | Enable PM base load | BOOL | [5 empty] | X
Control Command | 13 | 12 | 400014 | 03; 06; 16 | Disable PM base load | BOOL | [5 empty] | X
Control Command | 13 | 13 | 400014 | 03; 06; 16 | Reset horn | BOOL |  |  |  | X | X | X
Control Time Command | 58000 |  | 458001 | 03; 06; 16 | Year (2003-2099) | INT16s | AB | 0 |  | X | X | X
Control Time Command | 58001 |  | 458002 | 03; 06; 16 | Month (1-12) | INT16s | AB | 0 |  | X | X | X
Control Time Command | 58002 |  | 458003 | 03; 06; 16 | Date (1-31) | INT16s | AB | 0 |  | X | X | X
Control Time Command | 58003 |  | 458004 | 03; 06; 16 | Day (1-7, Monday - Sunday) | INT16s | AB | 0 |  | X | X | X
Control Time Command | 58004 |  | 458005 | 03; 06; 16 | Hour (0-23) | INT16s | AB | 0 |  | X | X | X
Control Time Command | 58005 |  | 458006 | 03; 06; 16 | Min (0-59) | INT16s | AB | 0 |  | X | X | X
Control Time Command | 58006 |  | 458007 | 03; 06; 16 | Sec (0-59) | INT16s | AB | 0 |  | X | X | X
Note on A4: More information about each function group is available in the description sheet.
Note on C4: Bit location of the function in the associated Modbus address.
Note on E4: 03 - Read single or multiple 06 - Write single 16 - Write multiple
Note on F4: The controller function name shows the name of the parameter in the Utility Software. Some functions might contain additional information.
Note on H4: AB - Most significant byte first ABCD - Most significant byte first and most significant word first
Note on I4: Example: Scaling = 1 Read Data = 266 Actual value = 26,6
Note on J4: Unit of the associated function
Note on K4: Indicates if the address is available in the BUS TIE breaker controller.
Note on L4: Indicates if the address is available in the MAINS controller.
Note on M4: Indicates if the address is available in the GENSET controller.

## Input register (04)
Input register (04)
Function group | Modbus address | Bit | PLC address | Modbus function code | Channel | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | BTB | MAINS | DG
AC Measurement | 500 |  | 300501 | 4 |  | Application version | INT16s | AB | 0 |  | X | X | X
AC Measurement | 501 |  | 300502 | 4 |  | Generator voltage L1-L2 | INT16s | AB | 0 | V |  |  | X
AC Measurement | 501 |  | 300502 | 4 |  | Bus A voltage L1-L2 | INT16s | AB | 0 | V | X
AC Measurement | 501 |  | 300502 | 4 |  | Mains voltage L1-L2 | INT16s | AB | 0 | V |  | X
AC Measurement | 502 |  | 300503 | 4 |  | Bus A voltage L2-L3 | INT16s | AB | 0 | V | X
AC Measurement | 502 |  | 300503 | 4 |  | Generator voltage L2-L3 | INT16s | AB | 0 | V |  |  | X
AC Measurement | 502 |  | 300503 | 4 |  | Mains voltage L2-L3 | INT16s | AB | 0 | V |  | X
AC Measurement | 503 |  | 300504 | 4 |  | Generator voltage L3-L1 | INT16s | AB | 0 | V |  |  | X
AC Measurement | 503 |  | 300504 | 4 |  | Mains voltage L3-L1 | INT16s | AB | 0 | V |  | X
AC Measurement | 503 |  | 300504 | 4 |  | Bus A voltage L3-L1 | INT16s | AB | 0 | V | X
AC Measurement | 504 |  | 300505 | 4 |  | Generator voltage L1-N | INT16s | AB | 0 | V |  |  | X
AC Measurement | 504 |  | 300505 | 4 |  | Bus A voltage L1-N | INT16s | AB | 0 | V | X
AC Measurement | 504 |  | 300505 | 4 |  | Mains voltage L1-N | INT16s | AB | 0 | V |  | X
AC Measurement | 505 |  | 300506 | 4 |  | Generator voltage L2-N | INT16s | AB | 0 | V |  |  | X
AC Measurement | 505 |  | 300506 | 4 |  | Bus A voltage L2-N | INT16s | AB | 0 | V | X
AC Measurement | 505 |  | 300506 | 4 |  | Mains voltage L2-N | INT16s | AB | 0 | V |  | X
AC Measurement | 506 |  | 300507 | 4 |  | Generator voltage L3-N | INT16s | AB | 0 | V |  |  | X
AC Measurement | 506 |  | 300507 | 4 |  | Bus A voltage L3-N | INT16s | AB | 0 | V | X
AC Measurement | 506 |  | 300507 | 4 |  | Mains voltage L3-N | INT16s | AB | 0 | V |  | X
AC Measurement | 507 |  | 300508 | 4 |  | Generator f L1 | INT16s | AB | 2 | Hz |  |  | X
AC Measurement | 507 |  | 300508 | 4 |  | Bus A f L1 | INT16s | AB | 2 | Hz | X
AC Measurement | 507 |  | 300508 | 4 |  | Mains f L1 | INT16s | AB | 2 | Hz |  | X
AC Measurement | 508 |  | 300509 | 4 |  | Generator f L2 | INT16s | AB | 2 | Hz |  |  | X
AC Measurement | 508 |  | 300509 | 4 |  | Mains f L2 | INT16s | AB | 2 | Hz |  | X
AC Measurement | 508 |  | 300509 | 4 |  | Bus A f L2 | INT16s | AB | 2 | Hz | X
AC Measurement | 509 |  | 300510 | 4 |  | Generator f L3 | INT16s | AB | 2 | Hz |  |  | X
AC Measurement | 509 |  | 300510 | 4 |  | Bus A f L3 | INT16s | AB | 2 | Hz | X
AC Measurement | 509 |  | 300510 | 4 |  | Mains f L3 | INT16s | AB | 2 | Hz |  | X
AC Measurement | 510 |  | 300511 | 4 |  | Bus A voltage phase angle L1-L2 | INT16s | AB | 1 | Deg | X
AC Measurement | 510 |  | 300511 | 4 |  | Generator voltage phase angle L1-L2 | INT16s | AB | 1 | Deg |  |  | X
AC Measurement | 510 |  | 300511 | 4 |  | Mains voltage phase angle L1-L2 | INT16s | AB | 1 | Deg |  | X
AC Measurement | 511 |  | 300512 | 4 |  | Generator voltage phase angle L2-L3 | INT16s | AB | 1 | Deg |  |  | X
AC Measurement | 511 |  | 300512 | 4 |  | Mains voltage phase angle L2-L3 | INT16s | AB | 1 | Deg |  | X
AC Measurement | 511 |  | 300512 | 4 |  | Bus A voltage phase angle L2-L3 | INT16s | AB | 1 | Deg | X
AC Measurement | 512 |  | 300513 | 4 |  | Bus A voltage phase angle L3-L1 | INT16s | AB | 1 | Deg | X
AC Measurement | 512 |  | 300513 | 4 |  | Generator voltage phase angle L3-L1 | INT16s | AB | 1 | Deg |  |  | X
AC Measurement | 512 |  | 300513 | 4 |  | Mains voltage phase angle L3-L1 | INT16s | AB | 1 | Deg |  | X
AC Measurement | 513 |  | 300514 | 4 |  | Generator current L1 | INT16s | AB | 0 | A |  |  | X
AC Measurement | 513 |  | 300514 | 4 |  | Mains current L1 | INT16s | AB | 0 | A |  | X
AC Measurement | 513 |  | 300514 | 4 |  | Bus A current L1 | INT16s | AB | 0 | A | X
AC Measurement | 514 |  | 300515 | 4 |  | Generator current L2 | INT16s | AB | 0 | A |  |  | X
AC Measurement | 514 |  | 300515 | 4 |  | Bus A current L2 | INT16s | AB | 0 | A | X
AC Measurement | 514 |  | 300515 | 4 |  | Mains current L2 | INT16s | AB | 0 | A |  | X
AC Measurement | 515 |  | 300516 | 4 |  | Generator current L3 | INT16s | AB | 0 | A |  |  | X
AC Measurement | 515 |  | 300516 | 4 |  | Bus A current L3 | INT16s | AB | 0 | A | X
AC Measurement | 515 |  | 300516 | 4 |  | Mains current L3 | INT16s | AB | 0 | A |  | X
AC Measurement | 516 |  | 300517 | 4 |  | Bus A power L1 | INT16s | AB | 0 | kW | X
AC Measurement | 516 |  | 300517 | 4 |  | Generator power L1 | INT16s | AB | 0 | kW |  |  | X
AC Measurement | 516 |  | 300517 | 4 |  | Mains power L1 | INT16s | AB | 0 | kW |  | X
AC Measurement | 517 |  | 300518 | 4 |  | Generator power L2 | INT16s | AB | 0 | kW |  |  | X
AC Measurement | 517 |  | 300518 | 4 |  | Bus A power L2 | INT16s | AB | 0 | kW | X
AC Measurement | 517 |  | 300518 | 4 |  | Mains power L2 | INT16s | AB | 0 | kW |  | X
AC Measurement | 518 |  | 300519 | 4 |  | Bus A power L3 | INT16s | AB | 0 | kW | X
AC Measurement | 518 |  | 300519 | 4 |  | Generator power L3 | INT16s | AB | 0 | kW |  |  | X
AC Measurement | 518 |  | 300519 | 4 |  | Mains power L3 | INT16s | AB | 0 | kW |  | X
AC Measurement | 519 |  | 300520 | 4 |  | Generator power | INT16s | AB | 0 | kW |  |  | X
AC Measurement | 519 |  | 300520 | 4 |  | Bus A power | INT16s | AB | 0 | kW | X
AC Measurement | 519 |  | 300520 | 4 |  | Mains power | INT16s | AB | 0 | kW |  | X
AC Measurement | 520 |  | 300521 | 4 |  | Generator reactive power L1 | INT16s | AB | 0 | kVAr |  |  | X
AC Measurement | 520 |  | 300521 | 4 |  | Bus A reactive power L1 | INT16s | AB | 0 | kVAr | X
AC Measurement | 520 |  | 300521 | 4 |  | Mains reactive power L1 | INT16s | AB | 0 | kVAr |  | X
AC Measurement | 521 |  | 300522 | 4 |  | Generator reactive power L2 | INT16s | AB | 0 | kVAr |  |  | X
AC Measurement | 521 |  | 300522 | 4 |  | Mains reactive power L2 | INT16s | AB | 0 | kVAr |  | X
AC Measurement | 521 |  | 300522 | 4 |  | Bus A reactive power L2 | INT16s | AB | 0 | kVAr | X
AC Measurement | 522 |  | 300523 | 4 |  | Generator reactive power L3 | INT16s | AB | 0 | kVAr |  |  | X
AC Measurement | 522 |  | 300523 | 4 |  | Bus A reactive power L3 | INT16s | AB | 0 | kVAr | X
AC Measurement | 522 |  | 300523 | 4 |  | Mains reactive power L3 | INT16s | AB | 0 | kVAr |  | X
AC Measurement | 523 |  | 300524 | 4 |  | Generator reactive power | INT16s | AB | 0 | kVAr |  |  | X
AC Measurement | 523 |  | 300524 | 4 |  | Bus A reactive power | INT16s | AB | 0 | kVAr | X
AC Measurement | 523 |  | 300524 | 4 |  | Mains reactive power | INT16s | AB | 0 | kVAr |  | X
AC Measurement | 524 |  | 300525 | 4 |  | Generator apparent power L1 | INT16s | AB | 0 | kVA |  |  | X
AC Measurement | 524 |  | 300525 | 4 |  | Bus A apparent power L1 | INT16s | AB | 0 | kVA | X
AC Measurement | 524 |  | 300525 | 4 |  | Mains apparent power L1 | INT16s | AB | 0 | kVA |  | X
AC Measurement | 525 |  | 300526 | 4 |  | Generator apparent power L2 | INT16s | AB | 0 | kVA |  |  | X
AC Measurement | 525 |  | 300526 | 4 |  | Bus A apparent power L2 | INT16s | AB | 0 | kVA | X
AC Measurement | 525 |  | 300526 | 4 |  | Mains apparent power L2 | INT16s | AB | 0 | kVA |  | X
AC Measurement | 526 |  | 300527 | 4 |  | Generator apparent power L3 | INT16s | AB | 0 | kVA |  |  | X
AC Measurement | 526 |  | 300527 | 4 |  | Bus A apparent power L3 | INT16s | AB | 0 | kVA | X
AC Measurement | 526 |  | 300527 | 4 |  | Mains apparent power L3 | INT16s | AB | 0 | kVA |  | X
AC Measurement | 527 |  | 300528 | 4 |  | Generator apparent power | INT16s | AB | 0 | kVA |  |  | X
AC Measurement | 527 |  | 300528 | 4 |  | Bus A apparent power | INT16s | AB | 0 | kVA | X
AC Measurement | 527 |  | 300528 | 4 |  | Mains apparent power | INT16s | AB | 0 | kVA |  | X
AC Measurement | 528 |  | 300529 | 4 |  | Generator Export, reactive energy counter | INT32s | ABCD | 0 | kVArh |  |  | X
AC Measurement | 528 |  | 300529 | 4 |  | Bus A Export, reactive energy counter | INT32s | ABCD | 0 | kVArh | X
AC Measurement | 528 |  | 300529 | 4 |  | Mains Export, reactive energy counter | INT32s | ABCD | 0 | kVArh |  | X
AC Measurement | 530 |  | 300531 | 4 |  | Bus A Export, active energy counter, day | INT32s | ABCD | 0 | kWh | X
AC Measurement | 530 |  | 300531 | 4 |  | Generator Export, active energy counter, day | INT32s | ABCD | 0 | kWh |  |  | X
AC Measurement | 530 |  | 300531 | 4 |  | Mains Export, active energy counter, day | INT32s | ABCD | 0 | kWh |  | X
AC Measurement | 532 |  | 300533 | 4 |  | Bus A Export, active energy counter, week | INT32s | ABCD | 0 | kWh | X
AC Measurement | 532 |  | 300533 | 4 |  | Generator Export, active energy counter, week | INT32s | ABCD | 0 | kWh |  |  | X
AC Measurement | 532 |  | 300533 | 4 |  | Mains Export, active energy counter, week | INT32s | ABCD | 0 | kWh |  | X
AC Measurement | 534 |  | 300535 | 4 |  | Generator Export, active energy counter, month | INT32s | ABCD | 0 | kWh |  |  | X
AC Measurement | 534 |  | 300535 | 4 |  | Bus A Export, active energy counter, month | INT32s | ABCD | 0 | kWh | X
AC Measurement | 534 |  | 300535 | 4 |  | Mains Export, active energy counter, month | INT32s | ABCD | 0 | kWh |  | X
AC Measurement | 536 |  | 300537 | 4 |  | Generator Export, active energy counter, total | INT32s | ABCD | 0 | kWh |  |  | X
AC Measurement | 536 |  | 300537 | 4 |  | Bus A Export, active energy counter, total | INT32s | ABCD | 0 | kWh | X
AC Measurement | 536 |  | 300537 | 4 |  | Mains Export, active energy counter, total | INT32s | ABCD | 0 | kWh |  | X
AC Measurement | 538 |  | 300539 | 4 |  | Generator PF | INT16s | AB | 2 | PF |  |  | X
AC Measurement | 538 |  | 300539 | 4 |  | Bus A PF | INT16s | AB | 2 | PF | X
AC Measurement | 538 |  | 300539 | 4 |  | Mains PF | INT16s | AB | 2 | PF |  | X
AC Measurement | 539 |  | 300540 | 4 |  | Bus B voltage L1-L2 | INT16s | AB | 0 | V | X | X | X
AC Measurement | 540 |  | 300541 | 4 |  | Bus B voltage L2-L3 | INT16s | AB | 0 | V | X | X | X
AC Measurement | 541 |  | 300542 | 4 |  | Bus B voltage L3-L1 | INT16s | AB | 0 | V | X | X | X
AC Measurement | 542 |  | 300543 | 4 |  | Bus B voltage L1-N | INT16s | AB | 0 | V | X | X | X
AC Measurement | 543 |  | 300544 | 4 |  | Bus B voltage L2-N | INT16s | AB | 0 | V | X | X | X
AC Measurement | 544 |  | 300545 | 4 |  | Bus B voltage L3-N | INT16s | AB | 0 | V | X | X | X
AC Measurement | 545 |  | 300546 | 4 |  | Bus B f L1 | INT16s | AB | 2 | Hz | X | X | X
AC Measurement | 546 |  | 300547 | 4 |  | Bus B f L2 | INT16s | AB | 2 | Hz | X | X | X
AC Measurement | 547 |  | 300548 | 4 |  | Bus B f L3 | INT16s | AB | 2 | Hz | X | X | X
AC Measurement | 548 |  | 300549 | 4 |  | Bus B voltage phase angle L1-L2 | INT16s | AB | 1 | Deg | X | X | X
AC Measurement | 549 |  | 300550 | 4 |  | Bus B voltage phase angle L2-L3 | INT16s | AB | 1 | Deg | X | X | X
AC Measurement | 550 |  | 300551 | 4 |  | Bus B voltage phase angle L3-L1 | INT16s | AB | 1 | Deg | X | X | X
AC Measurement | 551 |  | 300552 | 4 |  | U BB L1 - U GEN L1 phase angle | INT16s | AB | 1 | Deg |  |  | X
AC Measurement | 551 |  | 300552 | 4 |  | U BB A L1 - U BB B L1 phase angle | INT16s | AB | 1 | Deg | X
AC Measurement | 551 |  | 300552 | 4 |  | U BB L1 - U Mains L1 phase angle | INT16s | AB | 1 | Deg |  | X
AC Measurement | 552 |  | 300553 | 4 |  | U BB L2 - U GEN L2 phase angle | INT16s | AB | 1 | Deg |  |  | X
AC Measurement | 552 |  | 300553 | 4 |  | U BB A L2 - U BB B L2 phase angle | INT16s | AB | 1 | Deg | X
AC Measurement | 552 |  | 300553 | 4 |  | U BB L2 - U Mains L2 phase angle | INT16s | AB | 1 | Deg |  | X
AC Measurement | 553 |  | 300554 | 4 |  | U BB L3 - U GEN L3 phase angle | INT16s | AB | 1 | Deg |  |  | X
AC Measurement | 553 |  | 300554 | 4 |  | U BB A L3 - U BB B L3 phase angle | INT16s | AB | 1 | Deg | X
AC Measurement | 553 |  | 300554 | 4 |  | U BB L3 - U Mains L3 phase angle | INT16s | AB | 1 | Deg |  | X
AC Measurement | 554 |  | 300555 | 4 |  | Absolute running hours | INT32s | ABCD | 0 |  |  |  | X
AC Measurement | 556 |  | 300557 | 4 |  | Relative running hours | INT32s | ABCD | 0 |  |  |  | X
AC Measurement | 558 |  | 300559 | 4 |  | No. of alarms | INT16s | AB | 0 |  | X | X | X
AC Measurement | 559 |  | 300560 | 4 |  | No. of unacknowledged alarms | INT16s | AB | 0 |  | X | X | X
AC Measurement | 560 |  | 300561 | 4 |  | No. of active acknowledged alarms | INT16s | AB | 0 |  | X | X | X
AC Measurement | 561 |  | 300562 | 4 |  | Running minute counter, shutdown override | INT16s | AB | 0 |  |  |  | X
AC Measurement | 562 |  | 300563 | 4 |  | Running hour counter, shutdown override | INT16s | AB | 0 |  |  |  | X
AC Measurement | 563 |  | 300564 | 4 |  | No. of GB operations | INT16s | AB | 0 |  |  |  | X
AC Measurement | 563 |  | 300564 | 4 |  | No. of BTB operations | INT16s | AB | 0 |  | X
AC Measurement | 563 |  | 300564 | 4 |  | No. Of TB operations | INT16s | AB | 0 |  |  | X
AC Measurement | 564 |  | 300565 | 4 |  | No. of MB operations | INT16s | AB | 0 |  |  | X | X
AC Measurement | 566 |  | 300567 | 4 |  | Start attempts | INT16s | AB | 0 |  |  |  | X
AC Measurement | 567 |  | 300568 | 4 |  | DC supply term. 1-2 | INT16s | AB | 1 | V | X | X | X
AC Measurement | 569 |  | 300570 | 4 |  | Service timer 1 running hours | INT16s | AB | 0 |  |  |  | X
AC Measurement | 570 |  | 300571 | 4 |  | Service timer 1 running days | INT16s | AB | 0 |  |  |  | X
AC Measurement | 571 |  | 300572 | 4 |  | Service timer 2 running hours | INT16s | AB | 0 |  |  |  | X
AC Measurement | 572 |  | 300573 | 4 |  | Service timer 2 running days | INT16s | AB | 0 |  |  |  | X
AC Measurement | 573 |  | 300574 | 4 |  | Cos-phi | INT16s | AB | 2 | cosPhi | X | X | X
AC Measurement | 574 |  | 300575 | 4 |  | Cos-phi Inductive/Capacitive 0=Inductive, 1=Capacitive | INT16s | AB | 0 |  | X | X | X
AC Measurement | 576 |  | 300577 | 4 |  | RPM | INT16s | AB | 0 |  |  |  | X
AC Measurement | 577 |  | 300578 | 4 |  | Running hours load profile | INT32s | ABCD | 0 |  |  |  | X
AC Measurement | 583 |  | 300584 | 4 |  | Multi-input 46 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 584 |  | 300585 | 4 |  | Multi-input 47 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 585 |  | 300586 | 4 |  | Multi-input 48 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 591 |  | 300592 | 4 |  | Busbar power, Multi-input 47 | INT16s | AB | 0 | kW |  | X
AC Measurement | 591 |  | 300592 | 4 |  | Bus A power, Multi-input 47 | INT16s | AB | 0 | kW | X
AC Measurement | 592 |  | 300593 | 4 |  | Mains power, Multi-input 46 | INT16s | AB | 0 | kW |  | X | X
AC Measurement | 593 |  | 300594 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 594 |  | 300595 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 595 |  | 300596 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 596 |  | 300597 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 597 |  | 300598 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 598 |  | 300599 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 599 |  | 300600 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 600 |  | 300601 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 601 |  | 300602 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 602 |  | 300603 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 603 |  | 300604 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 604 |  | 300605 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 605 |  | 300606 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 606 |  | 300607 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 607 |  | 300608 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 608 |  | 300609 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 609 |  | 300610 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 610 |  | 300611 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 611 |  | 300612 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 612 |  | 300613 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 613 |  | 300614 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 614 |  | 300615 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 615 |  | 300616 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 616 |  | 300617 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 617 |  | 300618 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 618 |  | 300619 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 619 |  | 300620 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 620 |  | 300621 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 621 |  | 300622 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 622 |  | 300623 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 623 |  | 300624 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 624 |  | 300625 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 625 |  | 300626 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 626 |  | 300627 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 627 |  | 300628 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 628 |  | 300629 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 629 |  | 300630 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 630 |  | 300631 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 631 |  | 300632 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 632 |  | 300633 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 633 |  | 300634 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 634 |  | 300635 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 635 |  | 300636 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 636 |  | 300637 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 637 |  | 300638 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 638 |  | 300639 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 639 |  | 300640 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 640 |  | 300641 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 641 |  | 300642 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 642 |  | 300643 | 4 |  | Control register address 0 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 643 |  | 300644 | 4 |  | Control register address 1 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 644 |  | 300645 | 4 |  | Control register address 2 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 645 |  | 300646 | 4 |  | Control register address 3 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 646 |  | 300647 | 4 |  | Control register address 4 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 647 |  | 300648 | 4 |  | Control register address 5 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 648 |  | 300649 | 4 |  | Control register address 6 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 649 |  | 300650 | 4 |  | Control register address 7 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 650 |  | 300651 | 4 |  | Control register address 8 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 651 |  | 300652 | 4 |  | Control register address 9 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 652 |  | 300653 | 4 |  | Control register address 10 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 653 |  | 300654 | 4 |  | Control register address 11 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 654 |  | 300655 | 4 |  | Control register address 12 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 655 |  | 300656 | 4 |  | Control register address 13 | INT16s | AB | 0 |  | X | X | X
AC Measurement | 660 |  | 300661 | 4 |  | External Ain 1/CIO 308 no. 1. Input 8 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 661 |  | 300662 | 4 |  | External Ain 2/CIO 308 no. 1. Input 11 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 662 |  | 300663 | 4 |  | External Ain 3/CIO 308 no. 1. Input 14 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 663 |  | 300664 | 4 |  | External Ain 4/CIO 308 no. 1. Input 17 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 664 |  | 300665 | 4 |  | External Ain 5/CIO 308 no. 1. Input 20 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 665 |  | 300666 | 4 |  | External Ain 6/CIO 308 no. 1. Input 23 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 666 |  | 300667 | 4 |  | External Ain 7/CIO 308 no. 1. Input 26 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 667 |  | 300668 | 4 |  | External Ain 8/CIO 308 no. 1. Input 29 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 668 |  | 300669 | 4 |  | CIO 308 no. 2. Input 8 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 669 |  | 300670 | 4 |  | CIO 308 no. 2. Input 11 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 670 |  | 300671 | 4 |  | CIO 308 no. 2. Input 14 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 671 |  | 300672 | 4 |  | CIO 308 no. 2. Input 17 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 672 |  | 300673 | 4 |  | CIO 308 no. 2. Input 20 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 673 |  | 300674 | 4 |  | CIO 308 no. 2. Input 23 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 674 |  | 300675 | 4 |  | CIO 308 no. 2. Input 26 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 675 |  | 300676 | 4 |  | CIO 308 no. 2. Input 29 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 676 |  | 300677 | 4 |  | CIO 308 no. 3. Input 8 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 677 |  | 300678 | 4 |  | CIO 308 no. 3. Input 11 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 678 |  | 300679 | 4 |  | CIO 308 no. 3. Input 14 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 679 |  | 300680 | 4 |  | CIO 308 no. 3. Input 17 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 680 |  | 300681 | 4 |  | CIO 308 no. 3. Input 20 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 681 |  | 300682 | 4 |  | CIO 308 no. 3. Input 23 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 682 |  | 300683 | 4 |  | CIO 308 no. 3. Input 26 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 683 |  | 300684 | 4 |  | CIO 308 no. 3. Input 29 [Config] | INT16s | AB | 0 |  | X | X | X
AC Measurement | 696 |  | 300697 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 697 |  | 300698 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 698 |  | 300699 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 699 |  | 300700 | 4 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X
AC Measurement | 700 |  | 300701 | 4 |  | Actual nominal power (Includes derate etc.) | INT16s | AB | 0 |  | X | X | X
AC Measurement | 701 |  | 300702 | 4 |  | Mains power transducer used | INT16s | AB | 0 |  |  | X | X
AC Measurement | 702 |  | 300703 | 4 |  | Fan A running hours | INT32s | ABCD | 0 |  |  |  | X
AC Measurement | 704 |  | 300705 | 4 |  | Fan B running hours | INT32s | ABCD | 0 |  |  |  | X
AC Measurement | 706 |  | 300707 | 4 |  | Fan C running hours | INT32s | ABCD | 0 |  |  |  | X
AC Measurement | 708 |  | 300709 | 4 |  | Fan D running hours | INT32s | ABCD | 0 |  |  |  | X
AC Measurement | 790 |  | 300791 | 4 |  | Generator Export reactive energy counter, month | INT32s | ABCD | 0 | kVArh |  |  | X
AC Measurement | 790 |  | 300791 | 4 |  | Bus A Export reactive energy counter, month | INT32s | ABCD | 0 | kWh | X
AC Measurement | 790 |  | 300791 | 4 |  | Mains Export reactive energy counter, month | INT32s | ABCD | 0 | kWh |  | X
AC Measurement | 792 |  | 300793 | 4 |  | Generator Export reactive energy counter, week | INT32s | ABCD | 0 | kVArh |  |  | X
AC Measurement | 792 |  | 300793 | 4 |  | Bus A Export reactive energy counter, week | INT32s | ABCD | 0 | kWh | X
AC Measurement | 792 |  | 300793 | 4 |  | Mains Export reactive energy counter, week | INT32s | ABCD | 0 | kWh |  | X
AC Measurement | 794 |  | 300795 | 4 |  | Bus A Export reactive energy counter, total | INT32s | ABCD | 0 | kWh | X
AC Measurement | 794 |  | 300795 | 4 |  | Generator Export reactive energy counter, total | INT32s | ABCD | 0 | kVArh |  |  | X
AC Measurement | 794 |  | 300795 | 4 |  | Mains Export reactive energy counter, total | INT32s | ABCD | 0 | kWh |  | X
AC Measurement | 796 |  | 300797 | 4 |  | Bus A Import active energy counter, total | INT32s | ABCD | 0 | kWh | X
AC Measurement | 796 |  | 300797 | 4 |  | Generator Import active energy counter, total | INT32s | ABCD | 0 | kWh |  |  | X
AC Measurement | 796 |  | 300797 | 4 |  | Mains Import active energy counter, total | INT32s | ABCD | 0 | kWh |  | X
AC Measurement | 798 |  | 300799 | 4 |  | Generator Import active energy counter, month | INT32s | ABCD | 0 | kWh |  |  | X
AC Measurement | 798 |  | 300799 | 4 |  | Bus A Import active energy counter, month | INT32s | ABCD | 0 | kWh | X
AC Measurement | 798 |  | 300799 | 4 |  | Mains Import active energy counter, month | INT32s | ABCD | 0 | kWh |  | X
AC Measurement | 800 |  | 300801 | 4 |  | Generator Import active energy counter, week | INT32s | ABCD | 0 | kWh |  |  | X
AC Measurement | 800 |  | 300801 | 4 |  | Mains Import active energy counter, week | INT32s | ABCD | 0 | kWh |  | X
AC Measurement | 800 |  | 300801 | 4 |  | Bus A Import active energy counter, week | INT32s | ABCD | 0 | kWh | X
AC Measurement | 802 |  | 300803 | 4 |  | Bus A Import active energy counter, day | INT32s | ABCD | 0 | kWh | X
AC Measurement | 802 |  | 300803 | 4 |  | Generator Import active energy counter, day | INT32s | ABCD | 0 | kWh |  |  | X
AC Measurement | 802 |  | 300803 | 4 |  | Mains Import active energy counter, day | INT32s | ABCD | 0 | kWh |  | X
AC Measurement | 804 |  | 300805 | 4 |  | Generator Import reactive energy counter, total | INT32s | ABCD | 0 | kVArh |  |  | X
AC Measurement | 804 |  | 300805 | 4 |  | Bus A Import reactive energy counter, total | INT32s | ABCD | 0 | kWh | X
AC Measurement | 804 |  | 300805 | 4 |  | Mains Import reactive energy counter, total | INT32s | ABCD | 0 | kWh |  | X
AC Measurement | 806 |  | 300807 | 4 |  | Generator Import reactive energy counter, month | INT32s | ABCD | 0 | kVArh |  |  | X
AC Measurement | 806 |  | 300807 | 4 |  | Bus A Import reactive energy counter, month | INT32s | ABCD | 0 | kWh | X
AC Measurement | 806 |  | 300807 | 4 |  | Mains Import reactive energy counter, month | INT32s | ABCD | 0 | kWh |  | X
AC Measurement | 808 |  | 300809 | 4 |  | Bus A Import reactive energy counter, week | INT32s | ABCD | 0 | kWh | X
AC Measurement | 808 |  | 300809 | 4 |  | Generator Import reactive energy counter, week | INT32s | ABCD | 0 | kVArh |  |  | X
AC Measurement | 808 |  | 300809 | 4 |  | Mains Import reactive energy counter, week | INT32s | ABCD | 0 | kWh |  | X
AC Measurement | 810 |  | 300811 | 4 |  | Generator Import reactive energy counter, day | INT32s | ABCD | 0 | kVArh |  |  | X
AC Measurement | 810 |  | 300811 | 4 |  | Bus A Import reactive energy counter, day | INT32s | ABCD | 0 | kWh | X
AC Measurement | 810 |  | 300811 | 4 |  | Mains Import reactive energy counter, day | INT32s | ABCD | 0 | kWh |  | X
AC Measurement | 812 |  | 300813 | 4 |  | Pulse counter 01 | INT32s | ABCD | 0 |  | X | X | X
AC Measurement | 814 |  | 300815 | 4 |  | Pulse counter 02 | INT32s | ABCD | 0 |  | X | X | X
AC Measurement | 816 |  | 300817 | 4 |  | Demand of peak current 1 | INT16s | AB | 0 |  |  | X | X
AC Measurement | 817 |  | 300818 | 4 |  | Demand of peak current 2 | INT16s | AB | 0 |  |  | X | X
AC Measurement | 818 |  | 300819 | 4 |  | Demand of peak current 3 | INT16s | AB | 0 |  |  | X | X
AC Measurement | 819 |  | 300820 | 4 |  | Demand of avg. peak current 1 | INT16s | AB | 0 |  |  | X | X
AC Measurement | 820 |  | 300821 | 4 |  | Demand of avg. peak current 2 | INT16s | AB | 0 |  |  | X | X
AC Measurement | 821 |  | 300822 | 4 |  | Demand of avg. peak current 3 | INT16s | AB | 0 |  |  | X | X
AC Measurement | 822 |  | 300823 | 4 |  | Start attempts standard | INT16s | AB | 0 |  |  |  | X
AC Measurement | 823 |  | 300824 | 4 |  | Start attempts double starter | INT16s | AB | 0 |  |  |  | X
Alarm | 1000 | 0 | 301001 | 4 | 1000 | G -P&gt; 1 | BOOL | [5 empty] | X
Alarm | 1000 | 0 | 301001 | 4 | 1000 | BA -P&gt; 1 | BOOL |  |  |  | X
Alarm | 1000 | 0 | 301001 | 4 | 1000 | M -P&gt; 1 | BOOL |  |  |  |  | X
Alarm | 1000 | 1 | 301001 | 4 | 1010 | G -P&gt; 2 | BOOL | [5 empty] | X
Alarm | 1000 | 1 | 301001 | 4 | 1010 | BA -P&gt; 2 | BOOL |  |  |  | X
Alarm | 1000 | 1 | 301001 | 4 | 1010 | M -P&gt; 2 | BOOL |  |  |  |  | X
Alarm | 1000 | 3 | 301001 | 4 | 1030 | G I&gt; 1 | BOOL | [5 empty] | X
Alarm | 1000 | 3 | 301001 | 4 | 1030 | BA I&gt; 1 | BOOL |  |  |  | X
Alarm | 1000 | 3 | 301001 | 4 | 1030 | M I&gt; 1 | BOOL |  |  |  |  | X
Alarm | 1000 | 4 | 301001 | 4 | 1040 | G I&gt; 2 | BOOL | [5 empty] | X
Alarm | 1000 | 4 | 301001 | 4 | 1040 | BA I&gt; 2 | BOOL |  |  |  | X
Alarm | 1000 | 4 | 301001 | 4 | 1040 | M I&gt; 2 | BOOL |  |  |  |  | X
Alarm | 1000 | 5 | 301001 | 4 | 1050 | G I&gt; 3 | BOOL | [5 empty] | X
Alarm | 1000 | 5 | 301001 | 4 | 1050 | BA I&gt; 3 | BOOL |  |  |  | X
Alarm | 1000 | 5 | 301001 | 4 | 1050 | M I&gt; 3 | BOOL |  |  |  |  | X
Alarm | 1000 | 6 | 301001 | 4 | 1060 | G I&gt; 4 | BOOL | [5 empty] | X
Alarm | 1000 | 6 | 301001 | 4 | 1060 | BA I&gt; 4 | BOOL |  |  |  | X
Alarm | 1000 | 6 | 301001 | 4 | 1060 | M I&gt; 4 | BOOL |  |  |  |  | X
Alarm | 1000 | 7 | 301001 | 4 | 1087 | G I&gt; inv. | BOOL | [5 empty] | X
Alarm | 1000 | 7 | 301001 | 4 | 1087 | BA I&gt; inv. | BOOL |  |  |  | X
Alarm | 1000 | 7 | 301001 | 4 | 1087 | M I&gt; inv. | BOOL |  |  |  |  | X
Alarm | 1000 | 8 | 301001 | 4 | 1110 | G Iv&gt; | BOOL |  |  |  | X | X | X
Alarm | 1000 | 9 | 301001 | 4 | 1130 | G I&gt;&gt; 1 | BOOL | [5 empty] | X
Alarm | 1000 | 9 | 301001 | 4 | 1130 | BA I&gt;&gt; 1 | BOOL |  |  |  | X
Alarm | 1000 | 9 | 301001 | 4 | 1130 | M I&gt;&gt; 1 | BOOL |  |  |  |  | X
Alarm | 1000 | 10 | 301001 | 4 | 1140 | G I&gt;&gt; 2 | BOOL | [5 empty] | X
Alarm | 1000 | 10 | 301001 | 4 | 1140 | BA I&gt;&gt; 2 | BOOL |  |  |  | X
Alarm | 1000 | 10 | 301001 | 4 | 1140 | M I&gt;&gt; 2 | BOOL |  |  |  |  | X
Alarm | 1000 | 11 | 301001 | 4 | 1150 | G U&gt; 1 | BOOL | [5 empty] | X
Alarm | 1000 | 11 | 301001 | 4 | 1150 | BA U&gt; 1 | BOOL |  |  |  | X
Alarm | 1000 | 11 | 301001 | 4 | 1150 | M U&gt; 1 | BOOL |  |  |  |  | X
Alarm | 1000 | 12 | 301001 | 4 | 1160 | G U&gt; 2 | BOOL | [5 empty] | X
Alarm | 1000 | 12 | 301001 | 4 | 1160 | BA U&gt; 2 | BOOL |  |  |  | X
Alarm | 1000 | 12 | 301001 | 4 | 1160 | M U&gt; 2 | BOOL |  |  |  |  | X
Alarm | 1000 | 13 | 301001 | 4 | 1170 | G U&lt; 1 | BOOL | [5 empty] | X
Alarm | 1000 | 13 | 301001 | 4 | 1170 | BA U&lt; 1 | BOOL |  |  |  | X
Alarm | 1000 | 13 | 301001 | 4 | 1170 | M U&lt; 1 | BOOL |  |  |  |  | X
Alarm | 1000 | 14 | 301001 | 4 | 1180 | G U&lt; 2 | BOOL | [5 empty] | X
Alarm | 1000 | 14 | 301001 | 4 | 1180 | BA U&lt; 2 | BOOL |  |  |  | X
Alarm | 1000 | 14 | 301001 | 4 | 1180 | M U&lt; 2 | BOOL |  |  |  |  | X
Alarm | 1000 | 15 | 301001 | 4 | 1190 | G U&lt; 3 | BOOL | [5 empty] | X
Alarm | 1000 | 15 | 301001 | 4 | 1190 | M U&lt; 3 | BOOL |  |  |  |  | X
Alarm | 1000 | 15 | 301001 | 4 | 1190 | BA U&lt; 3 | BOOL |  |  |  | X
Alarm | 1001 | 0 | 301002 | 4 | 1210 | G f&gt; 1 | BOOL | [5 empty] | X
Alarm | 1001 | 0 | 301002 | 4 | 1210 | BA f&gt; 1 | BOOL |  |  |  | X
Alarm | 1001 | 0 | 301002 | 4 | 1210 | M f&gt; 1 | BOOL |  |  |  |  | X
Alarm | 1001 | 1 | 301002 | 4 | 1220 | BA f&gt; 2 | BOOL |  |  |  | X
Alarm | 1001 | 1 | 301002 | 4 | 1220 | G f&gt; 2 | BOOL | [5 empty] | X
Alarm | 1001 | 1 | 301002 | 4 | 1220 | M f&gt; 2 | BOOL |  |  |  |  | X
Alarm | 1001 | 2 | 301002 | 4 | 1230 | G f&gt; 3 | BOOL | [5 empty] | X
Alarm | 1001 | 2 | 301002 | 4 | 1230 | BA f&gt; 3 | BOOL |  |  |  | X
Alarm | 1001 | 2 | 301002 | 4 | 1230 | M f&gt; 3 | BOOL |  |  |  |  | X
Alarm | 1001 | 3 | 301002 | 4 | 1240 | BA f&lt; 1 | BOOL |  |  |  | X
Alarm | 1001 | 3 | 301002 | 4 | 1240 | G f&lt; 1 | BOOL | [5 empty] | X
Alarm | 1001 | 3 | 301002 | 4 | 1240 | M f&lt; 1 | BOOL |  |  |  |  | X
Alarm | 1001 | 4 | 301002 | 4 | 1250 | G f&lt; 2 | BOOL | [5 empty] | X
Alarm | 1001 | 4 | 301002 | 4 | 1250 | BA f&lt; 2 | BOOL |  |  |  | X
Alarm | 1001 | 4 | 301002 | 4 | 1250 | M f&lt; 2 | BOOL |  |  |  |  | X
Alarm | 1001 | 5 | 301002 | 4 | 1260 | G f&lt; 3 | BOOL | [5 empty] | X
Alarm | 1001 | 5 | 301002 | 4 | 1260 | M f&lt; 3 | BOOL |  |  |  |  | X
Alarm | 1001 | 5 | 301002 | 4 | 1260 | BA f&lt; 3 | BOOL |  |  |  | X
Alarm | 1001 | 6 | 301002 | 4 | 1270 | BB U&gt; 1 | BOOL |  |  |  | X | X | X
Alarm | 1001 | 7 | 301002 | 4 | 1280 | BB U&gt; 2 | BOOL |  |  |  | X | X | X
Alarm | 1001 | 8 | 301002 | 4 | 1290 | BB U&gt; 3 | BOOL |  |  |  | X | X | X
Alarm | 1001 | 9 | 301002 | 4 | 1300 | BB U&lt; 1 | BOOL |  |  |  | X | X | X
Alarm | 1001 | 10 | 301002 | 4 | 1310 | BB U&lt; 2 | BOOL |  |  |  | X | X | X
Alarm | 1001 | 11 | 301002 | 4 | 1320 | BB U&lt; 3 | BOOL |  |  |  | X | X | X
Alarm | 1001 | 12 | 301002 | 4 | 1330 | BB U&lt; 4 | BOOL |  |  |  | X | X | X
Alarm | 1001 | 13 | 301002 | 4 | 1350 | BB f&gt; 1 | BOOL |  |  |  | X | X | X
Alarm | 1001 | 14 | 301002 | 4 | 1360 | BB f&gt; 2 | BOOL |  |  |  | X | X | X
Alarm | 1001 | 15 | 301002 | 4 | 1370 | BB f&gt; 3 | BOOL |  |  |  | X | X | X
Alarm | 1002 | 0 | 301003 | 4 | 1380 | BB f&lt; 1 | BOOL |  |  |  | X | X | X
Alarm | 1002 | 1 | 301003 | 4 | 1390 | BB f&lt; 2 | BOOL |  |  |  | X | X | X
Alarm | 1002 | 2 | 301003 | 4 | 1400 | BB f&lt; 3 | BOOL |  |  |  | X | X | X
Alarm | 1002 | 3 | 301003 | 4 | 1410 | BB f&lt; 4 | BOOL |  |  |  | X | X | X
Alarm | 1002 | 4 | 301003 | 4 | 1420 | df/dt (ROCOF) | BOOL |  |  |  | X | X | X
Alarm | 1002 | 5 | 301003 | 4 | 1430 | Vector jump | BOOL |  |  |  | X | X | X
Alarm | 1002 | 6 | 301003 | 4 | 1440 | BB pos. seq. volt. low | BOOL |  |  |  | X | X | X
Alarm | 1002 | 7 | 301003 | 4 | 1450 | BA P&gt; 1 | BOOL |  |  |  | X
Alarm | 1002 | 7 | 301003 | 4 | 1450 | G P&gt; 1 | BOOL | [5 empty] | X
Alarm | 1002 | 7 | 301003 | 4 | 1450 | M P&gt; 1 | BOOL |  |  |  |  | X
Alarm | 1002 | 8 | 301003 | 4 | 1460 | G P&gt; 2 | BOOL | [5 empty] | X
Alarm | 1002 | 8 | 301003 | 4 | 1460 | BA P&gt; 2 | BOOL |  |  |  | X
Alarm | 1002 | 8 | 301003 | 4 | 1460 | M P&gt; 2 | BOOL |  |  |  |  | X
Alarm | 1002 | 9 | 301003 | 4 | 1470 | G P&gt; 3 | BOOL | [5 empty] | X
Alarm | 1002 | 9 | 301003 | 4 | 1470 | BA P&gt; 3 | BOOL |  |  |  | X
Alarm | 1002 | 9 | 301003 | 4 | 1470 | M P&gt; 3 | BOOL |  |  |  |  | X
Alarm | 1002 | 10 | 301003 | 4 | 1480 | G P&gt; 4 | BOOL | [5 empty] | X
Alarm | 1002 | 10 | 301003 | 4 | 1480 | BA P&gt; 4 | BOOL |  |  |  | X
Alarm | 1002 | 10 | 301003 | 4 | 1480 | M P&gt; 4 | BOOL |  |  |  |  | X
Alarm | 1002 | 11 | 301003 | 4 | 1490 | G P&gt; 5 | BOOL | [5 empty] | X
Alarm | 1002 | 11 | 301003 | 4 | 1490 | BA P&gt; 5 | BOOL |  |  |  | X
Alarm | 1002 | 11 | 301003 | 4 | 1490 | M P&gt; 5 | BOOL |  |  |  |  | X
Alarm | 1002 | 12 | 301003 | 4 | 1500 | Unbalance curr. 1 | BOOL |  |  |  |  | X | X
Alarm | 1002 | 13 | 301003 | 4 | 1510 | Unbalance volt. | BOOL |  |  |  |  | X | X
Alarm | 1002 | 14 | 301003 | 4 | 1520 | G -Q&gt; | BOOL | [5 empty] | X
Alarm | 1002 | 14 | 301003 | 4 | 1520 | BA -Q&gt; | BOOL |  |  |  | X
Alarm | 1002 | 14 | 301003 | 4 | 1520 | M -Q&gt; | BOOL |  |  |  |  | X
Alarm | 1002 | 15 | 301003 | 4 | 1530 | G Q&gt; | BOOL | [5 empty] | X
Alarm | 1002 | 15 | 301003 | 4 | 1530 | BA Q&gt; | BOOL |  |  |  | X
Alarm | 1002 | 15 | 301003 | 4 | 1530 | M Q&gt; | BOOL |  |  |  |  | X
Alarm | 1003 | 0 | 301004 | 4 | 1540 | Gen. neg. seq. I | BOOL | [5 empty] | X
Alarm | 1003 | 0 | 301004 | 4 | 1540 | Mains neg. seq. I | BOOL |  |  |  |  | X
Alarm | 1003 | 1 | 301004 | 4 | 1550 | Generator neg. seq. U | BOOL | [5 empty] | X
Alarm | 1003 | 1 | 301004 | 4 | 1550 | Bus A neg. seq. U | BOOL |  |  |  | X
Alarm | 1003 | 1 | 301004 | 4 | 1550 | Mains neg. seq. U | BOOL |  |  |  |  | X
Alarm | 1003 | 2 | 301004 | 4 | 1570 | Gen. zero seq. I | BOOL | [5 empty] | X
Alarm | 1003 | 2 | 301004 | 4 | 1570 | Bus A zero seq. I | BOOL |  |  |  | X
Alarm | 1003 | 2 | 301004 | 4 | 1570 | Mains zero seq. I | BOOL |  |  |  |  | X
Alarm | 1003 | 3 | 301004 | 4 | 1580 | Zero seq. U | BOOL | [5 empty] | X
Alarm | 1003 | 3 | 301004 | 4 | 1580 | Bus A zero seq. U | BOOL |  |  |  | X
Alarm | 1003 | 3 | 301004 | 4 | 1580 | Mains zero seq. U | BOOL |  |  |  |  | X
Alarm | 1003 | 4 | 301004 | 4 | 1600 | Directional overcurrent 1 | BOOL |  |  |  | X | X | X
Alarm | 1003 | 5 | 301004 | 4 | 1610 | Directional overcurrent 2 | BOOL |  |  |  | X | X | X
Alarm | 1003 | 6 | 301004 | 4 | 1620 | BB unbalance U | BOOL |  |  |  | X | X | X
Alarm | 1003 | 7 | 301004 | 4 | 1800 | NEL 1 I&gt; | BOOL |  |  |  |  | X | X
Alarm | 1003 | 8 | 301004 | 4 | 1810 | NEL 2 I&gt; | BOOL |  |  |  |  | X | X
Alarm | 1003 | 9 | 301004 | 4 | 1820 | NEL 3 I&gt; | BOOL |  |  |  |  | X | X
Alarm | 1003 | 10 | 301004 | 4 | 1830 | NEL 1 BB f&lt; | BOOL |  |  |  |  | X | X
Alarm | 1003 | 11 | 301004 | 4 | 1840 | NEL 2 BB f&lt; | BOOL |  |  |  |  | X | X
Alarm | 1003 | 12 | 301004 | 4 | 1850 | NEL 3 BB f&lt; | BOOL |  |  |  |  | X | X
Alarm | 1003 | 13 | 301004 | 4 | 1860 | NEL 1 P&gt; | BOOL |  |  |  |  | X | X
Alarm | 1003 | 14 | 301004 | 4 | 1870 | NEL 2 P&gt; | BOOL |  |  |  |  | X | X
Alarm | 1003 | 15 | 301004 | 4 | 1880 | NEL 3 P&gt; | BOOL |  |  |  |  | X | X
Alarm | 1004 | 0 | 301005 | 4 | 1890 | NEL 1 P&gt;&gt; | BOOL |  |  |  |  | X | X
Alarm | 1004 | 1 | 301005 | 4 | 1900 | NEL 2 P&gt;&gt; | BOOL |  |  |  |  | X | X
Alarm | 1004 | 2 | 301005 | 4 | 1910 | NEL 3 P&gt;&gt; | BOOL |  |  |  |  | X | X
Alarm | 1004 | 6 | 301005 | 4 | 1960 | U and Q&lt; 1 | BOOL |  |  |  |  | X | X
Alarm | 1004 | 7 | 301005 | 4 | 1970 | U and Q&lt; 2 | BOOL |  |  |  |  | X | X
Alarm | 1004 | 8 | 301005 | 4 | 1981 | GB ext. trip | BOOL | [5 empty] | X
Alarm | 1004 | 8 | 301005 | 4 | 1981 | BTB ext. trip | BOOL |  |  |  | X
Alarm | 1004 | 8 | 301005 | 4 | 1981 | TB ext. trip | BOOL |  |  |  |  | X
Alarm | 1004 | 9 | 301005 | 4 | 1983 | MB ext. trip | BOOL |  |  |  |  | X | X
Alarm | 1004 | 10 | 301005 | 4 | 1650 | Ut&lt; 1 monitoring active | BOOL | [5 empty] | X
Alarm | 1004 | 11 | 301005 | 4 | 1660 | Ut&lt; 1 | BOOL | [5 empty] | X
Alarm | 1004 | 12 | 301005 | 4 | 1690 | Ut&lt; 2 monitoring active | BOOL | [5 empty] | X
Alarm | 1004 | 13 | 301005 | 4 | 1700 | Ut&lt; 2 | BOOL | [5 empty] | X
Alarm | 1004 | 14 | 301005 | 4 | 1760 | G P dep. Q&lt; | BOOL | [5 empty] | X
Alarm | 1004 | 15 | 301005 | 4 | 1790 | G P dep. Q&gt; | BOOL | [5 empty] | X
Alarm | 1005 | 0 | 301006 | 4 | 2120 | Synchronising window | BOOL |  |  |  | X | X | X
Alarm | 1005 | 1 | 301006 | 4 | 2130 | Synchronising failure GB | BOOL | [5 empty] | X
Alarm | 1005 | 1 | 301006 | 4 | 2130 | Synchronising failure BTB | BOOL |  |  |  | X
Alarm | 1005 | 1 | 301006 | 4 | 2130 | Synchronising failure TB | BOOL |  |  |  |  | X
Alarm | 1005 | 2 | 301006 | 4 | 2140 | Synchronising failure MB | BOOL |  |  |  |  | X | X
Alarm | 1005 | 3 | 301006 | 4 | 2150 | Phase seq. failure A | BOOL |  |  |  | X | X | X
Alarm | 1005 | 4 | 301006 | 4 | 2160 | GB open failure | BOOL | [5 empty] | X
Alarm | 1005 | 4 | 301006 | 4 | 2160 | BTB open failure | BOOL |  |  |  | X
Alarm | 1005 | 4 | 301006 | 4 | 2160 | TB open failure | BOOL |  |  |  |  | X
Alarm | 1005 | 5 | 301006 | 4 | 2170 | BTB close failure | BOOL |  |  |  | X
Alarm | 1005 | 5 | 301006 | 4 | 2170 | GB close failure | BOOL | [5 empty] | X
Alarm | 1005 | 5 | 301006 | 4 | 2170 | TB close failure | BOOL |  |  |  |  | X
Alarm | 1005 | 6 | 301006 | 4 | 2180 | BTB pos. failure | BOOL |  |  |  | X
Alarm | 1005 | 6 | 301006 | 4 | 2180 | GB pos. failure | BOOL | [5 empty] | X
Alarm | 1005 | 6 | 301006 | 4 | 2180 | TB pos. failure | BOOL |  |  |  |  | X
Alarm | 1005 | 7 | 301006 | 4 | 2200 | MB open failure | BOOL |  |  |  |  | X | X
Alarm | 1005 | 8 | 301006 | 4 | 2210 | MB close failure | BOOL |  |  |  |  | X | X
Alarm | 1005 | 9 | 301006 | 4 | 2220 | MB pos. failure | BOOL |  |  |  |  | X | X
Alarm | 1005 | 10 | 301006 | 4 | 2270 | Close before excitation failure | BOOL | [5 empty] | X
Alarm | 1005 | 11 | 301006 | 4 | 2155 | Phase seq. failure B | BOOL |  |  |  | X | X | X
Alarm | 1006 | 0 | 301007 | 4 | 2560 | GOVERNOR regulation fail. | BOOL | [5 empty] | X
Alarm | 1006 | 1 | 301007 | 4 | 2630 | Deload error | BOOL | [5 empty] | X
Alarm | 1006 | 2 | 301007 | 4 | 2680 | AVR regulation fail. | BOOL | [5 empty] | X
Alarm | 1007 | 0 | 301008 | 4 | 3000 | Digital alarm input 77 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 1 | 301008 | 4 | 3010 | Digital alarm input 78 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 2 | 301008 | 4 | 3020 | Digital alarm input 79 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 3 | 301008 | 4 | 3030 | Digital alarm input 80 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 4 | 301008 | 4 | 3040 | Digital alarm input 81 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 5 | 301008 | 4 | 3050 | Digital alarm input 82 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 6 | 301008 | 4 | 3060 | Digital alarm input 83 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 7 | 301008 | 4 | 3070 | Digital alarm input 84 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 8 | 301008 | 4 | 3080 | Digital alarm input 85 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 9 | 301008 | 4 | 3090 | Digital alarm input 86 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 10 | 301008 | 4 | 3100 | Digital alarm input 87 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 11 | 301008 | 4 | 3110 | Digital alarm input 88 | BOOL |  |  |  | X | X | X
Alarm | 1007 | 12 | 301008 | 4 | 3120 | Digital alarm input 89 | BOOL |  |  |  | X | X | X
Alarm | 1008 | 0 | 301009 | 4 | 3130 | Digital alarm input 90 | BOOL |  |  |  | X | X | X
Alarm | 1010 | 0 | 301011 | 4 | 3400 | Multi-in. Alarm 46 | BOOL |  |  |  | X | X | X
Alarm | 1010 | 1 | 301011 | 4 | 3410 | Multi-in. Alarm 47 | BOOL |  |  |  | X | X | X
Alarm | 1010 | 2 | 301011 | 4 | 3420 | Multi-in. Alarm 48 | BOOL |  |  |  | X | X | X
Alarm | 1010 | 3 | 301011 | 4 | 3401 | Wire fail. 46 | BOOL |  |  |  | X | X | X
Alarm | 1010 | 4 | 301011 | 4 | 3411 | Wire fail. 47 | BOOL |  |  |  | X | X | X
Alarm | 1010 | 5 | 301011 | 4 | 3421 | Wire fail. 48 | BOOL |  |  |  | X | X | X
Alarm | 1010 | 12 | 301011 | 4 | 3490 | Digital alarm input 25 (Emergency stop) | BOOL |  |  |  | X | X | X
Alarm | 1011 | 7 | 301012 | 4 | 3570 | M-Logic alarm 1 | BOOL |  |  |  | X | X | X
Alarm | 1011 | 8 | 301012 | 4 | 3580 | M-Logic alarm 2 | BOOL |  |  |  | X | X | X
Alarm | 1011 | 9 | 301012 | 4 | 3590 | M-Logic alarm 3 | BOOL |  |  |  | X | X | X
Alarm | 1011 | 10 | 301012 | 4 | 3600 | M-Logic alarm 4 | BOOL |  |  |  | X | X | X
Alarm | 1011 | 11 | 301012 | 4 | 3610 | M-Logic alarm 5 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 0 | 301014 | 4 | 4120, 4140, 4160, 4180, 4200, 4220 | Multi input terminal 46.1 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 1 | 301014 | 4 | 4130, 4150, 4170, 4190, 4210, 4230 | Multi input terminal 46.2 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 2 | 301014 | 4 | 4240 | W. fail. 46 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 3 | 301014 | 4 | 4250, 4270, 4290, 4310, 4330, 4350 | Multi input terminal 47.1 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 4 | 301014 | 4 | 4260, 4280, 4300, 4320, 4340, 4360 | Multi input terminal 47.2 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 5 | 301014 | 4 | 4370 | W. fail. 47 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 6 | 301014 | 4 | 4380, 4400, 4420, 4440, 4460, 4480 | Multi input terminal 48.1 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 7 | 301014 | 4 | 4390, 4410, 4430, 4450, 4470, 4490 | Multi input terminal 48.2 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 8 | 301014 | 4 | 4500 | W. fail. 48 | BOOL |  |  |  | X | X | X
Alarm | 1013 | 9 | 301014 | 4 | 4510 | Overspeed 1 | BOOL | [5 empty] | X
Alarm | 1013 | 10 | 301014 | 4 | 4520 | Overspeed 2 | BOOL | [5 empty] | X
Alarm | 1013 | 11 | 301014 | 4 | 4530 | Crank failure | BOOL | [5 empty] | X
Alarm | 1013 | 12 | 301014 | 4 | 4540 | Running feedback failure | BOOL | [5 empty] | X
Alarm | 1013 | 13 | 301014 | 4 | 4550 | MPU wire failure | BOOL | [5 empty] | X
Alarm | 1013 | 14 | 301014 | 4 | 4560 | Hz/V failure | BOOL | [5 empty] | X
Alarm | 1013 | 15 | 301014 | 4 | 4570 | Start failure | BOOL | [5 empty] | X
Alarm | 1014 | 0 | 301015 | 4 | 4580 | Stop failure | BOOL | [5 empty] | X
Alarm | 1014 | 1 | 301015 | 4 | 4960 | U&lt; aux. term. 1 | BOOL |  |  |  | X | X | X
Alarm | 1014 | 2 | 301015 | 4 | 4970 | U&gt; aux. term. 1 | BOOL |  |  |  | X | X | X
Alarm | 1014 | 5 | 301015 | 4 | 4590 | Underspeed 1 | BOOL | [5 empty] | X
Alarm | 1015 | 0 | 301016 | 4 | 6110 | Service timer 1 | BOOL | [5 empty] | X
Alarm | 1015 | 1 | 301016 | 4 | 6120 | Service timer 2 | BOOL | [5 empty] | X
Alarm | 1015 | 2 | 301016 | 4 | 6270 | Stop coil wire break | BOOL | [5 empty] | X
Alarm | 1015 | 4 | 301016 | 4 | 6330 | Engine heater 1 | BOOL | [5 empty] | X
Alarm | 1015 | 5 | 301016 | 4 | 6410 | Battery test | BOOL | [5 empty] | X
Alarm | 1015 | 6 | 301016 | 4 | 6440 | Battery asymmetry 1 | BOOL | [5 empty] | X
Alarm | 1015 | 7 | 301016 | 4 | 6450 | Battery asymmetry 2 | BOOL | [5 empty] | X
Alarm | 1015 | 8 | 301016 | 4 | 6470 | Max. ventilation 1 | BOOL | [5 empty] | X
Alarm | 1015 | 9 | 301016 | 4 | 6480 | Max. ventilation 2 | BOOL | [5 empty] | X
Alarm | 1015 | 10 | 301016 | 4 | 6500 | Blk. swbd. error | BOOL | [5 empty] | X
Alarm | 1015 | 11 | 301016 | 4 | 6510 | Stp. swbd. error | BOOL | [5 empty] | X
Alarm | 1015 | 12 | 301016 | 4 | 6540 | Unit not in auto | BOOL |  |  |  | X | X | X
Alarm | 1015 | 13 | 301016 | 4 | 6550 | Fuel pump logic | BOOL | [5 empty] | X
Alarm | 1016 | 0 | 301017 | 4 | 5000 | Relay 16 | BOOL |  |  |  | X | X | X
Alarm | 1016 | 1 | 301017 | 4 | 5010 | Relay 18 | BOOL |  |  |  | X | X | X
Alarm | 1016 | 2 | 301017 | 4 | 5020 | Relay 20 | BOOL |  |  |  | X | X | X
Alarm | 1016 | 3 | 301017 | 4 | 5030 | Relay 23 | BOOL |  |  |  | X | X | X
Alarm | 1016 | 4 | 301017 | 4 | 5040 | Relay 26 | BOOL |  |  |  | X | X | X
Alarm | 1016 | 5 | 301017 | 4 | 5050 | Relay 27 | BOOL |  |  |  | X | X | X
Alarm | 1016 | 6 | 301017 | 4 | 5060 | Relay 28 | BOOL |  |  |  | X | X | X
Alarm | 1016 | 7 | 301017 | 4 | 5070 | Relay 30 | BOOL |  |  |  | X | X | X
Alarm | 1016 | 8 | 301017 | 4 | 5080 | Relay 32 | BOOL |  |  |  | X | X | X
Alarm | 1016 | 9 | 301017 | 4 | 8090 | Relay 34 | BOOL |  |  |  | X | X | X
Alarm | 1016 | 10 | 301017 | 4 | 5100 | Relay 36 | BOOL |  |  |  | X | X | X
Alarm | 1016 | 11 | 301017 | 4 | 5110 | Relay 39 | BOOL |  |  |  | X | X | X
Alarm | 1016 | 12 | 301017 | 4 | 5120 | Relay 41 | BOOL |  |  |  | X | X | X
Alarm | 1016 | 13 | 301017 | 4 | 5130 | Relay 43 | BOOL |  |  |  | X | X | X
Alarm | 1017 | 12 | 301018 | 4 |  | Run. coil relay | BOOL | [5 empty] | X
Alarm | 1017 | 13 | 301018 | 4 |  | Start prepare | BOOL | [5 empty] | X
Alarm | 1017 | 14 | 301018 | 4 |  | Start relay | BOOL | [5 empty] | X
Alarm | 1017 | 15 | 301018 | 4 |  | Stop coil relay | BOOL | [5 empty] | X
Alarm | 1018 | 0 | 301019 | 4 |  | Mains failure | BOOL |  |  |  |  | X | X
Alarm | 1018 | 1 | 301019 | 4 |  | MB position ON | BOOL |  |  |  |  | X | X
Alarm | 1018 | 2 | 301019 | 4 |  | DG ramp down | BOOL | [5 empty] | X
Alarm | 1018 | 3 | 301019 | 4 |  | Start GOV/AVR regulation | BOOL | [5 empty] | X
Alarm | 1018 | 4 | 301019 | 4 |  | GB position ON | BOOL | [5 empty] | X
Alarm | 1018 | 4 | 301019 | 4 |  | TB pos. ON | BOOL |  |  |  |  | X
Alarm | 1018 | 4 | 301019 | 4 |  | BTB pos. ON | BOOL |  |  |  | X
Alarm | 1018 | 5 | 301019 | 4 |  | GB synchronising | BOOL | [5 empty] | X
Alarm | 1018 | 5 | 301019 | 4 |  | BTB synchronising | BOOL |  |  |  | X
Alarm | 1018 | 5 | 301019 | 4 |  | TB synchronising | BOOL |  |  |  |  | X
Alarm | 1018 | 6 | 301019 | 4 |  | Engine running | BOOL | [5 empty] | X
Alarm | 1018 | 7 | 301019 | 4 | 6173 | Running detected, timer expired | BOOL | [5 empty] | X
Alarm | 1018 | 8 | 301019 | 4 | 6220 | DG Hz/V OK, timer expired | BOOL | [5 empty] | X
Alarm | 1018 | 8 | 301019 | 4 | 6220 | BB Hz/V OK, timer expired | BOOL |  |  |  | X | X
Alarm | 1018 | 9 | 301019 | 4 | 6410 | Battery test ongoing | BOOL | [5 empty] | X
Alarm | 1018 | 11 | 301019 | 4 |  | GB position OFF | BOOL | [5 empty] | X
Alarm | 1018 | 11 | 301019 | 4 |  | BTB position OFF | BOOL |  |  |  | X
Alarm | 1018 | 11 | 301019 | 4 |  | TB position OFF | BOOL |  |  |  |  | X
Alarm | 1018 | 12 | 301019 | 4 |  | MB position OFF | BOOL |  |  |  |  | X | X
Alarm | 1018 | 13 | 301019 | 4 |  | BB Hz/V OK | BOOL |  |  |  | X | X | X
Alarm | 1018 | 14 | 301019 | 4 |  | Single DG, MB synchronising | BOOL | [5 empty] | X
Alarm | 1018 | 15 | 301019 | 4 |  | Dry mode | BOOL | [5 empty] | X
Alarm | 1019 | 0 | 301020 | 4 |  | Block mode | BOOL |  |  |  | X | X | X
Alarm | 1019 | 1 | 301020 | 4 |  | Manual mode | BOOL | [5 empty] | X
Alarm | 1019 | 2 | 301020 | 4 |  | Semi auto mode | BOOL |  |  |  | X | X | X
Alarm | 1019 | 3 | 301020 | 4 |  | Auto mode | BOOL |  |  |  | X | X | X
Alarm | 1019 | 4 | 301020 | 4 |  | Test | BOOL |  |  |  |  | X | X
Alarm | 1019 | 5 | 301020 | 4 |  | Island | BOOL |  |  |  |  | X | X
Alarm | 1019 | 6 | 301020 | 4 |  | AMF | BOOL |  |  |  |  | X | X
Alarm | 1019 | 7 | 301020 | 4 |  | Peak shaving | BOOL |  |  |  |  | X | X
Alarm | 1019 | 8 | 301020 | 4 |  | Fixed power | BOOL |  |  |  |  | X | X
Alarm | 1019 | 9 | 301020 | 4 |  | Mains power export | BOOL |  |  |  |  | X | X
Alarm | 1019 | 10 | 301020 | 4 |  | Load takeover | BOOL |  |  |  |  | X | X
Alarm | 1019 | 11 | 301020 | 4 |  | Power management | BOOL | [5 empty] | X
Alarm | 1019 | 15 | 301020 | 4 |  | AMF active | BOOL |  |  |  |  | X | X
Alarm | 1020 | 0 | 301021 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1020 | 1 | 301021 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1020 | 2 | 301021 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1020 | 3 | 301021 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1020 | 4 | 301021 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1020 | 5 | 301021 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1020 | 6 | 301021 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1020 | 7 | 301021 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1020 | 8 | 301021 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1020 | 9 | 301021 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1020 | 10 | 301021 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1020 | 11 | 301021 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1020 | 12 | 301021 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1020 | 13 | 301021 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1021 | 0 | 301022 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1021 | 1 | 301022 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1021 | 12 | 301022 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1021 | 13 | 301022 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1021 | 14 | 301022 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1021 | 15 | 301022 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 0 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 1 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 2 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 3 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 4 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 5 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 6 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 7 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 8 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 9 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 10 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 11 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 12 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 13 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 14 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1022 | 15 | 301023 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 0 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 1 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 2 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 3 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 4 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 5 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 6 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 7 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 8 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 9 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 10 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 11 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 12 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 13 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 14 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1023 | 15 | 301024 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 0 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 1 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 2 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 3 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 4 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 5 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 6 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 7 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 8 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 9 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 10 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 11 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 12 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 13 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 14 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1024 | 15 | 301025 | 4 |  | See DRH manual | BOOL | [5 empty] | X
Alarm | 1026 | 0 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1026 | 1 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1026 | 2 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1026 | 3 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1026 | 4 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1026 | 5 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1026 | 6 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1026 | 7 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1026 | 8 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1026 | 9 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1026 | 10 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1026 | 11 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1026 | 12 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1026 | 13 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1026 | 14 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1026 | 15 | 301027 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 0 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 1 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 2 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 3 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 4 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 5 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 6 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 7 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 8 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 9 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 10 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 11 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 12 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 13 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 14 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1027 | 15 | 301028 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1028 | 0 | 301029 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1028 | 1 | 301029 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1028 | 2 | 301029 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1028 | 3 | 301029 | 4 |  | See H5/H7 manual | BOOL | [5 empty] | X
Alarm | 1031 | 1 | 301032 | 4 |  | CAN 1 missing ID 1 | BOOL |  |  |  | X | X | X
Alarm | 1031 | 2 | 301032 | 4 |  | CAN 1 missing ID 2 | BOOL |  |  |  | X | X | X
Alarm | 1031 | 3 | 301032 | 4 |  | CAN 1 missing ID 3 | BOOL |  |  |  | X | X | X
Alarm | 1031 | 4 | 301032 | 4 |  | CAN 1 missing ID 4 | BOOL |  |  |  | X | X | X
Alarm | 1031 | 5 | 301032 | 4 |  | CAN 1 missing ID 5 | BOOL |  |  |  | X | X | X
Alarm | 1031 | 6 | 301032 | 4 |  | CAN 1 missing ID 6 | BOOL |  |  |  | X | X | X
Alarm | 1031 | 7 | 301032 | 4 |  | CAN 1 missing ID 7 | BOOL |  |  |  | X | X | X
Alarm | 1031 | 8 | 301032 | 4 |  | CAN 1 missing ID 8 | BOOL |  |  |  | X | X | X
Alarm | 1031 | 9 | 301032 | 4 |  | CAN 1 missing ID 9 | BOOL |  |  |  | X | X | X
Alarm | 1031 | 10 | 301032 | 4 |  | CAN 1 missing ID 10 | BOOL |  |  |  | X | X | X
Alarm | 1031 | 11 | 301032 | 4 |  | CAN 1 missing ID 11 | BOOL |  |  |  | X | X | X
Alarm | 1031 | 12 | 301032 | 4 |  | CAN 1 missing ID 12 | BOOL |  |  |  | X | X | X
Alarm | 1031 | 13 | 301032 | 4 |  | CAN 1 missing ID 13 | BOOL |  |  |  | X | X | X
Alarm | 1031 | 14 | 301032 | 4 |  | CAN 1 missing ID 14 | BOOL |  |  |  | X | X | X
Alarm | 1031 | 15 | 301032 | 4 |  | CAN 1 missing ID 15 | BOOL |  |  |  | X | X | X
Alarm | 1032 | 0 | 301033 | 4 |  | CAN 1 missing ID 16 | BOOL |  |  |  | X | X | X
Alarm | 1032 | 2 | 301033 | 4 |  | CAN 2 missing ID 1 | BOOL |  |  |  | X | X | X
Alarm | 1032 | 3 | 301033 | 4 |  | CAN 2 missing ID 2 | BOOL |  |  |  | X | X | X
Alarm | 1032 | 4 | 301033 | 4 |  | CAN 2 missing ID 3 | BOOL |  |  |  | X | X | X
Alarm | 1032 | 5 | 301033 | 4 |  | CAN 2 missing ID 4 | BOOL |  |  |  | X | X | X
Alarm | 1032 | 6 | 301033 | 4 |  | CAN 2 missing ID 5 | BOOL |  |  |  | X | X | X
Alarm | 1032 | 7 | 301033 | 4 |  | CAN 2 missing ID 6 | BOOL |  |  |  | X | X | X
Alarm | 1032 | 8 | 301033 | 4 |  | CAN 2 missing ID 7 | BOOL |  |  |  | X | X | X
Alarm | 1032 | 9 | 301033 | 4 |  | CAN 2 missing ID 8 | BOOL |  |  |  | X | X | X
Alarm | 1032 | 10 | 301033 | 4 |  | CAN 2 missing ID 9 | BOOL |  |  |  | X | X | X
Alarm | 1032 | 11 | 301033 | 4 |  | CAN 2 missing ID 10 | BOOL |  |  |  | X | X | X
Alarm | 1032 | 12 | 301033 | 4 |  | CAN 2 missing ID 11 | BOOL |  |  |  | X | X | X
Alarm | 1032 | 13 | 301033 | 4 |  | CAN 2 missing ID 12 | BOOL |  |  |  | X | X | X
Alarm | 1032 | 14 | 301033 | 4 |  | CAN 2 missing ID 13 | BOOL |  |  |  | X | X | X
Alarm | 1032 | 15 | 301033 | 4 |  | CAN 2 missing ID 14 | BOOL |  |  |  | X | X | X
Alarm | 1033 | 0 | 301034 | 4 |  | CAN 2 missing ID 16 | BOOL |  |  |  | X | X | X
Alarm | 1033 | 1 | 301034 | 4 |  | CAN 2 missing ID 15 | BOOL |  |  |  | X | X | X
Alarm | 1033 | 2 | 301034 | 4 | 7520 | Communication error ext. | BOOL |  |  |  | X | X | X
Alarm | 1034 | 1 | 301035 | 4 |  | Ext. Modbus comm. error on CAN ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1034 | 1 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 1 | BOOL |  |  |  | X | X | X
Alarm | 1034 | 2 | 301035 | 4 |  | Ext. Modbus comm. error on CAN ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1034 | 2 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 2 | BOOL |  |  |  | X | X | X
Alarm | 1034 | 3 | 301035 | 4 |  | Ext. Modbus comm. error on CAN ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1034 | 3 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 3 | BOOL |  |  |  | X | X | X
Alarm | 1034 | 4 | 301035 | 4 |  | Ext. Modbus comm. error on CAN ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1034 | 4 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 4 | BOOL |  |  |  | X | X | X
Alarm | 1034 | 5 | 301035 | 4 |  | Ext. Modbus comm. error on CAN ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1034 | 5 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 5 | BOOL |  |  |  | X | X | X
Alarm | 1034 | 6 | 301035 | 4 |  | Ext. Modbus comm. error on CAN ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1034 | 6 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 6 | BOOL |  |  |  | X | X | X
Alarm | 1034 | 7 | 301035 | 4 |  | Ext. Modbus comm. error on CAN ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1034 | 7 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 7 | BOOL |  |  |  | X | X | X
Alarm | 1034 | 8 | 301035 | 4 |  | Ext. Modbus comm. error on CAN ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1034 | 8 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 8 | BOOL |  |  |  | X | X | X
Alarm | 1034 | 9 | 301035 | 4 |  | Ext. Modbus comm. error on CAN ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1034 | 9 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 9 | BOOL |  |  |  | X | X | X
Alarm | 1034 | 10 | 301035 | 4 |  | Ext. Modbus comm. error on CAN ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1034 | 10 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 10 | BOOL |  |  |  | X | X | X
Alarm | 1034 | 11 | 301035 | 4 |  | Ext. Modbus comm. error on CAN ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1034 | 11 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 11 | BOOL |  |  |  | X | X | X
Alarm | 1034 | 12 | 301035 | 4 |  | Ext. Modbus comm. error on CAN ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1034 | 12 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 12 | BOOL |  |  |  | X | X | X
Alarm | 1034 | 13 | 301035 | 4 |  | Ext. Modbus comm. error on CAN ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1034 | 13 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 13 | BOOL |  |  |  | X | X | X
Alarm | 1034 | 14 | 301035 | 4 |  | Ext. Modbus comm. error on CAN ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1034 | 14 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 14 | BOOL |  |  |  | X | X | X
Alarm | 1034 | 15 | 301035 | 4 |  | Ext. Modbus comm. error on CAN ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1034 | 15 | 301035 | 4 |  | Ext. Modbus comm. error, CAN ID 15 | BOOL |  |  |  | X | X | X
Alarm | 1035 | 0 | 301036 | 4 |  | Ext. Modbus comm. error on CAN ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1035 | 0 | 301036 | 4 |  | Ext. Modbus comm. error, CAN ID 16 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 0 | 301037 | 4 | 12000 | Ext. Analogue in. 1.1 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 1 | 301037 | 4 | 12010 | Ext. Analogue in. 1.2 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 3 | 301037 | 4 | 12030 | Ext. Analogue in. 2.1 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 4 | 301037 | 4 | 12040 | Ext. Analogue in. 2.2 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 6 | 301037 | 4 | 12060 | Ext. Analogue in. 3.1 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 7 | 301037 | 4 | 12070 | Ext. Analogue in. 3.2 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 9 | 301037 | 4 | 12090 | Ext. Analogue in. 4.1 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 10 | 301037 | 4 | 12100 | Ext. Analogue in. 4.2 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 12 | 301037 | 4 | 12120 | Ext. Analogue in. 5.1 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 13 | 301037 | 4 | 12130 | Ext. Analogue in. 5.2 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 15 | 301037 | 4 | 12150 | Ext. Analogue in. 6.1 | BOOL |  |  |  | X | X | X
Alarm | 1037 | 0 | 301038 | 4 | 12160 | Ext. Analogue in. 6.2 | BOOL |  |  |  | X | X | X
Alarm | 1037 | 2 | 301038 | 4 | 12180 | Ext. Analogue in. 7.1 | BOOL |  |  |  | X | X | X
Alarm | 1037 | 3 | 301038 | 4 | 12190 | Ext. Analogue in. 7.2 | BOOL |  |  |  | X | X | X
Alarm | 1037 | 5 | 301038 | 4 | 12210 | Ext. Analogue in. 8.1 | BOOL |  |  |  | X | X | X
Alarm | 1037 | 6 | 301038 | 4 | 12220 | Ext. Analogue in. 8.2 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 0 | 301039 | 4 | 12540 | External digital input 1 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 1 | 301039 | 4 | 12550 | External digital input 2 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 2 | 301039 | 4 | 12560 | External digital input 3 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 3 | 301039 | 4 | 12570 | External digital input 4 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 4 | 301039 | 4 | 12580 | External digital input 5 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 5 | 301039 | 4 | 12590 | External digital input 6 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 6 | 301039 | 4 | 12600 | External digital input 7 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 7 | 301039 | 4 | 12610 | External digital input 8 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 8 | 301039 | 4 | 12620 | External digital input 9 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 9 | 301039 | 4 | 12630 | External digital input 10 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 10 | 301039 | 4 | 12640 | External digital input 11 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 11 | 301039 | 4 | 12650 | External digital input 12 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 12 | 301039 | 4 | 12660 | External digital input 13 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 13 | 301039 | 4 | 12670 | External digital input 14 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 14 | 301039 | 4 | 12680 | External digital input 15 | BOOL |  |  |  | X | X | X
Alarm | 1038 | 15 | 301039 | 4 | 12690 | External digital input 16 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 0 | 301040 | 4 | 12790 | External digital output 1 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 1 | 301040 | 4 | 12800 | External digital output 2 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 2 | 301040 | 4 | 12810 | External digital output 3 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 3 | 301040 | 4 | 12820 | External digital output 4 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 4 | 301040 | 4 | 12830 | External digital output 5 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 5 | 301040 | 4 | 12840 | External digital output 6 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 6 | 301040 | 4 | 12850 | External digital output 7 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 7 | 301040 | 4 | 12860 | External digital output 8 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 8 | 301040 | 4 | 12870 | External digital output 9 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 9 | 301040 | 4 | 12880 | External digital output 10 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 10 | 301040 | 4 | 12890 | External digital output 11 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 11 | 301040 | 4 | 12900 | External digital output 12 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 12 | 301040 | 4 | 12910 | External digital output 13 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 13 | 301040 | 4 | 12920 | External digital output 14 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 14 | 301040 | 4 | 12930 | External digital output 15 | BOOL |  |  |  | X | X | X
Alarm | 1039 | 15 | 301040 | 4 | 12940 | External digital output 16 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 0 | 301041 | 4 |  | CAN 1 missing ID 1 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 1 | 301041 | 4 |  | CAN 1 missing ID 2 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 2 | 301041 | 4 |  | CAN 1 missing ID 3 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 3 | 301041 | 4 |  | CAN 1 missing ID 4 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 4 | 301041 | 4 |  | CAN 1 missing ID 5 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 5 | 301041 | 4 |  | CAN 1 missing ID 6 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 6 | 301041 | 4 |  | CAN 1 missing ID 7 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 7 | 301041 | 4 |  | CAN 1 missing ID 8 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 8 | 301041 | 4 |  | CAN 1 missing ID 9 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 9 | 301041 | 4 |  | CAN 1 missing ID 10 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 10 | 301041 | 4 |  | CAN 1 missing ID 11 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 11 | 301041 | 4 |  | CAN 1 missing ID 12 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 12 | 301041 | 4 |  | CAN 1 missing ID 13 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 13 | 301041 | 4 |  | CAN 1 missing ID 14 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 14 | 301041 | 4 |  | CAN 1 missing ID 15 | BOOL |  |  |  | X | X | X
Alarm | 1040 | 15 | 301041 | 4 |  | CAN 1 missing ID 16 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 0 | 301042 | 4 |  | CAN 1 missing ID 17 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 1 | 301042 | 4 |  | CAN 1 missing ID 18 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 2 | 301042 | 4 |  | CAN 1 missing ID 19 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 3 | 301042 | 4 |  | CAN 1 missing ID 20 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 4 | 301042 | 4 |  | CAN 1 missing ID 21 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 5 | 301042 | 4 |  | CAN 1 missing ID 22 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 6 | 301042 | 4 |  | CAN 1 missing ID 23 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 7 | 301042 | 4 |  | CAN 1 missing ID 24 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 8 | 301042 | 4 |  | CAN 1 missing ID 25 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 9 | 301042 | 4 |  | CAN 1 missing ID 26 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 10 | 301042 | 4 |  | CAN 1 missing ID 27 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 11 | 301042 | 4 |  | CAN 1 missing ID 28 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 12 | 301042 | 4 |  | CAN 1 missing ID 29 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 13 | 301042 | 4 |  | CAN 1 missing ID 30 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 14 | 301042 | 4 |  | CAN 1 missing ID 31 | BOOL |  |  |  | X | X | X
Alarm | 1041 | 15 | 301042 | 4 |  | CAN 1 missing ID 32 | BOOL |  |  |  | X | X | X
Alarm | 1042 | 0 | 301043 | 4 |  | CAN 1 missing ID 33 | BOOL |  |  |  | X | X | X
Alarm | 1042 | 1 | 301043 | 4 |  | CAN 1 missing ID 34 | BOOL |  |  |  | X | X | X
Alarm | 1042 | 2 | 301043 | 4 |  | CAN 1 missing ID 35 | BOOL |  |  |  | X | X | X
Alarm | 1042 | 3 | 301043 | 4 |  | CAN 1 missing ID 36 | BOOL |  |  |  | X | X | X
Alarm | 1042 | 4 | 301043 | 4 |  | CAN 1 missing ID 37 | BOOL |  |  |  | X | X | X
Alarm | 1042 | 5 | 301043 | 4 |  | CAN 1 missing ID 38 | BOOL |  |  |  | X | X | X
Alarm | 1042 | 6 | 301043 | 4 |  | CAN 1 missing ID 39 | BOOL |  |  |  | X | X | X
Alarm | 1042 | 7 | 301043 | 4 |  | CAN 1 missing ID 40 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 0 | 301044 | 4 |  | CAN 2 missing ID 1 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 1 | 301044 | 4 |  | CAN 2 missing ID 2 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 2 | 301044 | 4 |  | CAN 2 missing ID 3 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 3 | 301044 | 4 |  | CAN 2 missing ID 4 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 4 | 301044 | 4 |  | CAN 2 missing ID 5 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 5 | 301044 | 4 |  | CAN 2 missing ID 6 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 6 | 301044 | 4 |  | CAN 2 missing ID 7 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 7 | 301044 | 4 |  | CAN 2 missing ID 8 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 8 | 301044 | 4 |  | CAN 2 missing ID 9 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 9 | 301044 | 4 |  | CAN 2 missing ID 10 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 10 | 301044 | 4 |  | CAN 2 missing ID 11 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 11 | 301044 | 4 |  | CAN 2 missing ID 12 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 12 | 301044 | 4 |  | CAN 2 missing ID 13 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 13 | 301044 | 4 |  | CAN 2 missing ID 14 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 14 | 301044 | 4 |  | CAN 2 missing ID 15 | BOOL |  |  |  | X | X | X
Alarm | 1043 | 15 | 301044 | 4 |  | CAN 2 missing ID 16 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 0 | 301045 | 4 |  | CAN 2 missing ID 17 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 1 | 301045 | 4 |  | CAN 2 missing ID 18 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 2 | 301045 | 4 |  | CAN 2 missing ID 19 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 3 | 301045 | 4 |  | CAN 2 missing ID 20 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 4 | 301045 | 4 |  | CAN 2 missing ID 21 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 5 | 301045 | 4 |  | CAN 2 missing ID 22 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 6 | 301045 | 4 |  | CAN 2 missing ID 23 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 7 | 301045 | 4 |  | CAN 2 missing ID 24 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 8 | 301045 | 4 |  | CAN 2 missing ID 25 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 9 | 301045 | 4 |  | CAN 2 missing ID 26 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 10 | 301045 | 4 |  | CAN 2 missing ID 27 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 11 | 301045 | 4 |  | CAN 2 missing ID 28 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 12 | 301045 | 4 |  | CAN 2 missing ID 29 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 13 | 301045 | 4 |  | CAN 2 missing ID 30 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 14 | 301045 | 4 |  | CAN 2 missing ID 31 | BOOL |  |  |  | X | X | X
Alarm | 1044 | 15 | 301045 | 4 |  | CAN 2 missing ID 32 | BOOL |  |  |  | X | X | X
Alarm | 1045 | 0 | 301046 | 4 |  | CAN 2 missing ID 33 | BOOL |  |  |  | X | X | X
Alarm | 1045 | 1 | 301046 | 4 |  | CAN 2 missing ID 34 | BOOL |  |  |  | X | X | X
Alarm | 1045 | 2 | 301046 | 4 |  | CAN 2 missing ID 35 | BOOL |  |  |  | X | X | X
Alarm | 1045 | 3 | 301046 | 4 |  | CAN 2 missing ID 36 | BOOL |  |  |  | X | X | X
Alarm | 1045 | 4 | 301046 | 4 |  | CAN 2 missing ID 37 | BOOL |  |  |  | X | X | X
Alarm | 1045 | 5 | 301046 | 4 |  | CAN 2 missing ID 38 | BOOL |  |  |  | X | X | X
Alarm | 1045 | 6 | 301046 | 4 |  | CAN 2 missing ID 39 | BOOL |  |  |  | X | X | X
Alarm | 1045 | 7 | 301046 | 4 |  | CAN 2 missing ID 40 | BOOL |  |  |  | X | X | X
Alarm | 1050 | 0 | 301051 | 4 |  | Ready to autostart | BOOL | [5 empty] | X
Alarm | 1050 | 1 | 301051 | 4 |  | DG U&gt;30%*U nominal | BOOL | [5 empty] | X
Alarm | 1050 | 1 | 301051 | 4 |  | BA not below 30% Unom | BOOL |  |  |  | X
Alarm | 1050 | 1 | 301051 | 4 |  | Mains not below 30% Unom | BOOL |  |  |  |  | X
Alarm | 1050 | 2 | 301051 | 4 |  | BB U&gt;30%*U nominal | BOOL | [5 empty] | X
Alarm | 1050 | 2 | 301051 | 4 |  | BB not below 30% Unom | BOOL |  |  |  | X | X
Alarm | 1051 |  | 301052 | 4 |  | Virtual events 1-16 | INT16s | AB | 0 |  | X | X | X
Alarm | 1052 |  | 301053 | 4 |  | Virtual events 17-32 | INT16s | AB | 0 |  | X | X | X
Alarm | 1053 | 0 | 301054 | 4 | 6590 | Fan A Failure | BOOL | [5 empty] | X
Alarm | 1053 | 1 | 301054 | 4 | 6600 | Fan B Failure | BOOL | [5 empty] | X
Alarm | 1053 | 2 | 301054 | 4 | 6610 | Fan C Failure | BOOL | [5 empty] | X
Alarm | 1053 | 3 | 301054 | 4 | 6620 | Fan D Failure | BOOL | [5 empty] | X
Alarm | 1053 | 4 | 301054 | 4 | 4610 | Delta analogue 1 - fail 1 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 5 | 301054 | 4 | 4620 | Delta analogue 1 - fail 2 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 6 | 301054 | 4 | 4630 | Delta analogue 2 - fail 1 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 7 | 301054 | 4 | 4640 | Delta analogue 2 - fail 2 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 8 | 301054 | 4 | 4650 | Delta analogue 3 - fail 1 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 9 | 301054 | 4 | 4660 | Delta analogue 3 - fail 2 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 10 | 301054 | 4 | 4680 | Delta analogue 4 - fail 1 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 11 | 301054 | 4 | 4690 | Delta analogue 4 - fail 2 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 12 | 301054 | 4 | 4700 | Delta analogue 5 - fail 1 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 13 | 301054 | 4 | 4710 | Delta analogue 5 - fail 2 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 14 | 301054 | 4 | 4720 | Delta analogue 6 - fail 1 | BOOL |  |  |  | X | X | X
Alarm | 1053 | 15 | 301054 | 4 | 4730 | Delta analogue 6 - fail 2 | BOOL |  |  |  | X | X | X
Alarm | 1054 | 0 | 301055 | 4 |  | In> inverse | BOOL |  |  |  | X | X | X
Alarm | 1054 | 1 | 301055 | 4 |  | Ie> inverse | BOOL |  |  |  | X | X | X
Alarm | 1054 | 3 | 301055 | 4 | 6352 | External Engine Stop | BOOL | [5 empty] | X
Alarm | 1054 | 4 | 301055 | 4 | 1710 | Unbalance curr. 2 | BOOL |  |  |  | X | X | X
Alarm | 1054 | 5 | 301055 | 4 | 7480 | Avg U BB &gt; 1 | BOOL |  |  |  |  | X | X
Alarm | 1054 | 6 | 301055 | 4 | 7490 | Avg U BB &gt; 2 | BOOL |  |  |  |  | X | X
Alarm | 1054 | 7 | 301055 | 4 | 7440 | 4th CT -P> 1 | BOOL |  |  |  | X | X | X
Alarm | 1054 | 8 | 301055 | 4 | 7450 | 4th CT -P> 2 | BOOL |  |  |  | X | X | X
Alarm | 1054 | 9 | 301055 | 4 | 7460 | 4th CT P> 1 | BOOL |  |  |  | X | X | X
Alarm | 1054 | 10 | 301055 | 4 | 7470 | 4th CT P> 2 | BOOL |  |  |  | X | X | X
Alarm | 1055 | 0 | 301056 | 4 |  | LED 1 Red colour | BOOL |  |  |  | X | X | X
Alarm | 1055 | 1 | 301056 | 4 |  | LED 1 Yellow colour | BOOL |  |  |  | X | X | X
Alarm | 1055 | 2 | 301056 | 4 |  | LED 1 Green colour | BOOL |  |  |  | X | X | X
Alarm | 1055 | 3 | 301056 | 4 |  | LED 1 Flash | BOOL |  |  |  | X | X | X
Alarm | 1055 | 4 | 301056 | 4 |  | LED 2 Red colour | BOOL |  |  |  | X | X | X
Alarm | 1055 | 5 | 301056 | 4 |  | LED 2 Yellow colour | BOOL |  |  |  | X | X | X
Alarm | 1055 | 6 | 301056 | 4 |  | LED 2 Green colour | BOOL |  |  |  | X | X | X
Alarm | 1055 | 7 | 301056 | 4 |  | LED 2 Flash | BOOL |  |  |  | X | X | X
Alarm | 1055 | 8 | 301056 | 4 |  | LED 3 Red colour | BOOL |  |  |  | X | X | X
Alarm | 1055 | 9 | 301056 | 4 |  | LED 3 Yellow colour | BOOL |  |  |  | X | X | X
Alarm | 1055 | 10 | 301056 | 4 |  | LED 3 Green colour | BOOL |  |  |  | X | X | X
Alarm | 1055 | 11 | 301056 | 4 |  | LED 3 Flash | BOOL |  |  |  | X | X | X
Alarm | 1055 | 12 | 301056 | 4 |  | LED 4 Red colour | BOOL |  |  |  | X | X | X
Alarm | 1055 | 13 | 301056 | 4 |  | LED 4 Yellow colour | BOOL |  |  |  | X | X | X
Alarm | 1055 | 14 | 301056 | 4 |  | LED 4 Green colour | BOOL |  |  |  | X | X | X
Alarm | 1055 | 15 | 301056 | 4 |  | LED 4 Flash | BOOL |  |  |  | X | X | X
Alarm | 1056 | 0 | 301057 | 4 | 7830 | Digital AVR Communication Error | BOOL | [5 empty] | X
Alarm | 1056 | 1 | 301057 | 4 | 7761 | Digital AVR Warning | BOOL | [5 empty] | X
Alarm | 1056 | 2 | 301057 | 4 | 7763 | Digital AVR Trip | BOOL | [5 empty] | X
Alarm | 1057 | 0 | 301058 | 4 |  | Alarm active: Block start + breaker on | BOOL |  |  |  | X | X | X
Alarm | 1057 | 1 | 301058 | 4 |  | Alarm active: Warning | BOOL |  |  |  | X | X | X
Alarm | 1057 | 2 | 301058 | 4 |  | Alarm active: Open GB/TB/BTB | BOOL |  |  |  | X | X | X
Alarm | 1057 | 3 | 301058 | 4 |  | Alarm active: Open GB + stop with cooling down | BOOL |  |  |  | X | X | X
Alarm | 1057 | 4 | 301058 | 4 |  | Alarm active: Open GB + stop without cooling down | BOOL |  |  |  | X | X | X
Alarm | 1057 | 5 | 301058 | 4 |  | Alarm active: Open MB | BOOL |  |  |  | X | X | X
Alarm | 1057 | 6 | 301058 | 4 |  | Alarm active: Safety stop | BOOL |  |  |  | X | X | X
Alarm | 1057 | 7 | 301058 | 4 |  | Alarm active: If MB present Trip MB else Trip GB | BOOL |  |  |  | X | X | X
Alarm | 1057 | 8 | 301058 | 4 |  | Alarm active: Controlled stop (deload + cooldown) | BOOL |  |  |  | X | X | X
PM AC Measurement | 1500 |  | 301501 | 4 |  | Total power | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1501 |  | 301502 | 4 |  | Available power | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1502 |  | 301503 | 4 |  | Total nominal power | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1503 |  | 301504 | 4 |  | Total genset power | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1504 |  | 301505 | 4 |  | Total reactive power | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1505 |  | 301506 | 4 |  | Number of gensets in application | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1506 |  | 301507 | 4 |  | Plant type | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1507 |  | 301508 | 4 |  | Load-dependent stop, active setpoint | INT16s | AB | 0 |  |  |  | X
PM AC Measurement | 1508 |  | 301509 | 4 |  | Load-dependent start, active setpoint | INT16s | AB | 0 |  |  |  | X
PM AC Measurement | 1510 |  | 301511 | 4 |  | Nominal power ID 1 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1511 |  | 301512 | 4 |  | Nominal power ID 2 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1512 |  | 301513 | 4 |  | Nominal power ID 3 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1513 |  | 301514 | 4 |  | Nominal power ID 4 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1514 |  | 301515 | 4 |  | Nominal power ID 5 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1515 |  | 301516 | 4 |  | Nominal power ID 6 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1516 |  | 301517 | 4 |  | Nominal power ID 7 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1517 |  | 301518 | 4 |  | Nominal power ID 8 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1518 |  | 301519 | 4 |  | Nominal power ID 9 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1519 |  | 301520 | 4 |  | Nominal power ID 10 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1520 |  | 301521 | 4 |  | Nominal power ID 11 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1521 |  | 301522 | 4 |  | Nominal power ID 12 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1522 |  | 301523 | 4 |  | Nominal power ID 13 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1523 |  | 301524 | 4 |  | Nominal power ID 14 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1524 |  | 301525 | 4 |  | Nominal power ID 15 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1525 |  | 301526 | 4 |  | Nominal power ID 16 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1526 |  | 301527 | 4 |  | Active Power ID 1 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1527 |  | 301528 | 4 |  | Active Power ID 2 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1528 |  | 301529 | 4 |  | Active Power ID 3 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1529 |  | 301530 | 4 |  | Active Power ID 4 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1530 |  | 301531 | 4 |  | Active Power ID 5 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1531 |  | 301532 | 4 |  | Active Power ID 6 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1532 |  | 301533 | 4 |  | Active Power ID 7 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1533 |  | 301534 | 4 |  | Active Power ID 8 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1534 |  | 301535 | 4 |  | Active Power ID 9 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1535 |  | 301536 | 4 |  | Active Power ID 10 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1536 |  | 301537 | 4 |  | Active Power ID 11 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1537 |  | 301538 | 4 |  | Active Power ID 12 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1538 |  | 301539 | 4 |  | Active Power ID 13 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1539 |  | 301540 | 4 |  | Active Power ID 14 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1540 |  | 301541 | 4 |  | Active Power ID 15 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1541 |  | 301542 | 4 |  | Active Power ID 16 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1542 |  | 301543 | 4 |  | Reactive Power ID 1 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1543 |  | 301544 | 4 |  | Reactive Power ID 2 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1544 |  | 301545 | 4 |  | Reactive Power ID 3 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1545 |  | 301546 | 4 |  | Reactive Power ID 4 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1546 |  | 301547 | 4 |  | Reactive Power ID 5 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1547 |  | 301548 | 4 |  | Reactive Power ID 6 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1548 |  | 301549 | 4 |  | Reactive Power ID 7 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1549 |  | 301550 | 4 |  | Reactive Power ID 8 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1550 |  | 301551 | 4 |  | Reactive Power ID 9 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1551 |  | 301552 | 4 |  | Reactive Power ID 10 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1552 |  | 301553 | 4 |  | Reactive Power ID 11 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1553 |  | 301554 | 4 |  | Reactive Power ID 12 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1554 |  | 301555 | 4 |  | Reactive Power ID 13 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1555 |  | 301556 | 4 |  | Reactive Power ID 14 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1556 |  | 301557 | 4 |  | Reactive Power ID 15 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1557 |  | 301558 | 4 |  | Reactive Power ID 16 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1558 |  | 301559 | 4 |  | Priority of genset | INT16s | AB | 0 |  |  |  | X
PM AC Measurement | 1560 |  | 301561 | 4 |  | Power, mains 1A | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1561 |  | 301562 | 4 |  | Power, mains 1B | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1562 |  | 301563 | 4 |  | Power, mains 2A | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1563 |  | 301564 | 4 |  | Power, mains 2B | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1565 |  | 301566 | 4 |  | Reactive power mains 1A | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1566 |  | 301567 | 4 |  | Reactive power mains 1B | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1567 |  | 301568 | 4 |  | Reactive power mains 2A | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1568 |  | 301569 | 4 |  | Reactive power mains 2B | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1569 |  | 301570 | 4 |  | Active Power ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1570 |  | 301571 | 4 |  | Active Power ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1571 |  | 301572 | 4 |  | Active Power ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1572 |  | 301573 | 4 |  | Active Power ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1573 |  | 301574 | 4 |  | Active Power ID 21 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1574 |  | 301575 | 4 |  | Active Power ID 22 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1575 |  | 301576 | 4 |  | Active Power ID 23 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1576 |  | 301577 | 4 |  | Active Power ID 24 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1577 |  | 301578 | 4 |  | Active Power ID 25 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1578 |  | 301579 | 4 |  | Active Power ID 26 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1579 |  | 301580 | 4 |  | Active Power ID 27 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1580 |  | 301581 | 4 |  | Active Power ID 28 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1581 |  | 301582 | 4 |  | Active Power ID 29 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1582 |  | 301583 | 4 |  | Active Power ID 30 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1583 |  | 301584 | 4 |  | Active Power ID 31 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1584 |  | 301585 | 4 |  | Active Power ID 32 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1585 |  | 301586 | 4 |  | Reactive Power ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1586 |  | 301587 | 4 |  | Reactive Power ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1587 |  | 301588 | 4 |  | Reactive Power ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1588 |  | 301589 | 4 |  | Reactive Power ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1589 |  | 301590 | 4 |  | Reactive Power ID 21 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1590 |  | 301591 | 4 |  | Reactive Power ID 22 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1591 |  | 301592 | 4 |  | Reactive Power ID 23 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1592 |  | 301593 | 4 |  | Reactive Power ID 24 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1593 |  | 301594 | 4 |  | Reactive Power ID 25 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1594 |  | 301595 | 4 |  | Reactive Power ID 26 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1595 |  | 301596 | 4 |  | Reactive Power ID 27 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1596 |  | 301597 | 4 |  | Reactive Power ID 28 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1597 |  | 301598 | 4 |  | Reactive Power ID 29 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1598 |  | 301599 | 4 |  | Reactive Power ID 30 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1599 |  | 301600 | 4 |  | Reactive Power ID 31 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1600 |  | 301601 | 4 |  | Reactive Power ID 32 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1601 |  | 301602 | 4 |  | Active Power ID 33 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1602 |  | 301603 | 4 |  | Active Power ID 34 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1603 |  | 301604 | 4 |  | Active Power ID 35 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1604 |  | 301605 | 4 |  | Active Power ID 36 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1605 |  | 301606 | 4 |  | Active Power ID 37 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1606 |  | 301607 | 4 |  | Active Power ID 38 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1607 |  | 301608 | 4 |  | Active Power ID 39 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1608 |  | 301609 | 4 |  | Active Power ID 40 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1609 |  | 301610 | 4 |  | Reactive Power ID 33 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1610 |  | 301611 | 4 |  | Reactive Power ID 34 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1611 |  | 301612 | 4 |  | Reactive Power ID 35 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1612 |  | 301613 | 4 |  | Reactive Power ID 36 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1613 |  | 301614 | 4 |  | Reactive Power ID 37 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1614 |  | 301615 | 4 |  | Reactive Power ID 38 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1615 |  | 301616 | 4 |  | Reactive Power ID 39 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1616 |  | 301617 | 4 |  | Reactive Power ID 40 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1617 |  | 301618 | 4 |  | Plant mode mains 17 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1618 |  | 301619 | 4 |  | Plant mode mains 18 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1619 |  | 301620 | 4 |  | Plant mode mains 19 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1620 |  | 301621 | 4 |  | Plant mode mains 20 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1621 |  | 301622 | 4 |  | Plant mode mains 21 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1622 |  | 301623 | 4 |  | Plant mode mains 22 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1623 |  | 301624 | 4 |  | Plant mode mains 23 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1624 |  | 301625 | 4 |  | Plant mode mains 24 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1625 |  | 301626 | 4 |  | Plant mode mains 25 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1626 |  | 301627 | 4 |  | Plant mode mains 26 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1627 |  | 301628 | 4 |  | Plant mode mains 27 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1628 |  | 301629 | 4 |  | Plant mode mains 28 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1629 |  | 301630 | 4 |  | Plant mode mains 29 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1630 |  | 301631 | 4 |  | Plant mode mains 30 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1631 |  | 301632 | 4 |  | Plant mode mains 31 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1632 |  | 301633 | 4 |  | Plant mode mains 32 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1633 |  | 301634 | 4 |  | Bus power mains 17 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1634 |  | 301635 | 4 |  | Bus power mains 18 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1635 |  | 301636 | 4 |  | Bus power mains 19 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1636 |  | 301637 | 4 |  | Bus power mains 20 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1637 |  | 301638 | 4 |  | Bus power mains 21 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1638 |  | 301639 | 4 |  | Bus power mains 22 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1639 |  | 301640 | 4 |  | Bus power mains 23 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1640 |  | 301641 | 4 |  | Bus power mains 24 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1641 |  | 301642 | 4 |  | Bus power mains 25 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1642 |  | 301643 | 4 |  | Bus power mains 26 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1643 |  | 301644 | 4 |  | Bus power mains 27 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1644 |  | 301645 | 4 |  | Bus power mains 28 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1645 |  | 301646 | 4 |  | Bus power mains 29 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1646 |  | 301647 | 4 |  | Bus power mains 30 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1647 |  | 301648 | 4 |  | Bus power mains 31 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1648 |  | 301649 | 4 |  | Bus power mains 32 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1649 | 1 | 301650 | 4 |  | Mains transducer-configured, ID 17 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1649 | 2 | 301650 | 4 |  | Mains transducer-configured, ID 18 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1649 | 3 | 301650 | 4 |  | Mains transducer-configured, ID 19 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1649 | 4 | 301650 | 4 |  | Mains transducer-configured, ID 20 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1649 | 5 | 301650 | 4 |  | Mains transducer-configured, ID 21 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1649 | 6 | 301650 | 4 |  | Mains transducer-configured, ID 22 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1649 | 7 | 301650 | 4 |  | Mains transducer-configured, ID 23 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1649 | 8 | 301650 | 4 |  | Mains transducer-configured, ID 24 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1649 | 9 | 301650 | 4 |  | Mains transducer-configured, ID 25 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1649 | 10 | 301650 | 4 |  | Mains transducer-configured, ID 26 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1649 | 11 | 301650 | 4 |  | Mains transducer-configured, ID 27 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1649 | 12 | 301650 | 4 |  | Mains transducer-configured, ID 28 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1649 | 13 | 301650 | 4 |  | Mains transducer-configured, ID 29 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1649 | 14 | 301650 | 4 |  | Mains transducer-configured, ID 30 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1649 | 15 | 301650 | 4 |  | Mains transducer-configured, ID 31 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1649 | 0 | 301650 | 4 |  | Mains transducer-configured, ID 32 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 1 | 301651 | 4 |  | TB transducer-configured, ID 17 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 2 | 301651 | 4 |  | TB transducer-configured, ID 18 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 3 | 301651 | 4 |  | TB transducer-configured, ID 19 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 4 | 301651 | 4 |  | TB transducer-configured, ID 20 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 5 | 301651 | 4 |  | TB transducer-configured, ID 21 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 6 | 301651 | 4 |  | TB transducer-configured, ID 22 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 7 | 301651 | 4 |  | TB transducer-configured, ID 23 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 8 | 301651 | 4 |  | TB transducer-configured, ID 24 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 9 | 301651 | 4 |  | TB transducer-configured, ID 25 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 10 | 301651 | 4 |  | TB transducer-configured, ID 26 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 11 | 301651 | 4 |  | TB transducer-configured, ID 27 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 12 | 301651 | 4 |  | TB transducer-configured, ID 28 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 13 | 301651 | 4 |  | TB transducer-configured, ID 29 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 14 | 301651 | 4 |  | TB transducer-configured, ID 30 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 15 | 301651 | 4 |  | TB transducer-configured, ID 31 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1650 | 0 | 301651 | 4 |  | TB transducer-configured, ID 32 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1651 | 1 | 301652 | 4 |  | BTB transducer-configured, ID 33 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1651 | 2 | 301652 | 4 |  | BTB transducer-configured, ID 34 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1651 | 3 | 301652 | 4 |  | BTB transducer-configured, ID 35 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1651 | 4 | 301652 | 4 |  | BTB transducer-configured, ID 36 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1651 | 5 | 301652 | 4 |  | BTB transducer-configured, ID 37 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1651 | 6 | 301652 | 4 |  | BTB transducer-configured, ID 38 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1651 | 7 | 301652 | 4 |  | BTB transducer-configured, ID 39 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1651 | 8 | 301652 | 4 |  | BTB transducer-configured, ID 40 | BOOL |  |  |  | X | X | X
PM AC Measurement | 1652 | 1 | 301653 | 4 |  | ID 33 BTB controlled | BOOL |  |  |  | X | X | X
PM AC Measurement | 1652 | 2 | 301653 | 4 |  | ID 34 BTB controlled | BOOL |  |  |  | X | X | X
PM AC Measurement | 1652 | 3 | 301653 | 4 |  | ID 35 BTB controlled | BOOL |  |  |  | X | X | X
PM AC Measurement | 1652 | 4 | 301653 | 4 |  | ID 36 BTB controlled | BOOL |  |  |  | X | X | X
PM AC Measurement | 1652 | 5 | 301653 | 4 |  | ID 37 BTB controlled | BOOL |  |  |  | X | X | X
PM AC Measurement | 1652 | 6 | 301653 | 4 |  | ID 38 BTB controlled | BOOL |  |  |  | X | X | X
PM AC Measurement | 1652 | 7 | 301653 | 4 |  | ID 39 BTB controlled | BOOL |  |  |  | X | X | X
PM AC Measurement | 1652 | 8 | 301653 | 4 |  | ID 40 BTB controlled | BOOL |  |  |  | X | X | X
PM AC Measurement | 1653 |  | 301654 | 4 |  | Nominal power ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1654 |  | 301655 | 4 |  | Nominal power ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1655 |  | 301656 | 4 |  | Nominal power ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1656 |  | 301657 | 4 |  | Nominal power ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1657 |  | 301658 | 4 |  | Nominal power ID 21 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1658 |  | 301659 | 4 |  | Nominal power ID 22 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1659 |  | 301660 | 4 |  | Nominal power ID 23 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1660 |  | 301661 | 4 |  | Nominal power ID 24 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1661 |  | 301662 | 4 |  | Nominal power ID 25 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1662 |  | 301663 | 4 |  | Nominal power ID 26 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1663 |  | 301664 | 4 |  | Nominal power ID 27 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1664 |  | 301665 | 4 |  | Nominal power ID 28 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1665 |  | 301666 | 4 |  | Nominal power ID 29 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1666 |  | 301667 | 4 |  | Nominal power ID 30 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1667 |  | 301668 | 4 |  | Nominal power ID 31 | INT16s | AB | 0 |  | X | X | X
PM AC Measurement | 1668 |  | 301669 | 4 |  | Nominal power ID 32 | INT16s | AB | 0 |  | X | X | X
PM Alarm | 1700 | 0 | 301701 | 4 |  | TB available | BOOL |  |  |  | X | X | X
PM Alarm | 1700 | 1 | 301701 | 4 |  | Mains unit available | BOOL |  |  |  | X | X | X
PM Alarm | 1700 | 2 | 301701 | 4 |  | Any MB pos. ON | BOOL |  |  |  | X | X | X
PM Alarm | 1700 | 3 | 301701 | 4 |  | All MB pos. OFF | BOOL |  |  |  | X | X | X
PM Alarm | 1700 | 4 | 301701 | 4 |  | TB pos. ON (Mains Command Unit) | BOOL |  |  |  | X | X | X
PM Alarm | 1700 | 5 | 301701 | 4 |  | TB pos. OFF (Mains Command Unit) | BOOL |  |  |  | X | X | X
PM Alarm | 1700 | 6 | 301701 | 4 |  | Any GB pos. ON | BOOL |  |  |  | X | X | X
PM Alarm | 1700 | 7 | 301701 | 4 |  | All GB pos. OFF | BOOL |  |  |  | X | X | X
PM Alarm | 1700 | 8 | 301701 | 4 |  | Any TB pos. ON | BOOL |  |  |  | X | X | X
PM Alarm | 1700 | 9 | 301701 | 4 |  | All TB pos. OFF | BOOL |  |  |  | X | X | X
PM Alarm | 1700 | 10 | 301701 | 4 |  | Any BTB pos. ON | BOOL |  |  |  | X | X | X
PM Alarm | 1700 | 11 | 301701 | 4 |  | Any BTB pos. OFF | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 1 | 301702 | 4 |  | GB pos. ON ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 2 | 301702 | 4 |  | GB pos. ON ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 3 | 301702 | 4 |  | GB pos. ON ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 4 | 301702 | 4 |  | GB pos. ON ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 5 | 301702 | 4 |  | GB pos. ON ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 6 | 301702 | 4 |  | GB pos. ON ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 7 | 301702 | 4 |  | GB pos. ON ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 8 | 301702 | 4 |  | GB pos. ON ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 9 | 301702 | 4 |  | GB pos. ON ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 10 | 301702 | 4 |  | GB pos. ON ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 11 | 301702 | 4 |  | GB pos. ON ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 12 | 301702 | 4 |  | GB pos. ON ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 13 | 301702 | 4 |  | GB pos. ON ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 14 | 301702 | 4 |  | GB pos. ON ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 15 | 301702 | 4 |  | GB pos. ON ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1701 | 0 | 301702 | 4 |  | GB pos. ON ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 1 | 301703 | 4 |  | GB pos. OFF ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 2 | 301703 | 4 |  | GB pos. OFF ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 3 | 301703 | 4 |  | GB pos. OFF ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 4 | 301703 | 4 |  | GB pos. OFF ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 5 | 301703 | 4 |  | GB pos. OFF ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 6 | 301703 | 4 |  | GB pos. OFF ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 7 | 301703 | 4 |  | GB pos. OFF ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 8 | 301703 | 4 |  | GB pos. OFF ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 9 | 301703 | 4 |  | GB pos. OFF ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 10 | 301703 | 4 |  | GB pos. OFF ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 11 | 301703 | 4 |  | GB pos. OFF ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 12 | 301703 | 4 |  | GB pos. OFF ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 13 | 301703 | 4 |  | GB pos. OFF ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 14 | 301703 | 4 |  | GB pos. OFF ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 15 | 301703 | 4 |  | GB pos. OFF ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1702 | 0 | 301703 | 4 |  | GB pos. OFF ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 1 | 301704 | 4 |  | DG Hz/V OK, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 2 | 301704 | 4 |  | DG Hz/V OK, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 3 | 301704 | 4 |  | DG Hz/V OK, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 4 | 301704 | 4 |  | DG Hz/V OK, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 5 | 301704 | 4 |  | DG Hz/V OK, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 6 | 301704 | 4 |  | DG Hz/V OK, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 7 | 301704 | 4 |  | DG Hz/V OK, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 8 | 301704 | 4 |  | DG Hz/V OK, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 9 | 301704 | 4 |  | DG Hz/V OK, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 10 | 301704 | 4 |  | DG Hz/V OK, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 11 | 301704 | 4 |  | DG Hz/V OK, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 12 | 301704 | 4 |  | DG Hz/V OK, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 13 | 301704 | 4 |  | DG Hz/V OK, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 14 | 301704 | 4 |  | DG Hz/V OK, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 15 | 301704 | 4 |  | DG Hz/V OK, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1703 | 0 | 301704 | 4 |  | DG Hz/V OK, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1704 | 0 | 301705 | 4 |  | Mains OK, single mains | BOOL |  |  |  | X | X | X
PM Alarm | 1704 | 1 | 301705 | 4 |  | Mains OK, mains 1A | BOOL |  |  |  | X | X | X
PM Alarm | 1704 | 2 | 301705 | 4 |  | Mains OK, mains 1B | BOOL |  |  |  | X | X | X
PM Alarm | 1704 | 3 | 301705 | 4 |  | Mains OK, mains 2A | BOOL |  |  |  | X | X | X
PM Alarm | 1704 | 4 | 301705 | 4 |  | Mains OK, mains 2B | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 1 | 301706 | 4 |  | Ready for auto start, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 2 | 301706 | 4 |  | Ready for auto start, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 3 | 301706 | 4 |  | Ready for auto start, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 4 | 301706 | 4 |  | Ready for auto start, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 5 | 301706 | 4 |  | Ready for auto start, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 6 | 301706 | 4 |  | Ready for auto start, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 7 | 301706 | 4 |  | Ready for auto start, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 8 | 301706 | 4 |  | Ready for auto start, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 9 | 301706 | 4 |  | Ready for auto start, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 10 | 301706 | 4 |  | Ready for auto start, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 11 | 301706 | 4 |  | Ready for auto start, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 12 | 301706 | 4 |  | Ready for auto start, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 13 | 301706 | 4 |  | Ready for auto start, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 14 | 301706 | 4 |  | Ready for auto start, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 15 | 301706 | 4 |  | Ready for auto start, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1705 | 0 | 301706 | 4 |  | Ready for auto start, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1706 | 0 | 301707 | 4 |  | Mains not in semi, single mains | BOOL |  |  |  | X | X | X
PM Alarm | 1706 | 1 | 301707 | 4 |  | Mains not in semi, mains 1A | BOOL |  |  |  | X | X | X
PM Alarm | 1706 | 2 | 301707 | 4 |  | Mains not in semi, mains 1B | BOOL |  |  |  | X | X | X
PM Alarm | 1706 | 3 | 301707 | 4 |  | Mains not in semi, mains 2A | BOOL |  |  |  | X | X | X
PM Alarm | 1706 | 4 | 301707 | 4 |  | Mains not in semi, mains 2B | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 1 | 301708 | 4 |  | Any alarms, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 2 | 301708 | 4 |  | Any alarms, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 3 | 301708 | 4 |  | Any alarms, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 4 | 301708 | 4 |  | Any alarms, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 5 | 301708 | 4 |  | Any alarms, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 6 | 301708 | 4 |  | Any alarms, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 7 | 301708 | 4 |  | Any alarms, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 8 | 301708 | 4 |  | Any alarms, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 9 | 301708 | 4 |  | Any alarms, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 10 | 301708 | 4 |  | Any alarms, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 11 | 301708 | 4 |  | Any alarms, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 12 | 301708 | 4 |  | Any alarms, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 13 | 301708 | 4 |  | Any alarms, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 14 | 301708 | 4 |  | Any alarms, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 15 | 301708 | 4 |  | Any alarms, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1707 | 0 | 301708 | 4 |  | Any alarms, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1708 | 0 | 301709 | 4 |  | Any alarms, single mains | BOOL |  |  |  | X | X | X
PM Alarm | 1708 | 1 | 301709 | 4 |  | Any alarms, mains 1A | BOOL |  |  |  | X | X | X
PM Alarm | 1708 | 2 | 301709 | 4 |  | Any alarms, mains 1B | BOOL |  |  |  | X | X | X
PM Alarm | 1708 | 3 | 301709 | 4 |  | Any alarms, mains 2A | BOOL |  |  |  | X | X | X
PM Alarm | 1708 | 4 | 301709 | 4 |  | Any alarms, mains 2B | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 1 | 301710 | 4 |  | Engine running, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 2 | 301710 | 4 |  | Engine running, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 3 | 301710 | 4 |  | Engine running, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 4 | 301710 | 4 |  | Engine running, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 5 | 301710 | 4 |  | Engine running, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 6 | 301710 | 4 |  | Engine running, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 7 | 301710 | 4 |  | Engine running, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 8 | 301710 | 4 |  | Engine running, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 9 | 301710 | 4 |  | Engine running, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 10 | 301710 | 4 |  | Engine running, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 11 | 301710 | 4 |  | Engine running, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 12 | 301710 | 4 |  | Engine running, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 13 | 301710 | 4 |  | Engine running, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 14 | 301710 | 4 |  | Engine running, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 15 | 301710 | 4 |  | Engine running, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1709 | 0 | 301710 | 4 |  | Engine running, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1710 | 0 | 301711 | 4 |  | MB pos. ON, single mains | BOOL |  |  |  | X | X | X
PM Alarm | 1710 | 1 | 301711 | 4 |  | MB pos. ON, mains 1A | BOOL |  |  |  | X | X | X
PM Alarm | 1710 | 2 | 301711 | 4 |  | MB pos. ON, mains 1B | BOOL |  |  |  | X | X | X
PM Alarm | 1710 | 3 | 301711 | 4 |  | MB pos. ON, mains 2A | BOOL |  |  |  | X | X | X
PM Alarm | 1710 | 4 | 301711 | 4 |  | MB pos. ON, mains 2B | BOOL |  |  |  | X | X | X
PM Alarm | 1710 | 5 | 301711 | 4 |  | MB pos. OFF, single mains | BOOL |  |  |  | X | X | X
PM Alarm | 1710 | 6 | 301711 | 4 |  | MB pos. OFF, mains 1A | BOOL |  |  |  | X | X | X
PM Alarm | 1710 | 7 | 301711 | 4 |  | MB pos. OFF, mains 1B | BOOL |  |  |  | X | X | X
PM Alarm | 1710 | 8 | 301711 | 4 |  | MB pos. OFF, mains 2A | BOOL |  |  |  | X | X | X
PM Alarm | 1710 | 9 | 301711 | 4 |  | MB pos. OFF, mains 2B | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 1 | 301712 | 4 |  | GB synchronising, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 2 | 301712 | 4 |  | GB synchronising, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 3 | 301712 | 4 |  | GB synchronising, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 4 | 301712 | 4 |  | GB synchronising, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 5 | 301712 | 4 |  | GB synchronising, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 6 | 301712 | 4 |  | GB synchronising, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 7 | 301712 | 4 |  | GB synchronising, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 8 | 301712 | 4 |  | GB synchronising, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 9 | 301712 | 4 |  | GB synchronising, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 10 | 301712 | 4 |  | GB synchronising, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 11 | 301712 | 4 |  | GB synchronising, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 12 | 301712 | 4 |  | GB synchronising, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 13 | 301712 | 4 |  | GB synchronising, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 14 | 301712 | 4 |  | GB synchronising, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 15 | 301712 | 4 |  | GB synchronising, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1711 | 0 | 301712 | 4 |  | GB synchronising, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 1 | 301713 | 4 |  | Mains OK, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 2 | 301713 | 4 |  | Mains OK, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 3 | 301713 | 4 |  | Mains OK, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 4 | 301713 | 4 |  | Mains OK, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 5 | 301713 | 4 |  | Mains OK, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 6 | 301713 | 4 |  | Mains OK, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 7 | 301713 | 4 |  | Mains OK, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 8 | 301713 | 4 |  | Mains OK, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 9 | 301713 | 4 |  | Mains OK, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 10 | 301713 | 4 |  | Mains OK, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 11 | 301713 | 4 |  | Mains OK, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 12 | 301713 | 4 |  | Mains OK, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 13 | 301713 | 4 |  | Mains OK, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 14 | 301713 | 4 |  | Mains OK, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 15 | 301713 | 4 |  | Mains OK, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1712 | 0 | 301713 | 4 |  | Mains OK, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 1 | 301714 | 4 |  | Mains not in semi 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 2 | 301714 | 4 |  | Mains not in semi 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 3 | 301714 | 4 |  | Mains not in semi 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 4 | 301714 | 4 |  | Mains not in semi 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 5 | 301714 | 4 |  | Mains not in semi 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 6 | 301714 | 4 |  | Mains not in semi 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 7 | 301714 | 4 |  | Mains not in semi 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 8 | 301714 | 4 |  | Mains not in semi 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 9 | 301714 | 4 |  | Mains not in semi 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 10 | 301714 | 4 |  | Mains not in semi 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 11 | 301714 | 4 |  | Mains not in semi 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 12 | 301714 | 4 |  | Mains not in semi 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 13 | 301714 | 4 |  | Mains not in semi 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 14 | 301714 | 4 |  | Mains not in semi 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 15 | 301714 | 4 |  | Mains not in semi 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1713 | 0 | 301714 | 4 |  | Mains not in semi 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 1 | 301715 | 4 |  | Any alarms, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 2 | 301715 | 4 |  | Any alarms, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 3 | 301715 | 4 |  | Any alarms, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 4 | 301715 | 4 |  | Any alarms, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 5 | 301715 | 4 |  | Any alarms, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 6 | 301715 | 4 |  | Any alarms, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 7 | 301715 | 4 |  | Any alarms, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 8 | 301715 | 4 |  | Any alarms, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 9 | 301715 | 4 |  | Any alarms, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 10 | 301715 | 4 |  | Any alarms, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 11 | 301715 | 4 |  | Any alarms, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 12 | 301715 | 4 |  | Any alarms, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 13 | 301715 | 4 |  | Any alarms, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 14 | 301715 | 4 |  | Any alarms, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 15 | 301715 | 4 |  | Any alarms, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1714 | 0 | 301715 | 4 |  | Any alarms, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 1 | 301716 | 4 |  | MB pos. ON, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 2 | 301716 | 4 |  | MB pos. ON, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 3 | 301716 | 4 |  | MB pos. ON, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 4 | 301716 | 4 |  | MB pos. ON, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 5 | 301716 | 4 |  | MB pos. ON, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 6 | 301716 | 4 |  | MB pos. ON, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 7 | 301716 | 4 |  | MB pos. ON, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 8 | 301716 | 4 |  | MB pos. ON, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 9 | 301716 | 4 |  | MB pos. ON, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 10 | 301716 | 4 |  | MB pos. ON, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 11 | 301716 | 4 |  | MB pos. ON, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 12 | 301716 | 4 |  | MB pos. ON, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 13 | 301716 | 4 |  | MB pos. ON, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 14 | 301716 | 4 |  | MB pos. ON, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 15 | 301716 | 4 |  | MB pos. ON, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1715 | 0 | 301716 | 4 |  | MB pos. ON, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 1 | 301717 | 4 |  | MB pos. OFF, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 2 | 301717 | 4 |  | MB pos. OFF, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 3 | 301717 | 4 |  | MB pos. OFF, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 4 | 301717 | 4 |  | MB pos. OFF, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 5 | 301717 | 4 |  | MB pos. OFF, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 6 | 301717 | 4 |  | MB pos. OFF, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 7 | 301717 | 4 |  | MB pos. OFF, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 8 | 301717 | 4 |  | MB pos. OFF, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 9 | 301717 | 4 |  | MB pos. OFF, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 10 | 301717 | 4 |  | MB pos. OFF, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 11 | 301717 | 4 |  | MB pos. OFF, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 12 | 301717 | 4 |  | MB pos. OFF, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 13 | 301717 | 4 |  | MB pos. OFF, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 14 | 301717 | 4 |  | MB pos. OFF, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 15 | 301717 | 4 |  | MB pos. OFF, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1716 | 0 | 301717 | 4 |  | MB pos. OFF, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 1 | 301718 | 4 |  | Mains failure, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 2 | 301718 | 4 |  | Mains failure, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 3 | 301718 | 4 |  | Mains failure, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 4 | 301718 | 4 |  | Mains failure, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 5 | 301718 | 4 |  | Mains failure, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 6 | 301718 | 4 |  | Mains failure, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 7 | 301718 | 4 |  | Mains failure, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 8 | 301718 | 4 |  | Mains failure, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 9 | 301718 | 4 |  | Mains failure, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 10 | 301718 | 4 |  | Mains failure, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 11 | 301718 | 4 |  | Mains failure, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 12 | 301718 | 4 |  | Mains failure, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 13 | 301718 | 4 |  | Mains failure, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 14 | 301718 | 4 |  | Mains failure, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 15 | 301718 | 4 |  | Mains failure, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1717 | 0 | 301718 | 4 |  | Mains failure, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 1 | 301719 | 4 |  | MB synchronising, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 2 | 301719 | 4 |  | MB synchronising, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 3 | 301719 | 4 |  | MB synchronising, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 4 | 301719 | 4 |  | MB synchronising, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 5 | 301719 | 4 |  | MB synchronising, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 6 | 301719 | 4 |  | MB synchronising, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 7 | 301719 | 4 |  | MB synchronising, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 8 | 301719 | 4 |  | MB synchronising, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 9 | 301719 | 4 |  | MB synchronising, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 10 | 301719 | 4 |  | MB synchronising, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 11 | 301719 | 4 |  | MB synchronising, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 12 | 301719 | 4 |  | MB synchronising, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 13 | 301719 | 4 |  | MB synchronising, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 14 | 301719 | 4 |  | MB synchronising, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 15 | 301719 | 4 |  | MB synchronising, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1718 | 0 | 301719 | 4 |  | MB synchronising, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 1 | 301720 | 4 |  | TB pos. ON, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 2 | 301720 | 4 |  | TB pos. ON, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 3 | 301720 | 4 |  | TB pos. ON, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 4 | 301720 | 4 |  | TB pos. ON, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 5 | 301720 | 4 |  | TB pos. ON, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 6 | 301720 | 4 |  | TB pos. ON, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 7 | 301720 | 4 |  | TB pos. ON, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 8 | 301720 | 4 |  | TB pos. ON, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 9 | 301720 | 4 |  | TB pos. ON, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 10 | 301720 | 4 |  | TB pos. ON, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 11 | 301720 | 4 |  | TB pos. ON, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 12 | 301720 | 4 |  | TB pos. ON, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 13 | 301720 | 4 |  | TB pos. ON, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 14 | 301720 | 4 |  | TB pos. ON, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 15 | 301720 | 4 |  | TB pos. ON, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1719 | 0 | 301720 | 4 |  | TB pos. ON, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 1 | 301721 | 4 |  | TB pos. OFF, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 2 | 301721 | 4 |  | TB pos. OFF, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 3 | 301721 | 4 |  | TB pos. OFF, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 4 | 301721 | 4 |  | TB pos. OFF, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 5 | 301721 | 4 |  | TB pos. OFF, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 6 | 301721 | 4 |  | TB pos. OFF, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 7 | 301721 | 4 |  | TB pos. OFF, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 8 | 301721 | 4 |  | TB pos. OFF, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 9 | 301721 | 4 |  | TB pos. OFF, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 10 | 301721 | 4 |  | TB pos. OFF, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 11 | 301721 | 4 |  | TB pos. OFF, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 12 | 301721 | 4 |  | TB pos. OFF, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 13 | 301721 | 4 |  | TB pos. OFF, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 14 | 301721 | 4 |  | TB pos. OFF, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 15 | 301721 | 4 |  | TB pos. OFF, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1720 | 0 | 301721 | 4 |  | TB pos. OFF, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 1 | 301722 | 4 |  | TB synchronising, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 2 | 301722 | 4 |  | TB synchronising, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 3 | 301722 | 4 |  | TB synchronising, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 4 | 301722 | 4 |  | TB synchronising, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 5 | 301722 | 4 |  | TB synchronising, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 6 | 301722 | 4 |  | TB synchronising, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 7 | 301722 | 4 |  | TB synchronising, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 8 | 301722 | 4 |  | TB synchronising, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 9 | 301722 | 4 |  | TB synchronising, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 10 | 301722 | 4 |  | TB synchronising, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 11 | 301722 | 4 |  | TB synchronising, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 12 | 301722 | 4 |  | TB synchronising, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 13 | 301722 | 4 |  | TB synchronising, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 14 | 301722 | 4 |  | TB synchronising, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 15 | 301722 | 4 |  | TB synchronising, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1721 | 0 | 301722 | 4 |  | TB synchronising, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1722 | 1 | 301723 | 4 |  | Any alarms, ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1722 | 2 | 301723 | 4 |  | Any alarms, ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1722 | 3 | 301723 | 4 |  | Any alarms, ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1722 | 4 | 301723 | 4 |  | Any alarms, ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1722 | 5 | 301723 | 4 |  | Any alarms, ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1722 | 6 | 301723 | 4 |  | Any alarms, ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1722 | 7 | 301723 | 4 |  | Any alarms, ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1722 | 8 | 301723 | 4 |  | Any alarms, ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1725 | 1 | 301726 | 4 |  | BTB synchronising, ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1725 | 2 | 301726 | 4 |  | BTB synchronising, ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1725 | 3 | 301726 | 4 |  | BTB synchronising, ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1725 | 4 | 301726 | 4 |  | BTB synchronising, ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1725 | 5 | 301726 | 4 |  | BTB synchronising, ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1725 | 6 | 301726 | 4 |  | BTB synchronising, ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1725 | 7 | 301726 | 4 |  | BTB synchronising, ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1725 | 8 | 301726 | 4 |  | BTB synchronising, ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 1 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 2 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 3 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 4 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 5 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 6 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 7 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 8 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 9 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 10 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 11 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 12 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 13 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 14 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 15 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1727 | 0 | 301728 | 4 |  | Ext. Modbus comm. error, CAN ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1728 | 1 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1728 | 2 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1728 | 3 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1728 | 4 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1728 | 5 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1728 | 6 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1728 | 7 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1728 | 8 | 301729 | 4 |  | Ext. Modbus comm. error, CAN ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 1 | 301733 | 4 |  | BB Hz/V OK, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 2 | 301733 | 4 |  | BB Hz/V OK, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 3 | 301733 | 4 |  | BB Hz/V OK, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 4 | 301733 | 4 |  | BB Hz/V OK, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 5 | 301733 | 4 |  | BB Hz/V OK, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 6 | 301733 | 4 |  | BB Hz/V OK, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 7 | 301733 | 4 |  | BB Hz/V OK, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 8 | 301733 | 4 |  | BB Hz/V OK, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 9 | 301733 | 4 |  | BB Hz/V OK, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 10 | 301733 | 4 |  | BB Hz/V OK, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 11 | 301733 | 4 |  | BB Hz/V OK, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 12 | 301733 | 4 |  | BB Hz/V OK, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 13 | 301733 | 4 |  | BB Hz/V OK, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 14 | 301733 | 4 |  | BB Hz/V OK, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 15 | 301733 | 4 |  | BB Hz/V OK, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1732 | 0 | 301733 | 4 |  | BB Hz/V OK, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 1 | 301734 | 4 |  | BB Hz/V OK, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 2 | 301734 | 4 |  | BB Hz/V OK, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 3 | 301734 | 4 |  | BB Hz/V OK, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 4 | 301734 | 4 |  | BB Hz/V OK, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 5 | 301734 | 4 |  | BB Hz/V OK, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 6 | 301734 | 4 |  | BB Hz/V OK, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 7 | 301734 | 4 |  | BB Hz/V OK, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 8 | 301734 | 4 |  | BB Hz/V OK, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 9 | 301734 | 4 |  | BB Hz/V OK, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 10 | 301734 | 4 |  | BB Hz/V OK, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 11 | 301734 | 4 |  | BB Hz/V OK, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 12 | 301734 | 4 |  | BB Hz/V OK, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 13 | 301734 | 4 |  | BB Hz/V OK, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 14 | 301734 | 4 |  | BB Hz/V OK, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 15 | 301734 | 4 |  | BB Hz/V OK, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1733 | 0 | 301734 | 4 |  | BB Hz/V OK, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1734 | 1 | 301735 | 4 |  | BB Hz/V OK, ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1734 | 2 | 301735 | 4 |  | BB Hz/V OK, ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1734 | 3 | 301735 | 4 |  | BB Hz/V OK, ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1734 | 4 | 301735 | 4 |  | BB Hz/V OK, ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1734 | 5 | 301735 | 4 |  | BB Hz/V OK, ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1734 | 6 | 301735 | 4 |  | BB Hz/V OK, ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1734 | 7 | 301735 | 4 |  | BB Hz/V OK, ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1734 | 8 | 301735 | 4 |  | BB Hz/V OK, ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 1 | 301736 | 4 |  | BB Hz/V present, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 2 | 301736 | 4 |  | BB Hz/V present, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 3 | 301736 | 4 |  | BB Hz/V present, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 4 | 301736 | 4 |  | BB Hz/V present, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 5 | 301736 | 4 |  | BB Hz/V present, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 6 | 301736 | 4 |  | BB Hz/V present, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 7 | 301736 | 4 |  | BB Hz/V present, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 8 | 301736 | 4 |  | BB Hz/V present, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 9 | 301736 | 4 |  | BB Hz/V present, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 10 | 301736 | 4 |  | BB Hz/V present, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 11 | 301736 | 4 |  | BB Hz/V present, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 12 | 301736 | 4 |  | BB Hz/V present, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 13 | 301736 | 4 |  | BB Hz/V present, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 14 | 301736 | 4 |  | BB Hz/V present, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 15 | 301736 | 4 |  | BB Hz/V present, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1735 | 0 | 301736 | 4 |  | BB Hz/V present, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 1 | 301737 | 4 |  | BB Hz/V present, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 2 | 301737 | 4 |  | BB Hz/V present, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 3 | 301737 | 4 |  | BB Hz/V present, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 4 | 301737 | 4 |  | BB Hz/V present, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 5 | 301737 | 4 |  | BB Hz/V present, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 6 | 301737 | 4 |  | BB Hz/V present, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 7 | 301737 | 4 |  | BB Hz/V present, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 8 | 301737 | 4 |  | BB Hz/V present, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 9 | 301737 | 4 |  | BB Hz/V present, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 10 | 301737 | 4 |  | BB Hz/V present, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 11 | 301737 | 4 |  | BB Hz/V present, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 12 | 301737 | 4 |  | BB Hz/V present, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 13 | 301737 | 4 |  | BB Hz/V present, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 14 | 301737 | 4 |  | BB Hz/V present, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 15 | 301737 | 4 |  | BB Hz/V present, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1736 | 0 | 301737 | 4 |  | BB Hz/V present, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1737 | 1 | 301738 | 4 |  | BB Hz/V present, ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1737 | 2 | 301738 | 4 |  | BB Hz/V present, ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1737 | 3 | 301738 | 4 |  | BB Hz/V present, ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1737 | 4 | 301738 | 4 |  | BB Hz/V present, ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1737 | 5 | 301738 | 4 |  | BB Hz/V present, ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1737 | 6 | 301738 | 4 |  | BB Hz/V present, ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1737 | 7 | 301738 | 4 |  | BB Hz/V present, ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1737 | 8 | 301738 | 4 |  | BB Hz/V present, ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1738 | 1 | 301739 | 4 |  | BA Hz/V OK, ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1738 | 2 | 301739 | 4 |  | BA Hz/V OK, ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1738 | 3 | 301739 | 4 |  | BA Hz/V OK, ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1738 | 4 | 301739 | 4 |  | BA Hz/V OK, ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1738 | 5 | 301739 | 4 |  | BA Hz/V OK, ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1738 | 6 | 301739 | 4 |  | BA Hz/V OK, ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1738 | 7 | 301739 | 4 |  | BA Hz/V OK, ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1738 | 8 | 301739 | 4 |  | BA Hz/V OK, ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 1 | 301740 | 4 |  | DG Hz/V present, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 2 | 301740 | 4 |  | DG Hz/V present, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 3 | 301740 | 4 |  | DG Hz/V present, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 4 | 301740 | 4 |  | DG Hz/V present, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 5 | 301740 | 4 |  | DG Hz/V present, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 6 | 301740 | 4 |  | DG Hz/V present, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 7 | 301740 | 4 |  | DG Hz/V present, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 8 | 301740 | 4 |  | DG Hz/V present, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 9 | 301740 | 4 |  | DG Hz/V present, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 10 | 301740 | 4 |  | DG Hz/V present, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 11 | 301740 | 4 |  | DG Hz/V present, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 12 | 301740 | 4 |  | DG Hz/V present, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 13 | 301740 | 4 |  | DG Hz/V present, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 14 | 301740 | 4 |  | DG Hz/V present, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 15 | 301740 | 4 |  | DG Hz/V present, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1739 | 0 | 301740 | 4 |  | DG Hz/V present, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 1 | 301741 | 4 |  | Hz/V present, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 2 | 301741 | 4 |  | Hz/V present, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 3 | 301741 | 4 |  | Hz/V present, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 4 | 301741 | 4 |  | Hz/V present, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 5 | 301741 | 4 |  | Hz/V present, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 6 | 301741 | 4 |  | Hz/V present, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 7 | 301741 | 4 |  | Hz/V present, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 8 | 301741 | 4 |  | Hz/V present, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 9 | 301741 | 4 |  | Hz/V present, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 10 | 301741 | 4 |  | Hz/V present, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 11 | 301741 | 4 |  | Hz/V present, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 12 | 301741 | 4 |  | Hz/V present, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 13 | 301741 | 4 |  | Hz/V present, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 14 | 301741 | 4 |  | Hz/V present, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 15 | 301741 | 4 |  | Hz/V present, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1740 | 0 | 301741 | 4 |  | Hz/V present, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1741 | 1 | 301742 | 4 |  | BA Hz/V present, ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1741 | 2 | 301742 | 4 |  | BA Hz/V present, ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1741 | 3 | 301742 | 4 |  | BA Hz/V present, ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1741 | 4 | 301742 | 4 |  | BA Hz/V present, ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1741 | 5 | 301742 | 4 |  | BA Hz/V present, ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1741 | 6 | 301742 | 4 |  | BA Hz/V present, ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1741 | 7 | 301742 | 4 |  | BA Hz/V present, ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1741 | 8 | 301742 | 4 |  | BA Hz/V present, ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 1 | 301744 | 4 |  | Redundant backup present ID1 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 2 | 301744 | 4 |  | Redundant backup present ID2 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 3 | 301744 | 4 |  | Redundant backup present ID3 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 4 | 301744 | 4 |  | Redundant backup present ID4 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 5 | 301744 | 4 |  | Redundant backup present ID5 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 6 | 301744 | 4 |  | Redundant backup present ID6 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 7 | 301744 | 4 |  | Redundant backup present ID7 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 8 | 301744 | 4 |  | Redundant backup present ID8 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 9 | 301744 | 4 |  | Redundant backup present ID9 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 10 | 301744 | 4 |  | Redundant backup present ID10 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 11 | 301744 | 4 |  | Redundant backup present ID11 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 12 | 301744 | 4 |  | Redundant backup present ID12 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 13 | 301744 | 4 |  | Redundant backup present ID13 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 14 | 301744 | 4 |  | Redundant backup present ID14 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 15 | 301744 | 4 |  | Redundant backup present ID15 | BOOL |  |  |  | X | X | X
PM Alarm | 1743 | 0 | 301744 | 4 |  | Redundant backup present ID16 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 1 | 301745 | 4 |  | Redundant backup present ID17 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 2 | 301745 | 4 |  | Redundant backup present ID18 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 3 | 301745 | 4 |  | Redundant backup present ID19 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 4 | 301745 | 4 |  | Redundant backup present ID20 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 5 | 301745 | 4 |  | Redundant backup present ID21 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 6 | 301745 | 4 |  | Redundant backup present ID22 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 7 | 301745 | 4 |  | Redundant backup present ID23 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 8 | 301745 | 4 |  | Redundant backup present ID24 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 9 | 301745 | 4 |  | Redundant backup present ID25 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 10 | 301745 | 4 |  | Redundant backup present ID26 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 11 | 301745 | 4 |  | Redundant backup present ID27 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 12 | 301745 | 4 |  | Redundant backup present ID28 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 13 | 301745 | 4 |  | Redundant backup present ID29 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 14 | 301745 | 4 |  | Redundant backup present ID30 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 15 | 301745 | 4 |  | Redundant backup present ID31 | BOOL |  |  |  | X | X | X
PM Alarm | 1744 | 0 | 301745 | 4 |  | Redundant backup present ID32 | BOOL |  |  |  | X | X | X
PM Alarm | 1745 | 1 | 301746 | 4 |  | Redundant backup present ID33 | BOOL |  |  |  | X | X | X
PM Alarm | 1745 | 2 | 301746 | 4 |  | Redundant backup present ID34 | BOOL |  |  |  | X | X | X
PM Alarm | 1745 | 3 | 301746 | 4 |  | Redundant backup present ID35 | BOOL |  |  |  | X | X | X
PM Alarm | 1745 | 4 | 301746 | 4 |  | Redundant backup present ID36 | BOOL |  |  |  | X | X | X
PM Alarm | 1745 | 5 | 301746 | 4 |  | Redundant backup present ID37 | BOOL |  |  |  | X | X | X
PM Alarm | 1745 | 6 | 301746 | 4 |  | Redundant backup present ID38 | BOOL |  |  |  | X | X | X
PM Alarm | 1745 | 7 | 301746 | 4 |  | Redundant backup present ID39 | BOOL |  |  |  | X | X | X
PM Alarm | 1745 | 8 | 301746 | 4 |  | Redundant backup present ID40 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 1 | 301747 | 4 |  | Controller B active on ID1 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 2 | 301747 | 4 |  | Controller B active on ID2 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 3 | 301747 | 4 |  | Controller B active on ID3 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 4 | 301747 | 4 |  | Controller B active on ID4 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 5 | 301747 | 4 |  | Controller B active on ID5 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 6 | 301747 | 4 |  | Controller B active on ID6 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 7 | 301747 | 4 |  | Controller B active on ID7 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 8 | 301747 | 4 |  | Controller B active on ID8 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 9 | 301747 | 4 |  | Controller B active on ID9 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 10 | 301747 | 4 |  | Controller B active on ID10 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 11 | 301747 | 4 |  | Controller B active on ID11 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 12 | 301747 | 4 |  | Controller B active on ID12 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 13 | 301747 | 4 |  | Controller B active on ID13 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 14 | 301747 | 4 |  | Controller B active on ID14 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 15 | 301747 | 4 |  | Controller B active on ID15 | BOOL |  |  |  | X | X | X
PM Alarm | 1746 | 0 | 301747 | 4 |  | Controller B active on ID16 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 1 | 301748 | 4 |  | Controller B active on ID17 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 2 | 301748 | 4 |  | Controller B active on ID18 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 3 | 301748 | 4 |  | Controller B active on ID19 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 4 | 301748 | 4 |  | Controller B active on ID20 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 5 | 301748 | 4 |  | Controller B active on ID21 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 6 | 301748 | 4 |  | Controller B active on ID22 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 7 | 301748 | 4 |  | Controller B active on ID23 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 8 | 301748 | 4 |  | Controller B active on ID24 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 9 | 301748 | 4 |  | Controller B active on ID25 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 10 | 301748 | 4 |  | Controller B active on ID26 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 11 | 301748 | 4 |  | Controller B active on ID27 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 12 | 301748 | 4 |  | Controller B active on ID28 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 13 | 301748 | 4 |  | Controller B active on ID29 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 14 | 301748 | 4 |  | Controller B active on ID30 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 15 | 301748 | 4 |  | Controller B active on ID31 | BOOL |  |  |  | X | X | X
PM Alarm | 1747 | 0 | 301748 | 4 |  | Controller B active on ID32 | BOOL |  |  |  | X | X | X
PM Alarm | 1748 | 1 | 301749 | 4 |  | Controller B active on ID33 | BOOL |  |  |  | X | X | X
PM Alarm | 1748 | 2 | 301749 | 4 |  | Controller B active on ID34 | BOOL |  |  |  | X | X | X
PM Alarm | 1748 | 3 | 301749 | 4 |  | Controller B active on ID35 | BOOL |  |  |  | X | X | X
PM Alarm | 1748 | 4 | 301749 | 4 |  | Controller B active on ID36 | BOOL |  |  |  | X | X | X
PM Alarm | 1748 | 5 | 301749 | 4 |  | Controller B active on ID37 | BOOL |  |  |  | X | X | X
PM Alarm | 1748 | 6 | 301749 | 4 |  | Controller B active on ID38 | BOOL |  |  |  | X | X | X
PM Alarm | 1748 | 7 | 301749 | 4 |  | Controller B active on ID39 | BOOL |  |  |  | X | X | X
PM Alarm | 1748 | 8 | 301749 | 4 |  | Controller B active on ID40 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 1 | 301750 | 4 |  | Dry Mode active on ID1 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 2 | 301750 | 4 |  | Dry Mode active on ID2 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 3 | 301750 | 4 |  | Dry Mode active on ID3 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 4 | 301750 | 4 |  | Dry Mode active on ID4 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 5 | 301750 | 4 |  | Dry Mode active on ID5 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 6 | 301750 | 4 |  | Dry Mode active on ID6 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 7 | 301750 | 4 |  | Dry Mode active on ID7 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 8 | 301750 | 4 |  | Dry Mode active on ID8 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 9 | 301750 | 4 |  | Dry Mode active on ID9 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 10 | 301750 | 4 |  | Dry Mode active on ID10 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 11 | 301750 | 4 |  | Dry Mode active on ID11 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 12 | 301750 | 4 |  | Dry Mode active on ID12 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 13 | 301750 | 4 |  | Dry Mode active on ID13 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 14 | 301750 | 4 |  | Dry Mode active on ID14 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 15 | 301750 | 4 |  | Dry Mode active on ID15 | BOOL |  |  |  | X | X | X
PM Alarm | 1749 | 0 | 301750 | 4 |  | Dry Mode active on ID16 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 1 | 301751 | 4 |  | GB Pos ON, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 2 | 301751 | 4 |  | GB Pos ON, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 3 | 301751 | 4 |  | GB Pos ON, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 4 | 301751 | 4 |  | GB Pos ON, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 5 | 301751 | 4 |  | GB Pos ON, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 6 | 301751 | 4 |  | GB Pos ON, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 7 | 301751 | 4 |  | GB Pos ON, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 8 | 301751 | 4 |  | GB Pos ON, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 9 | 301751 | 4 |  | GB Pos ON, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 10 | 301751 | 4 |  | GB Pos ON, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 11 | 301751 | 4 |  | GB Pos ON, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 12 | 301751 | 4 |  | GB Pos ON, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 13 | 301751 | 4 |  | GB Pos ON, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 14 | 301751 | 4 |  | GB Pos ON, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 15 | 301751 | 4 |  | GB Pos ON, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1750 | 0 | 301751 | 4 |  | GB Pos ON, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 1 | 301752 | 4 |  | GB Pos OFF, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 2 | 301752 | 4 |  | GB Pos OFF, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 3 | 301752 | 4 |  | GB Pos OFF, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 4 | 301752 | 4 |  | GB Pos OFF, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 5 | 301752 | 4 |  | GB Pos OFF, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 6 | 301752 | 4 |  | GB Pos OFF, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 7 | 301752 | 4 |  | GB Pos OFF, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 8 | 301752 | 4 |  | GB Pos OFF, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 9 | 301752 | 4 |  | GB Pos OFF, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 10 | 301752 | 4 |  | GB Pos OFF, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 11 | 301752 | 4 |  | GB Pos OFF, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 12 | 301752 | 4 |  | GB Pos OFF, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 13 | 301752 | 4 |  | GB Pos OFF, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 14 | 301752 | 4 |  | GB Pos OFF, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 15 | 301752 | 4 |  | GB Pos OFF, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1751 | 0 | 301752 | 4 |  | GB Pos OFF, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 1 | 301753 | 4 |  | GB synchronising, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 2 | 301753 | 4 |  | GB synchronising, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 3 | 301753 | 4 |  | GB synchronising, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 4 | 301753 | 4 |  | GB synchronising, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 5 | 301753 | 4 |  | GB synchronising, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 6 | 301753 | 4 |  | GB synchronising, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 7 | 301753 | 4 |  | GB synchronising, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 8 | 301753 | 4 |  | GB synchronising, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 9 | 301753 | 4 |  | GB synchronising, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 10 | 301753 | 4 |  | GB synchronising, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 11 | 301753 | 4 |  | GB synchronising, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 12 | 301753 | 4 |  | GB synchronising, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 13 | 301753 | 4 |  | GB synchronising, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 14 | 301753 | 4 |  | GB synchronising, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 15 | 301753 | 4 |  | GB synchronising, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1752 | 0 | 301753 | 4 |  | GB synchronising, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 1 | 301754 | 4 |  | Hz/V OK, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 2 | 301754 | 4 |  | Hz/V OK, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 3 | 301754 | 4 |  | Hz/V OK, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 4 | 301754 | 4 |  | Hz/V OK, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 5 | 301754 | 4 |  | Hz/V OK, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 6 | 301754 | 4 |  | Hz/V OK, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 7 | 301754 | 4 |  | Hz/V OK, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 8 | 301754 | 4 |  | Hz/V OK, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 9 | 301754 | 4 |  | Hz/V OK, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 10 | 301754 | 4 |  | Hz/V OK, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 11 | 301754 | 4 |  | Hz/V OK, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 12 | 301754 | 4 |  | Hz/V OK, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 13 | 301754 | 4 |  | Hz/V OK, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 14 | 301754 | 4 |  | Hz/V OK, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 15 | 301754 | 4 |  | Hz/V OK, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1753 | 0 | 301754 | 4 |  | Hz/V OK, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 1 | 301755 | 4 |  | Ready for auto start, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 2 | 301755 | 4 |  | Ready for auto start, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 3 | 301755 | 4 |  | Ready for auto start, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 4 | 301755 | 4 |  | Ready for auto start, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 5 | 301755 | 4 |  | Ready for auto start, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 6 | 301755 | 4 |  | Ready for auto start, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 7 | 301755 | 4 |  | Ready for auto start, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 8 | 301755 | 4 |  | Ready for auto start, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 9 | 301755 | 4 |  | Ready for auto start, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 10 | 301755 | 4 |  | Ready for auto start, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 11 | 301755 | 4 |  | Ready for auto start, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 12 | 301755 | 4 |  | Ready for auto start, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 13 | 301755 | 4 |  | Ready for auto start, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 14 | 301755 | 4 |  | Ready for auto start, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 15 | 301755 | 4 |  | Ready for auto start, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1754 | 0 | 301755 | 4 |  | Ready for auto start, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 1 | 301756 | 4 |  | Running, ID 17 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 2 | 301756 | 4 |  | Running, ID 18 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 3 | 301756 | 4 |  | Running, ID 19 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 4 | 301756 | 4 |  | Running, ID 20 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 5 | 301756 | 4 |  | Running, ID 21 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 6 | 301756 | 4 |  | Running, ID 22 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 7 | 301756 | 4 |  | Running, ID 23 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 8 | 301756 | 4 |  | Running, ID 24 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 9 | 301756 | 4 |  | Running, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 10 | 301756 | 4 |  | Running, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 11 | 301756 | 4 |  | Running, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 12 | 301756 | 4 |  | Running, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 13 | 301756 | 4 |  | Running, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 14 | 301756 | 4 |  | Running, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 15 | 301756 | 4 |  | Running, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1755 | 0 | 301756 | 4 |  | Running, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 1 | 301757 | 4 |  | Dry Mode active on ID17 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 2 | 301757 | 4 |  | Dry Mode active on ID18 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 3 | 301757 | 4 |  | Dry Mode active on ID19 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 4 | 301757 | 4 |  | Dry Mode active on ID20 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 5 | 301757 | 4 |  | Dry Mode active on ID21 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 6 | 301757 | 4 |  | Dry Mode active on ID22 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 7 | 301757 | 4 |  | Dry Mode active on ID23 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 8 | 301757 | 4 |  | Dry Mode active on ID24 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 9 | 301757 | 4 |  | Dry Mode active on ID25 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 10 | 301757 | 4 |  | Dry Mode active on ID26 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 11 | 301757 | 4 |  | Dry Mode active on ID27 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 12 | 301757 | 4 |  | Dry Mode active on ID28 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 13 | 301757 | 4 |  | Dry Mode active on ID29 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 14 | 301757 | 4 |  | Dry Mode active on ID30 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 15 | 301757 | 4 |  | Dry Mode active on ID31 | BOOL |  |  |  | X | X | X
PM Alarm | 1756 | 0 | 301757 | 4 |  | Dry Mode active on ID32 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 1 | 301758 | 4 |  | MB pos. ON, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 2 | 301758 | 4 |  | MB pos. ON, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 3 | 301758 | 4 |  | MB pos. ON, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 4 | 301758 | 4 |  | MB pos. ON, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 5 | 301758 | 4 |  | MB pos. ON, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 6 | 301758 | 4 |  | MB pos. ON, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 7 | 301758 | 4 |  | MB pos. ON, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 8 | 301758 | 4 |  | MB pos. ON, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 9 | 301758 | 4 |  | MB pos. ON, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 10 | 301758 | 4 |  | MB pos. ON, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 11 | 301758 | 4 |  | MB pos. ON, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 12 | 301758 | 4 |  | MB pos. ON, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 13 | 301758 | 4 |  | MB pos. ON, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 14 | 301758 | 4 |  | MB pos. ON, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 15 | 301758 | 4 |  | MB pos. ON, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1757 | 0 | 301758 | 4 |  | MB pos. ON, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 1 | 301759 | 4 |  | MB pos. OFF, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 2 | 301759 | 4 |  | MB pos. OFF, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 3 | 301759 | 4 |  | MB pos. OFF, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 4 | 301759 | 4 |  | MB pos. OFF, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 5 | 301759 | 4 |  | MB pos. OFF, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 6 | 301759 | 4 |  | MB pos. OFF, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 7 | 301759 | 4 |  | MB pos. OFF, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 8 | 301759 | 4 |  | MB pos. OFF, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 9 | 301759 | 4 |  | MB pos. OFF, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 10 | 301759 | 4 |  | MB pos. OFF, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 11 | 301759 | 4 |  | MB pos. OFF, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 12 | 301759 | 4 |  | MB pos. OFF, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 13 | 301759 | 4 |  | MB pos. OFF, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 14 | 301759 | 4 |  | MB pos. OFF, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 15 | 301759 | 4 |  | MB pos. OFF, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1758 | 0 | 301759 | 4 |  | MB pos. OFF, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 1 | 301760 | 4 |  | MB synchronising, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 2 | 301760 | 4 |  | MB synchronising, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 3 | 301760 | 4 |  | MB synchronising, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 4 | 301760 | 4 |  | MB synchronising, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 5 | 301760 | 4 |  | MB synchronising, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 6 | 301760 | 4 |  | MB synchronising, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 7 | 301760 | 4 |  | MB synchronising, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 8 | 301760 | 4 |  | MB synchronising, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 9 | 301760 | 4 |  | MB synchronising, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 10 | 301760 | 4 |  | MB synchronising, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 11 | 301760 | 4 |  | MB synchronising, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 12 | 301760 | 4 |  | MB synchronising, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 13 | 301760 | 4 |  | MB synchronising, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 14 | 301760 | 4 |  | MB synchronising, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 15 | 301760 | 4 |  | MB synchronising, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1759 | 0 | 301760 | 4 |  | MB synchronising, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 1 | 301761 | 4 |  | TB pos. ON, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 2 | 301761 | 4 |  | TB pos. ON, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 3 | 301761 | 4 |  | TB pos. ON, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 4 | 301761 | 4 |  | TB pos. ON, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 5 | 301761 | 4 |  | TB pos. ON, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 6 | 301761 | 4 |  | TB pos. ON, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 7 | 301761 | 4 |  | TB pos. ON, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 8 | 301761 | 4 |  | TB pos. ON, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 9 | 301761 | 4 |  | TB pos. ON, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 10 | 301761 | 4 |  | TB pos. ON, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 11 | 301761 | 4 |  | TB pos. ON, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 12 | 301761 | 4 |  | TB pos. ON, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 13 | 301761 | 4 |  | TB pos. ON, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 14 | 301761 | 4 |  | TB pos. ON, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 15 | 301761 | 4 |  | TB pos. ON, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1760 | 0 | 301761 | 4 |  | TB pos. ON, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 1 | 301762 | 4 |  | TB pos. OFF, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 2 | 301762 | 4 |  | TB pos. OFF, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 3 | 301762 | 4 |  | TB pos. OFF, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 4 | 301762 | 4 |  | TB pos. OFF, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 5 | 301762 | 4 |  | TB pos. OFF, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 6 | 301762 | 4 |  | TB pos. OFF, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 7 | 301762 | 4 |  | TB pos. OFF, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 8 | 301762 | 4 |  | TB pos. OFF, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 9 | 301762 | 4 |  | TB pos. OFF, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 10 | 301762 | 4 |  | TB pos. OFF, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 11 | 301762 | 4 |  | TB pos. OFF, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 12 | 301762 | 4 |  | TB pos. OFF, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 13 | 301762 | 4 |  | TB pos. OFF, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 14 | 301762 | 4 |  | TB pos. OFF, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 15 | 301762 | 4 |  | TB pos. OFF, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1761 | 0 | 301762 | 4 |  | TB pos. OFF, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 1 | 301763 | 4 |  | TB synchronising, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 2 | 301763 | 4 |  | TB synchronising, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 3 | 301763 | 4 |  | TB synchronising, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 4 | 301763 | 4 |  | TB synchronising, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 5 | 301763 | 4 |  | TB synchronising, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 6 | 301763 | 4 |  | TB synchronising, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 7 | 301763 | 4 |  | TB synchronising, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 8 | 301763 | 4 |  | TB synchronising, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 9 | 301763 | 4 |  | TB synchronising, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 10 | 301763 | 4 |  | TB synchronising, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 11 | 301763 | 4 |  | TB synchronising, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 12 | 301763 | 4 |  | TB synchronising, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 13 | 301763 | 4 |  | TB synchronising, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 14 | 301763 | 4 |  | TB synchronising, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 15 | 301763 | 4 |  | TB synchronising, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1762 | 0 | 301763 | 4 |  | TB synchronising, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 1 | 301764 | 4 |  | Mains transducer-configured, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 2 | 301764 | 4 |  | Mains transducer-configured, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 3 | 301764 | 4 |  | Mains transducer-configured, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 4 | 301764 | 4 |  | Mains transducer-configured, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 5 | 301764 | 4 |  | Mains transducer-configured, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 6 | 301764 | 4 |  | Mains transducer-configured, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 7 | 301764 | 4 |  | Mains transducer-configured, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 8 | 301764 | 4 |  | Mains transducer-configured, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 9 | 301764 | 4 |  | Mains transducer-configured, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 10 | 301764 | 4 |  | Mains transducer-configured, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 11 | 301764 | 4 |  | Mains transducer-configured, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 12 | 301764 | 4 |  | Mains transducer-configured, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 13 | 301764 | 4 |  | Mains transducer-configured, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 14 | 301764 | 4 |  | Mains transducer-configured, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 15 | 301764 | 4 |  | Mains transducer-configured, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1763 | 0 | 301764 | 4 |  | Mains transducer-configured, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 1 | 301765 | 4 |  | TB transducer-configured, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 2 | 301765 | 4 |  | TB transducer-configured, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 3 | 301765 | 4 |  | TB transducer-configured, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 4 | 301765 | 4 |  | TB transducer-configured, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 5 | 301765 | 4 |  | TB transducer-configured, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 6 | 301765 | 4 |  | TB transducer-configured, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 7 | 301765 | 4 |  | TB transducer-configured, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 8 | 301765 | 4 |  | TB transducer-configured, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 9 | 301765 | 4 |  | TB transducer-configured, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 10 | 301765 | 4 |  | TB transducer-configured, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 11 | 301765 | 4 |  | TB transducer-configured, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 12 | 301765 | 4 |  | TB transducer-configured, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 13 | 301765 | 4 |  | TB transducer-configured, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 14 | 301765 | 4 |  | TB transducer-configured, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 15 | 301765 | 4 |  | TB transducer-configured, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1764 | 0 | 301765 | 4 |  | TB transducer-configured, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 1 | 301766 | 4 |  | Mains OK, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 2 | 301766 | 4 |  | Mains OK, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 3 | 301766 | 4 |  | Mains OK, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 4 | 301766 | 4 |  | Mains OK, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 5 | 301766 | 4 |  | Mains OK, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 6 | 301766 | 4 |  | Mains OK, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 7 | 301766 | 4 |  | Mains OK, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 8 | 301766 | 4 |  | Mains OK, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 9 | 301766 | 4 |  | Mains OK, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 10 | 301766 | 4 |  | Mains OK, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 11 | 301766 | 4 |  | Mains OK, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 12 | 301766 | 4 |  | Mains OK, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 13 | 301766 | 4 |  | Mains OK, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 14 | 301766 | 4 |  | Mains OK, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 15 | 301766 | 4 |  | Mains OK, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1765 | 0 | 301766 | 4 |  | Mains OK, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 1 | 301767 | 4 |  | Mains not in semi 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 2 | 301767 | 4 |  | Mains not in semi 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 3 | 301767 | 4 |  | Mains not in semi 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 4 | 301767 | 4 |  | Mains not in semi 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 5 | 301767 | 4 |  | Mains not in semi 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 6 | 301767 | 4 |  | Mains not in semi 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 7 | 301767 | 4 |  | Mains not in semi 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 8 | 301767 | 4 |  | Mains not in semi 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 9 | 301767 | 4 |  | Mains not in semi 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 10 | 301767 | 4 |  | Mains not in semi 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 11 | 301767 | 4 |  | Mains not in semi 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 12 | 301767 | 4 |  | Mains not in semi 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 13 | 301767 | 4 |  | Mains not in semi 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 14 | 301767 | 4 |  | Mains not in semi 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 15 | 301767 | 4 |  | Mains not in semi 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1766 | 0 | 301767 | 4 |  | Mains not in semi 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 1 | 301768 | 4 |  | Mains failure, ID 1 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 2 | 301768 | 4 |  | Mains failure, ID 2 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 3 | 301768 | 4 |  | Mains failure, ID 3 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 4 | 301768 | 4 |  | Mains failure, ID 4 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 5 | 301768 | 4 |  | Mains failure, ID 5 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 6 | 301768 | 4 |  | Mains failure, ID 6 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 7 | 301768 | 4 |  | Mains failure, ID 7 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 8 | 301768 | 4 |  | Mains failure, ID 8 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 9 | 301768 | 4 |  | Mains failure, ID 9 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 10 | 301768 | 4 |  | Mains failure, ID 10 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 11 | 301768 | 4 |  | Mains failure, ID 11 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 12 | 301768 | 4 |  | Mains failure, ID 12 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 13 | 301768 | 4 |  | Mains failure, ID 13 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 14 | 301768 | 4 |  | Mains failure, ID 14 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 15 | 301768 | 4 |  | Mains failure, ID 15 | BOOL |  |  |  | X | X | X
PM Alarm | 1767 | 0 | 301768 | 4 |  | Mains failure, ID 16 | BOOL |  |  |  | X | X | X
PM Alarm | 1770 | 1 | 301771 | 4 |  | Breaker synchronising, PV ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1770 | 2 | 301771 | 4 |  | Breaker synchronising, PV ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1770 | 3 | 301771 | 4 |  | Breaker synchronising, PV ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1770 | 4 | 301771 | 4 |  | Breaker synchronising, PV ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1770 | 5 | 301771 | 4 |  | Breaker synchronising, PV ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1770 | 6 | 301771 | 4 |  | Breaker synchronising, PV ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1770 | 7 | 301771 | 4 |  | Breaker synchronising, PV ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1770 | 8 | 301771 | 4 |  | Breaker synchronising, PV ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 1 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 2 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 3 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 4 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 5 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 6 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 7 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 8 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 9 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 10 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 11 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 12 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 13 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 14 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 15 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 0 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1771 | 1 | 301772 | 4 |  | PV running / Any LG breaker closed, ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 1 | 301773 | 4 |  | Ready to autostart, ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 2 | 301773 | 4 |  | Ready to autostart, ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 3 | 301773 | 4 |  | Ready to autostart, ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 4 | 301773 | 4 |  | Ready to autostart, ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 5 | 301773 | 4 |  | Ready to autostart, ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 6 | 301773 | 4 |  | Ready to autostart, ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 7 | 301773 | 4 |  | Ready to autostart, ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 8 | 301773 | 4 |  | Ready to autostart, ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 9 | 301773 | 4 |  | Ready to autostart, ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 10 | 301773 | 4 |  | Ready to autostart, ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 11 | 301773 | 4 |  | Ready to autostart, ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 12 | 301773 | 4 |  | Ready to autostart, ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 13 | 301773 | 4 |  | Ready to autostart, ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 14 | 301773 | 4 |  | Ready to autostart, ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 15 | 301773 | 4 |  | Ready to autostart, ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 0 | 301773 | 4 |  | Ready to autostart, ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1772 | 1 | 301773 | 4 |  | Ready to autostart, ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 1 | 301774 | 4 |  | Load Group 1 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 2 | 301774 | 4 |  | Load Group 1 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 3 | 301774 | 4 |  | Load Group 1 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 4 | 301774 | 4 |  | Load Group 1 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 5 | 301774 | 4 |  | Load Group 1 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 6 | 301774 | 4 |  | Load Group 1 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 7 | 301774 | 4 |  | Load Group 1 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 8 | 301774 | 4 |  | Load Group 1 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 9 | 301774 | 4 |  | Load Group 1 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 10 | 301774 | 4 |  | Load Group 1 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 11 | 301774 | 4 |  | Load Group 1 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 12 | 301774 | 4 |  | Load Group 1 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 13 | 301774 | 4 |  | Load Group 1 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 14 | 301774 | 4 |  | Load Group 1 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 15 | 301774 | 4 |  | Load Group 1 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 0 | 301774 | 4 |  | Load Group 1 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1773 | 1 | 301774 | 4 |  | Load Group 1 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 1 | 301775 | 4 |  | Load Group 2 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 2 | 301775 | 4 |  | Load Group 2 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 3 | 301775 | 4 |  | Load Group 2 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 4 | 301775 | 4 |  | Load Group 2 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 5 | 301775 | 4 |  | Load Group 2 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 6 | 301775 | 4 |  | Load Group 2 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 7 | 301775 | 4 |  | Load Group 2 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 8 | 301775 | 4 |  | Load Group 2 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 9 | 301775 | 4 |  | Load Group 2 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 10 | 301775 | 4 |  | Load Group 2 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 11 | 301775 | 4 |  | Load Group 2 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 12 | 301775 | 4 |  | Load Group 2 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 13 | 301775 | 4 |  | Load Group 2 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 14 | 301775 | 4 |  | Load Group 2 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 15 | 301775 | 4 |  | Load Group 2 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 0 | 301775 | 4 |  | Load Group 2 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1774 | 1 | 301775 | 4 |  | Load Group 2 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 1 | 301776 | 4 |  | Load Group 3 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 2 | 301776 | 4 |  | Load Group 3 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 3 | 301776 | 4 |  | Load Group 3 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 4 | 301776 | 4 |  | Load Group 3 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 5 | 301776 | 4 |  | Load Group 3 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 6 | 301776 | 4 |  | Load Group 3 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 7 | 301776 | 4 |  | Load Group 3 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 8 | 301776 | 4 |  | Load Group 3 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 9 | 301776 | 4 |  | Load Group 3 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 10 | 301776 | 4 |  | Load Group 3 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 11 | 301776 | 4 |  | Load Group 3 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 12 | 301776 | 4 |  | Load Group 3 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 13 | 301776 | 4 |  | Load Group 3 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 14 | 301776 | 4 |  | Load Group 3 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 15 | 301776 | 4 |  | Load Group 3 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 0 | 301776 | 4 |  | Load Group 3 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1775 | 1 | 301776 | 4 |  | Load Group 3 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 1 | 301777 | 4 |  | Load Group 4 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 2 | 301777 | 4 |  | Load Group 4 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 3 | 301777 | 4 |  | Load Group 4 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 4 | 301777 | 4 |  | Load Group 4 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 5 | 301777 | 4 |  | Load Group 4 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 6 | 301777 | 4 |  | Load Group 4 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 7 | 301777 | 4 |  | Load Group 4 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 8 | 301777 | 4 |  | Load Group 4 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 9 | 301777 | 4 |  | Load Group 4 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 10 | 301777 | 4 |  | Load Group 4 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 11 | 301777 | 4 |  | Load Group 4 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 12 | 301777 | 4 |  | Load Group 4 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 13 | 301777 | 4 |  | Load Group 4 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 14 | 301777 | 4 |  | Load Group 4 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 15 | 301777 | 4 |  | Load Group 4 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 0 | 301777 | 4 |  | Load Group 4 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1776 | 1 | 301777 | 4 |  | Load Group 4 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 1 | 301778 | 4 |  | Load Group 5 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 2 | 301778 | 4 |  | Load Group 5 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 3 | 301778 | 4 |  | Load Group 5 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 4 | 301778 | 4 |  | Load Group 5 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 5 | 301778 | 4 |  | Load Group 5 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 6 | 301778 | 4 |  | Load Group 5 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 7 | 301778 | 4 |  | Load Group 5 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 8 | 301778 | 4 |  | Load Group 5 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 9 | 301778 | 4 |  | Load Group 5 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 10 | 301778 | 4 |  | Load Group 5 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 11 | 301778 | 4 |  | Load Group 5 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 12 | 301778 | 4 |  | Load Group 5 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 13 | 301778 | 4 |  | Load Group 5 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 14 | 301778 | 4 |  | Load Group 5 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 15 | 301778 | 4 |  | Load Group 5 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 0 | 301778 | 4 |  | Load Group 5 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1777 | 1 | 301778 | 4 |  | Load Group 5 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 1 | 301779 | 4 |  | Load Group 6 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 2 | 301779 | 4 |  | Load Group 6 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 3 | 301779 | 4 |  | Load Group 6 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 4 | 301779 | 4 |  | Load Group 6 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 5 | 301779 | 4 |  | Load Group 6 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 6 | 301779 | 4 |  | Load Group 6 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 7 | 301779 | 4 |  | Load Group 6 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 8 | 301779 | 4 |  | Load Group 6 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 9 | 301779 | 4 |  | Load Group 6 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 10 | 301779 | 4 |  | Load Group 6 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 11 | 301779 | 4 |  | Load Group 6 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 12 | 301779 | 4 |  | Load Group 6 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 13 | 301779 | 4 |  | Load Group 6 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 14 | 301779 | 4 |  | Load Group 6 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 15 | 301779 | 4 |  | Load Group 6 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 0 | 301779 | 4 |  | Load Group 6 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1778 | 1 | 301779 | 4 |  | Load Group 6 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 1 | 301780 | 4 |  | Load Group 7 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 2 | 301780 | 4 |  | Load Group 7 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 3 | 301780 | 4 |  | Load Group 7 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 4 | 301780 | 4 |  | Load Group 7 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 5 | 301780 | 4 |  | Load Group 7 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 6 | 301780 | 4 |  | Load Group 7 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 7 | 301780 | 4 |  | Load Group 7 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 8 | 301780 | 4 |  | Load Group 7 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 9 | 301780 | 4 |  | Load Group 7 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 10 | 301780 | 4 |  | Load Group 7 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 11 | 301780 | 4 |  | Load Group 7 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 12 | 301780 | 4 |  | Load Group 7 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 13 | 301780 | 4 |  | Load Group 7 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 14 | 301780 | 4 |  | Load Group 7 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 15 | 301780 | 4 |  | Load Group 7 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 0 | 301780 | 4 |  | Load Group 7 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1779 | 1 | 301780 | 4 |  | Load Group 7 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 1 | 301781 | 4 |  | Load Group 8 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 2 | 301781 | 4 |  | Load Group 8 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 3 | 301781 | 4 |  | Load Group 8 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 4 | 301781 | 4 |  | Load Group 8 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 5 | 301781 | 4 |  | Load Group 8 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 6 | 301781 | 4 |  | Load Group 8 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 7 | 301781 | 4 |  | Load Group 8 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 8 | 301781 | 4 |  | Load Group 8 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 9 | 301781 | 4 |  | Load Group 8 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 10 | 301781 | 4 |  | Load Group 8 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 11 | 301781 | 4 |  | Load Group 8 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 12 | 301781 | 4 |  | Load Group 8 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 13 | 301781 | 4 |  | Load Group 8 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 14 | 301781 | 4 |  | Load Group 8 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 15 | 301781 | 4 |  | Load Group 8 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 0 | 301781 | 4 |  | Load Group 8 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1780 | 1 | 301781 | 4 |  | Load Group 8 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 1 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 2 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 3 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 4 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 5 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 6 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 7 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 8 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 9 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 10 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 11 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 12 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 13 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 14 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 15 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 0 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1781 | 1 | 301782 | 4 |  | Load Group 1 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 1 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 2 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 3 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 4 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 5 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 6 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 7 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 8 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 9 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 10 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 11 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 12 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 13 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 14 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 15 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 0 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1782 | 1 | 301783 | 4 |  | Load Group 2 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 1 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 2 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 3 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 4 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 5 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 6 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 7 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 8 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 9 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 10 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 11 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 12 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 13 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 14 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 15 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 0 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1783 | 1 | 301784 | 4 |  | Load Group 3 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 1 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 2 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 3 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 4 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 5 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 6 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 7 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 8 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 9 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 10 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 11 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 12 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 13 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 14 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 15 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 0 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1784 | 1 | 301785 | 4 |  | Load Group 4 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 1 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 2 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 3 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 4 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 5 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 6 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 7 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 8 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 9 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 10 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 11 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 12 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 13 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 14 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 15 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 0 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1785 | 1 | 301786 | 4 |  | Load Group 5 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 1 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 2 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 3 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 4 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 5 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 6 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 7 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 8 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 9 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 10 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 11 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 12 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 13 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 14 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 15 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 0 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1786 | 1 | 301787 | 4 |  | Load Group 6 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 1 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 2 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 3 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 4 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 5 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 6 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 7 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 8 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 9 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 10 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 11 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 12 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 13 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 14 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 15 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 0 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1787 | 1 | 301788 | 4 |  | Load Group 7 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 1 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 2 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 3 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 4 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 5 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 6 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 7 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 8 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 9 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 10 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 11 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 12 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 13 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 14 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 15 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 0 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1788 | 1 | 301789 | 4 |  | Load Group 8 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 1 | 301790 | 4 |  | Load Group 1 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 2 | 301790 | 4 |  | Load Group 1 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 3 | 301790 | 4 |  | Load Group 1 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 4 | 301790 | 4 |  | Load Group 1 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 5 | 301790 | 4 |  | Load Group 1 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 6 | 301790 | 4 |  | Load Group 1 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 7 | 301790 | 4 |  | Load Group 1 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 8 | 301790 | 4 |  | Load Group 1 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 9 | 301790 | 4 |  | Load Group 1 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 10 | 301790 | 4 |  | Load Group 1 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 11 | 301790 | 4 |  | Load Group 1 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 12 | 301790 | 4 |  | Load Group 1 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 13 | 301790 | 4 |  | Load Group 1 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 14 | 301790 | 4 |  | Load Group 1 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 15 | 301790 | 4 |  | Load Group 1 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 0 | 301790 | 4 |  | Load Group 1 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1789 | 1 | 301790 | 4 |  | Load Group 1 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 1 | 301791 | 4 |  | Load Group 2 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 2 | 301791 | 4 |  | Load Group 2 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 3 | 301791 | 4 |  | Load Group 2 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 4 | 301791 | 4 |  | Load Group 2 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 5 | 301791 | 4 |  | Load Group 2 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 6 | 301791 | 4 |  | Load Group 2 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 7 | 301791 | 4 |  | Load Group 2 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 8 | 301791 | 4 |  | Load Group 2 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 9 | 301791 | 4 |  | Load Group 2 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 10 | 301791 | 4 |  | Load Group 2 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 11 | 301791 | 4 |  | Load Group 2 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 12 | 301791 | 4 |  | Load Group 2 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 13 | 301791 | 4 |  | Load Group 2 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 14 | 301791 | 4 |  | Load Group 2 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 15 | 301791 | 4 |  | Load Group 2 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 0 | 301791 | 4 |  | Load Group 2 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1790 | 1 | 301791 | 4 |  | Load Group 2 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 1 | 301792 | 4 |  | Load Group 3 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 2 | 301792 | 4 |  | Load Group 3 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 3 | 301792 | 4 |  | Load Group 3 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 4 | 301792 | 4 |  | Load Group 3 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 5 | 301792 | 4 |  | Load Group 3 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 6 | 301792 | 4 |  | Load Group 3 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 7 | 301792 | 4 |  | Load Group 3 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 8 | 301792 | 4 |  | Load Group 3 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 9 | 301792 | 4 |  | Load Group 3 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 10 | 301792 | 4 |  | Load Group 3 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 11 | 301792 | 4 |  | Load Group 3 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 12 | 301792 | 4 |  | Load Group 3 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 13 | 301792 | 4 |  | Load Group 3 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 14 | 301792 | 4 |  | Load Group 3 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 15 | 301792 | 4 |  | Load Group 3 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 0 | 301792 | 4 |  | Load Group 3 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1791 | 1 | 301792 | 4 |  | Load Group 3 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 1 | 301793 | 4 |  | Load Group 4 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 2 | 301793 | 4 |  | Load Group 4 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 3 | 301793 | 4 |  | Load Group 4 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 4 | 301793 | 4 |  | Load Group 4 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 5 | 301793 | 4 |  | Load Group 4 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 6 | 301793 | 4 |  | Load Group 4 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 7 | 301793 | 4 |  | Load Group 4 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 8 | 301793 | 4 |  | Load Group 4 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 9 | 301793 | 4 |  | Load Group 4 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 10 | 301793 | 4 |  | Load Group 4 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 11 | 301793 | 4 |  | Load Group 4 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 12 | 301793 | 4 |  | Load Group 4 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 13 | 301793 | 4 |  | Load Group 4 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 14 | 301793 | 4 |  | Load Group 4 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 15 | 301793 | 4 |  | Load Group 4 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 0 | 301793 | 4 |  | Load Group 4 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1792 | 1 | 301793 | 4 |  | Load Group 4 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 1 | 301794 | 4 |  | Load Group 5 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 2 | 301794 | 4 |  | Load Group 5 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 3 | 301794 | 4 |  | Load Group 5 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 4 | 301794 | 4 |  | Load Group 5 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 5 | 301794 | 4 |  | Load Group 5 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 6 | 301794 | 4 |  | Load Group 5 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 7 | 301794 | 4 |  | Load Group 5 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 8 | 301794 | 4 |  | Load Group 5 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 9 | 301794 | 4 |  | Load Group 5 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 10 | 301794 | 4 |  | Load Group 5 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 11 | 301794 | 4 |  | Load Group 5 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 12 | 301794 | 4 |  | Load Group 5 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 13 | 301794 | 4 |  | Load Group 5 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 14 | 301794 | 4 |  | Load Group 5 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 15 | 301794 | 4 |  | Load Group 5 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 0 | 301794 | 4 |  | Load Group 5 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1793 | 1 | 301794 | 4 |  | Load Group 5 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 1 | 301795 | 4 |  | Load Group 6 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 2 | 301795 | 4 |  | Load Group 6 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 3 | 301795 | 4 |  | Load Group 6 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 4 | 301795 | 4 |  | Load Group 6 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 5 | 301795 | 4 |  | Load Group 6 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 6 | 301795 | 4 |  | Load Group 6 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 7 | 301795 | 4 |  | Load Group 6 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 8 | 301795 | 4 |  | Load Group 6 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 9 | 301795 | 4 |  | Load Group 6 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 10 | 301795 | 4 |  | Load Group 6 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 11 | 301795 | 4 |  | Load Group 6 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 12 | 301795 | 4 |  | Load Group 6 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 13 | 301795 | 4 |  | Load Group 6 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 14 | 301795 | 4 |  | Load Group 6 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 15 | 301795 | 4 |  | Load Group 6 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 0 | 301795 | 4 |  | Load Group 6 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1794 | 1 | 301795 | 4 |  | Load Group 6 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 1 | 301796 | 4 |  | Load Group 7 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 2 | 301796 | 4 |  | Load Group 7 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 3 | 301796 | 4 |  | Load Group 7 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 4 | 301796 | 4 |  | Load Group 7 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 5 | 301796 | 4 |  | Load Group 7 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 6 | 301796 | 4 |  | Load Group 7 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 7 | 301796 | 4 |  | Load Group 7 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 8 | 301796 | 4 |  | Load Group 7 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 9 | 301796 | 4 |  | Load Group 7 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 10 | 301796 | 4 |  | Load Group 7 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 11 | 301796 | 4 |  | Load Group 7 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 12 | 301796 | 4 |  | Load Group 7 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 13 | 301796 | 4 |  | Load Group 7 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 14 | 301796 | 4 |  | Load Group 7 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 15 | 301796 | 4 |  | Load Group 7 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 0 | 301796 | 4 |  | Load Group 7 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1795 | 1 | 301796 | 4 |  | Load Group 7 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 1 | 301797 | 4 |  | Load Group 8 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 2 | 301797 | 4 |  | Load Group 8 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 3 | 301797 | 4 |  | Load Group 8 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 4 | 301797 | 4 |  | Load Group 8 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 5 | 301797 | 4 |  | Load Group 8 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 6 | 301797 | 4 |  | Load Group 8 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 7 | 301797 | 4 |  | Load Group 8 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 8 | 301797 | 4 |  | Load Group 8 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 9 | 301797 | 4 |  | Load Group 8 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 10 | 301797 | 4 |  | Load Group 8 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 11 | 301797 | 4 |  | Load Group 8 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 12 | 301797 | 4 |  | Load Group 8 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 13 | 301797 | 4 |  | Load Group 8 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 14 | 301797 | 4 |  | Load Group 8 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 15 | 301797 | 4 |  | Load Group 8 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 0 | 301797 | 4 |  | Load Group 8 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Alarm | 1796 | 1 | 301797 | 4 |  | Load Group 8 Enabled - ID 33 | BOOL |  |  |  | X | X | X
Note on A4: More information about each function group is available in the description sheet.
Note on C4: Bit location of the function in the associated Modbus address.
Note on E4: 04 - Read single or multiple
Note on F4: The parameter number of the function.
Note on G4: The controller function name shows the name of the parameter in the Utility Software. Some functions might contain additional information.
Note on I4: AB - Most significant byte first ABCD - Most significant byte first and most significant word first
Note on J4: Example: Scaling = 1 Read Data = 266 Actual value = 26,6
Note on K4: Unit of the associated function
Note on L4: Indicates if the address is available in the BUS TIE breaker controller.
Note on M4: Indicates if the address is available in the MAINS controller.
Note on N4: Indicates if the address is available in the GENSET controller.