## About
ASC 150 Battery and Solar Parameter lists
Software version
The information contained in these parameter lists (Revision A) are applicable to software version 1.37.x of the AGC 150.
Controller types
This document includes the parameter lists for these controller types:
STORAGE controller
SOLAR controller
See the ASC 150 Storage Designer's handbook and ASC 150 Solar Designer's handbook for more information.
Parameters
The parameter lists are based on the parameters shown in the utility software, under Parameters.
Column names
Offset = The parameter address.
Channel = The parameter number.
Category = The selectable category in the parameter list.
Path = The path in the parameter tree.
Name = The name of the parameter.
Description = The parameter description. This is shown as mouseover text in the parameter list.
Default = The default value or selection for the parameter.
Minimum = The minimum value of the parameter range.*
Maximum = The maximum value of the parameter range.*
Unit = The unit of measurement for the parameter value.*
Selections = The drop-down choices for the parameter.*
Timer default = The default value for the timer.*
Timer minimum = The minimum value for the timer.*
Timer maximum = The maximum value for the timer.*
RelayA name = The selection for relay A.*
RelayB name = The selection for relay B.*
Default alarm action = The default alarm action when the parameter(s) are for an alarm.
Notes
* Only included where relevant.
Some parameter attributes (for example, Inhibits, and Auto acknowledge) are not included in the parameter list.
In addition to the parameters, the controllers also have a variety of other configurable settings. Examples include I/O & Hardware setup and Ethernet setting (TCP/IP). These are not included in the parameter lists.

## STORAGE
Offset | Channel | Category | Path | Name | Description | Default | Minimum | Maximum | Unit | Selections | Timer default | Timer minimum | Timer maximum | RelayA name | RelayB name | Default alarm action
1 | 1000 | Protection | AC configuration and protections > Power protections > Reverse power | -P> 1 | Reverse power protection level 1 (ANSI 32) | -100 | -200 | 0 | % |  | 100 | 1 | 1000 |  |  | Trip ESB
2 | 1010 | Protection | AC configuration and protections > Power protections > Reverse power | -P> 2 | Reverse power protection level 2 (ANSI 32) | -100 | -200 | 0 | % |  | 100 | 1 | 1000 |  |  | Trip ESB
4 | 1030 | Protection | AC configuration and protections > Current protections > Over-current | I> 1 | Overcurrent protection level 1 (ANSI 50) | 115 | 50 | 200 | % |  | 100 | 1 | 32000 |  |  | Warning
5 | 1040 | Protection | AC configuration and protections > Current protections > Over-current | I> 2 | Overcurrent protection level 2 (ANSI 50) | 120 | 50 | 200 | % |  | 50 | 1 | 32000 |  |  | Trip ESB
6 | 1050 | Protection | AC configuration and protections > Current protections > Over-current | I> 3 | Overcurrent protection level 3 (ANSI 50) | 115 | 50 | 200 | % |  | 100 | 1 | 32000 |  |  | Trip ESB
7 | 1060 | Protection | AC configuration and protections > Current protections > Over-current | I> 4 | Overcurrent protection level 4 (ANSI 50) | 120 | 50 | 200 | % |  | 50 | 1 | 32000 |  |  | Trip ESB
870 | 1070 | Protection | AC configuration and protections > Power protections > Reverse power | -P> 3 | Reverse power protection level 3 (ANSI 32) | -100 | -200 | 30 | % |  | 1000 | 0 | 30000 |  |  | Trip ESB
1377 | 1081 | Protection | AC configuration and protections > Current protections > Inverse time over-current | I> inverse Type | I> curve selection (IEC/IEEE inverse time overcurrent) | IEC Inverse |  |  |  | 0: IEC Inverse, 1: IEC Very Inverse, 2: IEC Extremely Inv., 3: IEEE Moderately Inv., 4: IEEE Very Inverse, 5: IEEE Extremely Inv., 6: Custom
1382 | 1082 | Protection | AC configuration and protections > Current protections > Inverse time over-current | I> inverse Limit | I> (IEC/IEEE inverse time overcurrent) | 110 | 50 | 200 | %
1378 | 1083 | Protection | AC configuration and protections > Current protections > Inverse time over-current | I> inverse TMS | I> (IEC/IEEE inverse time overcurrent) | 1 | 0.01 | 100 | /100
1379 | 1084 | Protection | AC configuration and protections > Current protections > Inverse time over-current | I> inverse k | I> (IEC/IEEE inverse time overcurrent) | 0.14 | 0.001 | 32 | s
1380 | 1085 | Protection | AC configuration and protections > Current protections > Inverse time over-current | I> inverse c | I> (IEC/IEEE inverse time overcurrent) | 0 | 0 | 32 | s
1381 | 1086 | Protection | AC configuration and protections > Current protections > Inverse time over-current | I> inverse a | I> (IEC/IEEE inverse time overcurrent) | 0.02 | 0.001 | 32 | /1000
1335 | 1087 | Protection | AC configuration and protections > Current protections > Inverse time over-current | I> inverse | I> setup (IEC/IEEE inverse time overcurrent) | [10 empty] | Trip ESB
1251 | 1101 | Protection | AC configuration and protections > Current protections > Voltage dependent over-current | ES Iv> (50%) | Voltage dependent overcurrent curve setting 1 | 110 | 50 | 200 | %
1252 | 1102 | Protection | AC configuration and protections > Current protections > Voltage dependent over-current | ES Iv> (60%) | Voltage dependent overcurrent curve setting 2 | 125 | 50 | 200 | %
1253 | 1103 | Protection | AC configuration and protections > Current protections > Voltage dependent over-current | ES Iv> (70%) | Voltage dependent overcurrent curve setting 3 | 140 | 50 | 200 | %
1254 | 1104 | Protection | AC configuration and protections > Current protections > Voltage dependent over-current | ES Iv> (80%) | Voltage dependent overcurrent curve setting 4 | 155 | 50 | 200 | %
1255 | 1105 | Protection | AC configuration and protections > Current protections > Voltage dependent over-current | ES Iv> (90%) | Voltage dependent overcurrent curve setting 5 | 170 | 50 | 200 | %
1256 | 1106 | Protection | AC configuration and protections > Current protections > Voltage dependent over-current | ES Iv> (100%) | Voltage dependent overcurrent curve setting 6 | 200 | 50 | 200 | %
9 | 1110 | Protection | AC configuration and protections > Current protections > Voltage dependent over-current | ES Iv> | Voltage dependent overcurrent protection (ANSI 50V) | [5 empty] | 10 | 1 | 100 |  |  | Trip ESB
10 | 1130 | Protection | AC configuration and protections > Current protections > Fast over-current | I>> 1 | Fast overcurrent protection level 1 (ANSI 50) | 150 | 150 | 300 | % |  | 20 | 0 | 32000 |  |  | Trip ESB
11 | 1140 | Protection | AC configuration and protections > Current protections > Fast over-current | I>> 2 | Fast overcurrent protection level 1 (ANSI 50) | 200 | 150 | 300 | % |  | 5 | 0 | 32000 |  |  | Trip ESB
12 | 1150 | Protection | AC configuration and protections > Voltage protections > Over-voltage | ES U> 1 | ESS overvoltage protection level 1 (ANSI 27) | 103 | 100 | 130 | % |  | 100 | 1 | 1000 |  |  | Warning
13 | 1160 | Protection | AC configuration and protections > Voltage protections > Over-voltage | ES U> 2 | ESS overvoltage protection level 2 (ANSI 27) | 105 | 100 | 130 | % |  | 50 | 1 | 1000 |  |  | Warning
14 | 1170 | Protection | AC configuration and protections > Voltage protections > Under-voltage | ES U< 1 | ESS undervoltage protection level 1 (ANSI 27) | 97 | 40 | 100 | % |  | 100 | 1 | 1000 |  |  | Warning
15 | 1180 | Protection | AC configuration and protections > Voltage protections > Under-voltage | ES U< 2 | ESS undervoltage protection level 2 (ANSI 27) | 95 | 40 | 100 | % |  | 50 | 1 | 1000 |  |  | Warning
16 | 1190 | Protection | AC configuration and protections > Voltage protections > Under-voltage | ES U< 3 | ESS undervoltage protection level 3 (ANSI 27) | 95 | 40 | 100 | % |  | 50 | 1 | 1000 |  |  | Warning
17 | 1201 | Protection | AC configuration and protections > Voltage protections > Voltage detect. type | ES U detect. type | ESS meassurement type phase-phase or phase-neutral | Ph-Ph |  |  |  | 0: Ph-Ph, 1: Ph-N
31 | 1202 | Protection | Busbar > Voltage protections > Voltage detect. type | BB U detect. type | Busbar meassurement type phase-phase or phase-neutral | Ph-Ph |  |  |  | 0: Ph-Ph, 1: Ph-N
1608 | 1203 | Protection | AC configuration and protections > Current protections > Unbalance current | Unbalance I | Current unbalance calculation method | Ref. to nominal |  |  |  | 0: Ref. to nominal, 1: Ref. to average
173 | 1204 | Protection | AC configuration and protections > Frequency protections > Frequency detection type | Freq. detect. type | Frequency trip type selection for over- and underfrequency alarms. | L1 or L2 or L3 |  |  |  | 0: L1, 1: L2, 2: L3, 3: L1 or L2 or L3, 4: L1 and L2 and L3
18 | 1210 | Protection | AC configuration and protections > Frequency protections > Over-frequency | ES f> 1 | ESS overfrequency protection level 1 (ANSI 81) | 103 | 100 | 120 | % |  | 100 | 2 | 1000 |  |  | Warning
19 | 1220 | Protection | AC configuration and protections > Frequency protections > Over-frequency | ES f> 2 | ESS overfrequency protection level 2 (ANSI 81) | 105 | 100 | 120 | % |  | 50 | 2 | 1000 |  |  | Warning
20 | 1230 | Protection | AC configuration and protections > Frequency protections > Over-frequency | ES f> 3 | ESS overfrequency protection level 3 (ANSI 81) | 105 | 100 | 120 | % |  | 50 | 2 | 1000 |  |  | Warning
21 | 1240 | Protection | AC configuration and protections > Frequency protections > Under-frequency | ES f< 1 | ESS underfrequency protection level 1 (ANSI 81) | 97 | 80 | 100 | % |  | 100 | 2 | 1000 |  |  | Warning
22 | 1250 | Protection | AC configuration and protections > Frequency protections > Under-frequency | ES f< 2 | ESS underfrequency protection level 2 (ANSI 81) | 95 | 80 | 100 | % |  | 50 | 2 | 1000 |  |  | Warning
23 | 1260 | Protection | AC configuration and protections > Frequency protections > Under-frequency | ES f< 3 | ESS underfrequency protection level 3 (ANSI 81) | 95 | 80 | 100 | % |  | 50 | 2 | 1000 |  |  | Warning
24 | 1270 | Protection | Busbar > Voltage protections > Over-voltage | BB U> 1 | Busbar overvoltage protection level 1 (ANSI 59) | 103 | 100 | 120 | % |  | 1000 | 4 | 9999 |  |  | Warning
25 | 1280 | Protection | Busbar > Voltage protections > Over-voltage | BB U> 2 | Busbar overvoltage protection level 2 (ANSI 59) | 105 | 100 | 120 | % |  | 500 | 4 | 9999 |  |  | Warning
26 | 1290 | Protection | Busbar > Voltage protections > Over-voltage | BB U> 3 | Busbar overvoltage protection level 3 (ANSI 59) | 105 | 100 | 120 | % |  | 500 | 4 | 9999 |  |  | Warning
27 | 1300 | Protection | Busbar > Voltage protections > Under-voltage | BB U< 1 | Busbar undervoltage protection level 1 (ANSI 59) | 97 | 40 | 100 | % |  | 1000 | 4 | 9999 |  |  | Warning
28 | 1310 | Protection | Busbar > Voltage protections > Under-voltage | BB U< 2 | Busbar undervoltage protection level 2 (ANSI 59) | 95 | 40 | 100 | % |  | 500 | 4 | 9999 |  |  | Warning
29 | 1320 | Protection | Busbar > Voltage protections > Under-voltage | BB U< 3 | Busbar undervoltage protection level 3 (ANSI 59) | 97 | 40 | 100 | % |  | 1000 | 4 | 9999 |  |  | Warning
30 | 1330 | Protection | Busbar > Voltage protections > Under-voltage | BB U< 4 | Busbar undervoltage protection level 4 (ANSI 59) | 95 | 40 | 100 | % |  | 500 | 4 | 9999 |  |  | Warning
32 | 1350 | Protection | Busbar > Frequency protections > Over-frequency | BB f> 1 | Busbar overfrequency protection level 1 (ANSI 81) | 103 | 100 | 120 | % |  | 1000 | 4 | 9999 |  |  | Warning
33 | 1360 | Protection | Busbar > Frequency protections > Over-frequency | BB f> 2 | Busbar overfrequency protection level 2 (ANSI 81) | 105 | 100 | 120 | % |  | 500 | 4 | 9999 |  |  | Warning
34 | 1370 | Protection | Busbar > Frequency protections > Over-frequency | BB f> 3 | Busbar overfrequency protection level 3 (ANSI 81) | 105 | 100 | 120 | % |  | 500 | 4 | 9999 |  |  | Warning
35 | 1380 | Protection | Busbar > Frequency protections > Under-frequency | BB f< 1 | Busbar underfrequency protection level 1 (ANSI 81) | 97 | 80 | 100 | % |  | 1000 | 4 | 9999 |  |  | Warning
36 | 1390 | Protection | Busbar > Frequency protections > Under-frequency | BB f< 2 | Busbar underfrequency protection level 2 (ANSI 81) | 95 | 80 | 100 | % |  | 500 | 4 | 9999 |  |  | Warning
37 | 1400 | Protection | Busbar > Frequency protections > Under-frequency | BB f< 3 | Busbar underfrequency protection level 3 (ANSI 81) | 97 | 80 | 100 | % |  | 1000 | 4 | 9999 |  |  | Warning
38 | 1410 | Protection | Busbar > Frequency protections > Under-frequency | BB f< 4 | Busbar underfrequency protection level 4 (ANSI 81) | 95 | 80 | 100 | % |  | 500 | 4 | 9999 |  |  | Warning
39 | 1420 | Protection | Busbar > Additional protections > ROCOF (df/dt) | df/dt (ROCOF) | Set point of ROCOF protection (rate of change of frequency) | 5 | 0.2 | 10 | Hz/s |  | 0 | 0 | 300 |  |  | Trip MB
40 | 1421 | Protection | Busbar > Additional protections > ROCOF (df/dt) | df/dt (ROCOF) | ROCOF protection delay in cycles | 6 | 3 | 20 | period(s)
41 | 1430 | Protection | Busbar > Additional protections > Vector shift | Vector shift | Set point in degrees of vector shift protection | 10 | 1 | 90 | deg | [6 empty] | Trip MB
1465 | 1436 | Protection | Busbar > Additional protections > Vector shift | Vector shift type | Vector shift trip selection | Individual phases |  |  |  | 0: Individual phases, 1: All phases
42 | 1440 | Protection | Busbar > Voltage protections > Positive sequence under-voltage | BB pos. seq. U | Positive sequence (busbar) voltage low ANSI 27) | 70 | 10 | 110 | % |  | 2 | 1 | 9 |  |  | Trip MB
43 | 1450 | Protection | AC configuration and protections > Power protections > Overload | P> 1 | ESS overload protection level 1 (ANSI 32) | 100 | -200 | 200 | % |  | 100 | 1 | 32000 |  |  | Warning
44 | 1460 | Protection | AC configuration and protections > Power protections > Overload | P> 2 | ESS overload protection level 2 (ANSI 32) | 110 | -200 | 200 | % |  | 50 | 1 | 32000 |  |  | Trip ESB
45 | 1470 | Protection | AC configuration and protections > Power protections > Overload | P> 3 | ESS overload protection level 3 (ANSI 32) | 100 | -200 | 200 | % |  | 100 | 1 | 32000 |  |  | Trip ESB
46 | 1480 | Protection | AC configuration and protections > Power protections > Overload | P> 4 | ESS overload protection level 4 (ANSI 32) | 110 | -200 | 200 | % |  | 50 | 1 | 32000 |  |  | Trip ESB
47 | 1490 | Protection | AC configuration and protections > Power protections > Overload | P< 5 | ESS overload protection level 5 (ANSI 32) | 30 | -200 | 200 | % |  | 32000 | 1 | 32000 |  |  | Trip ESB
48 | 1500 | Protection | AC configuration and protections > Current protections > Unbalance current | Unbalance I 1 | ESS unbalanced current (ANSI 60) | 30 | 0 | 100 | % |  | 100 | 1 | 1000 |  |  | Trip ESB
49 | 1510 | Protection | AC configuration and protections > Voltage protections > Voltage unbalance | ES Unbalance U | ESS unbalanced voltage (ANSI 60) | 10 | 0 | 50 | % |  | 100 | 1 | 1000 |  |  | Trip ESB
50 | 1520 | Protection | AC configuration and protections > Reactive power protections > Underexcitation | -Q> | Loss of excitation (ANSI 40) | 50 | 0 | 150 | % |  | 100 | 1 | 1000 |  |  | Warning
51 | 1530 | Protection | AC configuration and protections > Reactive power protections > Overexcitation | Q> | Overexcitation (ANSI 40) | 60 | 0 | 100 | % |  | 100 | 1 | 1000 |  |  | Warning
52 | 1540 | Protection | AC configuration and protections > Current protections > Negative sequence current | Negative. seq. I | Negative sequence current (ANSI 46) | 20 | 1 | 100 | % |  | 5 | 2 | 1000 |  |  | Trip MB
53 | 1550 | Protection | AC configuration and protections > Voltage protections > Negative sequence voltage | ES neg. seq. U | Negative sequence voltage (ANSI 47) | 5 | 1 | 100 | % |  | 5 | 2 | 1000 |  |  | Trip MB
54 | 1560 | Protection | AC configuration and protections > Voltage protections > Negative sequence voltage | Neg. seq. select | Negative sequence ESS or Busbar | ESS measurement |  |  |  | 0: ESS measurement, 1: BB measurement | 1 | 1 | 1 |  |  | Warning
55 | 1570 | Protection | AC configuration and protections > Current protections > Zero sequence current | Zero seq. I | Zero sequence current (ANSI 50I0) | 20 | 0 | 100 | % |  | 5 | 2 | 1000 |  |  | Trip MB
56 | 1580 | Protection | AC configuration and protections > Voltage protections > Zero sequence voltage | ES zero seq. U | Zero sequence voltage (ANSI 59U0) | 5 | 0 | 100 | % |  | 5 | 2 | 1000 |  |  | Trip MB
57 | 1590 | Protection | AC configuration and protections > Voltage protections > Zero sequence voltage | Zero seq. select | Zero sequence measurement selection | ESS measurement |  |  |  | 0: ESS measurement, 1: BB measurement | 1 | 1 | 1 |  |  | Warning
851 | 1600 | Protection | AC configuration and protections > Current protections > Directional over-current | I> direct. 1 | Directional overcurrent (ANSI 67) | 120 | -200 | 200 | % |  | 1 | 0 | 32000 |  |  | Trip MB
852 | 1610 | Protection | AC configuration and protections > Current protections > Directional over-current | I> direct. 2 | Directional overcurrent (ANSI 67) | 130 | -200 | 200 | % |  | 1 | 0 | 32000 |  |  | Trip MB
873 | 1620 | Protection | Busbar > Voltage protections > Voltage unbalance | BB unbalance U | Busbar unbalanced voltage (ANSI 60) | 6 | 0 | 50 | % |  | 100 | 1 | 1000 |  |  | Warning
58 | 1710 | Protection | AC configuration and protections > Current protections > Unbalance current | Unbalance I 2 | ESS unbalanced current level 2 (ANSI 60) | 40 | 0 | 100 | % |  | 100 | 1 | 1000 |  |  | Trip ESB
1494 | 1721 | Protection | AC configuration and protections > Current protections > Neutral inverse time over-current (4th CT) | In> inverse Type | In> curve selection (IEC/IEEE inverse time overcurrent (ANSI 51)) | IEC Inverse |  |  |  | 0: IEC Inverse, 1: IEC Very Inverse, 2: IEC Extremely Inv., 3: IEEE Moderately Inv., 4: IEEE Very Inverse, 5: IEEE Extremely Inv., 6: Custom
1495 | 1722 | Protection | AC configuration and protections > Current protections > Neutral inverse time over-current (4th CT) | In> inverse Limit | In> (IEC/IEEE inverse time overcurrent (ANSI 51)) | 30 | 2 | 120 | %
1496 | 1723 | Protection | AC configuration and protections > Current protections > Neutral inverse time over-current (4th CT) | In> inverse TMS | In> (IEC/IEEE inverse time overcurrent (ANSI 51)) | 1 | 0.01 | 100 | /100
1497 | 1724 | Protection | AC configuration and protections > Current protections > Neutral inverse time over-current (4th CT) | In> inverse k | In> (IEC/IEEE inverse time overcurrent (ANSI 51)) | 0.14 | 0.001 | 32 | s
1498 | 1725 | Protection | AC configuration and protections > Current protections > Neutral inverse time over-current (4th CT) | In> inverse c | In> (IEC/IEEE inverse time overcurrent (ANSI 51)) | 0 | 0 | 32 | s
1499 | 1726 | Protection | AC configuration and protections > Current protections > Neutral inverse time over-current (4th CT) | In> inverse a | In> (IEC/IEEE inverse time overcurrent (ANSI 51)) | 0.02 | 0.001 | 32 | /1000
1500 | 1727 | Protection | AC configuration and protections > Current protections > Neutral inverse time over-current (4th CT) | In> inverse | In> (IEC/IEEE inverse time overcurrent) | [10 empty] | Trip ESB
1501 | 1731 | Protection | AC configuration and protections > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse Type | Ie> curve selection (IEC/IEEE inverse time overcurrent) | IEC Inverse |  |  |  | 0: IEC Inverse, 1: IEC Very Inverse, 2: IEC Extremely Inv., 3: IEEE Moderately Inv., 4: IEEE Very Inverse, 5: IEEE Extremely Inv., 6: Custom
1502 | 1732 | Protection | AC configuration and protections > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse Limit | Ie> (IEC/IEEE inverse time overcurrent) | 10 | 2 | 120 | %
1503 | 1733 | Protection | AC configuration and protections > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse TMS | Ie> (IEC/IEEE inverse time overcurrent) | 1 | 0.01 | 100 | /100
1504 | 1734 | Protection | AC configuration and protections > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse k | Ie> (IEC/IEEE inverse time overcurrent) | 0.14 | 0.001 | 32 | s
1505 | 1735 | Protection | AC configuration and protections > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse c | Ie> (IEC/IEEE inverse time overcurrent) | 0 | 0 | 32 | s
1506 | 1736 | Protection | AC configuration and protections > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse a | Ie> (IEC/IEEE inverse time overcurrent) | 0.02 | 0.001 | 32 | /1000
1507 | 1737 | Protection | AC configuration and protections > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse | Ie> (IEC/IEEE inverse time overcurrent) | [10 empty] | Trip ESB
859 | 1920 | Protection | Busbar > Frequency protections > Over-frequency | BB f> 4 | Busbar overfrequency protection level 4 (ANSI 81) | 102 | 100 | 120 | % |  | 5600 | 1500 | 6000 |  |  | Warning
860 | 1930 | Protection | Busbar > Frequency protections > Under-frequency | BB f< 5 | Busbar underfrequency protection level 5 (ANSI 81) | 95 | 80 | 100 | % |  | 5600 | 1500 | 6000 |  |  | Warning
1413 | 1960 | Protection | AC configuration and protections > Voltage protections > Under-voltage with reverse vars | U and Q < 1 | U and Q< (Undervoltage and reactive power (ANSI 27+32RV) | 85 | 40 | 100 | % |  | 5 | 1 | 32000 |  |  | Warning
1414 | 1970 | Protection | AC configuration and protections > Voltage protections > Under-voltage with reverse vars | U and Q < 2 | U and Q< (Undervoltage and reactive power (ANSI 27+32RV) | 85 | 40 | 100 | % |  | 5 | 1 | 32000 |  |  | Warning
1273 | 1981 | Protection | Breakers > ES breaker > Breaker monitoring | ESB Ext tripped | ESB externally tripped alarm | [10 empty] | Warning
1274 | 1983 | Protection | Breakers > Mains breaker > Breaker monitoring | MB Ext. tripped | Mains Breaker externally tripped alarm | [10 empty] | Warning
1691 | 1991 | Protection | AC configuration and protections > Voltage protections > Under-voltage with reverse vars | I min. 1 | (U and Q< 1: Min Current level) | 0 | 0 | 20 | %
1692 | 1992 | Protection | AC configuration and protections > Voltage protections > Under-voltage with reverse vars | Angle 1 | (U and Q< 1: Min Phi angle) | 0 | 0 | 6 | deg
1693 | 1993 | Protection | AC configuration and protections > Voltage protections > Under-voltage with reverse vars | I min. 2 | (U and Q< 2: Min Current level) | 0 | 0 | 20 | %
1694 | 1994 | Protection | AC configuration and protections > Voltage protections > Under-voltage with reverse vars | Angle 2 | (U and Q< 2: Min Phi angle) | 0 | 0 | 6 | deg
65 | 2021 | Synchronisation | Synchronisation > Dynamic synchronisation | Sync. dfMax | Max. allowable frequency difference for Dynamic synchronisation | 0.3 | 0 | 0.5 | Hz
66 | 2022 | Synchronisation | Synchronisation > Dynamic synchronisation | Sync. dfMin | Min. allowable frequency difference for Dynamic synchronisation | 0 | -0.5 | 0.3 | Hz
67 | 2023 | Synchronisation | Synchronisation > Dynamic synchronisation | Sync. dUMax | Max. allowable voltage difference for Dynamic synchronisation | 5 | 2 | 10 | %
1615 | 2024 | Synchronisation | Synchronisation > Dynamic synchronisation | Sync. dUMin | Max. allowable value the regulated voltage must be below voltage to sync to | -5 | -10 | 0 | %
68 | 2025 | Synchronisation | Synchronisation > Dynamic synchronisation | Sync. time ESB | Max. allowable breaker closing time for Dynamic synchronisation | 50 | 40 | 300 | ms
69 | 2026 | Synchronisation | Synchronisation > Dynamic synchronisation | Sync. time MB | Max. allowable breaker closing time for Dynamic synchronisation | 50 | 40 | 300 | ms
1307 | 2111 | Synchronisation | AC configuration and protections > AC configuration > Voltage and frequency OK > Blackout / Hz/V OK | Blackout / f< | Max. allowable frequency difference from nominal setting BELOW nominal for closing in case of blackout. This setting is also used to determine Hz/V OK | 3 | 0 | 5 | Hz
94 | 2112 | Synchronisation | AC configuration and protections > AC configuration > Voltage and frequency OK > Blackout / Hz/V OK | Blackout / f> | Max. allowable frequency difference from nominal setting ABOVE nominal for closing in case of blackout. This setting is also used to determine Hz/V OK | 3 | 0 | 5 | Hz
1308 | 2113 | Synchronisation | AC configuration and protections > AC configuration > Voltage and frequency OK > Blackout / Hz/V OK | Blackout / U< | Max. allowable voltage difference from nominal setting BELOW nominal for closing in case of blackout. This setting is also used to determine Hz/V OK | 5 | 2 | 20 | %
95 | 2114 | Synchronisation | AC configuration and protections > AC configuration > Voltage and frequency OK > Blackout / Hz/V OK | Blackout / U> | Max. allowable voltage difference from nominal setting ABOVE nominal for closing in case of blackout. This setting is also used to determine Hz/V OK | 5 | 2 | 20 | %
98 | 2130 | Synchronisation | Synchronisation > Synchronisation failure > ESB synchronisation failure | ESB Sync failure | Max. allowable time for synchronisation of the ESS breaker (alarm) | [5 empty] | 600 | 50 | 9999 |  |  | Warning
99 | 2140 | Synchronisation | Synchronisation > Synchronisation failure > MB synchronisation failure | MB Sync failure | Max. allowable time for synchronisation of the connection breaker (alarm) | [5 empty] | 600 | 50 | 9999 |  |  | Warning
100 | 2150 | Synchronisation | AC configuration and protections > AC configuration > Phase sequence error | Phase seq error ES | Supervision of the rotation direction of BA | [5 empty] | 10 | 10 | 10 |  |  | Warning
1193 | 2154 | Synchronisation | AC configuration and protections > AC configuration > Phase direction | Phase rotation | Expected direction of the phase rotation | L1L2L3 |  |  |  | 0: L1L2L3, 1: L1L3L2
1616 | 2155 | Synchronisation | Busbar > AC configuration > Phase sequence error | Phase seq error BB | Supervision of the rotation direction of BB | [5 empty] | 10 | 10 | 10
101 | 2160 | Synchronisation | Breakers > ES breaker > Breaker monitoring | ESB Open fail | ESS breaker open failure | [5 empty] | 20 | 10 | 100 |  |  | Warning
102 | 2170 | Synchronisation | Breakers > ES breaker > Breaker monitoring | ESB Close fail | ESS breaker close failure | [5 empty] | 20 | 10 | 9000 |  |  | Warning
103 | 2180 | Synchronisation | Breakers > ES breaker > Breaker monitoring | ESB Pos fail | ESS breaker position feedback failure | [5 empty] | 10 | 10 | 50 |  |  | Warning
107 | 2200 | Synchronisation | Breakers > Mains breaker > Breaker monitoring | MB Open fail | Mains breaker open failure | [5 empty] | 20 | 10 | 100 |  |  | Warning
108 | 2210 | Synchronisation | Breakers > Mains breaker > Breaker monitoring | MB Close fail | Mains breaker close failure | [5 empty] | 20 | 10 | 50 |  |  | Warning
109 | 2220 | Synchronisation | Breakers > Mains breaker > Breaker monitoring | MB Pos fail | Mains breaker position feedback failure | [5 empty] | 10 | 10 | 50 |  |  | Warning
1646 | 2320 | Synchronisation | Synchronisation > Busbar blocked alarms | Busbar blocked | Busbar blocked by pos failure | [5 empty] | 10 | 10 | 50 |  |  | Warning
1936 | 2350 | Synchronisation | Breakers > ES breaker > Breaker configuration | ESB close seq. | ESB close sequence configuration. Can be used for delaying breaker close based on running status and timer | Automatic |  |  |  | 1: Automatic, 2: Wait for ESS run OK | 0 | 0 | 1000
91 | 2360 | Synchronisation | Breakers > ES breaker > Breaker configuration | Auto close cond | Breaker close condition in auto mode | Default |  |  |  | 0: Default, 1: Auto start and running
146 | 2611 | Regulation | Regulation > ESS loading and deloading > Ramp up rates | P ramp up | P ramp up speed | 2 | 0.1 | 100 | %/s
1282 | 2612 | Regulation | Regulation > ESS loading and deloading | Island ramp | Power ramp up loads/steps
148 | 2621 | Regulation | Regulation > ESS loading and deloading > Ramp down and offload rates | P ramp down | P ramp down speed | 2 | 0.1 | 100 | %/s
149 | 2622 | Regulation | Regulation > ESS loading and deloading > Ramp down and offload rates | Ramp open point | Max. allowable power when opening the breaker | 5 | 1 | 20 | %
879 | 2641 | Regulation | Regulation > ESS loading and deloading > Ramp up rates | Q ramp up | Q ramp up speed | 2 | 0.1 | 100 | %/s
1589 | 2642 | Regulation | Regulation > ESS loading and deloading | Q ramp lim. max | Ignore Q ramp in between of these min and max values | 90 | 1 | 110 | %
880 | 2651 | Regulation | Regulation > ESS loading and deloading > Ramp down and offload rates | Q ramp down | Q ramp down speed | 2 | 0.1 | 100 | %/s
1588 | 2652 | Regulation | Regulation > ESS loading and deloading | Q ramp lim. min | Ignore Q ramp in between of these min and max values | -10 | -20 | 50 | %
691 | 2661 | Regulation | Regulation > U/f ref. origin | U ref. origin | Sets the origin of the voltage reference sent out by the ASC when the setting of the U/f origin config (2663) parameter is met | Busbar measurement |  |  |  | 0: Nominal value, 1: Busbar measurement
692 | 2662 | Regulation | Regulation > U/f ref. origin | f ref. origin | Sets the origin of the frequency reference sent out by the ASC when the setting of the U/f origin config (2663) parameter is met | Busbar measurement |  |  |  | 0: Nominal value, 1: Busbar measurement
182 | 2663 | Regulation | Regulation > U/f ref. origin | Uf origin config | Sets when the U/f ref. origin parameters are active in an application | Mains on busbar |  |  |  | 0: Mains on busbar, 1: Mains or genset only, 2: Any voltage source on busbar
614 | 2664 | Regulation | Regulation > U/f ref. origin | U ref. gain | Adds a gain to the voltage reference compared to the nominal parameter. This is useful for adjusting for internal transformers of the PCS. | 0 | -100 | 100 | %
487 | 2671 | Regulation | Regulation > P reference gain | P ref. const. gain | Sets a constant local offset to the active power reference based on a percentage of nominel S to compensate for a constant power loss. | 0 | 0 | 10 | %
488 | 2672 | Regulation | Regulation > P reference gain | P ref. dyn. gain | Sets a dynamic local offset to the active power reference based on a percentage of the normal reference to compensate for a dynamic power loss. | 0 | 0 | 10 | %
1938 | 2681 | Regulation | Regulation > ESS loading and deloading > Ramp delays | P ramp delay | Minimum time between updating of ramped active power setpoint | 1 | 0 | 2 | s
1939 | 2682 | Regulation | Regulation > ESS loading and deloading > Ramp delays | Q ramp delay | Minimum time between updating of ramped reactive power setpoint | 1 | 0 | 2 | s
178 | 2741 | Regulation | Regulation > Delay regulation | Delay reg. | Keep reference at minimum dispatch at selected duration after start initiated | [5 empty] | 0 | 0 | 9900
183 | 2781 | Regulation | Regulation > Enable regulation | P reference | P reg. ena/dis. Applicable with single register (0x06) commands. With multiple register (0x10) commands P reg. always active
184 | 2782 | Regulation | Regulation > Enable regulation | Q reference | Q reg. ena/dis. Applicable with single register (0x06) commands. With multiple register (0x10) commands Q reg. always active
84 | 2801 | Regulation | Regulation > Droop | Droop config. | Enable droop and select origin of droop slopes. | ASC parameters |  |  |  | 0: ASC parameters, 1: BESS comm. reading
85 | 2803 | Regulation | Regulation > Droop | Droop f slope | Configure frequency droop slope in %P/Hz | 40 | 0 | 2000 | /10
86 | 2804 | Regulation | Regulation > Droop | Droop U slope | Configure voltage droop slope in %Q/V | 5 | 0 | 2000 | /10
303 | 2805 | Regulation | Regulation > Droop | Droop f offset | Configure a constant offset to the frequency droop slope while mains or gensets is connected. Can be used to adjust for PCS measurement errors | 0 | -10 | 10 | Hz
302 | 2806 | Regulation | Regulation > Droop | Droop U offset | Configure a constant offset to the voltage droop slope while mains or gensets is connected. Can be used to adjust for PCS measurement errors | 0 | -10 | 10 | V
241 | 2810 | Regulation | Regulation > Heartbeat timer | Heartbeat timer | Configure timeout period after last transmitted heartbeat signal before PCS activates an error. If disabled the timout value will not be transmitted | 20 | 0 | 28800 | sec
525 | 2821 | Regulation | Regulation > Hotel load | Hotel load setup | Enable hotel load | Multi input 20 |  |  |  | 0: Multi input 20, 1: Multi input 21, 2: Multi input 22, 3: Multi input 23
304 | 2823 | Regulation | Regulation > Hotel load | Hotel load range max | Hotel load transducer maximum setting | 0 | 0 | 20000 | kW
1875 | 2831 | Regulation | Regulation > Droop deadband | Droop DB over f | Droop/VSG deadband region for frequencies above nom f in Hz | 0 | 0 | 5 | Hz
1876 | 2832 | Regulation | Regulation > Droop deadband | Droop DB under f | Droop/VSG deadband region for frequencies below nom f in Hz | 0 | 0 | 5 | Hz
1877 | 2833 | Regulation | Regulation > Droop deadband | Droop DB over U | Droop/VSG deadband region for voltages above nom U in % of nom U | 0 | 0 | 10 | %
1878 | 2834 | Regulation | Regulation > Droop deadband | Droop DB under U | Droop/VSG deadband region for voltages below nom U in % of nom U | 0 | 0 | 10 | %
591 | 2900 | Regulation | Regulation > Frequency ramp limit | Over freq. ramp lim | If the measured frequency exceeds this setpoint then ramp down will be skipped | 0 | 0 | 5 | %
592 | 2910 | Regulation | Regulation > Frequency ramp limit | Under freq. ramp lim | If the measured frequency exceeds this setpoint then ramp up will be skipped | 0 | 0 | 5 | %
236 | 3490 | Digital In | I/O settings > Inputs > Digital input | Emergency STOP | Setup of digital input for emergency stop (terminal 4) | [5 empty] | 0 | 0 | 600 |  |  | Shutdown
1722 | 3570 | Digital In | Functions > M-Logic alarms > M-Logic alarm 01 | M-Logic alarm 01 | M-Logic alarm 1 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1723 | 3580 | Digital In | Functions > M-Logic alarms > M-Logic alarm 02 | M-Logic alarm 02 | M-Logic alarm 2 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1724 | 3590 | Digital In | Functions > M-Logic alarms > M-Logic alarm 03 | M-Logic alarm 03 | M-Logic alarm 3 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1725 | 3600 | Digital In | Functions > M-Logic alarms > M-Logic alarm 04 | M-Logic alarm 04 | M-Logic alarm 4 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1726 | 3610 | Digital In | Functions > M-Logic alarms > M-Logic alarm 05 | M-Logic alarm 05 | M-Logic alarm 5 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1824 | 3621 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 1 | M-Logic ext al 1 | Range selection for extended timer alarm 1 | Minute(s) - auto reset |  |  |  | 0: Minute(s) - manual reset, 1: Hour(s) - manual reset, 2: Day(s) - manual reset, 3: Minute(s) - auto reset, 4: Hour(s) - auto reset, 5: Day(s) - auto reset
1828 | 3622 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 1 | M-Logic ext al 1 | Extended timer alarm 1 setup | 50 | 1 | 3200 | [7 empty] | Warning
1825 | 3631 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 2 | M-Logic ext al 2 | Range selection for extended timer alarm 2 | Minute(s) - auto reset |  |  |  | 0: Minute(s) - manual reset, 1: Hour(s) - manual reset, 2: Day(s) - manual reset, 3: Minute(s) - auto reset, 4: Hour(s) - auto reset, 5: Day(s) - auto reset
1829 | 3632 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 2 | M-Logic ext al 2 | Extended timer alarm 2 setup | 50 | 1 | 3200 | [7 empty] | Warning
1826 | 3641 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 3 | M-Logic ext al 3 | Range selection for extended timer alarm 3 | Minute(s) - auto reset |  |  |  | 0: Minute(s) - manual reset, 1: Hour(s) - manual reset, 2: Day(s) - manual reset, 3: Minute(s) - auto reset, 4: Hour(s) - auto reset, 5: Day(s) - auto reset
1830 | 3642 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 3 | M-Logic ext al 3 | Extended timer alarm 3 setup | 50 | 1 | 3200 | [7 empty] | Warning
1827 | 3651 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 4 | M-Logic ext al 4 | Range selection for extended timer alarm 4 | Minute(s) - auto reset |  |  |  | 0: Minute(s) - manual reset, 1: Hour(s) - manual reset, 2: Day(s) - manual reset, 3: Minute(s) - auto reset, 4: Hour(s) - auto reset, 5: Day(s) - auto reset
1831 | 3652 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 4 | M-Logic ext al 4 | Extended timer alarm 4 setup | 50 | 1 | 3200 | [7 empty] | Warning
1853 | 3660 | Digital In | Functions > M-Logic alarms > M-Logic alarm 10 | M-Logic alarm 10 | M-Logic alarm 10 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1854 | 3670 | Digital In | Functions > M-Logic alarms > M-Logic alarm 11 | M-Logic alarm 11 | M-Logic alarm 11 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1855 | 3680 | Digital In | Functions > M-Logic alarms > M-Logic alarm 12 | M-Logic alarm 12 | M-Logic alarm 12 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1856 | 3690 | Digital In | Functions > M-Logic alarms > M-Logic alarm 13 | M-Logic alarm 13 | M-Logic alarm 13 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1857 | 3700 | Digital In | Functions > M-Logic alarms > M-Logic alarm 14 | M-Logic alarm 14 | M-Logic alarm 14 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1482 | 4601 | Analogue In | Functions > Delta alarms > Set 1 | Delta ana1 InpA | Input for A for analogue delta (A-B) alarm 1 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 95: Voltage DC 0.1V, 96: SOC, 102: ESS frequency, 103: ESS L-L voltage, 104: ESS actual P pct., 105: ESS actual Q pct., 110: Voltage DC 1V
1483 | 4602 | Analogue In | Functions > Delta alarms > Set 1 | Delta ana1 InpB | Input for B for analogue delta (A-B) alarm 1 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 95: Voltage DC 0.1V, 96: SOC, 102: ESS frequency, 103: ESS L-L voltage, 104: ESS actual P pct., 105: ESS actual Q pct., 110: Voltage DC 1V
1484 | 4603 | Analogue In | Functions > Delta alarms > Set 2 | Delta ana2 InpA | Input for A for analogue delta (A-B) alarm 2 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 95: Voltage DC 0.1V, 96: SOC, 102: ESS frequency, 103: ESS L-L voltage, 104: ESS actual P pct., 105: ESS actual Q pct., 110: Voltage DC 1V
1485 | 4604 | Analogue In | Functions > Delta alarms > Set 2 | Delta ana2 InpB | Input for B for analogue delta (A-B) alarm 2 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 95: Voltage DC 0.1V, 96: SOC, 102: ESS frequency, 103: ESS L-L voltage, 104: ESS actual P pct., 105: ESS actual Q pct., 110: Voltage DC 1V
1486 | 4605 | Analogue In | Functions > Delta alarms > Set 3 | Delta ana3 InpA | Input for A for analogue delta (A-B) alarm 3 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 95: Voltage DC 0.1V, 96: SOC, 102: ESS frequency, 103: ESS L-L voltage, 104: ESS actual P pct., 105: ESS actual Q pct., 110: Voltage DC 1V
1487 | 4606 | Analogue In | Functions > Delta alarms > Set 3 | Delta ana3 InpB | Input for B for analogue delta (A-B) alarm 3 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 95: Voltage DC 0.1V, 96: SOC, 102: ESS frequency, 103: ESS L-L voltage, 104: ESS actual P pct., 105: ESS actual Q pct., 110: Voltage DC 1V
1488 | 4610 | Analogue In | Functions > Delta alarms > Set 1 | Delta ana1 1 | Delta analogue alarm 1 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1489 | 4620 | Analogue In | Functions > Delta alarms > Set 1 | Delta ana1 2 | Delta analogue alarm 1 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1490 | 4630 | Analogue In | Functions > Delta alarms > Set 2 | Delta ana2 1 | Delta analogue alarm 2 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1491 | 4640 | Analogue In | Functions > Delta alarms > Set 2 | Delta ana2 2 | Delta analogue alarm 2 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1492 | 4650 | Analogue In | Functions > Delta alarms > Set 3 | Delta ana3 1 | Delta analogue alarm 3 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1493 | 4660 | Analogue In | Functions > Delta alarms > Set 3 | Delta ana3 2 | Delta analogue alarm 3 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1678 | 4671 | Analogue In | Functions > Delta alarms > Set 4 | Delta ana4 InpA | Input for A for analogue delta (A-B) alarm 4 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 95: Voltage DC 0.1V, 96: SOC, 102: ESS frequency, 103: ESS L-L voltage, 104: ESS actual P pct., 105: ESS actual Q pct., 110: Voltage DC 1V
1679 | 4672 | Analogue In | Functions > Delta alarms > Set 4 | Delta ana4 InpB | Input for B for analogue delta (A-B) alarm 4 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 95: Voltage DC 0.1V, 96: SOC, 102: ESS frequency, 103: ESS L-L voltage, 104: ESS actual P pct., 105: ESS actual Q pct., 110: Voltage DC 1V
1680 | 4673 | Analogue In | Functions > Delta alarms > Set 5 | Delta ana5 InpA | Input for A for analogue delta (A-B) alarm 5 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 95: Voltage DC 0.1V, 96: SOC, 102: ESS frequency, 103: ESS L-L voltage, 104: ESS actual P pct., 105: ESS actual Q pct., 110: Voltage DC 1V
1681 | 4674 | Analogue In | Functions > Delta alarms > Set 5 | Delta ana5 InpB | Input for B for analogue delta (A-B) alarm 5 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 95: Voltage DC 0.1V, 96: SOC, 102: ESS frequency, 103: ESS L-L voltage, 104: ESS actual P pct., 105: ESS actual Q pct., 110: Voltage DC 1V
1682 | 4675 | Analogue In | Functions > Delta alarms > Set 6 | Delta ana6 InpA | Input for A for analogue delta (A-B) alarm 6 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 95: Voltage DC 0.1V, 96: SOC, 102: ESS frequency, 103: ESS L-L voltage, 104: ESS actual P pct., 105: ESS actual Q pct., 110: Voltage DC 1V
1683 | 4676 | Analogue In | Functions > Delta alarms > Set 6 | Delta ana6 InpB | Input for B for analogue delta (A-B) alarm 6 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 95: Voltage DC 0.1V, 96: SOC, 102: ESS frequency, 103: ESS L-L voltage, 104: ESS actual P pct., 105: ESS actual Q pct., 110: Voltage DC 1V
1684 | 4680 | Analogue In | Functions > Delta alarms > Set 4 | Delta ana4 1 | Delta analogue alarm 4 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1685 | 4690 | Analogue In | Functions > Delta alarms > Set 4 | Delta ana4 2 | Delta analogue alarm 4 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1686 | 4700 | Analogue In | Functions > Delta alarms > Set 5 | Delta ana5 1 | Delta analogue alarm 5 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1687 | 4710 | Analogue In | Functions > Delta alarms > Set 5 | Delta ana5 2 | Delta analogue alarm 5 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1688 | 4720 | Analogue In | Functions > Delta alarms > Set 6 | Delta ana6 1 | Delta analogue alarm 6 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1689 | 4730 | Analogue In | Functions > Delta alarms > Set 6 | Delta ana6 2 | Delta analogue alarm 6 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
315 | 4960 | Analogue In | AC configuration and protections > Battery/Aux supply > Alarms | U< aux. term. 1 | Low supply voltage (terminals 1 and 2) | 18 | 8 | 32 | V |  | 10 | 0 | 9990 |  |  | Warning
316 | 4970 | Analogue In | AC configuration and protections > Battery/Aux supply > Alarms | U> aux. term. 1 | High supply voltage (terminals 1 and 2) | 30 | 12 | 36 | V |  | 10 | 0 | 9990 |  |  | Warning
245 | 5693 | Outputs | I/O settings > Outputs > Transducer > kW > P output current | P ref Output type | Active power reference transducer output type | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
251 | 5694 | Outputs | I/O settings > Outputs > Transducer > kW > P output current | P ref Output max | Transducer output maximum scale for ESS active power ref. | 500 | 0 | 20000 | kW
248 | 5695 | Outputs | I/O settings > Outputs > Transducer > kW > P output current | P ref Output min | Transducer output minimum scale for ESS active power ref. | 0 | -9999 | 20000 | kW
352 | 5802 | Outputs | I/O settings > Outputs > Transducer > Output 52 limits | AOUT 52 Limits | Minimum limit for analogue output 52 | -10 | -10.5 | 5 | V
353 | 5803 | Outputs | I/O settings > Outputs > Transducer > Output 52 limits | AOUT 52 Limits | Maximum limit for analogue output 52 | 10 | -5 | 10.5 | V
354 | 5812 | Outputs | I/O settings > Outputs > Transducer > Output 55 limits | AOUT 55 Limits | Minimum limit for analogue output 55 | -10 | -10.5 | 5 | V
355 | 5813 | Outputs | I/O settings > Outputs > Transducer > Output 55 limits | AOUT 55 Limits | Maximum limit for analogue output 55 | 10 | -5 | 10.5 | V
356 | 5823 | Outputs | I/O settings > Outputs > Transducer > kW > P output actual | P1 Output type | Power transducer output type | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
391 | 5824 | Outputs | I/O settings > Outputs > Transducer > kW > P output actual | P1 Output max | Transducer output maximum scale for ESS active power 1 | 500 | 0 | 20000 | kW
374 | 5825 | Outputs | I/O settings > Outputs > Transducer > kW > P output actual | P1 Output min | Transducer output minimum scale for ESS active power 1 | 0 | -9999 | 20000 | kW
359 | 5853 | Outputs | I/O settings > Outputs > Transducer > kVA | S Output type | Apparent power transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
394 | 5854 | Outputs | I/O settings > Outputs > Transducer > kVA | S Output max | Transducer output maximum scale for ESS apparent power | 600 | 0 | 20000 | kVA
377 | 5855 | Outputs | I/O settings > Outputs > Transducer > kVA | S Output min | Transducer output minimum scale for ESS apparent power | 0 | 0 | 20000 | kVA
360 | 5863 | Outputs | I/O settings > Outputs > Transducer > kvar | Q Output type | Reactive power transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
395 | 5864 | Outputs | I/O settings > Outputs > Transducer > kvar | Q Output max | Transducer output maximum scale for ESS reactive power | 400 | 0 | 16000 | kvar
378 | 5865 | Outputs | I/O settings > Outputs > Transducer > kvar | Q Output min | Transducer output minimum scale for ESS reactive power | 0 | -8000 | 16000 | kvar
361 | 5873 | Outputs | I/O settings > Outputs > Transducer > Cos phi | PF Output type | Power factor transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
396 | 5874 | Outputs | I/O settings > Outputs > Transducer > Cos phi | PF Output max | Transducer output maximum scale for the power factor | 0.8 | 0.5 | 0.99 | PF
379 | 5875 | Outputs | I/O settings > Outputs > Transducer > Cos phi | PF Output min | Transducer output minimum scale for the power factor | -0.8 | -0.99 | -0.5 | PF
362 | 5883 | Outputs | I/O settings > Outputs > Transducer > ESS Hz | f Output type | ESS frequency transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
397 | 5884 | Outputs | I/O settings > Outputs > Transducer > ESS Hz | f Output max | Transducer output maximum scale for ESS frequency | 55 | 0 | 70 | Hz
380 | 5885 | Outputs | I/O settings > Outputs > Transducer > ESS Hz | f Output min | Transducer output minimum scale for ESS frequency | 45 | 0 | 70 | Hz
363 | 5893 | Outputs | I/O settings > Outputs > Transducer > ESS voltage | U Output type | ESS voltage transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
398 | 5894 | Outputs | I/O settings > Outputs > Transducer > ESS voltage | U Output max | Transducer output maximum scale for ESS voltage | 500 | 0 | 28000 | V
381 | 5895 | Outputs | I/O settings > Outputs > Transducer > ESS voltage | U Output min | Transducer output minimum scale for ESS voltage | 0 | 0 | 28000 | V
364 | 5903 | Outputs | I/O settings > Outputs > Transducer > Ampere | I Output type | Current transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
399 | 5904 | Outputs | I/O settings > Outputs > Transducer > Ampere | I Output max | Transducer output maximum scale for current | 1000 | 0 | 9000 | A
382 | 5905 | Outputs | I/O settings > Outputs > Transducer > Ampere | I Output min | Transducer output minimum scale for current | 0 | 0 | 9000 | A
365 | 5913 | Outputs | I/O settings > Outputs > Transducer > Busbar voltage | U BB Output type | Busbar voltage transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
400 | 5914 | Outputs | I/O settings > Outputs > Transducer > Busbar voltage | U BB Output max | Transducer output maximum scale for busbar voltage | 500 | 0 | 28000 | V
383 | 5915 | Outputs | I/O settings > Outputs > Transducer > Busbar voltage | U BB Output min | Transducer output minimum scale for busbar voltage | 0 | 0 | 28000 | V
366 | 5923 | Outputs | I/O settings > Outputs > Transducer > Busbar Hz | f BB Output type | Busbar frequency transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
401 | 5924 | Outputs | I/O settings > Outputs > Transducer > Busbar Hz | f BB Output max | Transducer output maximum scale for busbar frequency | 55 | 0 | 70 | Hz
384 | 5925 | Outputs | I/O settings > Outputs > Transducer > Busbar Hz | f BB Output min | Transducer output minimum scale for busbar frequency | 45 | 0 | 70 | Hz
367 | 5933 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 20 | Inp. 20 Output type | Transducer output signal for Multi-input 20 | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
402 | 5934 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 20 | Inp. 20 Output max | Transducer output maximum scale for multi input 20 | 500 | -28000 | 28000
385 | 5935 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 20 | Inp. 20 Output min | Transducer output minimum scale for multi input 20 | 0 | -28000 | 28000
368 | 5943 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 21 | Inp. 21 Output type | Transducer output signal for Multi-input 21 | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
403 | 5944 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 21 | Inp. 21 Output max | Transducer output maximum scale for multi input 21 | 500 | -28000 | 28000
386 | 5945 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 21 | Inp. 21 Output min | Transducer output minimum scale for multi input 21 | 0 | -28000 | 28000
369 | 5953 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 22 | Inp. 22 Output type | Transducer output signal for Multi-input 22 | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
404 | 5954 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 22 | Inp. 22 Output max | Transducer output maximum scale for multi input 22 | 500 | -28000 | 28000
387 | 5955 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 22 | Inp. 22 Output min | Transducer output minimum scale for multi input 22 | 0 | -28000 | 28000
407 | 6001 | General | Basic settings > Nominal settings > Frequency | Nom. f 1 | Nominal ESS frequency set point 1 | 50 | 48 | 62 | Hz
408 | 6002 | General | Basic settings > Nominal settings > Power > 3 phase nominal | Nom. P 1 | Nominal ESS power set point 1 | 480 | 10 | 20000 | kW
409 | 6003 | General | Basic settings > Nominal settings > Current > 3 phase nominal | Nom. I 1 | Nominal ESS current set point 1 | 867 | 0 | 9000 | A
410 | 6004 | General | Basic settings > Nominal settings > Voltage > ESS nominal U | Nom. U 1 | Nominal ESS voltage set point 1 | 400 | 100 | 25000 | V
596 | 6005 | General | Basic settings > Nominal settings > Power > 3 phase nominal | Nom. Q 1 | Nominal ESS reactive power set point 1 | 480 | 10 | 20000 | kvar
742 | 6006 | General | Basic settings > Nominal settings > Power > 3 phase nominal | Nom. S 1 | Nominal ES apparent power set point 1 | 480 | 10 | 20000 | kVA
412 | 6007 | General | Alternative configuration > ESS nominal settings > Nominal set selection | Enable nom. set | Selection of nominal setting to be used | Nominal setting 1 |  |  |  | 0: Nominal setting 1, 1: Nominal setting 2, 2: Nominal setting 3, 3: Nominal setting 4
1460 | 6008 | General | Basic settings > Nominal settings > Current > 4th CT nominal | Nom. I E/N/M 1 | Nom I E/N/M 1 (Nominal current Earth/Neutral/Mains set point 1) | 867 | 0 | 9000 | A
413 | 6011 | General | Alternative configuration > ESS nominal settings > Nominal settings 2 | Nom. f 2 | Nominal ESS frequency set point 2 | 50 | 48 | 62 | Hz
414 | 6012 | General | Alternative configuration > ESS nominal settings > Nominal settings 2 | Nom. P 2 | Nominal ESS power set point 2 | 230 | 10 | 20000 | kW
415 | 6013 | General | Alternative configuration > ESS nominal settings > Nominal settings 2 | Nom. I 2 | Nominal ESS current set point 2 | 345 | 0 | 9000 | A
416 | 6014 | General | Alternative configuration > ESS nominal settings > Nominal settings 2 | Nom. U 2 | Nominal ESS voltage set point 2 | 400 | 100 | 25000 | V
597 | 6015 | General | Alternative configuration > ESS nominal settings > Nominal settings 2 | Nom. Q 2 | Nominal ESS reactive power set point 2 | 230 | 10 | 20000 | kvar
743 | 6016 | General | Alternative configuration > ESS nominal settings > Nominal settings 2 | Nom. S 2 | Nominal ES apparent power set point 2 | 230 | 10 | 20000 | kVA
1461 | 6017 | General | Alternative configuration > ESS nominal settings > Nominal settings 2 | Nom. I E/N/M 2 | Nom I E/N/M 2 (Nominal current Earth/Neutral/Mains set point 2) | 867 | 0 | 9000 | A
418 | 6021 | General | Alternative configuration > ESS nominal settings > Nominal settings 3 | Nom. f 3 | Nominal ESS frequency set point 3 | 60 | 48 | 62 | Hz
419 | 6022 | General | Alternative configuration > ESS nominal settings > Nominal settings 3 | Nom. P 3 | Nominal ESS power set point 3 | 230 | 10 | 20000 | kW
420 | 6023 | General | Alternative configuration > ESS nominal settings > Nominal settings 3 | Nom. I 3 | Nominal ESS current set point 3 | 345 | 0 | 9000 | A
421 | 6024 | General | Alternative configuration > ESS nominal settings > Nominal settings 3 | Nom. U 3 | Nominal ESS voltage set point 3 | 400 | 100 | 25000 | V
598 | 6025 | General | Alternative configuration > ESS nominal settings > Nominal settings 3 | Nom. Q 3 | Nominal ESS reactive power set point 3 | 230 | 10 | 20000 | kvar
744 | 6026 | General | Alternative configuration > ESS nominal settings > Nominal settings 3 | Nom. S 3 | Nominal ES apparent power set point 3 | 230 | 10 | 20000 | kVA
1462 | 6027 | General | Alternative configuration > ESS nominal settings > Nominal settings 3 | Nom. I E/N/M 3 | Nom I E/N/M 3 (Nominal current Earth/Neutral/Mains set point 3) | 867 | 0 | 9000 | A
423 | 6031 | General | Alternative configuration > ESS nominal settings > Nominal settings 4 | Nom. f 4 | Nominal ESS frequency set point 4 | 60 | 48 | 62 | Hz
424 | 6032 | General | Alternative configuration > ESS nominal settings > Nominal settings 4 | Nom. P 4 | Nominal ESS power set point 4 | 230 | 10 | 20000 | kW
425 | 6033 | General | Alternative configuration > ESS nominal settings > Nominal settings 4 | Nom. I 4 | Nominal ESS current set point 4 | 345 | 0 | 9000 | A
426 | 6034 | General | Alternative configuration > ESS nominal settings > Nominal settings 4 | Nom. U 4 | Nominal ESS voltage set point 4 | 400 | 100 | 25000 | V
599 | 6035 | General | Alternative configuration > ESS nominal settings > Nominal settings 4 | Nom. Q 4 | Nominal ESS reactive power set point 4 | 230 | 10 | 20000 | kvar
745 | 6036 | General | Alternative configuration > ESS nominal settings > Nominal settings 4 | Nom. S 4 | Nominal ES apparent power set point 4 | 230 | 10 | 20000 | kVA
1463 | 6037 | General | Alternative configuration > ESS nominal settings > Nominal settings 4 | Nom. I E/N/M 4 | Nom I E/N/M 4 (Nominal current Earth/Neutral/Mains set point 4) | 867 | 0 | 9000 | A
428 | 6041 | General | Basic settings > Measurement setup > Voltage transformer > ESS VT | ES primary U | ESS voltage transformer value primary side | 400 | 100 | 25000 | V
429 | 6042 | General | Basic settings > Measurement setup > Voltage transformer > ESS VT | ES secondary U | ESS voltage transformer value secondary side | 400 | 100 | 690 | V
430 | 6043 | General | Basic settings > Measurement setup > Current transformer > 3 phase CT | ES Primary I | ESS current transformer value primary side | 1000 | 5 | 9000 | A
431 | 6044 | General | Basic settings > Measurement setup > Current transformer > 3 phase CT | ES Secondary I | ESS current transformer value secondary side | 1A |  |  |  | 1: 1A, 5: 5A
1383 | 6045 | General | Basic settings > Measurement setup > Current transformer > 4th CT | E/N/M primary I | E/N/M Primary I (Earth/Neutral/Mains current transformer value Primary side) | 1000 | 5 | 9000 | A
1384 | 6046 | General | Basic settings > Measurement setup > Current transformer > 4th CT | E/N/M secondary I | E/N/M Secondary I (Earth/Neutral/Mains current transformer value secondary side) | 1A |  |  |  | 1: 1A, 5: 5A
432 | 6051 | General | Basic settings > Measurement setup > Voltage transformer > Busbar VT | BB primary U 1 | Busbar voltage transformer value primary side set point 1 | 400 | 100 | 25000 | V
433 | 6052 | General | Basic settings > Measurement setup > Voltage transformer > Busbar VT | BB second. U 1 | Busbar voltage transformer value secondary side set point 1 | 400 | 100 | 690 | V
1326 | 6053 | General | Basic settings > Nominal settings > Voltage > Busbar nominal U | BB nominal U 1 | Nominal busbar voltage set point 1 | 400 | 100 | 25000 | V
1582 | 6054 | General | Alternative configuration > Busbar nominal settings > Nominal set selection | Bus nom. set | Selection of nominal busbar setting to be used | Parameter set 1 |  |  |  | 0: Parameter set 1, 1: Parameter set 2, 2: BB Unom = ES Unom
1664 | 6055 | General | Basic settings > Nominal settings > Power > 4th CT nominal | 4th CT nom. P 1 | 4th CT Nominal power set point 1 | 480 | 10 | 9000 | kW
1579 | 6061 | General | Alternative configuration > Busbar nominal settings > Nominal settings 2 | BB primary U 2 | Busbar voltage transformer value primary side set point 2 | 400 | 100 | 25000 | V
1580 | 6062 | General | Alternative configuration > Busbar nominal settings > Nominal settings 2 | BB second. U 2 | Busbar voltage transformer value secondary side set point 2 | 400 | 100 | 690 | V
1578 | 6063 | General | Alternative configuration > Busbar nominal settings > Nominal settings 2 | BB nominal U 2 | Nominal busbar voltage set point 2 | 400 | 100 | 25000 | V
1665 | 6064 | General | Alternative configuration > Busbar nominal settings > Nominal settings 2 | 4th CT nom. P 2 | 4th CT Nominal power set point 2 | 230 | 10 | 9000 | kW
435 | 6071 | General | Basic settings > Application type > Plant type > Plant mode | Operation mode | ES operation mode | Power management |  |  |  | 0: Island operation, 1: Auto. Mains Failure, 2: Peak shaving, 3: Fixed power, 4: Mains Power Export, 6: Power management
436 | 6081 | General | Basic settings > Controller settings > Language | Language | Language selection | English |  |  |  | 0: English, 1: Language 1, 2: Language 2, 3: Language 3, 4: Language 4, 5: Language 5, 6: Language 6, 7: Language 7, 8: Language 8, 9: Language 9, 10: Language 10
486 | 6082 | General | Basic settings > Controller settings > Display | LED mimic | Change LED mimic scheme | Standard |  |  |  | 1: Standard, 3: Guided
485 | 6084 | General | Basic settings > Controller settings > Display | LED colors | Change LED color scheme | LED Color Scheme 1 |  |  |  | 0: LED Color Scheme 1, 1: LED Color Scheme 2
449 | 6130 | General | Functions > Alarm horn timer | Alarm horn | Setup of the Alarm Horn timer | [5 empty] | 200 | 0 | 9900
452 | 6160 | General | Regulation > Run detection | Run status | Setup of the Run Status output | [5 empty] | 50 | 0 | 3000
469 | 6231 | General | Breakers > ES breaker > Breaker configuration | ESB close delay | ESB close delay at blackout | [5 empty] | 20 | 0 | 300
518 | 6490 | General | Basic settings > Summer/Winter Time | Summer/Winter time | Enable switch to summer time
522 | 6540 | General | Functions > Not in Auto | Not in AUTO | Alarm for unit not in auto | [5 empty] | 3000 | 100 | 9000 |  |  | Warning
1912 | 6951 | General | Functions > Command timer > Command timer 1 | Command timer 1 week | Select which week(s) in month command timer 1 start/stop is active | All weeks in month |  |  |  | 0: All weeks in month, 1: First week (1 - 7), 2: Second week (8 - 14), 3: Third week (15 - 21), 4: Fourth week (22 - 28)
1913 | 6952 | General | Functions > Command timer > Command timer 2 | Command timer 2 week | Select which week(s) in month command timer 2 start/stop is active | All weeks in month |  |  |  | 0: All weeks in month, 1: First week (1 - 7), 2: Second week (8 - 14), 3: Third week (15 - 21), 4: Fourth week (22 - 28)
1914 | 6953 | General | Functions > Command timer > Command timer 3 | Command timer 3 week | Select which week(s) in month command timer 3 start/stop is active | All weeks in month |  |  |  | 0: All weeks in month, 1: First week (1 - 7), 2: Second week (8 - 14), 3: Third week (15 - 21), 4: Fourth week (22 - 28)
1915 | 6954 | General | Functions > Command timer > Command timer 4 | Command timer 4 week | Select which week(s) in month command timer 4 start/stop is active | All weeks in month |  |  |  | 0: All weeks in month, 1: First week (1 - 7), 2: Second week (8 - 14), 3: Third week (15 - 21), 4: Fourth week (22 - 28)
701 | 6961 | General | Functions > Command timer > Command timer 1 | Start timer 1 | Setup day(s) for activation of Command timer 1 | OFF |  |  |  | 0: OFF, 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
702 | 6962 | General | Functions > Command timer > Command timer 1 | Start timer 1 | Setup of hour for activation of Command timer 1 | 10 | 0 | 23 | Hours
703 | 6963 | General | Functions > Command timer > Command timer 1 | Start timer 1 | Setup of minute for activation of Command timer 1 | 0 | 0 | 59
705 | 6964 | General | Functions > Command timer > Command timer 1 | Stop timer 1 | Setup day(s) for deactivation of Command timer 1 | MO-TU-WE-TH-FR-SA-SU |  |  |  | 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
706 | 6965 | General | Functions > Command timer > Command timer 1 | Stop timer 1 | Setup of hour for deactivation of Command timer 1 | 10 | 0 | 23 | Hours
707 | 6966 | General | Functions > Command timer > Command timer 1 | Stop timer 1 | Setup of minute for deactivation of Command timer 1 | 0 | 0 | 59
709 | 6971 | General | Functions > Command timer > Command timer 2 | Start timer 2 | Setup day(s) for activation of Command timer 2 | OFF |  |  |  | 0: OFF, 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
710 | 6972 | General | Functions > Command timer > Command timer 2 | Start timer 2 | Setup of hour for activation of Command timer 2 | 10 | 0 | 23 | Hours
711 | 6973 | General | Functions > Command timer > Command timer 2 | Start timer 2 | Setup of minute for activation of Command timer 2 | 0 | 0 | 59
713 | 6974 | General | Functions > Command timer > Command timer 2 | Stop timer 2 | Setup day(s) for deactivation of Command timer 2 | MO-TU-WE-TH-FR-SA-SU |  |  |  | 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
714 | 6975 | General | Functions > Command timer > Command timer 2 | Stop timer 2 | Setup of hour for deactivation of Command timer 2 | 10 | 0 | 23 | Hours
715 | 6976 | General | Functions > Command timer > Command timer 2 | Stop timer 2 | Setup of minute for deactivation of Command timer 2 | 0 | 0 | 59
717 | 6981 | General | Functions > Command timer > Command timer 3 | Start timer 3 | Setup day(s) for activation of Command timer 3 | OFF |  |  |  | 0: OFF, 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
718 | 6982 | General | Functions > Command timer > Command timer 3 | Start timer 3 | Setup of hour for activation of Command timer 3 | 10 | 0 | 23 | Hours
719 | 6983 | General | Functions > Command timer > Command timer 3 | Start timer 3 | Setup of minute for activation of Command timer 3 | 0 | 0 | 59
721 | 6984 | General | Functions > Command timer > Command timer 3 | Stop timer 3 | Setup day(s) for deactivation of Command timer 3 | MO-TU-WE-TH-FR-SA-SU |  |  |  | 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
722 | 6985 | General | Functions > Command timer > Command timer 3 | Stop timer 3 | Setup of hour for deactivation of Command timer 3 | 10 | 0 | 23 | Hours
723 | 6986 | General | Functions > Command timer > Command timer 3 | Stop timer 3 | Setup of minute for deactivation of Command timer 3 | 0 | 0 | 59
725 | 6991 | General | Functions > Command timer > Command timer 4 | Start timer 4 | Setup day(s) for activation of Command timer 4 | OFF |  |  |  | 0: OFF, 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
726 | 6992 | General | Functions > Command timer > Command timer 4 | Start timer 4 | Setup of hour for activation of Command timer 4 | 10 | 0 | 23 | Hours
727 | 6993 | General | Functions > Command timer > Command timer 4 | Start timer 4 | Setup of minute for activation of Command timer 4 | 0 | 0 | 59
729 | 6994 | General | Functions > Command timer > Command timer 4 | Stop timer 4 | Setup day(s) for deactivation of Command timer 4 | MO-TU-WE-TH-FR-SA-SU |  |  |  | 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
730 | 6995 | General | Functions > Command timer > Command timer 4 | Stop timer 4 | Setup of hour for deactivation of Command timer 4 | 10 | 0 | 23 | Hours
731 | 6996 | General | Functions > Command timer > Command timer 4 | Stop timer 4 | Setup of minute for deactivation of Command timer 4 | 0 | 0 | 59
527 | 7001 | Mains | Power set points > Mains Power Export and Peak shaving > Day/Night power set point | Day Setting | Day time setting for peakshaving/mains power export | 750 | -20000 | 20000 | kW
528 | 7002 | Mains | Power set points > Mains Power Export and Peak shaving > Day/Night power set point | Night Setting | Night time setting for peakshaving/mains power export | 1000 | -20000 | 20000 | kW
529 | 7003 | Mains | Basic settings > Measurement setup > Mains transducer settings | Transducer range max | Mains power transducer maximum setting | 0 | 0 | 20000 | kW
530 | 7004 | Mains | Basic settings > Measurement setup > Mains transducer settings | Transducer range min | Mains power transducer minimum setting | 0 | -20000 | 0 | kW
1440 | 7005 | Mains | Basic settings > Measurement setup > Wiring connection > Mains Power measure | Mains power measure | Selection of mains power measuring input | 4th CT power meas (internal) |  |  |  | 0: Multi input 20 (transducer), 1: 4th CT power meas (internal), 4: DEIF Open communication, 5: Power meter communication
1508 | 7006 | Mains | Power set points > Mains Power Export and Peak shaving > Day/Night power set point | MPE/PS scale | Scaling of the PS/MPE reference | 1kW:1kW |  |  |  | 0: 1kW:1kW, 1: 1kW:10kW, 2: 1kW:100kW, 3: 1kW:1000kW
1666 | 7007 | Mains | Basic settings > Measurement setup > Mains transducer settings | Transd. range max Q | Mains reactive power transducer maximum setting | 0 | -20000 | 20000 | kvar
1667 | 7008 | Mains | Basic settings > Measurement setup > Mains transducer settings | Transd. range min Q | Mains reactive power transducer minimum setting | 0 | -20000 | 20000 | kvar
1668 | 7009 | Mains | Basic settings > Measurement setup > Wiring connection > Mains Power measure | Mains Q measure | Selection of mains Q power measuring input | 4th CT power meas (internal) |  |  |  | 0: Multi input 22 (transducer), 1: 4th CT power meas (internal), 4: DEIF Open communication, 5: Power meter communication
531 | 7011 | Mains | Power set points > Mains Power Export and Peak shaving > Day/Night settings | Start Hour | Start hour for peakshaving/mains power export | 8 | 0 | 23
532 | 7012 | Mains | Power set points > Mains Power Export and Peak shaving > Day/Night settings | Start Minute | Start minute for peakshaving/mains power export | 0 | 0 | 59
533 | 7013 | Mains | Power set points > Mains Power Export and Peak shaving > Day/Night settings | Stop Hour | Stop hour for peakshaving/mains power export | 16 | 0 | 23
534 | 7014 | Mains | Power set points > Mains Power Export and Peak shaving > Day/Night settings | Stop Minute | Stop hour for peakshaving/mains power export | 0 | 0 | 59
216 | 7021 | Mains | Basic settings > Measurement setup > Wiring connection > Power measure origin | ESS power meas. | Origin of AC power measurements | ASC measurements |  |  |  | 0: ASC measurements, 1: ESS communication, 2: DEIF open communication, 3: Power meter comm., 4: ASC measurements average
1598 | 7022 | Mains | Basic settings > Measurement setup > Wiring connection > Busbar/ESS measures | BB/ESS V/f meas. | Origin of AC busbar measurements | iE/ASC measurements |  |  |  | 0: iE/ASC measurements, 1: ESS communication
1937 | 7023 | Mains | Basic settings > Measurement setup > Wiring connection > Busbar/ESS measures | V/f from com. fail | BB/ESS Measures from ESS communication failure alarm | [5 empty] | 30 | 0 | 1000 |  |  | Shutdown
929 | 7031 | Mains | Power set points > Q Ref. off-grid | GEN cosphi lim I | Maximum genset cosphi inductive in off-grid operation | 0.8 | 0.1 | 1 | PF
930 | 7032 | Mains | Power set points > Q Ref. off-grid | GEN cosphi lim C | Maximum genset cosphi capacitive in off-grid operation | 1 | 0.1 | 1 | PF
234 | 7033 | Mains | Power set points > Q Ref. off-grid | Q type off-grid | ESS Q reference type in off-grid operation | Off |  |  |  | 0: Off, 1: Q share
642 | 7034 | Mains | Power set points > Q Ref. off-grid | GEN cosphi min I | Use ESS to add Q load to force GEN's to run at minimum specificed inductive power factor in off-grid operation | 1 | 0 | 1 | PF
541 | 7051 | Mains | Power set points > Fixed Power | Fixed Power | Fixed power set point | 500 | -20000 | 20000 | kW
542 | 7052 | Mains | Power set points > Fixed Power | Cosphi ref | Fixed cosphi set point | 0.9 | 0.6 | 1 | PF
1236 | 7053 | Mains | Power set points > Q Ref. grid-tied | Cosphi ref | Inductive or capacitive cos phi regulation | Inductive |  |  |  | 0: Inductive, 1: Capacitive
1370 | 7054 | Mains | Power set points > Q Ref. grid-tied | Contr. sett. Q | Fixed reactive power set point | 500 | -20000 | 20000 | kvar
1299 | 7055 | Mains | Power set points > Q Ref. grid-tied | Q type grid-tie | Q reference type in grid-tied operation | Cosphi superior |  |  |  | 0: Off, 1: Cosphi fixed, 2: Cosphi imp/exp, 3: Cosphi superior, 4: Q fixed, 5: Q imp/exp
1300 | 7056 | Mains | Power set points > Fixed Power | FP scale | Scaling of the FP reference | 1kW:1kW |  |  |  | 0: 1kW:1kW, 1: 1kW:10kW, 2: 1kW:100kW, 3: 1kW:1000kW
543 | 7061 | Mains | Mains > AMF functions > AMF voltage timers | U mains failure | Timer for mains failure voltage detection | [5 empty] | 50 | 5 | 9900
544 | 7062 | Mains | Mains > AMF functions > AMF voltage timers | Mains OK Delay U | Timer for mains voltage ok detection | [5 empty] | 60 | 2 | 9900
545 | 7063 | Mains | Mains > Voltage and frequency limits > Voltage settings | Low Voltage | Set point for mains voltage range low | 90 | 30 | 100 | %
546 | 7064 | Mains | Mains > Voltage and frequency limits > Voltage settings | High Voltage | Set point for mains voltage range high | 110 | 100 | 120 | %
874 | 7065 | Mains | Mains > Voltage and frequency limits > Voltage settings | Unbalance voltage | Mains voltage unbalance setting | 100 | 2 | 100 | %
548 | 7071 | Mains | Mains > AMF functions > AMF frequency timers | f mains failure | Timer for mains failure frequency detection | [5 empty] | 50 | 5 | 9900
549 | 7072 | Mains | Mains > AMF functions > AMF frequency timers | Mains OK Delay f | Timer for mains frequency ok detection | [5 empty] | 60 | 2 | 9900
550 | 7073 | Mains | Mains > Voltage and frequency limits > Frequency settings | Low Frequency | Set point for mains frequency range low | 95 | 80 | 100 | %
551 | 7074 | Mains | Mains > Voltage and frequency limits > Frequency settings | High Frequency | Set point for mains frequency range high | 105 | 100 | 120 | %
552 | 7081 | Mains | Mains > AMF functions > Modeshift | Modeshift | Allow switch to AMF mode | Mode shift off |  |  |  | 0: Mode shift off, 1: Mode shift on
553 | 7082 | Mains | Breakers > Mains breaker > Breaker configuration | MB close delay | MB breaker close delay. | [5 empty] | 5 | 0 | 300
554 | 7083 | Mains | Synchronisation > Mains parallel settings | Back Synchronising | Synchronising ON/OFF
555 | 7084 | Mains | Synchronisation > Mains parallel settings | Sync. to mains | Allow synchronising MB
846 | 7085 | Mains | Breakers > Mains breaker > Breaker configuration | MB Load time | Time needed to charge Mains breaker spring before closing | [5 empty] | 0 | 0 | 300
472 | 7086 | Mains | Breakers > ESS inhibit MB/TB | Inhibit MB/TB open | If enabled the PCS can delay a normal MB or TB open sequence until a certain grid mode is active. This setting will not delay an sequence during a mains failure
174 | 7091 | Mains | Mains > Voltage and frequency limits > Voltage settings | Low Volt. Hyst. | Low voltage mains hysteresis | 0 | 0 | 70 | %
175 | 7092 | Mains | Mains > Voltage and frequency limits > Voltage settings | High Volt Hyst. | High voltage mains hysteresis | 0 | 0 | 20 | %
176 | 7093 | Mains | Mains > Voltage and frequency limits > Frequency settings | Low Freq. Hyst. | Low frequency mains hysteresis | 0 | 0 | 20 | %
177 | 7094 | Mains | Mains > Voltage and frequency limits > Frequency settings | High Freq Hyst. | High frequency mains hysteresis | 0 | 0 | 20 | %
557 | 7501 | Communication | Power set points > External power set point | Comm bus control P | Modbus communication. Power control ON/OFF.
560 | 7502 | Communication | Power set points > External power set point | Comm bus ctrl cosphi | Modbus communication. cosphi control ON/OFF.
561 | 7503 | Communication | Power set points > External power set point | Comm bus control Q | Modbus communication. Reactive power control ON/OFF.
636 | 7504 | Communication | Power set points > External power set point | Comm. bus P Q scale | Sets the scale which the controller accepts external setpoints for percent of nominal P/Q. Parameter 7501 or 7503 must be enabled | 1% |  |  |  | 0: 1%, 1: 0.1%, 2: 0.01%
562 | 7511 | Communication | Communication > RS485 > RS485 1 > Settings | Ext. comm. ID 1 | Configuration of external communication port 1 Modbus Slave ID number | 3 | 1 | 247
563 | 7512 | Communication | Communication > RS485 > RS485 1 > Settings | Ext. comm.speed1 | Configuration of external communication port 1 speed | 9600 Baud |  |  |  | 0: 9600 Baud, 1: 19200 Baud, 2: 38400 Baud, 3: 115200 Baud
565 | 7513 | Communication | Communication > RS485 > RS485 1 > Communication error | Ext comm. error 1 | External communication port 1 supervision | [5 empty] | 100 | 10 | 1000
1099 | 7521 | Communication | Communication > RS485 > RS485 2 > Settings | Ext. comm. ID 2 | Configuration of external communication port 2 Modbus Slave ID number | 3 | 1 | 247
1100 | 7522 | Communication | Communication > RS485 > RS485 2 > Settings | Ext. comm.speed2 | Configuration of external communication port 2 speed | 9600 Baud |  |  |  | 0: 9600 Baud, 1: 19200 Baud, 2: 38400 Baud, 3: 115200 Baud
951 | 7523 | Communication | Communication > RS485 > RS485 2 > Communication error | Ext comm. error 2 | External communication port 2 supervision | [5 empty] | 100 | 10 | 1000
566 | 7531 | Communication | Communication > Power management ID | PM CAN ID | Internal communication ID number | 25 | 25 | 40
567 | 7532 | Communication | Power management > Communication failures | CAN fail mode | Selection of running mode in case of CAN failure. | MANUAL |  |  |  | 0: No reg, 1: MANUAL, 2: No mode change
568 | 7533 | Communication | Power management > Communication failures | Miss. all units | Configuration of CAN failure alarm. All ID's missing. | [10 empty] | Warning
569 | 7534 | Communication | Power management > Communication failures | Fatal CAN error | Configuration of CAN failure alarm. Fatal CAN error. More ID's missing than configured in menu 8800. | [10 empty] | Warning
570 | 7535 | Communication | Power management > Communication failures | Any GEN missing | Configuration of CAN failure alarm. Any ID missing. | [10 empty] | Warning
571 | 7536 | Communication | Power management > Communication failures | Any MAINS miss. | Configuration of CAN failure alarm. Any ID missing. | [10 empty] | Warning
242 | 7541 | Communication | Communication > ESS | ESS comm. intf. | Sets the modbus communication interface for the control telegrams. If Modbus TCP/IP client is chosen it will use the configuration set up from the Network parameters menu. | Modbus RTU client 1 |  |  |  | 0: Modbus RTU client 1, 2: Modbus RTU client 2, 1: Modbus TCP/IP client, 3: CAN port A, 4: CAN port B
749 | 7542 | Communication | Communication > BMS | BMS comm. intf. | Sets the modbus communication interface for the BMS telegrams. If Modbus TCP/IP client is chosen it will use the configuration set up from the Network parameters menu. | Modbus RTU client 1 |  |  |  | 0: Modbus RTU client 1, 2: Modbus RTU client 2, 1: Modbus TCP/IP client, 3: CAN port A, 4: CAN port B
750 | 7543 | Communication | Communication > PDS | PDS comm. intf. | Sets the modbus communication interface for the PDS telegrams. If Modbus TCP/IP client is chosen it will use the configuration set up from the Network parameters menu. | Modbus RTU client 1 |  |  |  | 0: Modbus RTU client 1, 2: Modbus RTU client 2, 1: Modbus TCP/IP client
751 | 7544 | Communication | Communication > Power Meter > Meter comm. settings | Meter comm. intf. | Sets the modbus communication interface for the Power meter telegrams. If Modbus TCP/IP client is chosen it will use the configuration set up from the Network parameters menu. | Modbus RTU client 2 |  |  |  | 0: Modbus RTU client 1, 2: Modbus RTU client 2
197 | 7545 | Communication | Communication > ESS | ESS Modbus ID | Sets the Modbus ID of the servers/PCS. Applies to both modbus TCP/IP and RTU. | 3 | 0 | 247
746 | 7553 | Communication | Communication > RS485 | RTU broadcast ID | If enabled this ID will be used instead of the default broadcast ID 0 for write telegrams | 0 | 0 | 255
198 | 7561 | Communication | Communication > ESS | ESS Modbus prot. | ESS communication protocol | Off |  |  |  | 0: Off, 50: ABB PCS100, 108: Alfen BCU, 47: ATESS Growatt, 51: Ausar MAE v4, 96: CAT BDP 250, 98: CAT BDP 1000, 136: CubEnergy BCU, 77: Danfoss Vacon NXP, 73: DEIF AGC GEN (For test only!), 49: DEIF Generic, 5: DEIF Open, 102: Delta EPCS 1200/1500/1725, 142: Delta PCS 1000, 114: Delta PCS 100HV, 84: Dynapower CPS-1500, 105: Dynapower MPS-125, 119: Enjoy PCS, 81: EPC power, 52: FIMER PVS980-58BC, 135: Faro BCU, 151: FoxESS BESS, 109: Huawei SACU ESS smartlogger, 140: Jinko JKP 1xxxHN-CA PCS, 83: Jinko PCS, 99: Kehua BCS-B-HUD Series, 134: Kehua Tech KC541A, 113: KStar GSE 50-630 PCS, 129: Kubank LEMS BCU, 137: Lithion GB, 72: LS PowerBRiC, 80: MatterEnergy PCS, 88: MEGAREVO MPS, 130: Moura BCU, 139: Nari PCS-9567AN, 122: Nomad BCU, 106: Northvolt VMS, 91: Oztek OZpcs-RS40, 100: Pixii PowerShaper, 149: PowerElectronics PCS, 86: Sicon PCS, 133: Sicon VSG, 45: SinExcel PWS1, 92: SinExcel PWS2 30K, 104: SinExcel 30P, 116: Sinosoar SP100H, 150: Solax ESS trene X3, 138: Sungiga SCU, 141: Sungrow EMS300, 70: Sungrow LC100 Utility LFP, 121: Sungrow LC100 Utility LFP v1.12, 60: Sungrow STXXXCP-50HV, 101: Sungrow Powerstack ST, 103: Sungrow LC200, 127: Sungrow LC200 DPS, 117: Sungrow LC200 Multi PCS, 126: Sungrow LC200 Single PCS, 132: Sungrow LC300, 55: TRUMPF TruConvert ACDC, 54: TRUMPF TruConvert DCDC, 57: Vertiv Custom, 125: WEG BIW610 PCS, 89: InPower PCS, 131: YUNT PCS
1317 | 7562 | Communication |  | ESS CAN prot. | ESS CAN communication protocols | OFF |  |  |  | 0: OFF, 1: EODev
1815 | 7563 | Communication |  | ESS CAN baudrate | Baudrate for ESS CAN protocol | 250k |  |  |  | 0: 125k, 1: 250k, 2: 500k
199 | 7564 | Communication | Communication > ESS | RTU tx write type | Selection between unicast or broadcast control topology | Unicast |  |  |  | 0: Unicast, 1: Broadcast
200 | 7565 | Communication | Communication > ESS | Tx min. interval | Minimum time delay between telegrams transmitted to inverters. | [5 empty] | 5 | 1 | 100
201 | 7566 | Communication | Communication > ESS | Tx write fnc. | Selection between function codes to use in write register telegrams for inverter communication | Multiple register 0x10 |  |  |  | 0: Single register 0x06, 1: Multiple register 0x10
203 | 7570 | Communication | Communication > ESS | ESS comm. error | ESS Communication error | [5 empty] | 30 | 0 | 1000 |  |  | Warning
204 | 7580 | Communication | Communication > ESS | ESS warning | ESS warning | [5 empty] | 0 | 0 | 1000 |  |  | Warning
205 | 7590 | Communication | Communication > ESS | ESS shutdown | ESS shutdown | [5 empty] | 0 | 0 | 1000 |  |  | Shutdown
88 | 7610 | Communication | Communication > BMS | BMS warning | BMS Warning | [5 empty] | 0 | 0 | 1000 |  |  | Warning
89 | 7620 | Communication | Communication > BMS | BMS shutdown | BMS Shutdown | [5 empty] | 0 | 0 | 1000 |  |  | Shutdown
1559 | 7681 | Communication | Communication > BMS | BMS Modbus ID | Battery management system communication ID | 3 | 1 | 247
1583 | 7682 | Communication | Communication > BMS | BMS Modbus prot. | Battery management system Protocol | OFF |  |  |  | 0: OFF, 7: Allsparkpower BMS, 30: BMSer Single Cluster, 13: BMSer Technology V1, 41: BMSer v2.3.10, 28: BYD Cube Pro, 6: CATL air cooled BMS, 15: CATL EnerOne BMS, 37: CATL EnerOne Plus BMS, 8: CellCheck CM BMS, 11: Coslight ESMU BMS, 4: DEIF Generic, 26: Enervenue BMS, 9: EOS Energy Block, 32: EVE MBMU BMS, 14: Gold BMS, 27: Gotion BMS, 39: Greatpower BMS, 16: GTZKNE FX34 BMS, 10: GTZKNE WK-BMS-C, 21: HagalOcean PD-003V2 BMS, 19: HoyCore HC01CUBE, 29: Huasu S02/03 BMS, 20: Huasu S04 BMS, 31: Huasu S06 BMS, 33: Huasu Single Cluster, 40: Jinko Utility BMS, 23: KGooer BMS, 35: Lanli Tech BMS, 25: Lithium Valley BMS, 12: Narada BMS V1 w Ctrl, 17: Polarium BMS, 5: PowerCube H1/H2, 38: Qualtech BMS, 24: Sunwoda Main BCMU, 22: Sunwoda BCMU, 18: SYL G. S. Air cooled, 36: SYL G. S. Liq cooled, 34: WEG BMS
1318 | 7683 | Communication |  | BMS CAN prot. | BMS CAN communication protocols | OFF |  |  |  | 0: OFF, 1: Volvo Penta BE-C-03-GE
1816 | 7684 | Communication |  | BMS CAN baudrate | Baudrate for BMS CAN protocol | 250k |  |  |  | 0: 125k, 1: 250k, 2: 500k
1584 | 7690 | Communication | Communication > BMS | BMS comm. error | Battery management system communication error | [5 empty] | 30 | 0 | 1000 |  |  | Warning
1113 | 7701 | Communication | Communication > Power Meter > GEN Meter | GEN meter ID | Configuration of external communication GEN power meter ID number | 3 | 1 | 247
1117 | 7702 | Communication | Communication > Power Meter > ESS Meter | ESS meter ID | Configuration of external communication ES power meter ID number | 3 | 1 | 247
1116 | 7703 | Communication | Communication > Power Meter > Mains Meter | Mains meter ID | Configuration of external communication Mains power meter ID number | 3 | 1 | 247
1119 | 7721 | Communication | Communication > Power Meter > GEN Meter | GEN meter prot. | Configuration of external communication GEN power meter protocol | OFF |  |  |  | 0: OFF, 1: DEIF MIB7000C, 2: DEIF MIC4000, 3: DEIF MIC-2, 4: DEIF MTR-3/4, 5: Schneider iEM3000, 6: Schneider EM6400, 7: Socomec Multis L40, 8: Schneider PM5560, 9: Socomec Diris A40, 10: EDS-MMCT3-E-C, 11: Gossen, 12: EDMI, 13: DEIF Genset Control, 14: APS PMU-100, 15: ABB SACE Emax 2, 16: ABB A43/A44, 17: Accuvim-L, 18: Secure Elite 100/300 series, 19: DSE 8xxx, 7xxx, 6xxx and 4xxx, 20: Cummins PC 3.x/PCC 3300, 21: DEIF MIB8000, 22: Eastron Smart X96, 23: Eastron SDM630MCT, 24: CAT EMCP 4, 25: Secure Elite 440/500 series, 26: Acrel ADL, 27: Eastron Smart X96 with DI, 28: Configurable power meter, 29: Kohler APM403, 30: ComAp IntelliGen 500 g2
1120 | 7722 | Communication | Communication > Power Meter > GEN Meter | GEN nbr. nodes | Configuration of external communication GEN power meter number of nodes | 1 | 1 | 16
1122 | 7723 | Communication | Communication > Power Meter > ESS Meter | ESS meter prot. | Configuration of external communication ES power meter protocol | OFF |  |  |  | 0: OFF, 1: DEIF MIB7000C, 2: DEIF MIC4000, 3: DEIF MIC-2, 4: DEIF MTR-3/4, 5: Schneider iEM3000, 6: Schneider EM6400, 7: Socomec Multis L40, 8: Schneider PM5560, 9: Socomec Diris A40, 10: EDS-MMCT3-E-C, 11: Gossen, 12: EDMI, 13: DEIF Genset Control, 14: APS PMU-100, 15: ABB SACE Emax 2, 16: ABB A43/A44, 17: Accuvim-L, 18: Secure Elite 100/300 series, 21: DEIF MIB8000, 22: Eastron Smart X96, 23: Eastron SDM630MCT, 25: Secure Elite 440/500 series, 26: Acrel ADL, 27: Eastron Smart X96 with DI, 28: Configurable power meter, 29: Kohler APM403
1121 | 7725 | Communication | Communication > Power Meter > Mains Meter | Mains met. prot | Configuration of external communication Mains power meter protocol | OFF |  |  |  | 0: OFF, 1: DEIF MIB7000C, 2: DEIF MIC4000, 3: DEIF MIC-2, 4: DEIF MTR-3/4, 5: Schneider iEM3000, 6: Schneider EM6400, 7: Socomec Multis L40, 8: Schneider PM5560, 9: Socomec Diris A40, 10: EDS-MMCT3-E-C, 11: Gossen, 12: EDMI, 13: DEIF Genset Control, 14: APS PMU-100, 15: ABB SACE Emax 2, 16: ABB A43/A44, 17: Accuvim-L, 18: Secure Elite 100/300 series, 19: DSE 8xxx, 7xxx, 6xxx and 4xxx, 20: Cummins PC 3.x/PCC 3300, 21: DEIF MIB8000, 22: Eastron Smart X96, 23: Eastron SDM630MCT, 25: Secure Elite 440/500 series, 26: Acrel ADL, 27: Eastron Smart X96 with DI, 28: Configurable power meter, 29: Kohler APM403, 30: ComAp IntelliGen 500 g2
1128 | 7726 | Communication | Communication > Power Meter > Mains Meter | Mains nbr. node | Configuration of external communication Mains power meter number of nodes | 1 | 1 | 16
1124 | 7730 | Communication | Communication > Power Meter > GEN Meter | GEN meter err. | External communication GEN power meter supervision | [5 empty] | 0 | 0 | 600 |  |  | Warning
1126 | 7740 | Communication | Communication > Power Meter > ESS Meter | ESS meter err. | External communication ES power meter supervision | [5 empty] | 0 | 0 | 600 |  |  | Warning
1125 | 7750 | Communication | Communication > Power Meter > Mains Meter | Mains meter err | External communication Mains power meter supervision | [5 empty] | 0 | 0 | 600 |  |  | Warning
1127 | 7761 | Communication | Communication > Power Meter > Meter comm. settings | Pow. met. Tx min int | Minimum time delay between telegrams transmitted to power meters from ASC. (If both ESS and Power meters are on same interface, then ESS interval will overrule this parameter.) | [5 empty] | 5 | 1 | 100
1437 | 7841 | Communication | Communication > CAN protocols | CAN A Protocol | CAN bus protocol selection | OFF |  |  |  | 0: OFF, 5: AOP2, 11: Ext. Modules DEIF, 15: ESS CAN protocol, 16: BMS CAN protocol
1438 | 7842 | Communication | Communication > CAN protocols | CAN B Protocol | CAN bus protocol selection | PMS Primary |  |  |  | 0: OFF, 6: PMS Primary, 5: AOP2, 2: PMS Secondary, 11: Ext. Modules DEIF, 15: ESS CAN protocol, 16: BMS CAN protocol
1439 | 7843 | Communication | Communication > CAN protocols | VCAN C Protocol | Ethernet CAN bus protocol selection | OFF |  |  |  | 0: OFF, 6: PMS Primary, 2: PMS Secondary
1183 | 7871 | Communication | Power management > Communication failures | Any BTB missing | Alarm is activated, if the communication to any BTB unit failed | [10 empty] | Warning
1191 | 7872 | Communication | Power management > Communication failures | Appl. hazard | Alarm is activated, if different applications are installed in the controllers. | [5 empty] | 150 | 150 | 150 |  |  | Warning
865 | 7874 | Communication | Power management > Communication failures | Any LoadG miss. | Alarm is activated, if the communication to any ALC unit failed | [10 empty] | Warning
866 | 7875 | Communication | Power management > Communication failures | Any SOLAR miss. | Alarm is activated, if the communication to any PV unit failed | [10 empty] | Warning
867 | 7876 | Communication | Power management > Communication failures | Any BATTRY miss | Alarm is activated, if the communication to any Battery unit failed | [10 empty] | Warning
1711 | 7891 | Communication | I/O settings > External I/O > CIO > Enable | CIO Enable | Configuration of CIO enable | OFF |  |  |  | 0: OFF, 3: ON
1639 | 7900 | Communication | Communication > Ethernet comm. error | Ethernet comm. error | Ethernet communication supervision | [5 empty] | 100 | 10 | 1000 |  |  | Warning
1109 | 7911 | Communication | Communication > PDS | PDS comm. ID | PDS communication ID | 5 | 1 | 247
624 | 7912 | Communication | Communication > PDS | PDS prot. | PDS protocol selection | OFF |  |  |  | 0: OFF, 1: SinExcel DC/DC PDS, 2: SinExcel PDS1-750K
1105 | 7920 | Communication | Communication > PDS | PDS comm. error | PDS communication error | [5 empty] | 30 | 0 | 1000 |  |  | Warning
111 | 7930 | Communication | Communication > PDS | PDS warning | PDS Warning | [5 empty] | 0 | 0 | 1000 |  |  | Warning
112 | 7940 | Communication | Communication > PDS | PDS shutdown | PDS Shutdown | [5 empty] | 0 | 0 | 1000 |  |  | Shutdown
882 | 7950 | Communication | Communication > PDS | PDS activate | Setup if PDS should be active or not
806 | 7960 | Communication | Communication > ESS | DEIF Generic offset | Configure for the DEIF Generic protocol which Modbus address offset should be used for read input registers. | 30000 |  |  |  | 0: 30000, 1: 1000
1882 | 8011 | Power Man | Power management > Q loadshare | Q source prio | Select which hybrid source should have higher priority on Q loadshare. If set to OFF then equal loadshare between hybrid sources. | OFF |  |  |  | 0: OFF, 1: ESS, 2: PV
618 | 8021 | Power Man | Power management > Start/stop for Island | Start/stop | Setup type of Auto start/stop signal to use | Remote |  |  |  | 0: Remote, 1: Local
1186 | 8022 | Power Man | Power management > Mode update | Mode update | Mode update (Update local or all units) | Update all |  |  |  | 0: Update local, 1: Update all
869 | 8023 | Power Man | Power management > Easy connect | Easy connect | Enable/disable easy connect
464 | 8041 | Power Man | Power management > PMS isochronous master | PMS Isochr. master | The battery with the lowest PMS ID with this flag enabled is allowed to be the controlling isochronous master in off-grid applications with gensets. Meaning the gensets wil operate in fixed power regulation controlled by this battery
465 | 8042 | Power Man | Power management > PMS isochronous master | PMS Isochr. mode req | Set the required grid mode before the ESS can act as a PMS isochronous Master | V/f mode only |  |  |  | 0: V/f mode only, 1: V/f or droop mode
1648 | 8043 | Power Man | Power management > PMS isochronous master | PMS Isochr. Q ctrl | Select which mode should be used for reactive power regulation between ESS isochronous master and gensets in off-grid | OFF |  |  |  | 0: OFF, 1: GEN cosphi lim
580 | 8044 | Power Man | Power management > PMS isochronous master | PMS Iso. loadshare | If enabled and there is another battery ready for loadsharing then the PMS isochronous master will follow ramps to not take all the load instantly
1554 | 8100 | Power Man | Power management > BTB | BTB request |  | 90 | 1 | 100 | % |  | 100 | 0 | 9900
1555 | 8101 | Power Man | Power management > BTB | BTB request |  | 200 | 1 | 5000 | kW |  | 100 | 100 | 100
1556 | 8103 | Power Man | Power management > BTB | BTB req. mode |  | Percentage |  |  |  | 0: Percentage, 1: kW
660 | 8121 | Power Man | Power management > Ground relay | Ground relay | Ground relay (selection of relay output for star point grounding)
1699 | 8124 | Power Man | Power management > Ground relay | Ground failure | General ground failure | [5 empty] | 10 | 10 | 300 |  |  | Trip ESB
1605 | 8126 | Power Man | Power management > Ground relay | Gnd relay type | Choose whether to use continous or pulse relay configuration | Continuous |  |  |  | 0: Continuous, 1: Pulse
1700 | 8131 | Power Man | Power management > Ground relay > Ground breaker position failure | Gnd Open fail | Ground breaker open failure | [5 empty] | 10 | 10 | 300 |  |  | Trip ESB
1701 | 8133 | Power Man | Power management > Ground relay > Ground breaker position failure | Gnd Close fail | Ground breaker close failure | [5 empty] | 10 | 10 | 300 |  |  | Shutdown
1702 | 8135 | Power Man | Power management > Ground relay > Ground breaker position failure | Gnd Pos fail | Ground breaker position failure | [5 empty] | 10 | 10 | 300 |  |  | Trip ESB
1742 | 8151 | Power Man | Power management > Ground relay > Ground breaker setting | Gnd close conf | Configure when to close the ground relay. | Hz/V OK |  |  |  | 0: Hz/V OK, 3: Start active
1769 | 8152 | Power Man | Power management > Ground relay > Ground breaker setting | Gnd priority | Configure whether gensets or batteries in plant should take priority over ground relay when their nominal sizes are the same. | GEN priority |  |  |  | 0: GEN priority, 1: ESS priority
1771 | 8201 | Power Man | Power management > SOC balancing | SOC balancing | All batteries in parallel where this is enabled will discharge/charge as a single battery unit. (Must be set for all ASC's!) | Proportional |  |  |  | 0: Proportional, 1: Exponential, 2: Nominal, 3: Nominal Exponential
1781 | 8202 | Power Man | Power management > SOC balancing | Plant SOC max | SOC maximum for batteries in SOC balancing (Must be same for all ASC's) | 90 | 0 | 100 | %
1782 | 8203 | Power Man | Power management > SOC balancing | Plant SOC thr. high | SOC threshold 2 for batteries in SOC balancing (Must be same for all ASC's) | 80 | 0 | 100 | %
1783 | 8204 | Power Man | Power management > SOC balancing | Plant SOC thr. low | SOC threshold 1 for batteries in SOC balancing (Must be same for all ASC's) | 40 | 0 | 100 | %
1784 | 8205 | Power Man | Power management > SOC balancing | Plant SOC min | SOC minimum for batteries in SOC balancing (Must be same for all ASC's) | 20 | 0 | 100 | %
1785 | 8211 | Power Man | Power management > SOC balancing > SOC balancing tuning | Discharge tuner | Tuning of discharge weighting in SOC balancing for this battery unit | 1 | 0.1 | 2 | /10
1786 | 8212 | Power Man | Power management > SOC balancing > SOC balancing tuning | Charge tuner | Tuning of charge weighting in SOC balancing for this battery unit | 1 | 0.1 | 2 | /10
871 | 8351 | Power Man | Power management > Open PMS | Open PMS | Enable/Disable Open PMS - selection only valid if operation mode (6071) is set to Power Management
872 | 8352 | Power Man | Power management > Open PMS | Open PMS mode | Open PMS operation mode - selection is valid only if there is no AGC Mains in the plant and ext. mains is enabled in the I/O and hardware setup tab | Mains Power Export |  |  |  | 0: Peak shaving, 1: Fixed power, 2: Mains Power Export
1673 | 8800 | Power Man | Power management > Communication failures | CAN miss amount | Configure the amount of units missing, in order for the Fatal CAN Error alarm (7534) to activate. (Parameter is shared on all PMS units) | 2 | 2 | 32
1832 | 8930 | Power Man | Power management > Spinning reserve | Spinning reserve | Minimum spinning reserve in Plant | 100 | 0 | 30000 | kW
1372 | 9030 | Jump | Basic settings > Measurement setup > Scaling > Scaling | Scaling | Select the voltage range of operation | 100 to 25000V |  |  |  | 0: 10 to 2500V, 1: 100 to 25000V, 2: 10 to 160kV, 3: 0.4k to 75kV
695 | 9111 | Jump | Basic settings > Controller settings > Password | Customer password | Setup of Customer Password | 2000 | 1 | 32000
696 | 9112 | Jump | Basic settings > Controller settings > Password | Service password | Setup of Service Password | 2001 | 1 | 32000
697 | 9113 | Jump | Basic settings > Controller settings > Password | Master password | Setup of Master Password | 2002 | 1 | 32000
1107 | 9131 | Jump | Basic settings > Measurement setup > Wiring connection > AC configuration | AC configuration | Menu is used to choose between the different AC measurement systems. | 3 phase 3W4 |  |  |  | 0: 3 phase 3W4, 10: 3 phase 3W3, 1: 2 phase L1L3, 2: 2 phase L1L2, 3: 1 phase L1
946 | 9132 | Jump | Basic settings > Measurement setup > Wiring connection > AC configuration | AC configuration BB | Bus connection of Neutral wire | 3 phase 3W4 |  |  |  | 0: 3 phase 3W4, 10: 3 phase 3W3
698 | 9141 | Jump | Synchronisation > Angle offset | Angle comp. BB/ESS 1 | Phase angle displacement for applications with y1 and y11 transformer | 0 | -179 | 179 | deg
1581 | 9142 | Jump | Synchronisation > Angle offset | Angle comp. BB/ESS 2 | Transformer phase compensation setting 2 | 0 | -179 | 179 | deg
699 | 9151 | Jump | Basic settings > Controller settings > Display > Display Control | Backlight dimmer | Setup of backlight level | 12 | 0 | 15
939 | 9152 | Jump | Basic settings > Controller settings > Display > Display Control | Green LEDs dimmer | Adjust level for green leds | 15 | 1 | 15
940 | 9153 | Jump | Basic settings > Controller settings > Display > Display Control | Red LEDs dimmer | Adjust level for red leds | 15 | 1 | 15
685 | 9154 | Jump | Basic settings > Controller settings > Display > Display Control | Contrast setting | Display contrast level | 0 | -20 | 20
937 | 9155 | Jump | Basic settings > Controller settings > Display > Display Control | Sleep mode | Sleep mode enable | [5 empty] | 60 | 1 | 1800 | Limits | Limits
1227 | 9157 | Jump | Basic settings > Controller settings > Display > Display Control | Alarm Jump | Display behavior when and alarm is activated. ON: jump to the Alarm list, OFF: stay at present view | On |  |  |  | 0: Off, 1: On
797 | 9158 | Jump | Basic settings > Controller settings > Display > Display Control | Engineering units | Engineering units Bar/celsius or Psi/fahrenheit | Bar/celsius |  |  |  | 0: Bar/celsius, 1: Psi/fahrenheit
1819 | 9159 | Jump | Communication > Remote Display | Remote display setup | Setup of remote display | OFF |  |  |  | 0: OFF, 1: ON view only, 2: ON view + controls
1275 | 9181 | Jump | Functions > Quick setup | Quick Setup Mode | Quick Setup - Plant setup | Off |  |  |  | 0: Off, 1: Setup stand alone, 2: Setup plant
1276 | 9182 | Jump | Functions > Quick setup | Quick Setup Canline | Quick Setup - Power Management CAN setup | CAN PM Primary |  |  |  | 0: Off, 1: CAN PM Primary, 2: CAN PM Secondary
1277 | 9183 | Jump | Functions > Quick setup | Quick Setup MB type | Quick setup | Pulse |  |  |  | 0: Pulse, 1: No MB, 3: Continuous, 4: Compact
1278 | 9184 | Jump | Functions > Quick setup | Quick Setup ESB type | Quick setup ESB configuration. Also used for choosing ESB type in Easy connect. | Pulse |  |  |  | 0: Pulse, 1: No ESB, 3: Continuous, 4: Compact
1279 | 9185 | Jump | Functions > Quick setup | Quick Setup mains | Quick setup | Mains present |  |  |  | 0: Mains present, 1: No mains present
1281 | 9186 | Jump | Functions > Quick setup | Quick Setup ESS | Quick setup | Standard |  |  |  | 0: Single controller, 1: Standard
1284 | 9191 | Jump | Functions > Appl. broadcast | Appl. Broadcast type | Broadcast application | Off |  |  |  | 0: Off, 1: Broadcast, 2: Broadcast+Activate
1285 | 9192 | Jump | Functions > Appl. broadcast | Appl.no to Broadcast | Selection of application to be broadcasted | 1 | 1 | 4
1602 | 9220 | Jump | Basic settings > Controller settings > Parameter filter | Parameter list setup | Parameter list selection | Master tree |  |  |  | 0: Parameter list, 1: Custom tree, 2: Service tree, 3: Master tree
1603 | 11200 | USW | USW specific parameters > Parameter name | Parameter name | This parameter can be used to identify which parameter list is used on the unit
1305 | 14201 | Prot: 4th CT | Basic settings > Measurement setup > 4th CT protection > 4th CT input selector | 4th CT trip select | 4th CT selection of alarm type due to use of this input. | OFF |  |  |  | 0: OFF, 1: Mains/BB current, 2: Neutral current, 3: Earth fault current
1079 | 14210 | Prot: 4th CT | AC configuration and protections > Current protections > Neutral over-current (4th CT) | 4th CT In> 1 | 4th CT neutral current protection level 1 | 30 | 2 | 120 | % |  | 100 | 1 | 32000 |  |  | Warning
1080 | 14220 | Prot: 4th CT | AC configuration and protections > Current protections > Neutral over-current (4th CT) | 4th CT In> 2 | 4th CT neutral current protection level 2 | 30 | 2 | 120 | % |  | 100 | 1 | 32000 |  |  | Warning
1081 | 14230 | Prot: 4th CT | AC configuration and protections > Current protections > Earth fault over-current (4th CT) | 4th CT Ie> 1 | 4th CT earth current protection level 1 | 10 | 2 | 120 | % |  | 100 | 1 | 32000 |  |  | Warning
1082 | 14240 | Prot: 4th CT | AC configuration and protections > Current protections > Earth fault over-current (4th CT) | 4th CT Ie> 2 | 4th CT earth current protection level 2 | 10 | 2 | 120 | % |  | 100 | 1 | 32000 |  |  | Warning
752 | 14250 | Prot: 4th CT |  | 4th CT I> 1 | 4th CT busbar current protection level 1 | 115 | 50 | 200 | % |  | 100 | 1 | 32000 |  |  | Warning
753 | 14260 | Prot: 4th CT |  | 4th CT I> 2 | 4th CT busbar current protection level 2 | 120 | 50 | 200 | % |  | 100 | 1 | 32000 |  |  | Warning
606 | 14270 | Prot: 4th CT | AC configuration and protections > Power protections > Overload 4th CT | 4th CT -P> 1 | 4th CT Reverse power protection level 1 | -5 | -200 | 0 | % |  | 100 | 1 | 1000 |  |  | Warning
607 | 14280 | Prot: 4th CT | AC configuration and protections > Power protections > Overload 4th CT | 4th CT -P> 2 | 4th CT Reverse power protection level 2 | -5 | -200 | 0 | % |  | 100 | 1 | 1000 |  |  | Warning
608 | 14290 | Prot: 4th CT | AC configuration and protections > Power protections > Overload 4th CT | 4th CT P> 1 | 4th CT overload protection level 1 | 100 | -200 | 200 | % |  | 100 | 1 | 32000 |  |  | Warning
609 | 14300 | Prot: 4th CT | AC configuration and protections > Power protections > Overload 4th CT | 4th CT P> 2 | 4th CT overload protection level 2 | 110 | -200 | 200 | % |  | 50 | 1 | 32000 |  |  | Warning
230 | 15011 | Ext. Ctrl. | External control > Min. GEN load settings | Min GEN load 1 | Minimum genset load percentage in island operation 1 | 30 | -50 | 100 | %
231 | 15012 | Ext. Ctrl. | External control > Min. GEN load settings | Min GEN load 2 | Minimum genset load percentage in island operation 2 | 30 | -50 | 100 | %
229 | 15013 | Ext. Ctrl. | External control > Min. GEN load settings | Min GEN load set | Minimum genset load percentage island selection | Min. GEN load set 1 |  |  |  | 0: Min. GEN load set 1, 1: Min. GEN load set 2
523 | 15014 | Ext. Ctrl. | External control > Optimal GEN load settings | Opt. GEN load %1 | Percentage of genset load which can be produced by the gensets before the battery will help take the load. Power Source only! | 80 | 0 | 100 | %
524 | 15015 | Ext. Ctrl. | External control > Optimal GEN load settings | Opt. GEN load %2 | Percentage of genset load which can be produced by the gensets before the battery will help take the load. Power Source only! | 70 | 0 | 100 | %
526 | 15016 | Ext. Ctrl. | External control > Optimal GEN load settings | Opt. GEN load set | Selection of active optimal genset load setting. If set to off the gensets can take as much load as nom. P allows. Power Source only! | Optimal GEN load set off |  |  |  | 0: Optimal GEN load set off, 1: Optimal GEN load set pct 1, 2: Optimal GEN load set pct 2, 3: Optimal GEN load set pct 1 + Dynamic ST/ST, 4: Optimal GEN load set pct 2 + Dynamic ST/ST
637 | 15070 | Ext. Ctrl. | External control > GEN reverse power alarms | GEN P< 1 | GEN reverse power alarm 1 | -5 | -200 | 100 | % |  | 100 | 1 | 32000 |  |  | Warning
638 | 15080 | Ext. Ctrl. | External control > GEN reverse power alarms | GEN P< 2 | GEN reverse power alarm 2 | -5 | -200 | 100 | % |  | 100 | 1 | 32000 |  |  | Warning
1111 | 15090 | Ext. Ctrl. | External control > GEN spinning reserve alarms | GEN spinning res. 1 | Genset spinning reserve alarm 1 (Only genset power is used for calculation) | 30 | 0 | 100 | % |  | 100 | 1 | 32000
1112 | 15100 | Ext. Ctrl. | External control > GEN spinning reserve alarms | GEN spinning res. 2 | Genset spinning reserve alarm 2 (Only genset power is used for calculation) | 10 | 0 | 100 | % |  | 100 | 1 | 32000
113 | 15151 | Ext. Ctrl. | External control > External GEN start/stop | SOC GEN start limit | When the SOC gets below this limit, the Start/stop ext. GEN output is activated after the timer runs out. Only active when SOC GEN control is enabled. | 30 | 0 | 100 | % |  | 10 | 0 | 3200
114 | 15153 | Ext. Ctrl. | External control > External GEN start/stop | SOC GEN stop limit | When the SOC gets above this limit, the Start/stop ext. GEN output is deactivated after the timer runs out. Only active when SOC GEN control is enabled. | 50 | 0 | 100 | % |  | 15 | 5 | 3200
117 | 15155 | Ext. Ctrl. | External control > External GEN start/stop | SOC GEN control | Enables the SOC limits to set the start/stop signal for ext. GENs. Can be used on its own or in combination with Sys P GEN control. | Local SOC |  |  |  | 0: Local SOC, 1: Plant SOC
115 | 15161 | Ext. Ctrl. | External control > External GEN start/stop | Sys P GEN start lim | When the system load is above this limit, the Start/stop ext. GEN output is activated after the timer runs out. Only active when Sys P GEN control is enabled. | 200 | 0 | 20000 | kW |  | 10 | 0 | 3200
116 | 15163 | Ext. Ctrl. | External control > External GEN start/stop | Sys P GEN stop limit | When the system load is below this limit, the Start/stop ext. GEN output is deactivated after the timer runs out. Only active when Sys P GEN control is enabled. | 50 | 0 | 20000 | kW |  | 15 | 5 | 3200
625 | 15165 | Ext. Ctrl. | External control > External GEN start/stop | Sys P GEN control | Enables the system load limits to set the start/stop signal for ext. GENs. Can be used on its own or in combination with SOC GEN control.
626 | 15170 | Ext. Ctrl. | External control > External GEN start/stop | Ext. GEN start error | If the an ext. GEN start request is active, and no GEN is detected on the busbar within a given timeframe an alarm is activated. | [5 empty] | 30 | 1 | 1000 |  |  | Warning
478 | 15180 | Ext. Ctrl. | External control > External GEN start/stop | Ext. GEN break. open | Sets the breaker open point of ext. GENs in percent of nominal ext. GEN power. When the total ext. GEN power gets below this point the start/stop can turn off. | 5 | 0 | 100 | %
1859 | 15210 | Ext. Ctrl. | External control > External GEN start/stop | Dyn LDStart offset | Batteries will reduce power output to reach this percentage above LDstart on gensets | 2 | 0 | 10 | % |  | 100 | 0 | 1000
1860 | 15220 | Ext. Ctrl. | External control > External GEN start/stop | Dyn LDStop offset | Batteries will increase power output to reach this percentage below LDstop on gensets | 2 | 0 | 10 | % |  | 100 | 0 | 1000
1863 | 15230 | Ext. Ctrl. | External control > External GEN start/stop | Dyn LDStart percent | Expected LD Start percentage in external system | 90 | 10 | 100 | %
1864 | 15240 | Ext. Ctrl. | External control > External GEN start/stop | Dyn LDStop percent | Expected LD Stop percentage in external system | 40 | 10 | 100 | %
1290 | 17022 | Battery | Battery > Charge Scheme | Mains charging | If enabled, the ESS can recharge from mains. The set point is the maximum charging rate. If the ESS is running as Battery Leading, it will not recharge from mains | 100 | 0 | 100 | %
501 | 17024 | Battery | Battery > Charge Scheme | Mains charging limit | When operating in peak shaving, MPE or fixed power - use the peak shaving, MPE or fixed power setpoint as a the mains charging limit.
463 | 17025 | Battery | Battery > Charge Scheme | Mains charge mode | Sets the active charging scheme used for mains parallel applications. | SOC + plant assist charging |  |  |  | 0: SOC based charging only, 1: SOC + plant assist charging
1866 | 17026 | Battery | Battery > Charge Scheme | Mains chrg thr | The SOC threshold where charging from Mains shall stop when plant assist charging | SOC high |  |  |  | 2: SOC high, 3: SOC maximum
1094 | 17031 | Battery | Battery > Charge Scheme | GEN charge pct | This sets how much the battery is allowed to load the gensets in percentage of their nom. P when charging. The battery will decrease the charging setpoint if the gensets is loaded above this point. Only active if 17033 is enabled and set to Percent. | 100 | 0 | 100 | %
1095 | 17032 | Battery | Battery > Charge Scheme | GEN charge P | This power must be available as spinning reserve while the ESS is recharging. This should be above the genset start limit. Only active if 17033 is enabled and set to Power. | 200 | 0 | 5000 | kW
1106 | 17033 | Battery | Battery > Charge Scheme | GEN charge Mode | If enabled, the ESS can recharge from the gensets. This parameter determines whether parameter 17031 (Percent) or 17032 (Power) is used. | GEN Charge in Percent |  |  |  | 0: GEN Charge in Percent, 1: GEN Charge in Power, 2: Use Optimal genset load in percent
1298 | 17041 | Battery | Battery > Charge Scheme | PV charging | If enabled, the ESS can recharge from PV. The set point is the maximum charging rate. | 100 | 0 | 100 | %
1865 | 17042 | Battery | Battery > Charge Scheme | PV charge thr | The SOC threshold where charging from PV shall stop | SOC maximum |  |  |  | 2: SOC high, 3: SOC maximum
1547 | 17051 | Battery | Battery > SOC settings > SOC setting 1 | SOC 1 minimum | SOC parameter set 1 - SOC minimum | 20 | 0 | 100 | %
1550 | 17052 | Battery | Battery > SOC settings > SOC setting 1 | SOC 1 maximum | SOC parameter set 1 - SOC maximum | 90 | 0 | 100 | %
1287 | 17053 | Battery | Battery > SOC settings > SOC setting 1 | SOC 1 thr. low | SOC Parameter set 1 - SOC threshold low | 40 | 0 | 100 | %
1291 | 17054 | Battery | Battery > SOC settings > SOC setting 1 | SOC 1 thr. high | SOC Parameter set 1 - SOC threshold high | 80 | 0 | 100 | %
1553 | 17055 | Battery | Battery > SOC settings | SOC settings | Select SOC setting | SOC Setting 1 |  |  |  | 0: SOC Setting 1, 1: SOC Setting 2, 2: SOC Setting 3
811 | 17056 | Battery | Battery > SOC settings | SOC resolution | Configure which resolution of SOC should be applied for regulation | 1% |  |  |  | 0: 1%, 1: 0.1%, 2: 0.01%
1548 | 17061 | Battery | Battery > SOC settings > SOC setting 2 | SOC 2 minimum | SOC parameter set 2 - SOC minimum | 20 | 0 | 100 | %
1551 | 17062 | Battery | Battery > SOC settings > SOC setting 2 | SOC 2 maximum | SOC parameter set 2 - SOC maximum | 90 | 0 | 100 | %
1288 | 17063 | Battery | Battery > SOC settings > SOC setting 2 | SOC 2 thr. low | SOC Parameter set 2 - SOC threshold low | 40 | 0 | 100 | %
1292 | 17064 | Battery | Battery > SOC settings > SOC setting 2 | SOC 2 thr. high | SOC Parameter set 2 - SOC threshold high | 80 | 0 | 100 | %
1549 | 17071 | Battery | Battery > SOC settings > SOC setting 3 | SOC 3 minimum | SOC parameter set 3 - SOC minimum | 20 | 0 | 100 | %
1552 | 17072 | Battery | Battery > SOC settings > SOC setting 3 | SOC 3 maximum | SOC parameter set 3 - SOC maximum | 90 | 0 | 100 | %
1289 | 17073 | Battery | Battery > SOC settings > SOC setting 3 | SOC 3 thr. low | SOC Parameter set 3 - SOC threshold low | 40 | 0 | 100 | %
1293 | 17074 | Battery | Battery > SOC settings > SOC setting 3 | SOC 3 thr. high | SOC Parameter set 3 - SOC threshold high | 80 | 0 | 100 | %
1091 | 17081 | Battery | Battery > Operation modes | ESS Operation mode | Battery operation mode | Battery Assisting |  |  |  | 0: Battery Leading, 1: Battery Assisting
1092 | 17082 | Battery | Battery > Operation modes | ESS Power direction | Batteries charged from AC bus or DC bus only | AC Charge and discharge |  |  |  | 0: AC Discharge only, 1: AC Charge and discharge
612 | 17091 | Battery | Battery > Dispatch limits | Minimum dispatch | Maxiumum power to charge | -100 | -100 | 100 | %
1093 | 17092 | Battery | Battery > Dispatch limits | Maximum dispatch | Maximum power to dispatch | 100 | -100 | 100 | %
1129 | 17110 | Battery | Battery > SOC/SOH Alarms > SOC Alarms | SOC < 1 | State Of Charge Minimum alarm 01 | 20 | 0 | 100 | % | [6 empty] | Warning
1131 | 17120 | Battery | Battery > SOC/SOH Alarms > SOC Alarms | SOC > 2 | State Of Charge Maximum alarm 01 | 80 | 0 | 100 | % | [6 empty] | Warning
1133 | 17130 | Battery | Battery > SOC/SOH Alarms > SOH Alarms | SOH minimum 01 | State Of Health Minimum alarm 01 | 20 | 0 | 100 | % | [6 empty] | Warning
1134 | 17140 | Battery | Battery > SOC/SOH Alarms > SOH Alarms | SOH minimum 02 | State Of Health Minimum alarm 02 | 15 | 0 | 100 | % | [6 empty] | Warning
1265 | 17150 | Battery | Battery > DC protection | DC dU max | Sets maximum DC voltage deviation between BMS output and PCS input in percentage of the BMS output DC voltage | 5 | 0 | 100 | % |  | 3 | 1 | 1000 |  |  | Warning
516 | 17161 | Battery | Battery > DC protection | Max charge volt. | If enabled this value will overwrite the maximum allowed DC charge voltage read from the BMS | 980 | 0 | 3200 | V
517 | 17163 | Battery | Battery > DC protection | Min discharge volt. | If enabled this value will overwrite the minimum allowed discharge DC voltage read from the BMS | 720 | 0 | 3200 | V
513 | 17201 | Battery | Battery > PDS operation | PDS spin. res. %1 | Percentage of produced PDS power which should be reserved locally as extra available battery discharge capacity. | 90 | 0 | 100 | %
514 | 17202 | Battery | Battery > PDS operation | PDS spin. res. %2 | Percentage of produced PDS power which should be reserved locally as extra available battery discharge capacity. | 60 | 0 | 100 | %
515 | 17203 | Battery | Battery > PDS operation | PDS spin. res. set | Selection of which PDS spinning reserve percentage to actively use. PDS power not locally reserved can be used in addition to the maximum battery discharge power. | PDS Spinning reserve pct 01 |  |  |  | 0: PDS Spinning reserve pct 01, 1: PDS Spinning reserve pct 02
217 | 17301 | Battery | Regulation > Instant P Max | Instant P max. | Enable instant P max calculation based on communication from Battery.
1455 | 17400 | Battery | Battery > Maintenance charge | Maintenance charge | If enabled, the ASC will attempt to charge the battery until the threshold in 17401 has been reached. This setting will disregard the SOC completely and solely charge based on the current maximum charge capacity from BMS
1456 | 17401 | Battery | Battery > Maintenance charge | Charge cap. thr | Maintenance charging stops when the maximum charge capacity from the BMS decreases to this value | 0 | 0 | 20000 | kW

## SOLAR
Offset | Channel | Category | Path | Name | Description | Default | Minimum | Maximum | Unit | Selections | Timer default | Timer minimum | Timer maximum | RelayA name | RelayB name | Default alarm action
1 | 1000 | Protection | AC configuration and protections > Power protections > Reverse power | -P> 1 | Reverse power protection level 1 (ANSI 32) | -5 | -200 | 0 | % |  | 100 | 1 | 1000 |  |  | Trip PVB
2 | 1010 | Protection | AC configuration and protections > Power protections > Reverse power | -P> 2 | Reverse power protection level 2 (ANSI 32) | -5 | -200 | 0 | % |  | 100 | 1 | 1000 |  |  | Trip PVB
4 | 1030 | Protection | AC configuration and protections > Current protections > Over-current | I> 1 | Overcurrent protection level 1 (ANSI 50) | 115 | 50 | 200 | % |  | 100 | 1 | 32000 |  |  | Warning
5 | 1040 | Protection | AC configuration and protections > Current protections > Over-current | I> 2 | Overcurrent protection level 2 (ANSI 50) | 120 | 50 | 200 | % |  | 50 | 1 | 32000 |  |  | Trip PVB
6 | 1050 | Protection | AC configuration and protections > Current protections > Over-current | I> 3 | Overcurrent protection level 3 (ANSI 50) | 115 | 50 | 200 | % |  | 100 | 1 | 32000 |  |  | Trip PVB
7 | 1060 | Protection | AC configuration and protections > Current protections > Over-current | I> 4 | Overcurrent protection level 4 (ANSI 50) | 120 | 50 | 200 | % |  | 50 | 1 | 32000 |  |  | Trip PVB
870 | 1070 | Protection | AC configuration and protections > Power protections > Reverse power | -P> 3 | Reverse power protection level 3 (ANSI 32) | -5 | -200 | 30 | % |  | 1000 | 0 | 30000 |  |  | Trip PVB
1377 | 1081 | Protection | AC configuration and protections > Current protections > Inverse time over-current | I> inverse Type | I> curve selection (IEC/IEEE inverse time overcurrent) | IEC Inverse |  |  |  | 0: IEC Inverse, 1: IEC Very Inverse, 2: IEC Extremely Inv., 3: IEEE Moderately Inv., 4: IEEE Very Inverse, 5: IEEE Extremely Inv., 6: Custom
1382 | 1082 | Protection | AC configuration and protections > Current protections > Inverse time over-current | I> inverse Limit | I> (IEC/IEEE inverse time overcurrent) | 110 | 50 | 200 | %
1378 | 1083 | Protection | AC configuration and protections > Current protections > Inverse time over-current | I> inverse TMS | I> (IEC/IEEE inverse time overcurrent) | 1 | 0.01 | 100 | /100
1379 | 1084 | Protection | AC configuration and protections > Current protections > Inverse time over-current | I> inverse k | I> (IEC/IEEE inverse time overcurrent) | 0.14 | 0.001 | 32 | s
1380 | 1085 | Protection | AC configuration and protections > Current protections > Inverse time over-current | I> inverse c | I> (IEC/IEEE inverse time overcurrent) | 0 | 0 | 32 | s
1381 | 1086 | Protection | AC configuration and protections > Current protections > Inverse time over-current | I> inverse a | I> (IEC/IEEE inverse time overcurrent) | 0.02 | 0.001 | 32 | /1000
1335 | 1087 | Protection | AC configuration and protections > Current protections > Inverse time over-current | I> inverse | I> setup (IEC/IEEE inverse time overcurrent) | [10 empty] | Trip PVB
1251 | 1101 | Protection | AC configuration and protections > Current protections > Voltage dependent over-current | PV Iv> (50%) | Voltage dependent overcurrent curve setting 1 | 110 | 50 | 200 | %
1252 | 1102 | Protection | AC configuration and protections > Current protections > Voltage dependent over-current | PV Iv> (60%) | Voltage dependent overcurrent curve setting 2 | 125 | 50 | 200 | %
1253 | 1103 | Protection | AC configuration and protections > Current protections > Voltage dependent over-current | PV Iv> (70%) | Voltage dependent overcurrent curve setting 3 | 140 | 50 | 200 | %
1254 | 1104 | Protection | AC configuration and protections > Current protections > Voltage dependent over-current | PV Iv> (80%) | Voltage dependent overcurrent curve setting 4 | 155 | 50 | 200 | %
1255 | 1105 | Protection | AC configuration and protections > Current protections > Voltage dependent over-current | PV Iv> (90%) | Voltage dependent overcurrent curve setting 5 | 170 | 50 | 200 | %
1256 | 1106 | Protection | AC configuration and protections > Current protections > Voltage dependent over-current | PV Iv> (100%) | Voltage dependent overcurrent curve setting 6 | 200 | 50 | 200 | %
9 | 1110 | Protection | AC configuration and protections > Current protections > Voltage dependent over-current | PV Iv> | Voltage dependent overcurrent protection (ANSI 50V) | [5 empty] | 10 | 1 | 100 |  |  | Trip PVB
10 | 1130 | Protection | AC configuration and protections > Current protections > Fast over-current | I>> 1 | Fast overcurrent protection level 1 (ANSI 50) | 150 | 150 | 300 | % |  | 20 | 0 | 32000 |  |  | Trip PVB
11 | 1140 | Protection | AC configuration and protections > Current protections > Fast over-current | I>> 2 | Fast overcurrent protection level 1 (ANSI 50) | 200 | 150 | 300 | % |  | 5 | 0 | 32000 |  |  | Trip PVB
12 | 1150 | Protection | AC configuration and protections > Voltage protections > Over-voltage | PV U> 1 | PV overvoltage protection level 1 (ANSI 27) | 103 | 100 | 130 | % |  | 100 | 1 | 1000 |  |  | Warning
13 | 1160 | Protection | AC configuration and protections > Voltage protections > Over-voltage | PV U> 2 | PV overvoltage protection level 2 (ANSI 27) | 105 | 100 | 130 | % |  | 50 | 1 | 1000 |  |  | Warning
14 | 1170 | Protection | AC configuration and protections > Voltage protections > Under-voltage | PV U< 1 | PV undervoltage protection level 1 (ANSI 27) | 97 | 40 | 100 | % |  | 100 | 1 | 1000 |  |  | Warning
15 | 1180 | Protection | AC configuration and protections > Voltage protections > Under-voltage | PV U< 2 | PV undervoltage protection level 2 (ANSI 27) | 95 | 40 | 100 | % |  | 50 | 1 | 1000 |  |  | Warning
16 | 1190 | Protection | AC configuration and protections > Voltage protections > Under-voltage | PV U< 3 | PV undervoltage protection level 3 (ANSI 27) | 95 | 40 | 100 | % |  | 50 | 1 | 1000 |  |  | Warning
17 | 1201 | Protection | AC configuration and protections > Voltage protections > Voltage detect. type | PV U detect. type | PV meassurement type phase-phase or phase-neutral | Ph-Ph |  |  |  | 0: Ph-Ph, 1: Ph-N
31 | 1202 | Protection | Busbar > Voltage protections > Voltage detect. type | BB U detect. type | Busbar meassurement type phase-phase or phase-neutral | Ph-Ph |  |  |  | 0: Ph-Ph, 1: Ph-N
1608 | 1203 | Protection | AC configuration and protections > Current protections > Unbalance current | Unbalance I | Current unbalance calculation method | Ref. to nominal |  |  |  | 0: Ref. to nominal, 1: Ref. to average
173 | 1204 | Protection | AC configuration and protections > Frequency protections > Frequency detection type | Freq. detect. type | Frequency trip type selection for over- and underfrequency alarms. | L1 or L2 or L3 |  |  |  | 0: L1, 1: L2, 2: L3, 3: L1 or L2 or L3, 4: L1 and L2 and L3
18 | 1210 | Protection | AC configuration and protections > Frequency protections > Over-frequency | PV f> 1 | PV overfrequency protection level 1 (ANSI 81) | 103 | 100 | 120 | % |  | 100 | 2 | 1000 |  |  | Warning
19 | 1220 | Protection | AC configuration and protections > Frequency protections > Over-frequency | PV f> 2 | PV overfrequency protection level 2 (ANSI 81) | 105 | 100 | 120 | % |  | 50 | 2 | 1000 |  |  | Warning
20 | 1230 | Protection | AC configuration and protections > Frequency protections > Over-frequency | PV f> 3 | PV overfrequency protection level 3 (ANSI 81) | 105 | 100 | 120 | % |  | 50 | 2 | 1000 |  |  | Warning
21 | 1240 | Protection | AC configuration and protections > Frequency protections > Under-frequency | PV f< 1 | PV underfrequency protection level 1 (ANSI 81) | 97 | 80 | 100 | % |  | 100 | 2 | 1000 |  |  | Warning
22 | 1250 | Protection | AC configuration and protections > Frequency protections > Under-frequency | PV f< 2 | PV underfrequency protection level 2 (ANSI 81) | 95 | 80 | 100 | % |  | 50 | 2 | 1000 |  |  | Warning
23 | 1260 | Protection | AC configuration and protections > Frequency protections > Under-frequency | PV f< 3 | PV underfrequency protection level 3 (ANSI 81) | 95 | 80 | 100 | % |  | 50 | 2 | 1000 |  |  | Warning
24 | 1270 | Protection | Busbar > Voltage protections > Over-voltage | BB U> 1 | Busbar overvoltage protection level 1 (ANSI 59) | 103 | 100 | 120 | % |  | 1000 | 4 | 9999 |  |  | Warning
25 | 1280 | Protection | Busbar > Voltage protections > Over-voltage | BB U> 2 | Busbar overvoltage protection level 2 (ANSI 59) | 105 | 100 | 120 | % |  | 500 | 4 | 9999 |  |  | Warning
26 | 1290 | Protection | Busbar > Voltage protections > Over-voltage | BB U> 3 | Busbar overvoltage protection level 3 (ANSI 59) | 105 | 100 | 120 | % |  | 500 | 4 | 9999 |  |  | Warning
27 | 1300 | Protection | Busbar > Voltage protections > Under-voltage | BB U< 1 | Busbar undervoltage protection level 1 (ANSI 59) | 97 | 40 | 100 | % |  | 1000 | 4 | 9999 |  |  | Warning
28 | 1310 | Protection | Busbar > Voltage protections > Under-voltage | BB U< 2 | Busbar undervoltage protection level 2 (ANSI 59) | 95 | 40 | 100 | % |  | 500 | 4 | 9999 |  |  | Warning
29 | 1320 | Protection | Busbar > Voltage protections > Under-voltage | BB U< 3 | Busbar undervoltage protection level 3 (ANSI 59) | 97 | 40 | 100 | % |  | 1000 | 4 | 9999 |  |  | Warning
30 | 1330 | Protection | Busbar > Voltage protections > Under-voltage | BB U< 4 | Busbar undervoltage protection level 4 (ANSI 59) | 95 | 40 | 100 | % |  | 500 | 4 | 9999 |  |  | Warning
32 | 1350 | Protection | Busbar > Frequency protections > Over-frequency | BB f> 1 | Busbar overfrequency protection level 1 (ANSI 81) | 103 | 100 | 120 | % |  | 1000 | 4 | 9999 |  |  | Warning
33 | 1360 | Protection | Busbar > Frequency protections > Over-frequency | BB f> 2 | Busbar overfrequency protection level 2 (ANSI 81) | 105 | 100 | 120 | % |  | 500 | 4 | 9999 |  |  | Warning
34 | 1370 | Protection | Busbar > Frequency protections > Over-frequency | BB f> 3 | Busbar overfrequency protection level 3 (ANSI 81) | 105 | 100 | 120 | % |  | 500 | 4 | 9999 |  |  | Warning
35 | 1380 | Protection | Busbar > Frequency protections > Under-frequency | BB f< 1 | Busbar underfrequency protection level 1 (ANSI 81) | 97 | 80 | 100 | % |  | 1000 | 4 | 9999 |  |  | Warning
36 | 1390 | Protection | Busbar > Frequency protections > Under-frequency | BB f< 2 | Busbar underfrequency protection level 2 (ANSI 81) | 95 | 80 | 100 | % |  | 500 | 4 | 9999 |  |  | Warning
37 | 1400 | Protection | Busbar > Frequency protections > Under-frequency | BB f< 3 | Busbar underfrequency protection level 3 (ANSI 81) | 97 | 80 | 100 | % |  | 1000 | 4 | 9999 |  |  | Warning
38 | 1410 | Protection | Busbar > Frequency protections > Under-frequency | BB f< 4 | Busbar underfrequency protection level 4 (ANSI 81) | 95 | 80 | 100 | % |  | 500 | 4 | 9999 |  |  | Warning
39 | 1420 | Protection | Busbar > Additional protections > ROCOF (df/dt) | df/dt (ROCOF) | Set point of ROCOF protection (rate of change of frequency) | 5 | 0.2 | 10 | Hz/s |  | 0 | 0 | 300 |  |  | Trip MB
40 | 1421 | Protection | Busbar > Additional protections > ROCOF (df/dt) | df/dt (ROCOF) | ROCOF protection delay in cycles | 6 | 3 | 20 | period(s)
41 | 1430 | Protection | Busbar > Additional protections > Vector shift | Vector shift | Set point in degrees of vector shift protection | 10 | 1 | 90 | deg | [6 empty] | Trip MB
1465 | 1436 | Protection | Busbar > Additional protections > Vector shift | Vector shift type | Vector shift trip selection | Individual phases |  |  |  | 0: Individual phases, 1: All phases
42 | 1440 | Protection | Busbar > Voltage protections > Positive sequence under-voltage | BB pos. seq. U | Positive sequence (busbar) voltage low ANSI 27) | 70 | 10 | 110 | % |  | 2 | 1 | 9 |  |  | Trip MB
43 | 1450 | Protection | AC configuration and protections > Power protections > Overload | P> 1 | PV overload protection level 1 (ANSI 32) | 100 | -200 | 200 | % |  | 100 | 1 | 32000 |  |  | Warning
44 | 1460 | Protection | AC configuration and protections > Power protections > Overload | P> 2 | PV overload protection level 2 (ANSI 32) | 110 | -200 | 200 | % |  | 50 | 1 | 32000 |  |  | Trip PVB
45 | 1470 | Protection | AC configuration and protections > Power protections > Overload | P> 3 | PV overload protection level 3 (ANSI 32) | 100 | -200 | 200 | % |  | 100 | 1 | 32000 |  |  | Trip PVB
46 | 1480 | Protection | AC configuration and protections > Power protections > Overload | P> 4 | PV overload protection level 4 (ANSI 32) | 110 | -200 | 200 | % |  | 50 | 1 | 32000 |  |  | Trip PVB
47 | 1490 | Protection | AC configuration and protections > Power protections > Overload | P< 5 | PV overload protection level 5 (ANSI 32) | 30 | -200 | 200 | % |  | 32000 | 1 | 32000 |  |  | Trip PVB
48 | 1500 | Protection | AC configuration and protections > Current protections > Unbalance current | Unbalance I 1 | PV unbalanced current (ANSI 60) | 30 | 0 | 100 | % |  | 100 | 1 | 1000 |  |  | Trip PVB
49 | 1510 | Protection | AC configuration and protections > Voltage protections > Voltage unbalance | PV Unbalance U | PV unbalanced voltage (ANSI 60) | 10 | 0 | 50 | % |  | 100 | 1 | 1000 |  |  | Trip PVB
50 | 1520 | Protection | AC configuration and protections > Reactive power protections > Underexcitation | -Q> | Loss of excitation (ANSI 40) | 50 | 0 | 150 | % |  | 100 | 1 | 1000 |  |  | Warning
51 | 1530 | Protection | AC configuration and protections > Reactive power protections > Overexcitation | Q> | Overexcitation (ANSI 40) | 60 | 0 | 100 | % |  | 100 | 1 | 1000 |  |  | Warning
52 | 1540 | Protection | AC configuration and protections > Current protections > Negative sequence current | Negative. seq. I | Negative sequence current (ANSI 46) | 20 | 1 | 100 | % |  | 5 | 2 | 1000 |  |  | Trip MB
53 | 1550 | Protection | AC configuration and protections > Voltage protections > Negative sequence voltage | PV neg. seq. U | Negative sequence voltage (ANSI 47) | 5 | 1 | 100 | % |  | 5 | 2 | 1000 |  |  | Trip MB
54 | 1560 | Protection | AC configuration and protections > Voltage protections > Negative sequence voltage | Neg. seq. select | Negative sequence PV or Busbar | PV measurement |  |  |  | 0: PV measurement, 1: BB measurement | 1 | 1 | 1
55 | 1570 | Protection | AC configuration and protections > Current protections > Zero sequence current | Zero seq. I | Zero sequence current (ANSI 50I0) | 20 | 0 | 100 | % |  | 5 | 2 | 1000 |  |  | Trip MB
56 | 1580 | Protection | AC configuration and protections > Voltage protections > Zero sequence voltage | PV zero seq. U | Zero sequence voltage (ANSI 59U0) | 5 | 0 | 100 | % |  | 5 | 2 | 1000 |  |  | Trip MB
57 | 1590 | Protection | AC configuration and protections > Voltage protections > Zero sequence voltage | Zero seq. select | Zero sequence measurement selection | PV measurement |  |  |  | 0: PV measurement, 1: BB measurement | 1 | 1 | 1
851 | 1600 | Protection | AC configuration and protections > Current protections > Directional over-current | I> direct. 1 | Directional overcurrent (ANSI 67) | 120 | -200 | 200 | % |  | 1 | 0 | 32000 |  |  | Trip MB
852 | 1610 | Protection | AC configuration and protections > Current protections > Directional over-current | I> direct. 2 | Directional overcurrent (ANSI 67) | 130 | -200 | 200 | % |  | 1 | 0 | 32000 |  |  | Trip MB
873 | 1620 | Protection | Busbar > Voltage protections > Voltage unbalance | BB unbalance U | Busbar unbalanced voltage (ANSI 60) | 6 | 0 | 50 | % |  | 100 | 1 | 1000 |  |  | Warning
58 | 1710 | Protection | AC configuration and protections > Current protections > Unbalance current | Unbalance I 2 | PV unbalanced current level 2 (ANSI 60) | 40 | 0 | 100 | % |  | 100 | 1 | 1000 |  |  | Trip PVB
1494 | 1721 | Protection | AC configuration and protections > Current protections > Neutral inverse time over-current (4th CT) | In> inverse Type | In> curve selection (IEC/IEEE inverse time overcurrent (ANSI 51)) | IEC Inverse |  |  |  | 0: IEC Inverse, 1: IEC Very Inverse, 2: IEC Extremely Inv., 3: IEEE Moderately Inv., 4: IEEE Very Inverse, 5: IEEE Extremely Inv., 6: Custom
1495 | 1722 | Protection | AC configuration and protections > Current protections > Neutral inverse time over-current (4th CT) | In> inverse Limit | In> (IEC/IEEE inverse time overcurrent (ANSI 51)) | 30 | 2 | 120 | %
1496 | 1723 | Protection | AC configuration and protections > Current protections > Neutral inverse time over-current (4th CT) | In> inverse TMS | In> (IEC/IEEE inverse time overcurrent (ANSI 51)) | 1 | 0.01 | 100 | /100
1497 | 1724 | Protection | AC configuration and protections > Current protections > Neutral inverse time over-current (4th CT) | In> inverse k | In> (IEC/IEEE inverse time overcurrent (ANSI 51)) | 0.14 | 0.001 | 32 | s
1498 | 1725 | Protection | AC configuration and protections > Current protections > Neutral inverse time over-current (4th CT) | In> inverse c | In> (IEC/IEEE inverse time overcurrent (ANSI 51)) | 0 | 0 | 32 | s
1499 | 1726 | Protection | AC configuration and protections > Current protections > Neutral inverse time over-current (4th CT) | In> inverse a | In> (IEC/IEEE inverse time overcurrent (ANSI 51)) | 0.02 | 0.001 | 32 | /1000
1500 | 1727 | Protection | AC configuration and protections > Current protections > Neutral inverse time over-current (4th CT) | In> inverse | In> (IEC/IEEE inverse time overcurrent) | [10 empty] | Trip PVB
1501 | 1731 | Protection | AC configuration and protections > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse Type | Ie> curve selection (IEC/IEEE inverse time overcurrent) | IEC Inverse |  |  |  | 0: IEC Inverse, 1: IEC Very Inverse, 2: IEC Extremely Inv., 3: IEEE Moderately Inv., 4: IEEE Very Inverse, 5: IEEE Extremely Inv., 6: Custom
1502 | 1732 | Protection | AC configuration and protections > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse Limit | Ie> (IEC/IEEE inverse time overcurrent) | 10 | 2 | 120 | %
1503 | 1733 | Protection | AC configuration and protections > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse TMS | Ie> (IEC/IEEE inverse time overcurrent) | 1 | 0.01 | 100 | /100
1504 | 1734 | Protection | AC configuration and protections > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse k | Ie> (IEC/IEEE inverse time overcurrent) | 0.14 | 0.001 | 32 | s
1505 | 1735 | Protection | AC configuration and protections > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse c | Ie> (IEC/IEEE inverse time overcurrent) | 0 | 0 | 32 | s
1506 | 1736 | Protection | AC configuration and protections > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse a | Ie> (IEC/IEEE inverse time overcurrent) | 0.02 | 0.001 | 32 | /1000
1507 | 1737 | Protection | AC configuration and protections > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse | Ie> (IEC/IEEE inverse time overcurrent) | [10 empty] | Trip PVB
859 | 1920 | Protection | Busbar > Frequency protections > Over-frequency | BB f> 4 | Busbar overfrequency protection level 4 (ANSI 81) | 102 | 100 | 120 | % |  | 5600 | 1500 | 6000 |  |  | Warning
860 | 1930 | Protection | Busbar > Frequency protections > Under-frequency | BB f< 5 | Busbar underfrequency protection level 5 (ANSI 81) | 95 | 80 | 100 | % |  | 5600 | 1500 | 6000 |  |  | Warning
1413 | 1960 | Protection | AC configuration and protections > Voltage protections > Under-voltage with reverse vars | U and Q < 1 | U and Q< (Undervoltage and reactive power (ANSI 27+32RV) | 85 | 40 | 100 | % |  | 5 | 1 | 32000 |  |  | Warning
1414 | 1970 | Protection | AC configuration and protections > Voltage protections > Under-voltage with reverse vars | U and Q < 2 | U and Q< (Undervoltage and reactive power (ANSI 27+32RV) | 85 | 40 | 100 | % |  | 5 | 1 | 32000 |  |  | Warning
1273 | 1981 | Protection | Breakers > PV breaker > Breaker monitoring | PVB ext tripped | PVB externally tripped alarm | [10 empty] | Warning
1274 | 1983 | Protection | Breakers > Mains breaker > Breaker monitoring | MB Ext. tripped | Mains Breaker externally tripped alarm | [10 empty] | Warning
1691 | 1991 | Protection | AC configuration and protections > Voltage protections > Under-voltage with reverse vars | I min. 1 | (U and Q< 1: Min Current level) | 0 | 0 | 20 | %
1692 | 1992 | Protection | AC configuration and protections > Voltage protections > Under-voltage with reverse vars | Angle 1 | (U and Q< 1: Min Phi angle) | 0 | 0 | 6 | deg
1693 | 1993 | Protection | AC configuration and protections > Voltage protections > Under-voltage with reverse vars | I min. 2 | (U and Q< 2: Min Current level) | 0 | 0 | 20 | %
1694 | 1994 | Protection | AC configuration and protections > Voltage protections > Under-voltage with reverse vars | Angle 2 | (U and Q< 2: Min Phi angle) | 0 | 0 | 6 | deg
1307 | 2111 | Synchronisation | AC configuration and protections > AC configuration > Voltage and frequency OK > Blackout / Hz/V OK | Blackout / f< | Max. allowable frequency difference from nominal setting BELOW nominal for closing in case of blackout. This setting is also used to determine Hz/V OK | 3 | 0 | 5 | Hz
94 | 2112 | Synchronisation | AC configuration and protections > AC configuration > Voltage and frequency OK > Blackout / Hz/V OK | Blackout / f> | Max. allowable frequency difference from nominal setting ABOVE nominal for closing in case of blackout. This setting is also used to determine Hz/V OK | 3 | 0 | 5 | Hz
1308 | 2113 | Synchronisation | AC configuration and protections > AC configuration > Voltage and frequency OK > Blackout / Hz/V OK | Blackout / U< | Max. allowable voltage difference from nominal setting BELOW nominal for closing in case of blackout. This setting is also used to determine Hz/V OK | 5 | 2 | 20 | %
95 | 2114 | Synchronisation | AC configuration and protections > AC configuration > Voltage and frequency OK > Blackout / Hz/V OK | Blackout / U> | Max. allowable voltage difference from nominal setting ABOVE nominal for closing in case of blackout. This setting is also used to determine Hz/V OK | 5 | 2 | 20 | %
100 | 2150 | Synchronisation | AC configuration and protections > AC configuration > Phase sequence error | Phase seq error PV | Supervision of the rotation direction of BA | [5 empty] | 10 | 10 | 10 |  |  | Warning
1193 | 2154 | Synchronisation | AC configuration and protections > AC configuration > Phase direction | Phase rotation | Expected direction of the phase rotation | L1L2L3 |  |  |  | 0: L1L2L3, 1: L1L3L2
1616 | 2155 | Synchronisation | Busbar > AC configuration > Phase sequence error | Phase seq error BB | Supervision of the rotation direction of BB | [5 empty] | 10 | 10 | 10 |  |  | Warning
101 | 2160 | Synchronisation | Breakers > PV breaker > Breaker monitoring | PVB open fail | PV breaker open failure | [5 empty] | 20 | 10 | 100 |  |  | Warning
102 | 2170 | Synchronisation | Breakers > PV breaker > Breaker monitoring | PVB close fail | PV breaker close failure | [5 empty] | 20 | 10 | 9000 |  |  | Warning
103 | 2180 | Synchronisation | Breakers > PV breaker > Breaker monitoring | PVB pos fail | PV breaker position feedback failure | [5 empty] | 10 | 10 | 50 |  |  | Warning
107 | 2200 | Synchronisation | Breakers > Mains breaker > Breaker monitoring | MB Open fail | Mains breaker open failure | [5 empty] | 20 | 10 | 100 |  |  | Warning
108 | 2210 | Synchronisation | Breakers > Mains breaker > Breaker monitoring | MB Close fail | Mains breaker close failure | [5 empty] | 20 | 10 | 50 |  |  | Warning
109 | 2220 | Synchronisation | Breakers > Mains breaker > Breaker monitoring | MB Pos fail | Mains breaker position feedback failure | [5 empty] | 10 | 10 | 50 |  |  | Warning
1646 | 2320 | Synchronisation | Power management > Busbar blocked alarms | Busbar blocked | Busbar blocked by pos failure | [5 empty] | 10 | 10 | 50 |  |  | Warning
146 | 2611 | Regulation | Regulation > PV loading and deloading > Ramp up rates | P ramp up | P ramp up speed | 2 | 0.1 | 100 | %/s
148 | 2621 | Regulation | Regulation > PV loading and deloading > Ramp down and offload rates | P ramp down | P ramp down speed | 2 | 0.1 | 100 | %/s
149 | 2622 | Regulation | Regulation > PV loading and deloading > Ramp down and offload rates | Ramp open point | Max. allowable power when opening the breaker | 5 | 1 | 20 | %
228 | 2631 | Regulation |  | Closed loop | Compensate for loses to achieve requested power at PV measuring point
879 | 2641 | Regulation | Regulation > PV loading and deloading > Ramp up rates | Q ramp up | Q ramp up speed | 2 | 0.1 | 100 | %/s
1589 | 2642 | Regulation | Regulation > PV loading and deloading | Q ramp lim. max | Ignore Q ramp in between of these min and max values | 90 | 1 | 110 | %
880 | 2651 | Regulation | Regulation > PV loading and deloading > Ramp down and offload rates | Q ramp down | Q ramp down speed | 2 | 0.1 | 100 | %/s
1588 | 2652 | Regulation | Regulation > PV loading and deloading | Q ramp lim. min | Ignore Q ramp in between of these min and max values | -10 | -20 | 50 | %
487 | 2671 | Regulation | Regulation > P reference gain | P ref. const. gain | Sets a constant local offset to the active power reference based on a percentage of nominel S to compensate for a constant power loss. | 0 | 0 | 10 | %
488 | 2672 | Regulation | Regulation > P reference gain | P ref. dyn. gain | Sets a dynamic local offset to the active power reference based on a percentage of the normal reference to compensate for a dynamic power loss. | 0 | 0 | 10 | %
1938 | 2681 | Regulation | Regulation > PV loading and deloading > Ramp delays | P ramp delay | Minimum time between updating of ramped active power setpoint | 1 | 0 | 2 | s
1939 | 2682 | Regulation | Regulation > PV loading and deloading > Ramp delays | Q ramp delay | Minimum time between updating of ramped reactive power setpoint | 1 | 0 | 2 | s
178 | 2741 | Regulation | Regulation > Delay regulation | Delay reg. | Keep reference at minimum dispatch at selected duration after start initiated | [5 empty] | 0 | 0 | 9900
183 | 2781 | Regulation | Regulation > Enable regulation | P reference | P reg. ena/dis. Applicable with single register (0x06) commands. With multiple register (0x10) commands P reg. always active
184 | 2782 | Regulation | Regulation > Enable regulation | Q reference | Q reg. ena/dis. Applicable with single register (0x06) commands. With multiple register (0x10) commands Q reg. always active
1557 | 2783 | Regulation | Power set points > P and Q ref enable/disable - Sunspec only | P ref. Enable | Sunspec only: P ref. ena/dis. Applicable with single register (0x06) commands. With multiple register (0x10) commands P ref enable always active
1558 | 2784 | Regulation | Power set points > P and Q ref enable/disable - Sunspec only | Q ref. Enable | Sunspec only: Q ref. ena/dis. Applicable with single register (0x06) commands. With multiple register (0x10) commands Q ref enable always active
241 | 2810 | Regulation |  | PV fallback tmr | Sunspec only: Sets the time in seconds before timeout for power limit | 0 | 0 | 28800 | sec
525 | 2821 | Regulation | Regulation > Hotel load | Hotel load setup | Enable hotel load | Multi input 20 |  |  |  | 0: Multi input 20, 1: Multi input 21, 2: Multi input 22, 3: Multi input 23
304 | 2823 | Regulation | Regulation > Hotel load | Hotel load range max | Hotel load transducer maximum setting | 0 | 0 | 20000 | kW
236 | 3490 | Digital In | I/O settings > Inputs > Digital input | Emergency STOP | Setup of digital input for emergency stop (terminal 4) | [5 empty] | 0 | 0 | 600 |  |  | Shutdown
1722 | 3570 | Digital In | Functions > M-Logic alarms > M-Logic alarm 01 | M-Logic alarm 01 | M-Logic alarm 1 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1723 | 3580 | Digital In | Functions > M-Logic alarms > M-Logic alarm 02 | M-Logic alarm 02 | M-Logic alarm 2 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1724 | 3590 | Digital In | Functions > M-Logic alarms > M-Logic alarm 03 | M-Logic alarm 03 | M-Logic alarm 3 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1725 | 3600 | Digital In | Functions > M-Logic alarms > M-Logic alarm 04 | M-Logic alarm 04 | M-Logic alarm 4 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1726 | 3610 | Digital In | Functions > M-Logic alarms > M-Logic alarm 05 | M-Logic alarm 05 | M-Logic alarm 5 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1824 | 3621 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 1 | M-Logic ext al 1 | Range selection for extended timer alarm 1 | Minute(s) - auto reset |  |  |  | 0: Minute(s) - manual reset, 1: Hour(s) - manual reset, 2: Day(s) - manual reset, 3: Minute(s) - auto reset, 4: Hour(s) - auto reset, 5: Day(s) - auto reset
1828 | 3622 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 1 | M-Logic ext al 1 | Extended timer alarm 1 setup | 50 | 1 | 3200
1825 | 3631 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 2 | M-Logic ext al 2 | Range selection for extended timer alarm 2 | Minute(s) - auto reset |  |  |  | 0: Minute(s) - manual reset, 1: Hour(s) - manual reset, 2: Day(s) - manual reset, 3: Minute(s) - auto reset, 4: Hour(s) - auto reset, 5: Day(s) - auto reset
1829 | 3632 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 2 | M-Logic ext al 2 | Extended timer alarm 2 setup | 50 | 1 | 3200
1826 | 3641 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 3 | M-Logic ext al 3 | Range selection for extended timer alarm 3 | Minute(s) - auto reset |  |  |  | 0: Minute(s) - manual reset, 1: Hour(s) - manual reset, 2: Day(s) - manual reset, 3: Minute(s) - auto reset, 4: Hour(s) - auto reset, 5: Day(s) - auto reset
1830 | 3642 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 3 | M-Logic ext al 3 | Extended timer alarm 3 setup | 50 | 1 | 3200
1827 | 3651 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 4 | M-Logic ext al 4 | Range selection for extended timer alarm 4 | Minute(s) - auto reset |  |  |  | 0: Minute(s) - manual reset, 1: Hour(s) - manual reset, 2: Day(s) - manual reset, 3: Minute(s) - auto reset, 4: Hour(s) - auto reset, 5: Day(s) - auto reset
1831 | 3652 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 4 | M-Logic ext al 4 | Extended timer alarm 4 setup | 50 | 1 | 3200
1853 | 3660 | Digital In | Functions > M-Logic alarms > M-Logic alarm 10 | M-Logic alarm 10 | M-Logic alarm 10 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1854 | 3670 | Digital In | Functions > M-Logic alarms > M-Logic alarm 11 | M-Logic alarm 11 | M-Logic alarm 11 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1855 | 3680 | Digital In | Functions > M-Logic alarms > M-Logic alarm 12 | M-Logic alarm 12 | M-Logic alarm 12 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1856 | 3690 | Digital In | Functions > M-Logic alarms > M-Logic alarm 13 | M-Logic alarm 13 | M-Logic alarm 13 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1857 | 3700 | Digital In | Functions > M-Logic alarms > M-Logic alarm 14 | M-Logic alarm 14 | M-Logic alarm 14 | [5 empty] | 100 | 0 | 32000 |  |  | Warning
1482 | 4601 | Analogue In | Functions > Delta alarms > Set 1 | Delta ana1 InpA | Input for A for analogue delta (A-B) alarm 1 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
1483 | 4602 | Analogue In | Functions > Delta alarms > Set 1 | Delta ana1 InpB | Input for B for analogue delta (A-B) alarm 1 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
1484 | 4603 | Analogue In | Functions > Delta alarms > Set 2 | Delta ana2 InpA | Input for A for analogue delta (A-B) alarm 2 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
1485 | 4604 | Analogue In | Functions > Delta alarms > Set 2 | Delta ana2 InpB | Input for B for analogue delta (A-B) alarm 2 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
1486 | 4605 | Analogue In | Functions > Delta alarms > Set 3 | Delta ana3 InpA | Input for A for analogue delta (A-B) alarm 3 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
1487 | 4606 | Analogue In | Functions > Delta alarms > Set 3 | Delta ana3 InpB | Input for B for analogue delta (A-B) alarm 3 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
1488 | 4610 | Analogue In | Functions > Delta alarms > Set 1 | Delta ana1 1 | Delta analogue alarm 1 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1489 | 4620 | Analogue In | Functions > Delta alarms > Set 1 | Delta ana1 2 | Delta analogue alarm 1 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1490 | 4630 | Analogue In | Functions > Delta alarms > Set 2 | Delta ana2 1 | Delta analogue alarm 2 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1491 | 4640 | Analogue In | Functions > Delta alarms > Set 2 | Delta ana2 2 | Delta analogue alarm 2 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1492 | 4650 | Analogue In | Functions > Delta alarms > Set 3 | Delta ana3 1 | Delta analogue alarm 3 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1493 | 4660 | Analogue In | Functions > Delta alarms > Set 3 | Delta ana3 2 | Delta analogue alarm 3 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1678 | 4671 | Analogue In | Functions > Delta alarms > Set 4 | Delta ana4 InpA | Input for A for analogue delta (A-B) alarm 4 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
1679 | 4672 | Analogue In | Functions > Delta alarms > Set 4 | Delta ana4 InpB | Input for B for analogue delta (A-B) alarm 4 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
1680 | 4673 | Analogue In | Functions > Delta alarms > Set 5 | Delta ana5 InpA | Input for A for analogue delta (A-B) alarm 5 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
1681 | 4674 | Analogue In | Functions > Delta alarms > Set 5 | Delta ana5 InpB | Input for B for analogue delta (A-B) alarm 5 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
1682 | 4675 | Analogue In | Functions > Delta alarms > Set 6 | Delta ana6 InpA | Input for A for analogue delta (A-B) alarm 6 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
1683 | 4676 | Analogue In | Functions > Delta alarms > Set 6 | Delta ana6 InpB | Input for B for analogue delta (A-B) alarm 6 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
1684 | 4680 | Analogue In | Functions > Delta alarms > Set 4 | Delta ana4 1 | Delta analogue alarm 4 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1685 | 4690 | Analogue In | Functions > Delta alarms > Set 4 | Delta ana4 2 | Delta analogue alarm 4 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1686 | 4700 | Analogue In | Functions > Delta alarms > Set 5 | Delta ana5 1 | Delta analogue alarm 5 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1687 | 4710 | Analogue In | Functions > Delta alarms > Set 5 | Delta ana5 2 | Delta analogue alarm 5 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1688 | 4720 | Analogue In | Functions > Delta alarms > Set 6 | Delta ana6 1 | Delta analogue alarm 6 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
1689 | 4730 | Analogue In | Functions > Delta alarms > Set 6 | Delta ana6 2 | Delta analogue alarm 6 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990 |  |  | Warning
315 | 4960 | Analogue In | AC configuration and protections > Battery/Aux supply > Alarms | U< aux. term. 1 | Low supply voltage (terminals 1 and 2) | 18 | 8 | 32 | V |  | 10 | 0 | 9990 |  |  | Warning
316 | 4970 | Analogue In | AC configuration and protections > Battery/Aux supply > Alarms | U> aux. term. 1 | High supply voltage (terminals 1 and 2) | 30 | 12 | 36 | V |  | 10 | 0 | 9990 |  |  | Warning
352 | 5802 | Outputs | I/O settings > Outputs > Transducer > Output 52 limits | AOUT 52 Limits | Minimum limit for analogue output 52 | -10 | -10.5 | 5 | V
353 | 5803 | Outputs | I/O settings > Outputs > Transducer > Output 52 limits | AOUT 52 Limits | Maximum limit for analogue output 52 | 10 | -5 | 10.5 | V
354 | 5812 | Outputs | I/O settings > Outputs > Transducer > Output 55 limits | AOUT 55 Limits | Minimum limit for analogue output 55 | -10 | -10.5 | 5 | V
355 | 5813 | Outputs | I/O settings > Outputs > Transducer > Output 55 limits | AOUT 55 Limits | Maximum limit for analogue output 55 | 10 | -5 | 10.5 | V
356 | 5823 | Outputs | I/O settings > Outputs > Transducer > kW > P output actual | P1 Output type | Power transducer output type | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
391 | 5824 | Outputs | I/O settings > Outputs > Transducer > kW > P output actual | P1 Output max | Transducer output maximum scale for PV active power 1 | 500 | 0 | 20000 | kW
374 | 5825 | Outputs | I/O settings > Outputs > Transducer > kW > P output actual | P1 Output min | Transducer output minimum scale for PV active power 1 | 0 | -9999 | 20000 | kW
359 | 5853 | Outputs | I/O settings > Outputs > Transducer > kVA | S Output type | Apparent power transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
394 | 5854 | Outputs | I/O settings > Outputs > Transducer > kVA | S Output max | Transducer output maximum scale for PV apparent power | 600 | 0 | 20000 | kVA
377 | 5855 | Outputs | I/O settings > Outputs > Transducer > kVA | S Output min | Transducer output minimum scale for PV apparent power | 0 | 0 | 20000 | kVA
360 | 5863 | Outputs | I/O settings > Outputs > Transducer > kvar | Q Output type | Reactive power transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
395 | 5864 | Outputs | I/O settings > Outputs > Transducer > kvar | Q Output max | Transducer output maximum scale for PV reactive power | 400 | 0 | 16000 | kvar
378 | 5865 | Outputs | I/O settings > Outputs > Transducer > kvar | Q Output min | Transducer output minimum scale for PV reactive power | 0 | -8000 | 16000 | kvar
361 | 5873 | Outputs | I/O settings > Outputs > Transducer > Cos phi | PF Output type | Power factor transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
396 | 5874 | Outputs | I/O settings > Outputs > Transducer > Cos phi | PF Output max | Transducer output maximum scale for the power factor | 0.8 | 0.5 | 0.99 | PF
379 | 5875 | Outputs | I/O settings > Outputs > Transducer > Cos phi | PF Output min | Transducer output minimum scale for the power factor | -0.8 | -0.99 | -0.5 | PF
362 | 5883 | Outputs | I/O settings > Outputs > Transducer > PV Hz | f Output type | PV frequency transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
397 | 5884 | Outputs | I/O settings > Outputs > Transducer > PV Hz | f Output max | Transducer output maximum scale for PV frequency | 55 | 0 | 70 | Hz
380 | 5885 | Outputs | I/O settings > Outputs > Transducer > PV Hz | f Output min | Transducer output minimum scale for PV frequency | 45 | 0 | 70 | Hz
363 | 5893 | Outputs | I/O settings > Outputs > Transducer > PV voltage | U Output type | PV voltage transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
398 | 5894 | Outputs | I/O settings > Outputs > Transducer > PV voltage | U Output max | Transducer output maximum scale for PV voltage | 500 | 0 | 28000 | V
381 | 5895 | Outputs | I/O settings > Outputs > Transducer > PV voltage | U Output min | Transducer output minimum scale for PV voltage | 0 | 0 | 28000 | V
364 | 5903 | Outputs | I/O settings > Outputs > Transducer > Ampere | I Output type | Current transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
399 | 5904 | Outputs | I/O settings > Outputs > Transducer > Ampere | I Output max | Transducer output maximum scale for current | 1000 | 0 | 9000 | A
382 | 5905 | Outputs | I/O settings > Outputs > Transducer > Ampere | I Output min | Transducer output minimum scale for current | 0 | 0 | 9000 | A
365 | 5913 | Outputs | I/O settings > Outputs > Transducer > Busbar voltage | U BB Output type | Busbar voltage transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
400 | 5914 | Outputs | I/O settings > Outputs > Transducer > Busbar voltage | U BB Output max | Transducer output maximum scale for busbar voltage | 500 | 0 | 28000 | V
383 | 5915 | Outputs | I/O settings > Outputs > Transducer > Busbar voltage | U BB Output min | Transducer output minimum scale for busbar voltage | 0 | 0 | 28000 | V
366 | 5923 | Outputs | I/O settings > Outputs > Transducer > Busbar Hz | f BB Output type | Busbar frequency transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
401 | 5924 | Outputs | I/O settings > Outputs > Transducer > Busbar Hz | f BB Output max | Transducer output maximum scale for busbar frequency | 55 | 0 | 70 | Hz
384 | 5925 | Outputs | I/O settings > Outputs > Transducer > Busbar Hz | f BB Output min | Transducer output minimum scale for busbar frequency | 45 | 0 | 70 | Hz
367 | 5933 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 20 | Inp. 20 Output type | Transducer output signal for Multi-input 20 | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
402 | 5934 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 20 | Inp. 20 Output max | Transducer output maximum scale for multi input 20 | 500 | -28000 | 28000
385 | 5935 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 20 | Inp. 20 Output min | Transducer output minimum scale for multi input 20 | 0 | -28000 | 28000
368 | 5943 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 21 | Inp. 21 Output type | Transducer output signal for Multi-input 21 | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
403 | 5944 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 21 | Inp. 21 Output max | Transducer output maximum scale for multi input 21 | 500 | -28000 | 28000
386 | 5945 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 21 | Inp. 21 Output min | Transducer output minimum scale for multi input 21 | 0 | -28000 | 28000
369 | 5953 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 22 | Inp. 22 Output type | Transducer output signal for Multi-input 22 | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V
404 | 5954 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 22 | Inp. 22 Output max | Transducer output maximum scale for multi input 22 | 500 | -28000 | 28000
387 | 5955 | Outputs | I/O settings > Outputs > Transducer > Multi input > Multi input 22 | Inp. 22 Output min | Transducer output minimum scale for multi input 22 | 0 | -28000 | 28000
407 | 6001 | General | Basic settings > Nominal settings > Frequency | Nom. f 1 | Nominal PV frequency set point 1 | 50 | 48 | 62 | Hz
408 | 6002 | General | Basic settings > Nominal settings > Power > 3 phase nominal | Nom. P 1 | Nominal PV power set point 1 | 480 | 10 | 20000 | kW
409 | 6003 | General | Basic settings > Nominal settings > Current > 3 phase nominal | Nom. I 1 | Nominal PV current set point 1 | 867 | 0 | 9000 | A
410 | 6004 | General | Basic settings > Nominal settings > Voltage > PV nominal U | Nom. U 1 | Nominal PV voltage set point 1 | 400 | 100 | 25000 | V
596 | 6005 | General | Basic settings > Nominal settings > Power > 3 phase nominal | Nom. Q 1 | Nominal PV reactive power set point 1 | 480 | 10 | 20000 | kvar
742 | 6006 | General | Basic settings > Nominal settings > Power > 3 phase nominal | Nom. S 1 | Nominal PV apparent power set point 1 | 480 | 10 | 20000 | kVA
412 | 6007 | General | Alternative configuration > PV nominal settings > Nominal set selection | Enable nom. set | Selection of nominal setting to be used | Nominal setting 1 |  |  |  | 0: Nominal setting 1, 1: Nominal setting 2, 2: Nominal setting 3, 3: Nominal setting 4
1460 | 6008 | General | Basic settings > Nominal settings > Current > 4th CT nominal | Nom. I E/N/M 1 | Nom I E/N/M 1 (Nominal current Earth/Neutral/Mains set point 1) | 867 | 0 | 9000 | A
413 | 6011 | General | Alternative configuration > PV nominal settings > Nominal settings 2 | Nom. f 2 | Nominal PV frequency set point 2 | 50 | 48 | 62 | Hz
414 | 6012 | General | Alternative configuration > PV nominal settings > Nominal settings 2 | Nom. P 2 | Nominal PV power set point 2 | 230 | 10 | 20000 | kW
415 | 6013 | General | Alternative configuration > PV nominal settings > Nominal settings 2 | Nom. I 2 | Nominal PV current set point 2 | 345 | 0 | 9000 | A
416 | 6014 | General | Alternative configuration > PV nominal settings > Nominal settings 2 | Nom. U 2 | Nominal PV voltage set point 2 | 400 | 100 | 25000 | V
597 | 6015 | General | Alternative configuration > PV nominal settings > Nominal settings 2 | Nom. Q 2 | Nominal PV reactive power set point 2 | 230 | 10 | 20000 | kvar
743 | 6016 | General | Alternative configuration > PV nominal settings > Nominal settings 2 | Nom. S 2 | Nominal PV apparent power set point 2 | 230 | 10 | 20000 | kVA
1461 | 6017 | General | Alternative configuration > PV nominal settings > Nominal settings 2 | Nom. I E/N/M 2 | Nom I E/N/M 2 (Nominal current Earth/Neutral/Mains set point 2) | 867 | 0 | 9000 | A
418 | 6021 | General | Alternative configuration > PV nominal settings > Nominal settings 3 | Nom. f 3 | Nominal PV frequency set point 3 | 60 | 48 | 62 | Hz
419 | 6022 | General | Alternative configuration > PV nominal settings > Nominal settings 3 | Nom. P 3 | Nominal PV power set point 3 | 230 | 10 | 20000 | kW
420 | 6023 | General | Alternative configuration > PV nominal settings > Nominal settings 3 | Nom. I 3 | Nominal PV current set point 3 | 345 | 0 | 9000 | A
421 | 6024 | General | Alternative configuration > PV nominal settings > Nominal settings 3 | Nom. U 3 | Nominal PV voltage set point 3 | 400 | 100 | 25000 | V
598 | 6025 | General | Alternative configuration > PV nominal settings > Nominal settings 3 | Nom. Q 3 | Nominal PV reactive power set point 3 | 230 | 10 | 20000 | kvar
744 | 6026 | General | Alternative configuration > PV nominal settings > Nominal settings 3 | Nom. S 3 | Nominal PV apparent power set point 3 | 230 | 10 | 20000 | kVA
1462 | 6027 | General | Alternative configuration > PV nominal settings > Nominal settings 3 | Nom. I E/N/M 3 | Nom I E/N/M 3 (Nominal current Earth/Neutral/Mains set point 3) | 867 | 0 | 9000 | A
423 | 6031 | General | Alternative configuration > PV nominal settings > Nominal settings 4 | Nom. f 4 | Nominal PV frequency set point 4 | 60 | 48 | 62 | Hz
424 | 6032 | General | Alternative configuration > PV nominal settings > Nominal settings 4 | Nom. P 4 | Nominal PV power set point 4 | 230 | 10 | 20000 | kW
425 | 6033 | General | Alternative configuration > PV nominal settings > Nominal settings 4 | Nom. I 4 | Nominal PV current set point 4 | 345 | 0 | 9000 | A
426 | 6034 | General | Alternative configuration > PV nominal settings > Nominal settings 4 | Nom. U 4 | Nominal PV voltage set point 4 | 400 | 100 | 25000 | V
599 | 6035 | General | Alternative configuration > PV nominal settings > Nominal settings 4 | Nom. Q 4 | Nominal PV reactive power set point 4 | 230 | 10 | 20000 | kvar
745 | 6036 | General | Alternative configuration > PV nominal settings > Nominal settings 4 | Nom. S 4 | Nominal PV apparent power set point 4 | 230 | 10 | 20000 | kVA
1463 | 6037 | General | Alternative configuration > PV nominal settings > Nominal settings 4 | Nom. I E/N/M 4 | Nom I E/N/M 4 (Nominal current Earth/Neutral/Mains set point 4) | 867 | 0 | 9000 | A
428 | 6041 | General | Basic settings > Measurement setup > Voltage transformer > PV VT | PV primary U | PV voltage transformer value primary side | 400 | 100 | 25000 | V
429 | 6042 | General | Basic settings > Measurement setup > Voltage transformer > PV VT | PV secondary U | PV voltage transformer value secondary side | 400 | 100 | 690 | V
430 | 6043 | General | Basic settings > Measurement setup > Current transformer > 3 phase CT | PV Primary I | PV current transformer value primary side | 1000 | 5 | 9000 | A
431 | 6044 | General | Basic settings > Measurement setup > Current transformer > 3 phase CT | PV Secondary I | PV current transformer value secondary side | 1A |  |  |  | 1: 1A, 5: 5A
1383 | 6045 | General | Basic settings > Measurement setup > Current transformer > 4th CT | E/N/M primary I | E/N/M Primary I (Earth/Neutral/Mains current transformer value Primary side) | 1000 | 5 | 9000 | A
1384 | 6046 | General | Basic settings > Measurement setup > Current transformer > 4th CT | E/N/M secondary I | E/N/M Secondary I (Earth/Neutral/Mains current transformer value secondary side) | 1A |  |  |  | 1: 1A, 5: 5A
432 | 6051 | General | Basic settings > Measurement setup > Voltage transformer > Busbar VT | BB primary U 1 | Busbar voltage transformer value primary side set point 1 | 400 | 100 | 25000 | V
433 | 6052 | General | Basic settings > Measurement setup > Voltage transformer > Busbar VT | BB second. U 1 | Busbar voltage transformer value secondary side set point 1 | 400 | 100 | 690 | V
1326 | 6053 | General | Basic settings > Nominal settings > Voltage > Busbar nominal U | BB nominal U 1 | Nominal busbar voltage set point 1 | 400 | 100 | 25000 | V
1582 | 6054 | General | Alternative configuration > Busbar nominal settings > Nominal set selection | Bus nom. set | Selection of nominal busbar setting to be used | Parameter set 1 |  |  |  | 0: Parameter set 1, 1: Parameter set 2, 2: BB Unom = PV Unom
1664 | 6055 | General | Basic settings > Nominal settings > Power > 4th CT nominal | 4th CT nom. P 1 | 4th CT Nominal power set point 1 | 480 | 10 | 9000 | kW
1579 | 6061 | General | Alternative configuration > Busbar nominal settings > Nominal settings 2 | BB primary U 2 | Busbar voltage transformer value primary side set point 2 | 400 | 100 | 25000 | V
1580 | 6062 | General | Alternative configuration > Busbar nominal settings > Nominal settings 2 | BB second. U 2 | Busbar voltage transformer value secondary side set point 2 | 400 | 100 | 690 | V
1578 | 6063 | General | Alternative configuration > Busbar nominal settings > Nominal settings 2 | BB nominal U 2 | Nominal busbar voltage set point 2 | 400 | 100 | 25000 | V
1665 | 6064 | General | Alternative configuration > Busbar nominal settings > Nominal settings 2 | 4th CT nom. P 2 | 4th CT Nominal power set point 2 | 230 | 10 | 9000 | kW
435 | 6071 | General | Basic settings > Application type > Plant type > Plant mode | Operation mode | PV operation mode | Power management |  |  |  | 0: Island operation, 2: Peak shaving, 3: Fixed power, 4: Mains Power Export, 6: Power management
436 | 6081 | General | Basic settings > Controller settings > Language | Language | Language selection | English |  |  |  | 0: English, 1: Language 1, 2: Language 2, 3: Language 3, 4: Language 4, 5: Language 5, 6: Language 6, 7: Language 7, 8: Language 8, 9: Language 9, 10: Language 10
486 | 6082 | General | Basic settings > Controller settings > Display | LED mimic | Change LED mimic scheme | Standard |  |  |  | 1: Standard, 3: Guided
485 | 6084 | General | Basic settings > Controller settings > Display | LED colors | Change LED color scheme | LED Color Scheme 1 |  |  |  | 0: LED Color Scheme 1, 1: LED Color Scheme 2
449 | 6130 | General | Functions > Alarm horn timer | Alarm horn | Setup of the alarm horn timer | [5 empty] | 200 | 0 | 9900
452 | 6160 | General | Regulation > Run status | Run status | Setup of the run status output | [5 empty] | 50 | 0 | 3000
1617 | 6241 | General | Regulation > PV derate settings > Derate settings 1 | Instant S max 1 | Derate apparent power as a function of analog input | Multi input 20 |  |  |  | 0: Multi input 20, 1: Multi input 21, 2: Multi input 22, 3: Multi input 23, 4: MLogic, 18: CIO 308 1.08, 19: CIO 308 1.11, 20: CIO 308 1.14, 21: CIO 308 1.17, 22: CIO 308 1.20, 23: CIO 308 1.23, 24: CIO 308 1.26, 25: CIO 308 1.29, 26: CIO 308 2.08, 27: CIO 308 2.11, 28: CIO 308 2.14, 29: CIO 308 2.17, 30: CIO 308 2.20, 31: CIO 308 2.23, 32: CIO 308 2.26, 33: CIO 308 2.29, 34: CIO 308 3.08, 35: CIO 308 3.11, 36: CIO 308 3.14, 37: CIO 308 3.17, 38: CIO 308 3.20, 39: CIO 308 3.23, 40: CIO 308 3.26, 41: CIO 308 3.29
1618 | 6242 | General | Regulation > PV derate settings > Derate settings 1 | Start derate at | Start point | 16 | 0 | 20000
1619 | 6243 | General | Regulation > PV derate settings > Derate settings 1 | Derate slope | Rate of derate | 5 | 0.1 | 100 | %
1620 | 6246 | General | Regulation > PV derate settings > Derate settings 1 | Derate limit | Derate start limit and selection of Proportional or inverse slope | 80 | 0 | 100 | %
1621 | 6251 | General | Regulation > PV derate settings > Derate settings 2 | Instant S max 2 | Derate apparent power as a function of analog input | Multi input 20 |  |  |  | 0: Multi input 20, 1: Multi input 21, 2: Multi input 22, 3: Multi input 23, 4: MLogic, 5: EIC Cooling water temp., 6: EIC Oil temp., 7: EIC Ambient temp., 8: EIC Intercool temp., 9: EIC Fuel temp., 18: CIO 308 1.08, 19: CIO 308 1.11, 20: CIO 308 1.14, 21: CIO 308 1.17, 22: CIO 308 1.20, 23: CIO 308 1.23, 24: CIO 308 1.26, 25: CIO 308 1.29, 26: CIO 308 2.08, 27: CIO 308 2.11, 28: CIO 308 2.14, 29: CIO 308 2.17, 30: CIO 308 2.20, 31: CIO 308 2.23, 32: CIO 308 2.26, 33: CIO 308 2.29, 34: CIO 308 3.08, 35: CIO 308 3.11, 36: CIO 308 3.14, 37: CIO 308 3.17, 38: CIO 308 3.20, 39: CIO 308 3.23, 40: CIO 308 3.26, 41: CIO 308 3.29
1622 | 6252 | General | Regulation > PV derate settings > Derate settings 2 | Start derate at | Start point | 16 | 0 | 20000
1623 | 6253 | General | Regulation > PV derate settings > Derate settings 2 | Derate slope | Rate of derate | 5 | 0.1 | 100 | %
1624 | 6256 | General | Regulation > PV derate settings > Derate settings 2 | Derate limit | Derate start limit and selection of Proportional or inverse slope | 80 | 0 | 100 | %
474 | 6261 | General | Regulation > PV derate settings > Derate settings 3 | Instant S max 3 | Derate apparent power as a function of analog input | Multi input 20 |  |  |  | 0: Multi input 20, 1: Multi input 21, 2: Multi input 22, 3: Multi input 23, 4: MLogic, 18: CIO 308 1.08, 19: CIO 308 1.11, 20: CIO 308 1.14, 21: CIO 308 1.17, 22: CIO 308 1.20, 23: CIO 308 1.23, 24: CIO 308 1.26, 25: CIO 308 1.29, 26: CIO 308 2.08, 27: CIO 308 2.11, 28: CIO 308 2.14, 29: CIO 308 2.17, 30: CIO 308 2.20, 31: CIO 308 2.23, 32: CIO 308 2.26, 33: CIO 308 2.29, 34: CIO 308 3.08, 35: CIO 308 3.11, 36: CIO 308 3.14, 37: CIO 308 3.17, 38: CIO 308 3.20, 39: CIO 308 3.23, 40: CIO 308 3.26, 41: CIO 308 3.29
475 | 6262 | General | Regulation > PV derate settings > Derate settings 3 | Start derate at | Start point | 16 | 0 | 20000
476 | 6263 | General | Regulation > PV derate settings > Derate settings 3 | Derate slope | Rate of derate | 5 | 0.1 | 100 | %
477 | 6266 | General | Regulation > PV derate settings > Derate settings 3 | Derate limit | Derate start limit and selection of Proportional or inverse slope | 80 | 0 | 100 | %
518 | 6490 | General | Basic settings > Summer/Winter Time | Summer/Winter time | Enable switch to summer time
522 | 6540 | General | Functions > Not in Auto | Not in AUTO | Alarm for unit not in auto | [5 empty] | 3000 | 100 | 9000
1912 | 6951 | General | Functions > Command timer > Command timer 1 | Command timer 1 week | Select which week(s) in month command timer 1 start/stop is active | All weeks in month |  |  |  | 0: All weeks in month, 1: First week (1 - 7), 2: Second week (8 - 14), 3: Third week (15 - 21), 4: Fourth week (22 - 28)
1913 | 6952 | General | Functions > Command timer > Command timer 2 | Command timer 2 week | Select which week(s) in month command timer 2 start/stop is active | All weeks in month |  |  |  | 0: All weeks in month, 1: First week (1 - 7), 2: Second week (8 - 14), 3: Third week (15 - 21), 4: Fourth week (22 - 28)
1914 | 6953 | General | Functions > Command timer > Command timer 3 | Command timer 3 week | Select which week(s) in month command timer 3 start/stop is active | All weeks in month |  |  |  | 0: All weeks in month, 1: First week (1 - 7), 2: Second week (8 - 14), 3: Third week (15 - 21), 4: Fourth week (22 - 28)
1915 | 6954 | General | Functions > Command timer > Command timer 4 | Command timer 4 week | Select which week(s) in month command timer 4 start/stop is active | All weeks in month |  |  |  | 0: All weeks in month, 1: First week (1 - 7), 2: Second week (8 - 14), 3: Third week (15 - 21), 4: Fourth week (22 - 28)
701 | 6961 | General | Functions > Command timer > Command timer 1 | Start timer 1 | Setup day(s) for activation of Command timer 1 | OFF |  |  |  | 0: OFF, 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
702 | 6962 | General | Functions > Command timer > Command timer 1 | Start timer 1 | Setup of hour for activation of Command timer 1 | 10 | 0 | 23 | Hours
703 | 6963 | General | Functions > Command timer > Command timer 1 | Start timer 1 | Setup of minute for activation of Command timer 1 | 0 | 0 | 59
705 | 6964 | General | Functions > Command timer > Command timer 1 | Stop timer 1 | Setup day(s) for deactivation of Command timer 1 | MO-TU-WE-TH-FR-SA-SU |  |  |  | 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
706 | 6965 | General | Functions > Command timer > Command timer 1 | Stop timer 1 | Setup of hour for deactivation of Command timer 1 | 10 | 0 | 23 | Hours
707 | 6966 | General | Functions > Command timer > Command timer 1 | Stop timer 1 | Setup of minute for deactivation of Command timer 1 | 0 | 0 | 59
709 | 6971 | General | Functions > Command timer > Command timer 2 | Start timer 2 | Setup day(s) for activation of Command timer 2 | OFF |  |  |  | 0: OFF, 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
710 | 6972 | General | Functions > Command timer > Command timer 2 | Start timer 2 | Setup of hour for activation of Command timer 2 | 10 | 0 | 23 | Hours
711 | 6973 | General | Functions > Command timer > Command timer 2 | Start timer 2 | Setup of minute for activation of Command timer 2 | 0 | 0 | 59
713 | 6974 | General | Functions > Command timer > Command timer 2 | Stop timer 2 | Setup day(s) for deactivation of Command timer 2 | MO-TU-WE-TH-FR-SA-SU |  |  |  | 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
714 | 6975 | General | Functions > Command timer > Command timer 2 | Stop timer 2 | Setup of hour for deactivation of Command timer 2 | 10 | 0 | 23 | Hours
715 | 6976 | General | Functions > Command timer > Command timer 2 | Stop timer 2 | Setup of minute for deactivation of Command timer 2 | 0 | 0 | 59
717 | 6981 | General | Functions > Command timer > Command timer 3 | Start timer 3 | Setup day(s) for activation of Command timer 3 | OFF |  |  |  | 0: OFF, 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
718 | 6982 | General | Functions > Command timer > Command timer 3 | Start timer 3 | Setup of hour for activation of Command timer 3 | 10 | 0 | 23 | Hours
719 | 6983 | General | Functions > Command timer > Command timer 3 | Start timer 3 | Setup of minute for activation of Command timer 3 | 0 | 0 | 59
721 | 6984 | General | Functions > Command timer > Command timer 3 | Stop timer 3 | Setup day(s) for deactivation of Command timer 3 | MO-TU-WE-TH-FR-SA-SU |  |  |  | 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
722 | 6985 | General | Functions > Command timer > Command timer 3 | Stop timer 3 | Setup of hour for deactivation of Command timer 3 | 10 | 0 | 23 | Hours
723 | 6986 | General | Functions > Command timer > Command timer 3 | Stop timer 3 | Setup of minute for deactivation of Command timer 3 | 0 | 0 | 59
725 | 6991 | General | Functions > Command timer > Command timer 4 | Start timer 4 | Setup day(s) for activation of Command timer 4 | OFF |  |  |  | 0: OFF, 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
726 | 6992 | General | Functions > Command timer > Command timer 4 | Start timer 4 | Setup of hour for activation of Command timer 4 | 10 | 0 | 23 | Hours
727 | 6993 | General | Functions > Command timer > Command timer 4 | Start timer 4 | Setup of minute for activation of Command timer 4 | 0 | 0 | 59
729 | 6994 | General | Functions > Command timer > Command timer 4 | Stop timer 4 | Setup day(s) for deactivation of Command timer 4 | MO-TU-WE-TH-FR-SA-SU |  |  |  | 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU
730 | 6995 | General | Functions > Command timer > Command timer 4 | Stop timer 4 | Setup of hour for deactivation of Command timer 4 | 10 | 0 | 23 | Hours
731 | 6996 | General | Functions > Command timer > Command timer 4 | Stop timer 4 | Setup of minute for deactivation of Command timer 4 | 0 | 0 | 59
527 | 7001 | Mains | Power set points > Mains Power Export and Peak shaving > Day/Night power set point | Day Setting | Day time setting for peakshaving/mains power export | 750 | -20000 | 20000 | kW
528 | 7002 | Mains | Power set points > Mains Power Export and Peak shaving > Day/Night power set point | Night Setting | Night time setting for peakshaving/mains power export | 1000 | -20000 | 20000 | kW
529 | 7003 | Mains | Basic settings > Measurement setup > Mains transducer settings | Transducer range max | Mains power transducer maximum setting | 0 | 0 | 20000 | kW
530 | 7004 | Mains | Basic settings > Measurement setup > Mains transducer settings | Transducer range min | Mains power transducer minimum setting | 0 | -20000 | 0 | kW
1440 | 7005 | Mains | Basic settings > Measurement setup > Wiring connection > Mains Power measure | Mains power measure | Selection of mains power measuring input | 4th CT power meas (internal) |  |  |  | 0: Multi input 20 (transducer), 1: 4th CT power meas (internal), 4: DEIF Open communication, 5: Power meter communication
1508 | 7006 | Mains | Power set points > Mains Power Export and Peak shaving > Day/Night power set point | MPE/PS scale | Scaling of the PS/MPE reference | 1kW:1kW |  |  |  | 0: 1kW:1kW, 1: 1kW:10kW, 2: 1kW:100kW, 3: 1kW:1000kW
1666 | 7007 | Mains | Basic settings > Measurement setup > Mains transducer settings | Transd. range max Q | Mains reactive power transducer maximum setting | 0 | -20000 | 20000 | kvar
1667 | 7008 | Mains | Basic settings > Measurement setup > Mains transducer settings | Transd. range min Q | Mains reactive power transducer minimum setting | 0 | -20000 | 20000 | kvar
1668 | 7009 | Mains | Basic settings > Measurement setup > Wiring connection > Mains Power measure | Mains Q measure | Selection of mains Q power measuring input | 4th CT power meas (internal) |  |  |  | 0: Multi input 22 (transducer), 1: 4th CT power meas (internal), 4: DEIF Open communication, 5: Power meter communication
531 | 7011 | Mains | Power set points > Mains Power Export and Peak shaving > Day/Night settings | Start Hour | Start hour for peakshaving/mains power export | 8 | 0 | 23
532 | 7012 | Mains | Power set points > Mains Power Export and Peak shaving > Day/Night settings | Start Minute | Start minute for peakshaving/mains power export | 0 | 0 | 59
533 | 7013 | Mains | Power set points > Mains Power Export and Peak shaving > Day/Night settings | Stop Hour | Stop hour for peakshaving/mains power export | 16 | 0 | 23
534 | 7014 | Mains | Power set points > Mains Power Export and Peak shaving > Day/Night settings | Stop Minute | Stop hour for peakshaving/mains power export | 0 | 0 | 59
216 | 7021 | Mains | Basic settings > Measurement setup > Wiring connection > Power measure origin | PV power meas. | Origin of AC power measurements | ASC measurements |  |  |  | 0: ASC measurements, 1: PV communication, 2: DEIF open communication, 3: Power meter comm., 4: ASC measurements average
1598 | 7022 | Mains | Basic settings > Measurement setup > Wiring connection > Busbar/PV measures | BB/PV V/f meas. | Origin of AC busbar measurements | ASC measurements |  |  |  | 0: ASC measurements, 1: PV communication
1937 | 7023 | Mains | Basic settings > Measurement setup > Wiring connection > Busbar/PV measures | V/f from com. fail | BB/PV Measures from PV communication failure alarm | [5 empty] | 30 | 0 | 1000 |  |  | Shutdown
929 | 7031 | Mains | Power set points > Q Ref. off-grid | GEN cosphi lim I | Maximum genset cosphi inductive in off-grid operation | 0.8 | 0.1 | 1 | PF
930 | 7032 | Mains | Power set points > Q Ref. off-grid | GEN cosphi lim C | Maximum genset cosphi capacitive in off-grid operation | 1 | 0.1 | 1 | PF
234 | 7033 | Mains | Power set points > Q Ref. off-grid | Q type off-grid | PV Q reference type in off-grid operation | Off |  |  |  | 0: Off, 1: Q share
642 | 7034 | Mains | Power set points > Q Ref. off-grid | GEN cosphi min I | Use PV to add Q load to force GEN's to run at minimum specificed inductive power factor in off-grid operation | 1 | 0 | 1 | PF
541 | 7051 | Mains | Power set points > Fixed Power | Fixed Power | Fixed power set point | 500 | 0 | 20000 | kW
542 | 7052 | Mains | Power set points > Fixed Power | Cosphi ref | Fixed cosphi set point | 0.9 | 0.6 | 1 | PF
1236 | 7053 | Mains | Power set points > Q Ref. grid-tied | Cosphi ref | Inductive or capacitive cos phi regulation | Inductive |  |  |  | 0: Inductive, 1: Capacitive
1370 | 7054 | Mains | Power set points > Q Ref. grid-tied | Contr. sett. Q | Fixed reactive power set point | 500 | -20000 | 20000 | kvar
1299 | 7055 | Mains | Power set points > Q Ref. grid-tied | Q type grid-tie | Q reference type in grid-tied operation | Cosphi superior |  |  |  | 0: Off, 1: Cosphi fixed, 2: Cosphi imp/exp, 3: Cosphi superior, 4: Q fixed, 5: Q imp/exp
1300 | 7056 | Mains | Power set points > Fixed Power | FP scale | Scaling of the FP reference | 1kW:1kW |  |  |  | 0: 1kW:1kW, 1: 1kW:10kW, 2: 1kW:100kW, 3: 1kW:1000kW
543 | 7061 | Mains | Mains > AMF functions > AMF voltage timers | U mains failure | Timer for mains failure voltage detection | [5 empty] | 50 | 5 | 9900
544 | 7062 | Mains | Mains > AMF functions > AMF voltage timers | Mains OK Delay U | Timer for mains voltage ok detection | [5 empty] | 60 | 2 | 9900
545 | 7063 | Mains | Mains > Voltage and frequency limits > Voltage settings | Low Voltage | Set point for mains voltage range low | 90 | 30 | 100 | %
546 | 7064 | Mains | Mains > Voltage and frequency limits > Voltage settings | High Voltage | Set point for mains voltage range high | 110 | 100 | 120 | %
874 | 7065 | Mains | Mains > Voltage and frequency limits > Voltage settings | Unbalance voltage | Mains voltage unbalance setting | 100 | 2 | 100 | %
548 | 7071 | Mains | Mains > AMF functions > AMF frequency timers | f mains failure | Timer for mains failure frequency detection | [5 empty] | 50 | 5 | 9900
549 | 7072 | Mains | Mains > AMF functions > AMF frequency timers | Mains OK Delay f | Timer for mains frequency ok detection | [5 empty] | 60 | 2 | 9900
550 | 7073 | Mains | Mains > Voltage and frequency limits > Frequency settings | Low Frequency | Set point for mains frequency range low | 95 | 80 | 100 | %
551 | 7074 | Mains | Mains > Voltage and frequency limits > Frequency settings | High Frequency | Set point for mains frequency range high | 105 | 100 | 120 | %
552 | 7081 | Mains | Mains > AMF functions > Modeshift | Modeshift | Allow switch to AMF mode | Mode shift off |  |  |  | 0: Mode shift off, 1: Mode shift on
553 | 7082 | Mains | Breakers > Mains breaker > Breaker configuration | MB close delay | MB breaker close delay. | [5 empty] | 5 | 0 | 300
846 | 7085 | Mains | Breakers > Mains breaker > Breaker configuration | MB Load time | Time needed to charge Mains breaker spring before closing | [5 empty] | 0 | 0 | 300
174 | 7091 | Mains | Mains > Voltage and frequency limits > Voltage settings | Low Volt. Hyst. | Low voltage mains hysteresis | 0 | 0 | 70 | %
175 | 7092 | Mains | Mains > Voltage and frequency limits > Voltage settings | High Volt Hyst. | High voltage mains hysteresis | 0 | 0 | 20 | %
176 | 7093 | Mains | Mains > Voltage and frequency limits > Frequency settings | Low Freq. Hyst. | Low frequency mains hysteresis | 0 | 0 | 20 | %
177 | 7094 | Mains | Mains > Voltage and frequency limits > Frequency settings | High Freq Hyst. | High frequency mains hysteresis | 0 | 0 | 20 | %
557 | 7501 | Communication | Power set points > External power set point | Comm bus control P | Modbus communication. Power control ON/OFF.
560 | 7502 | Communication | Power set points > External power set point | Comm bus ctrl cosphi | Modbus communication. cosphi control ON/OFF.
561 | 7503 | Communication | Power set points > External power set point | Comm bus control Q | Modbus communication. Reactive power control ON/OFF.
636 | 7504 | Communication | Power set points > External power set point | Comm. bus P Q scale | Sets the scale which the controller accepts external setpoints for percent of nominal P/Q. Parameter 7501 or 7503 must be enabled | 1% |  |  |  | 0: 1%, 1: 0.1%, 2: 0.01%
562 | 7511 | Communication | Communication > RS485 > RS485 1 > Settings | Ext. comm. ID 1 | Configuration of external communication port 1 Modbus server ID number | 3 | 1 | 247
563 | 7512 | Communication | Communication > RS485 > RS485 1 > Settings | Ext. comm.speed1 | Configuration of external communication port 1 speed | 9600 Baud |  |  |  | 0: 9600 Baud, 1: 19200 Baud, 2: 38400 Baud, 3: 115200 Baud
565 | 7513 | Communication | Communication > RS485 > RS485 1 > Communication error | Ext comm. error 1 | External communication port 1 supervision | [5 empty] | 100 | 10 | 1000 |  |  | Warning
1099 | 7521 | Communication | Communication > RS485 > RS485 2 > Settings | Ext. comm. ID 2 | Configuration of external communication port 2 Modbus server ID number | 3 | 1 | 247
1100 | 7522 | Communication | Communication > RS485 > RS485 2 > Settings | Ext. comm.speed2 | Configuration of external communication port 2 speed | 9600 Baud |  |  |  | 0: 9600 Baud, 1: 19200 Baud, 2: 38400 Baud, 3: 115200 Baud
951 | 7523 | Communication | Communication > RS485 > RS485 2 > Communication error | Ext comm. error 2 | External communication port 2 supervision | [5 empty] | 100 | 10 | 1000 |  |  | Warning
566 | 7531 | Communication | Communication > Power management ID | PM CAN ID | Internal communication ID number | 25 | 25 | 40
567 | 7532 | Communication | Power management > Communication failures | CAN fail mode | Selection of running mode in case of CAN failure. | MANUAL |  |  |  | 0: No reg, 1: MANUAL, 2: No mode change
568 | 7533 | Communication | Power management > Communication failures | Miss. all units | Configuration of CAN failure alarm. All ID's missing. | [10 empty] | Warning
569 | 7534 | Communication | Power management > Communication failures | Fatal CAN error | Configuration of CAN failure alarm. Fatal CAN error. More ID's missing than configured in menu 8800. | [10 empty] | Warning
570 | 7535 | Communication | Power management > Communication failures | Any GEN missing | Configuration of CAN failure alarm. Any ID missing. | [10 empty] | Warning
571 | 7536 | Communication | Power management > Communication failures | Any MAINS miss. | Configuration of CAN failure alarm. Any ID missing. | [10 empty] | Warning
242 | 7541 | Communication | Communication > PV | PV comm. intf | Sets the modbus communication interface for the control telegrams. If Modbus TCP/IP client is chosen it will use the configuration set up from the Network parameters menu. | Modbus RTU client 1 |  |  |  | 0: Modbus RTU client 1, 2: Modbus RTU client 2, 1: Modbus TCP/IP client
243 | 7542 | Communication | Communication > Weather station | Weather intf. | Sets the modbus communication interface for the weather telegrams.If Modbus TCP/IP client is chosen it will use the configuration set up from the Network parameters menu. | Modbus RTU client 1 |  |  |  | 0: Modbus RTU client 1, 2: Modbus RTU client 2, 1: Modbus TCP/IP client
751 | 7544 | Communication | Communication > Power Meter > Meter comm. settings | Meter comm. intf. | Sets the modbus communication interface for the Power meter telegrams. If Modbus TCP/IP client is chosen it will use the configuration set up from the Network parameters menu. | Modbus RTU client 2 |  |  |  | 0: Modbus RTU client 1, 2: Modbus RTU client 2
197 | 7545 | Communication | Communication > PV | PV comm. ID | Sets the Modbus ID of the servers/inverters. Applies to both modbus TCP/IP and RTU. | 3 | 0 | 247
196 | 7551 | Communication | Communication > PV | Mon. comm. ID | Lowest communication ID of inverter included in PV monitoring scheme | 3 | 1 | 247
746 | 7553 | Communication | Communication > RS485 | RTU broadcast ID | If enabled this ID will be used instead of the default broadcast ID 0 for write telegrams (RTU only) | 0 | 0 | 255
198 | 7561 | Communication | Communication > PV | PV protocol | PV communication protocol | Off |  |  |  | 0: Off, 110: Bluelog XC, 107: Canadian CSI-110K-T4001A-E, 66: CPS (Chint Power) Boost 100-250kW, 85: DEIF AGC GEN (For test only!), 5: DEIF Open, 76: Deye SUN 30-50k-G03, 120: Eachenergy PV, 56: FIMER PVS980, 148: FoxEss R/V, 152: FoxEss R-125-G2, 94: Solis Logger NISE, 59: Goodwe HT series, 67: Growatt CP100-CP250, 68: Growatt CP500-CP2520, 69: Growatt MAC, MAX and MID series, 48: Growatt UE-series, 64: Havells 1-40kW, 61: Havells 50-70kW, 53: Havells 80-136kW, 16: Huawei smartlogger, 63: Huawei V.3, 124: Hypontech PV, 87: Ingeteam 3Play - ABS, 79: INVT XG series, 143: Kehua Logger KM ACU50, 97: Kehua SPI, 118: LIVOLTEK SunSpec, 78: Matter Energy SPI20k-160k, 58: Polycab 50-60kW, 93: Power One, 123: SAJ C6, 4: Schneider CL 30/33/50/60, 147: Sineng Sacu Datalogger, 115: Sineng SP320K, 18: SMA cluster controller, 71: SMA Data Manager, 90: Sofar -G3, 65: Sofar Solar 1-40kW, 62: Sofar Solar 50-70kW, 75: Sofar Solar 80-136kW, 23: SolarEdge, 82: SolarEdge PPC, 112: Solax MIC-G2/Pro-G2, 111: Solax X3-FORTH/MEGA G2, 22: Solis (Ginlong), 128: Solis Logger, 46: Sungrow Logger 1000, 13: Sungrow SG series, 6: SunSpec Generic, 74: Thea, 145: WEG SIW400g, 144: WEG SIW610
199 | 7562 | Communication | Communication > PV | RTU tx write type | Selection between unicast or broadcast control topology (RTU only) | Unicast |  |  |  | 0: Unicast, 1: Broadcast
200 | 7563 | Communication | Communication > PV | Tx min. interval | Minimum time delay between telegrams transmitted to inverters. | [5 empty] | 5 | 1 | 100
201 | 7564 | Communication | Communication > PV | Tx write fnc. | Selection between function codes to use in write register telegrams for inverter communication | Multiple register 0x10 |  |  |  | 0: Single register 0x06, 1: Multiple register 0x10
202 | 7565 | Communication | Communication > PV | RTU PV monitoring | Enable/disable of PV monitoring and selection of the number of inverters to monitor (RTU only) | 1 | 1 | 32
1108 | 7567 | Communication | Communication > PV | PV comm. password | Only used for Solax MIC-G2/Pro-G2 PV protocol | 0 | 0 | 32767
203 | 7570 | Communication | Communication > PV | PV comm. error | PV Communication error | [5 empty] | 30 | 0 | 1000 |  |  | Warning
204 | 7580 | Communication | Communication > PV | PV warning | PV warning | [5 empty] | 0 | 0 | 1000 |  |  | Warning
205 | 7590 | Communication | Communication > PV | PV shutdown | PV shutdown | [5 empty] | 0 | 0 | 1000 |  |  | Shutdown
206 | 7600 | Communication | Communication > PV | PV monitor err. | PV monitoring supervision alarm | [5 empty] | 30 | 0 | 1000 |  |  | Warning
213 | 7660 | Communication | Communication > Weather station | Weatherstation comm | Weather Station communication ID | 3 | 1 | 247
214 | 7661 | Communication | Communication > Weather station | Weather protocol | Weather Station Protocol selection | OFF |  |  |  | 0: OFF, 3: Kipp and Zonen RT1, 4: CAT LEXE 1440, 5: Seven Sensor 3S-IS, 6: Seven Sensor 3S-TP, 7: Seven Sensor 3S-CWS
215 | 7670 | Communication | Communication > Weather station | Weather comm err | Weather Station communication error | [5 empty] | 30 | 0 | 1000 |  |  | Warning
1113 | 7701 | Communication | Communication > Power Meter > GEN Meter | GEN meter ID | Configuration of external communication GEN power meter ID number | 3 | 1 | 247
1117 | 7702 | Communication | Communication > Power Meter > PV Meter | PV meter ID | Configuration of external communication PV power meter ID number | 3 | 1 | 247
1116 | 7703 | Communication | Communication > Power Meter > Mains Meter | Mains meter ID | Configuration of external communication Mains power meter ID number | 3 | 1 | 247
1119 | 7721 | Communication | Communication > Power Meter > GEN Meter | GEN meter prot. | Configuration of external communication GEN power meter protocol | OFF |  |  |  | 0: OFF, 1: DEIF MIB7000C, 2: DEIF MIC4000, 3: DEIF MIC-2, 4: DEIF MTR-3/4, 5: Schneider iEM3000, 6: Schneider EM6400, 7: Socomec Multis L40, 8: Schneider PM5560, 9: Socomec Diris A40, 10: EDS-MMCT3-E-C, 11: Gossen, 12: EDMI, 13: DEIF Genset Control, 14: APS PMU-100, 15: ABB SACE Emax 2, 16: ABB A43/A44, 17: Accuvim-L, 18: Secure Elite 100/300 series, 19: DSE 8xxx, 7xxx, 6xxx and 4xxx, 20: Cummins PC 3.x/PCC 3300, 21: DEIF MIB8000, 22: Eastron Smart X96, 23: Eastron SDM630MCT, 24: CAT EMCP 4, 25: Secure Elite 440/500 series, 26: Acrel ADL, 27: Eastron Smart X96 with DI, 28: Configurable power meter, 29: Kohler APM403, 30: ComAp IntelliGen 500 g2
1120 | 7722 | Communication | Communication > Power Meter > GEN Meter | GEN nbr. nodes | Configuration of external communication GEN power meter number of nodes | 1 | 1 | 16
1122 | 7723 | Communication | Communication > Power Meter > PV Meter | PV meter prot. | Configuration of external communication PV power meter protocol | OFF |  |  |  | 0: OFF, 1: DEIF MIB7000C, 2: DEIF MIC4000, 3: DEIF MIC-2, 4: DEIF MTR-3/4, 5: Schneider iEM3000, 6: Schneider EM6400, 7: Socomec Multis L40, 8: Schneider PM5560, 9: Socomec Diris A40, 10: EDS-MMCT3-E-C, 11: Gossen, 12: EDMI, 13: DEIF Genset Control, 14: APS PMU-100, 15: ABB SACE Emax 2, 16: ABB A43/A44, 17: Accuvim-L, 18: Secure Elite 100/300 series, 21: DEIF MIB8000, 22: Eastron Smart X96, 23: Eastron SDM630MCT, 25: Secure Elite 440/500 series, 26: Acrel ADL, 27: Eastron Smart X96 with DI, 28: Configurable power meter, 29: Kohler APM403
1123 | 7724 | Communication | Communication > Power Meter > PV Meter | PV nbr. nodes | Configuration of external communication PV power meter number of nodes | 1 | 1 | 16
1121 | 7725 | Communication | Communication > Power Meter > Mains Meter | Mains met. prot | Configuration of external communication Mains power meter protocol | OFF |  |  |  | 0: OFF, 1: DEIF MIB7000C, 2: DEIF MIC4000, 3: DEIF MIC-2, 4: DEIF MTR-3/4, 5: Schneider iEM3000, 6: Schneider EM6400, 7: Socomec Multis L40, 8: Schneider PM5560, 9: Socomec Diris A40, 10: EDS-MMCT3-E-C, 11: Gossen, 12: EDMI, 13: DEIF Genset Control, 14: APS PMU-100, 15: ABB SACE Emax 2, 16: ABB A43/A44, 17: Accuvim-L, 18: Secure Elite 100/300 series, 19: DSE 8xxx, 7xxx, 6xxx and 4xxx, 20: Cummins PC 3.x/PCC 3300, 21: DEIF MIB8000, 22: Eastron Smart X96, 23: Eastron SDM630MCT, 25: Secure Elite 440/500 series, 26: Acrel ADL, 27: Eastron Smart X96 with DI, 28: Configurable power meter, 29: Kohler APM403, 30: ComAp IntelliGen 500 g2
1128 | 7726 | Communication | Communication > Power Meter > Mains Meter | Mains nbr. node | Configuration of external communication Mains power meter number of nodes | 1 | 1 | 16
1124 | 7730 | Communication | Communication > Power Meter > GEN Meter | GEN meter err. | External communication GEN power meter supervision | [5 empty] | 0 | 0 | 600 |  |  | Warning
1126 | 7740 | Communication | Communication > Power Meter > PV Meter | PV meter err. | External communication PV power meter supervision | [5 empty] | 0 | 0 | 600 |  |  | Warning
1125 | 7750 | Communication | Communication > Power Meter > Mains Meter | Mains meter err | External communication Mains power meter supervision | [5 empty] | 0 | 0 | 600 |  |  | Warning
1127 | 7761 | Communication | Communication > Power Meter > Meter comm. settings | Pow. met. Tx min int | Minimum time delay between telegrams transmitted to power meters from ASC. (If both PV and Power meters are on same interface, then PV interval will overrule this parameter.) | [5 empty] | 5 | 1 | 100
1437 | 7841 | Communication | Communication > CAN protocols | CAN A Protocol | CAN bus protocol selection | OFF |  |  |  | 0: OFF, 5: AOP2, 11: Ext. Modules DEIF
1438 | 7842 | Communication | Communication > CAN protocols | CAN B Protocol | CAN bus protocol selection | PMS Primary |  |  |  | 0: OFF, 6: PMS Primary, 5: AOP2, 2: PMS Secondary, 11: Ext. Modules DEIF
1439 | 7843 | Communication | Communication > CAN protocols | VCAN C Protocol | Ethernet CAN bus protocol selection | OFF |  |  |  | 0: OFF, 6: PMS Primary, 2: PMS Secondary
1183 | 7871 | Communication | Power management > Communication failures | Any BTB missing | Alarm is activated, if the communication to any BTB unit failed
1191 | 7872 | Communication | Power management > Communication failures | Appl. hazard | Alarm is activated, if different applications are installed in the controllers. | [5 empty] | 150 | 150 | 150 |  |  | Warning
865 | 7874 | Communication | Power management > Communication failures | Any LoadG miss. | Alarm is activated, if the communication to any ALC unit failed | [10 empty] | Warning
866 | 7875 | Communication | Power management > Communication failures | Any SOLAR miss. | Alarm is activated, if the communication to any PV unit failed | [10 empty] | Warning
867 | 7876 | Communication | Power management > Communication failures | Any BATTRY miss | Alarm is activated, if the communication to any Battery unit failed | [10 empty] | Warning
1711 | 7891 | Communication | I/O settings > External I/O > CIO > Enable | CIO Enable | Configuration of CIO enable | OFF |  |  |  | 0: OFF, 3: ON
1639 | 7900 | Communication | Communication > Ethernet comm. error | Ethernet comm. error | Ethernet communication supervision | [5 empty] | 100 | 10 | 1000 |  |  | Warning
575 | 8001 | Power Man | Power management > Spinning reserve | Spin. res. grid-tie | Spinning reserve in mains parallel operation | 0 | 0 | 100 | %
576 | 8002 | Power Man | Power management > Spinning reserve | Spin. res. off-grid | Spinning reserve in island operation | 10 | 0 | 100 | %
579 | 8003 | Power Man | Power management > Spinning reserve | Spin. res. origin | Origin of spinning reservation | ASC settings |  |  |  | 0: ASC settings, 1: PV communication
1882 | 8011 | Power Man | Power management > Q loadshare | Q source prio | Select which hybrid source should have higher priority on Q loadshare. If set to OFF then equal loadshare between hybrid sources. | OFF |  |  |  | 0: OFF, 1: ESS, 2: PV
1186 | 8022 | Power Man | Power management > Mode update | Mode update | Mode update (Update local or all units) | Update all |  |  |  | 0: Update local, 1: Update all
869 | 8023 | Power Man | Power management > Easy connect | Easy connect | Enable/disable easy connect
871 | 8351 | Power Man | Power management > Open PMS | Open PMS | Enable/Disable Open PMS - selection only valid if operation mode (6071) is set to Power Management
872 | 8352 | Power Man | Power management > Open PMS | Open PMS mode | Open PMS operation mode - selection is valid only if there is no AGC Mains in the plant and ext. mains is enabled in the I/O and hardware setup tab | Mains Power Export |  |  |  | 0: Peak shaving, 1: Fixed power, 2: Mains Power Export
633 | 8361 | Power Man | Power management > Maximise PV power | Maximise PV power | Maximise PV power so GENs are stopped when PV power is sufficiently large (requires a running battery on the busbar)
634 | 8362 | Power Man | Power management > Maximise PV power | PV P - DG stop lim. | Minimum nominal PV power for stopping of the last GEN to be allowed | 0 | 0 | 100 | % |  | 10 | 0 | 900
635 | 8364 | Power Man | Power management > Maximise PV power | PV P - DG start lim. | Minimum nominal PV power before a GEN is started | 0 | 0 | 100 | % |  | 10 | 0 | 900
1673 | 8800 | Power Man | Power management > Communication failures | CAN miss amount | Configure the amount of units missing, in order for the Fatal CAN Error alarm (7534) to activate. (Parameter is shared on all PMS units) | 2 | 2 | 32
1372 | 9030 | Jump | Basic settings > Measurement setup > Scaling > Scaling | Scaling | Select the voltage range of operation | 100 to 25000V |  |  |  | 0: 10 to 2500V, 1: 100 to 25000V, 2: 10 to 160kV, 3: 0.4k to 75kV
695 | 9111 | Jump | Basic settings > Controller settings > Password | Customer password | Setup of Customer Password | 2000 | 1 | 32000
696 | 9112 | Jump | Basic settings > Controller settings > Password | Service password | Setup of Service Password | 2001 | 1 | 32000
697 | 9113 | Jump | Basic settings > Controller settings > Password | Master password | Setup of Master Password | 2002 | 1 | 32000
1107 | 9131 | Jump | Basic settings > Measurement setup > Wiring connection > AC configuration | AC configuration | Menu is used to choose between the different AC measurement systems. | 3 phase 3W4 |  |  |  | 0: 3 phase 3W4, 10: 3 phase 3W3, 1: 2 phase L1L3, 2: 2 phase L1L2, 3: 1 phase L1
946 | 9132 | Jump | Basic settings > Measurement setup > Wiring connection > AC configuration | AC configuration BB | Bus connection of Neutral wire | 3 phase 3W4 |  |  |  | 0: 3 phase 3W4, 10: 3 phase 3W3
699 | 9151 | Jump | Basic settings > Controller settings > Display > Display Control | Backlight dimmer | Setup of backlight level | 12 | 0 | 15
939 | 9152 | Jump | Basic settings > Controller settings > Display > Display Control | Green LEDs dimmer | Adjust level for green leds | 15 | 1 | 15
940 | 9153 | Jump | Basic settings > Controller settings > Display > Display Control | Red LEDs dimmer | Adjust level for red leds | 15 | 1 | 15
685 | 9154 | Jump | Basic settings > Controller settings > Display > Display Control | Contrast setting | Display contrast level | 0 | -20 | 20
937 | 9155 | Jump | Basic settings > Controller settings > Display > Display Control | Sleep mode | Sleep mode enable | [5 empty] | 60 | 1 | 1800 | Limits | Limits
1227 | 9157 | Jump | Basic settings > Controller settings > Display > Display Control | Alarm Jump | Display behavior when and alarm is activated. ON: jump to the Alarm list, OFF: stay at present view | On |  |  |  | 0: Off, 1: On
797 | 9158 | Jump | Basic settings > Controller settings > Display > Display Control | Engineering units | Engineering units Bar/celsius or Psi/fahrenheit | Bar/celsius |  |  |  | 0: Bar/celsius, 1: Psi/fahrenheit
1819 | 9159 | Jump | Communication > Remote Display | Remote display setup | Setup of remote display | OFF |  |  |  | 0: OFF, 1: ON view only, 2: ON view + controls
1275 | 9181 | Jump | Functions > Quick setup | Quick Setup Mode | Quick Setup - Plant setup | Off |  |  |  | 0: Off, 1: Setup stand alone, 2: Setup plant
1276 | 9182 | Jump | Functions > Quick setup | Quick Setup Canline | Quick Setup - Power Management CAN setup | CAN PM Primary |  |  |  | 0: Off, 1: CAN PM Primary, 2: CAN PM Secondary
1277 | 9183 | Jump | Functions > Quick setup | Quick Setup MB type | Quick setup | Pulse |  |  |  | 0: Pulse, 1: No MB, 3: Continuous, 4: Compact
1278 | 9184 | Jump | Functions > Quick setup | Quick Setup PVB type | Quick setup PVB configuration. Also used for choosing PVB type in Easy connect. | Pulse |  |  |  | 0: Pulse, 1: No PVB, 3: Continuous, 4: Compact
1279 | 9185 | Jump | Functions > Quick setup | Quick Setup mains | Quick setup | Mains present |  |  |  | 0: Mains present, 1: No mains present
1281 | 9186 | Jump | Functions > Quick setup | Quick Setup PV | Quick setup | Standard |  |  |  | 0: Single controller, 1: Standard
1284 | 9191 | Jump | Functions > Appl. broadcast | Appl. Broadcast type | Broadcast application | Off |  |  |  | 0: Off, 1: Broadcast, 2: Broadcast+Activate
1285 | 9192 | Jump | Functions > Appl. broadcast | Appl.no to Broadcast | Selection of application to be broadcasted | 1 | 1 | 4
1602 | 9220 | Jump | Basic settings > Controller settings > Parameter filter | Parameter list setup | Parameter list selection | Master tree |  |  |  | 0: Parameter list, 1: Custom tree, 2: Service tree, 3: Master tree
1603 | 11200 | USW | USW specific parameters > Parameter name | Parameter name | This parameter can be used to identify which parameter list is used on the unit
1305 | 14201 | Prot: 4th CT | Basic settings > Measurement setup > 4th CT protection > 4th CT input selector | 4th CT trip select | 4th CT selection of alarm type due to use of this input. | OFF |  |  |  | 0: OFF, 1: Mains/BB current, 2: Neutral current, 3: Earth fault current
1079 | 14210 | Prot: 4th CT | AC configuration and protections > Current protections > Neutral over-current (4th CT) | 4th CT In> 1 | 4th CT neutral current protection level 1 | 30 | 2 | 120 | % |  | 100 | 1 | 32000 |  |  | Warning
1080 | 14220 | Prot: 4th CT | AC configuration and protections > Current protections > Neutral over-current (4th CT) | 4th CT In> 2 | 4th CT neutral current protection level 2 | 30 | 2 | 120 | % |  | 100 | 1 | 32000 |  |  | Warning
1081 | 14230 | Prot: 4th CT | AC configuration and protections > Current protections > Earth fault over-current (4th CT) | 4th CT Ie> 1 | 4th CT earth current protection level 1 | 10 | 2 | 120 | % |  | 100 | 1 | 32000 |  |  | Warning
1082 | 14240 | Prot: 4th CT | AC configuration and protections > Current protections > Earth fault over-current (4th CT) | 4th CT Ie> 2 | 4th CT earth current protection level 2 | 10 | 2 | 120 | % |  | 100 | 1 | 32000 |  |  | Warning
752 | 14250 | Prot: 4th CT |  | 4th CT I> 1 | 4th CT busbar current protection level 1 | 115 | 50 | 200 | % |  | 100 | 1 | 32000 |  |  | Warning
753 | 14260 | Prot: 4th CT |  | 4th CT I> 2 | 4th CT busbar current protection level 2 | 120 | 50 | 200 | % |  | 100 | 1 | 32000 |  |  | Warning
606 | 14270 | Prot: 4th CT | AC configuration and protections > Power protections > Overload 4th CT | 4th CT -P> 1 | 4th CT Reverse power protection level 1 | -5 | -200 | 0 | % |  | 100 | 1 | 1000 |  |  | Warning
607 | 14280 | Prot: 4th CT | AC configuration and protections > Power protections > Overload 4th CT | 4th CT -P> 2 | 4th CT Reverse power protection level 2 | -5 | -200 | 0 | % |  | 100 | 1 | 1000 |  |  | Warning
608 | 14290 | Prot: 4th CT | AC configuration and protections > Power protections > Overload 4th CT | 4th CT P> 1 | 4th CT overload protection level 1 | 100 | -200 | 200 | % |  | 100 | 1 | 32000 |  |  | Warning
609 | 14300 | Prot: 4th CT | AC configuration and protections > Power protections > Overload 4th CT | 4th CT P> 2 | 4th CT overload protection level 2 | 110 | -200 | 200 | % |  | 50 | 1 | 32000 |  |  | Warning
230 | 15011 | Ext. Ctrl. | External control > Min. GEN load settings | Min GEN load 1 | Minimum GEN load percentage in island operation 1 | 30 | -50 | 100 | %
231 | 15012 | Ext. Ctrl. | External control > Min. GEN load settings | Min GEN load 2 | Minimum GEN load percentage in island operation 2 | 30 | -50 | 100 | %
229 | 15013 | Ext. Ctrl. | External control > Min. GEN load settings | Min GEN load set | Minimum GEN load percentage island selection | Min. GEN load set 1 |  |  |  | 0: Min. GEN load set 1, 1: Min. GEN load set 2
637 | 15070 | Ext. Ctrl. | External control > GEN reverse power alarms | GEN P< 1 | GEN reverse power alarm 1 | -5 | -200 | 100 | % |  | 100 | 1 | 32000
638 | 15080 | Ext. Ctrl. | External control > GEN reverse power alarms | GEN P< 2 | GEN reverse power alarm 2 | -5 | -200 | 100 | % |  | 100 | 1 | 32000
1111 | 15090 | Ext. Ctrl. | External control > GEN spinning reserve alarms | GEN spinning res. 1 | GEN spinning reserve alarm 1 | 30 | 0 | 100 | % |  | 100 | 1 | 32000
1112 | 15100 | Ext. Ctrl. | External control > GEN spinning reserve alarms | GEN spinning res. 2 | GEN spinning reserve alarm 2 | 10 | 0 | 100 | % |  | 100 | 1 | 32000
612 | 17091 | Solar | Solar > Dispatch limits | Minimum dispatch | Minimum power to dispatch | 0 | 0 | 100 | %
1093 | 17092 | Solar | Solar > Dispatch limits | Maximum dispatch | Maximum power to dispatch | 100 | 0 | 100 | %
458 | 17181 | Solar | Solar > Start prepare | PV prepare | Setup of start prepare timer | [5 empty] | 0 | 0 | 9900
757 | 17182 | Solar | Solar > Start prepare | PV BB fail inh stop | Busbar fail time before stop | [5 empty] | 0 | 0 | 600
276 | 17271 | Solar | Solar > Weather, POA and BOM > POA Irradiation | POA irr. 1 | Input selection POA irradiation 1 | DEIF open communication |  |  |  | 40: PV communication, 41: DEIF open communication, 42: Weather Station Communication, 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
277 | 17273 | Solar | Solar > Weather, POA and BOM > POA Irradiation | POA irr. 2 | Input selection POA irradiation 2 | DEIF open communication |  |  |  | 40: PV communication, 41: DEIF open communication, 42: Weather Station Communication, 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
278 | 17275 | Solar | Solar > Weather, POA and BOM > POA Irradiation | POA irr. 3 | Input selection POA irradiation 3 | DEIF open communication |  |  |  | 40: PV communication, 41: DEIF open communication, 42: Weather Station Communication, 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
279 | 17281 | Solar | Solar > Weather, POA and BOM > BOM Temperature | BOM temp. 1 | Input selection BOM temperature 1 | DEIF open communication |  |  |  | 40: PV communication, 41: DEIF open communication, 42: Weather Station Communication, 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
280 | 17283 | Solar | Solar > Weather, POA and BOM > BOM Temperature | BOM temp. 2 | Input selection BOM temperature 2 | DEIF open communication |  |  |  | 40: PV communication, 41: DEIF open communication, 42: Weather Station Communication, 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
281 | 17285 | Solar | Solar > Weather, POA and BOM > BOM Temperature | BOM temp. 3 | Input selection BOM temperature 3 | DEIF open communication |  |  |  | 40: PV communication, 41: DEIF open communication, 42: Weather Station Communication, 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
282 | 17291 | Solar | Solar > Weather, POA and BOM > POA/BOM weight | POA irr. wgt. 1 | Weighing factor for POA irradiation 1 | 100 | 0 | 100 | %
283 | 17292 | Solar | Solar > Weather, POA and BOM > POA/BOM weight | POA irr. wgt. 2 | Weighing factor for POA irradiation 2 | 0 | 0 | 100 | %
284 | 17293 | Solar | Solar > Weather, POA and BOM > POA/BOM weight | POA irr. wgt. 3 | Weighing factor for POA irradiation 3 | 0 | 0 | 100 | %
286 | 17294 | Solar | Solar > Weather, POA and BOM > POA/BOM weight | BOM temp wgt. 1 | Weighing factor for BOM temperature 1 | 100 | 0 | 100 | %
287 | 17295 | Solar | Solar > Weather, POA and BOM > POA/BOM weight | BOM temp wgt. 2 | Weighing factor for BOM temperature 2 | 0 | 0 | 100 | %
288 | 17296 | Solar | Solar > Weather, POA and BOM > POA/BOM weight | BOM temp wgt. 3 | Weighing factor for BOM temperature 3 | 0 | 0 | 100 | %
217 | 17301 | Solar | Solar > Instant P Max | Instant P max. | Enable instant P max calculation based on POA/GHI irradiance and BOM temp. | POA + BOM |  |  |  | 0: POA + BOM, 1: GHI + BOM, 2: No sensors
285 | 17303 | Solar | Solar > Instant P Max | P temp. coeff. | Panel power temperature coefficient | -0.38 | -0.99 | 0 | /100
218 | 17304 | Solar | Solar > Instant P Max | Inv. efficiency | Efficiency of inverter | 100 | 80 | 100 | %
90 | 17305 | Solar | Solar > Instant P Max | Irradia. sensor | Multiplier for POA/GHI irradiance sensor input. | 100 | 50 | 200 | %
289 | 17311 | Solar | Solar > Weather, POA and BOM > Weather Data 1 | GHI irradiance | Input selection global horizontal irradiation | DEIF open communication |  |  |  | 40: PV communication, 41: DEIF open communication, 42: Weather Station Communication, 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
290 | 17313 | Solar | Solar > Weather, POA and BOM > Weather Data 1 | Ambient temp. | Input selection ambient temperature | DEIF open communication |  |  |  | 40: PV communication, 41: DEIF open communication, 42: Weather Station Communication, 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
291 | 17315 | Solar | Solar > Weather, POA and BOM > Weather Data 1 | Rel. humidity | Input selection relative humidity | DEIF open communication |  |  |  | 40: PV communication, 41: DEIF open communication, 42: Weather Station Communication, 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
292 | 17321 | Solar | Solar > Weather, POA and BOM > Weather Data 2 | Barometric pres. | Input selection barometric pressure | DEIF open communication |  |  |  | 40: PV communication, 41: DEIF open communication, 42: Weather Station Communication, 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
293 | 17323 | Solar | Solar > Weather, POA and BOM > Weather Data 2 | Wind speed | Input selection wind speed | DEIF open communication |  |  |  | 40: PV communication, 41: DEIF open communication, 42: Weather Station Communication, 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
294 | 17325 | Solar | Solar > Weather, POA and BOM > Weather Data 2 | Wind direction | Input selection wind direction | DEIF open communication |  |  |  | 40: PV communication, 41: DEIF open communication, 42: Weather Station Communication, 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
295 | 17331 | Solar | Solar > Weather, POA and BOM > Weather Data 3 | Rain fall | Input selection rain fall | DEIF open communication |  |  |  | 40: PV communication, 41: DEIF open communication, 42: Weather Station Communication, 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
296 | 17333 | Solar | Solar > Weather, POA and BOM > Weather Data 3 | Snow depth | Input selection snow depth | DEIF open communication |  |  |  | 40: PV communication, 41: DEIF open communication, 42: Weather Station Communication, 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29
1817 | 17341 | Solar | Solar > Curtailment | Curtail. thres. | Minimum percentage of the power ref. that the PV should be able to produce before the controller sees it as PV being curtailed | 100 | 0 | 100 | %