## Information
ASC 150 Storage M-Logic descriptions
Software version
The information contained in this spreadsheet (Revision A of document 4189341429) is applicable to software version 1.30.0 of the ASC 150.
Monitoring M-Logic
You can use Modbus to see the state of each M-Logic line (function code 04, Modbus addresses 1150 to 1174).
More information
ASC 150 Storage Designer's handbook: This document has more information about some of the M-Logic functions.
Application notes, M-Logic AGC-4 Mk II: This document has a general introduction to M-Logic.
It also contains information and examples for generic M-Logic functions. You can download this document from:
https://www.deif.com/documentation/agc-4-mk-ii/
ASC 150 Modbus server tables: Some of the M-Logic functions are also available over Modbus.

## ASC_150_Storage_M-Logic_Events
Category | Name | Options | From SW version | The controller activates the event when …
Alarms | Unacknowledged alarm |  |  | One or more alarms are unacknowledged.
Alarms | Phase seq. error ES |  |  | A phase sequence error alarm is activated on the ESS side of the ESB.
Alarms | Phase seq. error BB |  |  | A phase sequence error alarm is activated on the busbar side of the ESB.
Alarms | M-Logic alarm 1 |  |  | M-Logic alarm 1 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 2 |  |  | M-Logic alarm 2 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 3 |  |  | M-Logic alarm 3 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 4 |  |  | M-Logic alarm 4 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 5 |  |  | M-Logic alarm 5 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 10 |  | 1180 | M-Logic alarm 10 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 11 |  | 1180 | M-Logic alarm 11 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 12 |  | 1180 | M-Logic alarm 12 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 13 |  | 1180 | M-Logic alarm 13 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 14 |  | 1180 | M-Logic alarm 14 is activated (by the corresponding M-Logic output).
Alarms | M-Logic ext alarm 1 |  | 1060 | M-Logic extended timer alarm 1 is activated (by the corresponding M-Logic output).
Alarms | M-Logic ext alarm 2 |  | 1060 | M-Logic extended timer alarm 2 is activated (by the corresponding M-Logic output).
Alarms | M-Logic ext alarm 3 |  | 1060 | M-Logic extended timer alarm 3 is activated (by the corresponding M-Logic output).
Alarms | M-Logic ext alarm 4 |  | 1060 | M-Logic extended timer alarm 4 is activated (by the corresponding M-Logic output).
Alarms - AC | BB U> 1 |  |  | Busbar over-voltage 1 alarm is activated.
Alarms - AC | BB U> 2 |  |  | Busbar over-voltage 2 alarm is activated.
Alarms - AC | BB U> 3 |  |  | Busbar over-voltage 3 alarm is activated.
Alarms - AC | BB U< 1 |  |  | Busbar under-voltage 1 alarm is activated.
Alarms - AC | BB U< 2 |  |  | Busbar under-voltage 2 alarm is activated.
Alarms - AC | BB U< 3 |  |  | Busbar under-voltage 3 alarm is activated.
Alarms - AC | BB U< 4 |  |  | Busbar under-voltage 4 alarm is activated.
Alarms - AC | BB f> 1 |  |  | Busbar over-frequency 1 alarm is activated.
Alarms - AC | BB f> 2 |  |  | Busbar over-frequency 2 alarm is activated.
Alarms - AC | BB f> 3 |  |  | Busbar over-frequency 3 alarm is activated.
Alarms - AC | BB f> 4 |  |  | Busbar over-frequency 4 alarm is activated.
Alarms - AC | BB f< 1 |  |  | Busbar under-frequency 1 alarm is activated.
Alarms - AC | BB f< 2 |  |  | Busbar under-frequency 2 alarm is activated.
Alarms - AC | BB f< 3 |  |  | Busbar under-frequency 3 alarm is activated.
Alarms - AC | BB f< 4 |  |  | Busbar under-frequency 4 alarm is activated.
Alarms - AC | BB f< 5 |  |  | Busbar under-frequency 5 alarm is activated.
Alarms - AC | ES I> 1 |  |  | ESS over-current 1 alarm is activated.
Alarms - AC | ES I> 2 |  |  | ESS over-current 2 alarm is activated.
Alarms - AC | ES I> 3 |  |  | ESS over-current 3 alarm is activated.
Alarms - AC | ES I> 4 |  |  | ESS over-current 4 alarm is activated.
Alarms - AC | ES Iv> |  |  | ESS voltage-dependent over-current alarm is activated.
Alarms - AC | ES P> 1 |  |  | ESS overload 1 alarm is activated.
Alarms - AC | ES P> 2 |  |  | ESS overload 2 alarm is activated.
Alarms - AC | ES P> 3 |  |  | ESS overload 3 alarm is activated.
Alarms - AC | ES P> 4 |  |  | ESS overload 4 alarm is activated.
Alarms - AC | ES P> 5 |  |  | ESS overload 5 alarm is activated.
Alarms - AC | ES -P> 1 |  |  | ESS reverse power 1 alarm is activated.
Alarms - AC | ES -P> 2 |  |  | ESS reverse power 2 alarm is activated.
Alarms - AC | ES -P> 3 |  | 1070 | ESS reverse power 3 alarm is activated.
Alarms - AC | 4th CT Busbar Over Current 1 |  | 1120 | Busbar over-current alarm 1 (measured by the 4th current transformer) is activated.
Alarms - AC | 4th CT Busbar Over Current 2 |  | 1120 | Busbar over-current alarm 2 (measured by the 4th current transformer) is activated.
Alarms - AC | 4th CT Neutral Over Current 1 |  | 1200 | Neutral (N) over-current alarm 1 (measured by the 4th current transformer) is activated.
Alarms - AC | 4th CT Neutral Over Current 2 |  | 1200 | Neutral (N) over-current alarm 2 (measured by the 4th current transformer) is activated.
Alarms - AC | 4th CT Earth Over Current 1 |  | 1200 | Earth over-current alarm 1 (measured by the 4th current transformer) is activated.
Alarms - AC | 4th CT Earth Over Current 2 |  | 1200 | Earth over-current alarm 2 (measured by the 4th current transformer) is activated.
Alarms - AC | 4th P> 1 |  |  | Overload 1 alarm (measured by the 4th current transformer) is activated.
Alarms - AC | 4th P> 2 |  |  | Overload 2 alarm (measured by the 4th current transformer) is activated.
Alarms - AC | 4th -P> 1 |  |  | Reverse power 1 alarm (measured by the 4th current transformer) is activated.
Alarms - AC | 4th -P> 2 |  |  | Reverse power 2 alarm (measured by the 4th current transformer) is activated.
Alarms - AC | ES Unbalance current 1 |  |  | ESS current unbalance 1 alarm is activated.
Alarms - AC | ES Unbalance current 2 |  |  | ESS current unbalance 2 alarm is activated.
Alarms - AC | ES Unbalance voltage |  |  | ESS voltage unbalance alarm is activated.
Alarms - AC | ROCOF (df/dt) |  |  | ROCOF alarm is activated.
Alarms - AC | Vector shift |  |  | Vector shift alarm is activated.
Alarms - AC | ES U> 1 |  |  | ESS over-voltage 1 alarm is activated.
Alarms - AC | ES U> 2 |  |  | ESS over-voltage 2 alarm is activated.
Alarms - AC | ES U< 1 |  |  | ESS under-voltage 1 alarm is activated.
Alarms - AC | ES U< 2 |  |  | ESS under-voltage 2 alarm is activated.
Alarms - AC | ES U< 3 |  |  | ESS under-voltage 3 alarm is activated.
Alarms - AC | ES f> 1 |  |  | ESS over-frequency 1 alarm is activated.
Alarms - AC | ES f> 2 |  |  | ESS over-frequency 2 alarm is activated.
Alarms - AC | ES f> 3 |  |  | ESS over-frequency 3 alarm is activated.
Alarms - AC | ES f< 1 |  |  | ESS under-frequency 1 alarm is activated.
Alarms - AC | ES f< 2 |  |  | ESS under-frequency 2 alarm is activated.
Alarms - AC | ES f< 3 |  |  | ESS under-frequency 3 alarm is activated.
Alarms - AC | ES I>> 1 |  |  | ESS fast over-current 1 alarm is activated.
Alarms - AC | ES I>> 2 |  |  | ESS fast over-current 2 alarm is activated.
Alarms - AC | ES -Q> |  |  | ESS loss of excitation alarm is activated.
Alarms - AC | ES Q> |  |  | ESS over-excitation alarm is activated.
Alarms - AC | ES negative seq. I |  |  | ESS negative sequence current alarm is activated.
Alarms - AC | ES negative seq. U |  |  | ESS negative sequence voltage alarm is activated.
Alarms - AC | ES zero seq. I |  |  | ESS zero sequence current alarm is activated.
Alarms - AC | ES zero seq. U |  |  | ESS zero sequence voltage alarm is activated.
Alarms - AC | ES positive seq. U |  |  | ESS positive sequence voltage alarm is activated.
Alarms - AC | Directional overcurrent 1 |  |  | ESS directional over-current 1 alarm is activated.
Alarms - AC | Directional overcurrent 2 |  |  | ESS directional over-current 2 alarm is activated.
Alarms - AC | BB Unbalance voltage |  |  | Busbar voltage unbalance alarm is activated.
Alarms - AC | Uq<1 |  |  | U and Q < 1 (menu 1960) (ESS voltage is low, with zero or negative kvar from ESS) is activated.
Alarms - AC | Uq<2 |  |  | U and Q < 2 (menu 1970) (ESS voltage is low, with zero or negative kvar from ESS) is activated.
Alarms - Digital inputs | Digital input 20 |  |  | The alarm configured for digital input 20 is active.
Alarms - Digital inputs | Digital input 21 |  |  | The alarm configured for digital input 21 is active.
Alarms - Digital inputs | Digital input 22 |  |  | The alarm configured for digital input 22 is active.
Alarms - Digital inputs | Digital input 23 |  |  | The alarm configured for digital input 23 is active.
Alarms - Digital inputs | Digital input 39 |  |  | The alarm configured for digital input 39 is active.
Alarms - Digital inputs | Digital input 40 |  |  | The alarm configured for digital input 40 is active.
Alarms - Digital inputs | Digital input 41 |  |  | The alarm configured for digital input 41 is active.
Alarms - Digital inputs | Digital input 42 |  |  | The alarm configured for digital input 42 is active.
Alarms - Digital inputs | Digital input 43 |  |  | The alarm configured for digital input 43 is active.
Alarms - Digital inputs | Digital input 44 |  |  | The alarm configured for digital input 44 is active.
Alarms - Digital inputs | Digital input 45 |  |  | The alarm configured for digital input 45 is active.
Alarms - Digital inputs | Digital input 46 |  |  | The alarm configured for digital input 46 is active.
Alarms - Digital inputs | Digital input 47 |  |  | The alarm configured for digital input 47 is active.
Alarms - Digital inputs | Digital input 48 |  |  | The alarm configured for digital input 48 is active.
Alarms - Digital inputs | Digital input 49 |  |  | The alarm configured for digital input 49 is active.
Alarms - Digital inputs | Digital input 50 |  |  | The alarm configured for digital input 50 is active.
Alarms - Digital inputs | Digital input 20 wire fail |  |  | A wire failure was detected for digital input 20.
Alarms - Digital inputs | Digital input 21 wire fail |  |  | A wire failure was detected for digital input 21.
Alarms - Digital inputs | Digital input 22 wire fail |  |  | A wire failure was detected for digital input 22.
Alarms - Digital inputs | Digital input 23 wire fail |  |  | A wire failure was detected for digital input 23.
Alarms - Analogue inputs | Supply low terminal 1 |  |  | Low auxiliary supply voltage alarm.
Alarms - Analogue inputs | Supply High terminal 1 |  |  | High auxiliary supply voltage alarm.
Alarms - Analogue inputs | Multi input 20 1 |  |  | Alarm 1 for multi-input 20 is active.
Alarms - Analogue inputs | Multi input 21 1 |  |  | Alarm 1 for multi-input 21 is active.
Alarms - Analogue inputs | Multi input 22 1 |  |  | Alarm 1 for multi-input 22 is active.
Alarms - Analogue inputs | Multi input 23 1 |  |  | Alarm 1 for multi-input 23 is active.
Alarms - Analogue inputs | Multi input 20 2 |  |  | Alarm 2 for multi-input 20 is active.
Alarms - Analogue inputs | Multi input 21 2 |  |  | Alarm 2 for multi-input 21 is active.
Alarms - Analogue inputs | Multi input 22 2 |  |  | Alarm 2 for multi-input 22 is active.
Alarms - Analogue inputs | Multi input 23 2 |  |  | Alarm 2 for multi-input 23 is active.
Alarms - Analogue inputs | Analogue input 20 wire fail |  |  | A wire failure was detected for analogue input 20.
Alarms - Analogue inputs | Analogue input 21 wire fail |  |  | A wire failure was detected for analogue input 21.
Alarms - Analogue inputs | Analogue input 22 wire fail |  |  | A wire failure was detected for analogue input 22.
Alarms - Analogue inputs | Analogue input 23 wire fail |  |  | A wire failure was detected for analogue input 23.
Alarms - Battery | ESS Warning |  |  | ESS Warning alarm is activated.
Alarms - Battery | ESS Shutdown |  |  | ESS Shutdown alarm is activated.
Alarms - Battery | BMS Warning |  |  | BMS Warning alarm is activated.
Alarms - Battery | BMS Shutdown |  |  | BMS Shutdown alarm is activated.
Alarms - Battery | PDS Warning | S4 PREMIUM |  | PDS Warning alarm is activated.
Alarms - Battery | PDS Shutdown | S4 PREMIUM |  | PDS Shutdown alarm is activated.
Alarms - Battery | SOC Low Alarm |  |  | SOC Low Alarm alarm is activated.
Alarms - Battery | SOC High Alarm |  |  | SOC High Alarm alarm is activated.
Alarms - Battery | DC dU Max |  |  | The DC voltage deviation between the BMS output and the PCS input, as a percent of the BMS output DC voltage, is too high.
Alarms - GEN | Ext. Gen start error |  |  | Ext. DG start error alarm (menu 15170) (a generator start request is active, but no generator is detected on the busbar within the specified time) is activated.
Alarms - GEN | Gen reverse power 1 |  |  | Generator reverse power alarm 1 (menu 15070) is activated.
Alarms - GEN | Gen reverse power 2 |  |  | Generator reverse power alarm 2 (menu 15080) is activated.
Alarms - GEN | Gen spinning reserve 1 |  |  | Spinning reserve alarm 1 (menu 15090) is activated (only generator power is used for the calculation).
Alarms - GEN | Gen spinning reserve 2 |  |  | Spinning reserve alarm 2 (menu 15100) is activated (only generator power is used for the calculation).
Alarms - Breakers | ESB open failure |  |  | ESB open failure alarm is activated.
Alarms - Breakers | ESB close failure |  |  | ESB close failure alarm is activated.
Alarms - Breakers | ESB pos. failure |  |  | ESB position failure alarm is activated.
Alarms - Breakers | ESB sync. failure |  |  | ESB synchronisation failure alarm is activated.
Alarms - Breakers | ESB ext. Tripped |  |  | ESB externally tripped alarm is activated.
Alarms - Breakers | MB open failure |  |  | MB open failure alarm is activated.
Alarms - Breakers | MB close failure |  |  | MB close failure alarm is activated.
Alarms - Breakers | MB pos. failure |  |  | MB position failure alarm is activated.
Alarms - Breakers | MB sync. failure |  |  | MB synchronisation failure alarm is activated.
Alarms - Breakers | MB ext. Tripped |  |  | MB externally tripped alarm is activated.
Alarms - Power management | Missing all units |  |  | Power management - Missing all units alarm is activated.
Alarms - Power management | Fatal CAN error |  |  | Power management - Fatal CAN error alarm is activated.
Alarms - Power management | Any Gen missing |  |  | Power management - Any Gen missing alarm is activated.
Alarms - Power management | Any mains missing |  |  | Power management - Any mains missing alarm is activated.
Alarms - Power management | Any LG missing |  |  | Power management - Any LG missing alarm is activated.
CIO Alarms | CIO 116 No. 1 In. 10 |  |  | CIO 116 No. 1 In. 10 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 11 |  |  | CIO 116 No. 1 In. 11 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 12 |  |  | CIO 116 No. 1 In. 12 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 13 |  |  | CIO 116 No. 1 In. 13 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 14 |  |  | CIO 116 No. 1 In. 14 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 15 |  |  | CIO 116 No. 1 In. 15 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 16 |  |  | CIO 116 No. 1 In. 16 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 17 |  |  | CIO 116 No. 1 In. 17 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 19 |  |  | CIO 116 No. 1 In. 19 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 20 |  |  | CIO 116 No. 1 In. 20 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 21 |  |  | CIO 116 No. 1 In. 21 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 22 |  |  | CIO 116 No. 1 In. 22 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 23 |  |  | CIO 116 No. 1 In. 23 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 24 |  |  | CIO 116 No. 1 In. 24 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 25 |  |  | CIO 116 No. 1 In. 25 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 26 |  |  | CIO 116 No. 1 In. 26 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 10 |  |  | CIO 116 No. 2 In. 10 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 11 |  |  | CIO 116 No. 2 In. 11 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 12 |  |  | CIO 116 No. 2 In. 12 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 13 |  |  | CIO 116 No. 2 In. 13 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 14 |  |  | CIO 116 No. 2 In. 14 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 15 |  |  | CIO 116 No. 2 In. 15 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 16 |  |  | CIO 116 No. 2 In. 16 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 17 |  |  | CIO 116 No. 2 In. 17 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 19 |  |  | CIO 116 No. 2 In. 19 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 20 |  |  | CIO 116 No. 2 In. 20 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 21 |  |  | CIO 116 No. 2 In. 21 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 22 |  |  | CIO 116 No. 2 In. 22 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 23 |  |  | CIO 116 No. 2 In. 23 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 24 |  |  | CIO 116 No. 2 In. 24 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 25 |  |  | CIO 116 No. 2 In. 25 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 26 |  |  | CIO 116 No. 2 In. 26 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 10 |  |  | CIO 116 No. 3 In. 10 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 11 |  |  | CIO 116 No. 3 In. 11 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 12 |  |  | CIO 116 No. 3 In. 12 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 13 |  |  | CIO 116 No. 3 In. 13 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 14 |  |  | CIO 116 No. 3 In. 14 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 15 |  |  | CIO 116 No. 3 In. 15 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 16 |  |  | CIO 116 No. 3 In. 16 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 17 |  |  | CIO 116 No. 3 In. 17 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 19 |  |  | CIO 116 No. 3 In. 19 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 20 |  |  | CIO 116 No. 3 In. 20 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 21 |  |  | CIO 116 No. 3 In. 21 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 22 |  |  | CIO 116 No. 3 In. 22 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 23 |  |  | CIO 116 No. 3 In. 23 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 24 |  |  | CIO 116 No. 3 In. 24 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 25 |  |  | CIO 116 No. 3 In. 25 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 26 |  |  | CIO 116 No. 3 In. 26 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 8.1 |  |  | CIO 308 No. 1 In. 8.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 8.2 |  |  | CIO 308 No. 1 In. 8.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 11.1 |  |  | CIO 308 No. 1 In. 11.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 11.2 |  |  | CIO 308 No. 1 In. 11.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 14.1 |  |  | CIO 308 No. 1 In. 14.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 14.2 |  |  | CIO 308 No. 1 In. 14.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 17.1 |  |  | CIO 308 No. 1 In. 17.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 17.2 |  |  | CIO 308 No. 1 In. 17.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 20.1 |  |  | CIO 308 No. 1 In. 20.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 20.2 |  |  | CIO 308 No. 1 In. 20.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 23.1 |  |  | CIO 308 No. 1 In. 23.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 23.2 |  |  | CIO 308 No. 1 In. 23.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 26.1 |  |  | CIO 308 No. 1 In. 26.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 26.2 |  |  | CIO 308 No. 1 In. 26.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 29.1 |  |  | CIO 308 No. 1 In. 29.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 29.2 |  |  | CIO 308 No. 1 In. 29.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 8.1 |  |  | CIO 308 No. 2 In. 8.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 8.2 |  |  | CIO 308 No. 2 In. 8.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 11.1 |  |  | CIO 308 No. 2 In. 11.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 11.2 |  |  | CIO 308 No. 2 In. 11.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 14.1 |  |  | CIO 308 No. 2 In. 14.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 14.2 |  |  | CIO 308 No. 2 In. 14.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 17.1 |  |  | CIO 308 No. 2 In. 17.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 17.2 |  |  | CIO 308 No. 2 In. 17.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 20.1 |  |  | CIO 308 No. 2 In. 20.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 20.2 |  |  | CIO 308 No. 2 In. 20.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 23.1 |  |  | CIO 308 No. 2 In. 23.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 23.2 |  |  | CIO 308 No. 2 In. 23.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 26.1 |  |  | CIO 308 No. 2 In. 26.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 26.2 |  |  | CIO 308 No. 2 In. 26.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 29.1 |  |  | CIO 308 No. 2 In. 29.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 29.2 |  |  | CIO 308 No. 2 In. 29.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 8.1 |  |  | CIO 308 No. 3 In. 8.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 8.2 |  |  | CIO 308 No. 3 In. 8.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 11.1 |  |  | CIO 308 No. 3 In. 11.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 11.2 |  |  | CIO 308 No. 3 In. 11.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 14.1 |  |  | CIO 308 No. 3 In. 14.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 14.2 |  |  | CIO 308 No. 3 In. 14.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 17.1 |  |  | CIO 308 No. 3 In. 17.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 17.2 |  |  | CIO 308 No. 3 In. 17.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 20.1 |  |  | CIO 308 No. 3 In. 20.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 20.2 |  |  | CIO 308 No. 3 In. 20.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 23.1 |  |  | CIO 308 No. 3 In. 23.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 23.2 |  |  | CIO 308 No. 3 In. 23.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 26.1 |  |  | CIO 308 No. 3 In. 26.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 26.2 |  |  | CIO 308 No. 3 In. 26.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 29.1 |  |  | CIO 308 No. 3 In. 29.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 29.2 |  |  | CIO 308 No. 3 In. 29.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 8 wire fail |  |  | A wire failure was detected for CIO 308 No. 1 In. 8.
CIO Alarms | CIO 308 No. 1 In. 11 wire fail |  |  | A wire failure was detected for CIO 308 No. 1 In. 11.
CIO Alarms | CIO 308 No. 1 In. 14 wire fail |  |  | A wire failure was detected for CIO 308 No. 1 In. 14.
CIO Alarms | CIO 308 No. 1 In. 17 wire fail |  |  | A wire failure was detected for CIO 308 No. 1 In. 17.
CIO Alarms | CIO 308 No. 1 In. 20 wire fail |  |  | A wire failure was detected for CIO 308 No. 1 In. 20.
CIO Alarms | CIO 308 No. 1 In. 23 wire fail |  |  | A wire failure was detected for CIO 308 No. 1 In. 23.
CIO Alarms | CIO 308 No. 1 In. 26 wire fail |  |  | A wire failure was detected for CIO 308 No. 1 In. 26.
CIO Alarms | CIO 308 No. 1 In. 29 wire fail |  |  | A wire failure was detected for CIO 308 No. 1 In. 29.
CIO Alarms | CIO 308 No. 2 In. 8 wire fail |  |  | A wire failure was detected for CIO 308 No. 2 In. 8.
CIO Alarms | CIO 308 No. 2 In. 11 wire fail |  |  | A wire failure was detected for CIO 308 No. 2 In. 11.
CIO Alarms | CIO 308 No. 2 In. 14 wire fail |  |  | A wire failure was detected for CIO 308 No. 2 In. 14.
CIO Alarms | CIO 308 No. 2 In. 17 wire fail |  |  | A wire failure was detected for CIO 308 No. 2 In. 17.
CIO Alarms | CIO 308 No. 2 In. 20 wire fail |  |  | A wire failure was detected for CIO 308 No. 2 In. 20.
CIO Alarms | CIO 308 No. 2 In. 23 wire fail |  |  | A wire failure was detected for CIO 308 No. 2 In. 23.
CIO Alarms | CIO 308 No. 2 In. 26 wire fail |  |  | A wire failure was detected for CIO 308 No. 2 In. 26.
CIO Alarms | CIO 308 No. 2 In. 29 wire fail |  |  | A wire failure was detected for CIO 308 No. 2 In. 29.
CIO Alarms | CIO 308 No. 3 In. 8 wire fail |  |  | A wire failure was detected for CIO 308 No. 3 In. 8.
CIO Alarms | CIO 308 No. 3 In. 11 wire fail |  |  | A wire failure was detected for CIO 308 No. 3 In. 11.
CIO Alarms | CIO 308 No. 3 In. 14 wire fail |  |  | A wire failure was detected for CIO 308 No. 3 In. 14.
CIO Alarms | CIO 308 No. 3 In. 17 wire fail |  |  | A wire failure was detected for CIO 308 No. 3 In. 17.
CIO Alarms | CIO 308 No. 3 In. 20 wire fail |  |  | A wire failure was detected for CIO 308 No. 3 In. 20.
CIO Alarms | CIO 308 No. 3 In. 23 wire fail |  |  | A wire failure was detected for CIO 308 No. 3 In. 23.
CIO Alarms | CIO 308 No. 3 In. 26 wire fail |  |  | A wire failure was detected for CIO 308 No. 3 In. 26.
CIO Alarms | CIO 308 No. 3 In. 29 wire fail |  |  | A wire failure was detected for CIO 308 No. 3 In. 29.
CIO Alarms | CIO 116 No. 1 module missing |  |  | The controller cannot communicate with CIO 116 No. 1.
CIO Alarms | CIO 116 No. 2 module missing |  |  | The controller cannot communicate with CIO 116 No. 2.
CIO Alarms | CIO 116 No. 3 module missing |  |  | The controller cannot communicate with CIO 116 No. 3.
CIO Alarms | CIO 208 No. 1 module missing |  |  | The controller cannot communicate with CIO 208 No. 1.
CIO Alarms | CIO 208 No. 2 module missing |  |  | The controller cannot communicate with CIO 208 No. 2.
CIO Alarms | CIO 208 No. 3 module missing |  |  | The controller cannot communicate with CIO 208 No. 3.
CIO Alarms | CIO 308 No. 1 module missing |  |  | The controller cannot communicate with CIO 308 No. 1.
CIO Alarms | CIO 308 No. 2 module missing |  |  | The controller cannot communicate with CIO 308 No. 2.
CIO Alarms | CIO 308 No. 3 module missing |  |  | The controller cannot communicate with CIO 308 No. 3.
Limits | BB U> 1 |  |  | BB over-voltage 1 (menu 1270) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB U> 2 |  |  | BB over-voltage 2 (menu 1280) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB U> 3 |  |  | BB over-voltage 3 (menu 1290) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB U< 1 |  |  | BB under-voltage 1 (menu 1300) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB U< 2 |  |  | BB under-voltage 2 (menu 1310) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB U< 3 |  |  | BB under-voltage 3 (menu 1320) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB U< 4 |  |  | BB under-voltage 4 (menu 1330) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB f> 1 |  |  | BB over-frequency 1 (menu 1350) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB f> 2 |  |  | BB over-frequency 2 (menu 1360) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB f> 3 |  |  | BB over-frequency 3 (menu 1370) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB f> 4 |  |  | BB over-frequency 4 (menu 1920) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB f< 1 |  |  | BB under-frequency 1 (menu 1380) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB f< 2 |  |  | BB under-frequency 2 (menu 1390) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB f< 3 |  |  | BB under-frequency 3 (menu 1400) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB f< 4 |  |  | BB under-frequency 4 (menu 1410) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB f< 5 |  |  | BB under-frequency 5 (menu 1930) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES I> 1 |  |  | ESS over-current 1 (menu 1030) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES I> 2 |  |  | ESS over-current 2 (menu 1040) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES I> 3 |  |  | ESS over-current 3 (menu 1050) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES I> 4 |  |  | ESS over-current 4 (menu 1060) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Busbar Over Current 1 |  | 1120 | Over-current 1 (menu 14250) (measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Busbar Over Current 2 |  | 1120 | Over-current 2 (menu 14260) (measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Neutral Over Current 1 |  | 1200 | Neutral over-current 1 (menu 14210) (as measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Neutral Over Current 2 |  | 1200 | Neutral over-current 2 (menu 14220) (as measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Earth Over Current 1 |  | 1200 | Earth over-current 1 (menu 14230) (as measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Earth Over Current 2 |  | 1200 | Earth over-current 2 (menu 14240) (as measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES P> 1 |  |  | ESS overload 1 (menu 1450) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES P> 2 |  |  | ESS overload 2 (menu 1460) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES P> 3 |  |  | ESS overload 3 (menu 1470) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES P> 4 |  |  | ESS overload 4 (menu 1480) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES P> 5 |  |  | ESS overload or reverse power 5 (menu 1490) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES -P> 1 |  |  | ESS reverse power 1 (menu 1000) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES -P> 2 |  |  | ESS reverse power 2 (menu 1010) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES -P> 3 |  | 1070 | ESS reverse power 3 (menu 1070) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th P> 1 |  |  | Overload 1 (menu 14290) (measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th P> 2 |  |  | Overload 2 (menu 14300) (measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th -P> 1 |  |  | Reverse power 1 (menu 14270) (measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th -P> 2 |  |  | Reverse power 2 (menu 14280) (measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES U> 1 |  |  | ESS over-voltage 1 (menu 1150) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES U> 2 |  |  | ESS over-voltage 2 (menu 1160) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES U< 1 |  |  | ESS under-voltage 1 (menu 1170) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES U< 2 |  |  | ESS under-voltage 2 (menu 1180) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES U< 3 |  |  | ESS under-voltage 3 (menu 1190) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES f> 1 |  |  | ESS over-frequency 1 (menu 1210) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES f> 2 |  |  | ESS over-frequency 2 (menu 1220) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES f> 3 |  |  | ESS over-frequency 3 (menu 1230) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES f< 1 |  |  | ESS under-frequency 1 (menu 1240) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES f< 2 |  |  | ESS under-frequency 2 (menu 1250) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | ES f< 3 |  |  | ESS under-frequency 3 (menu 1260) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 39 |  |  | Digital input 39 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 40 |  |  | Digital input 40 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 41 |  |  | Digital input 41 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 42 |  |  | Digital input 42 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 43 |  |  | Digital input 43 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 44 |  |  | Digital input 44 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 45 |  |  | Digital input 45 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 46 |  |  | Digital input 46 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 47 |  |  | Digital input 47 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 48 |  |  | Digital input 48 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 49 |  |  | Digital input 49 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 50 |  |  | Digital input 50 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 20 1 |  |  | Multi-input 20 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 21 1 |  |  | Multi-input 21 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 22 1 |  |  | Multi-input 22 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 23 1 |  |  | Multi-input 23 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 20 2 |  |  | Multi-input 20 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 21 2 |  |  | Multi-input 21 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 22 2 |  |  | Multi-input 22 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 23 2 |  |  | Multi-input 23 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 20 wirefail |  |  | Multi-input 20 wire break detection outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 21 wirefail |  |  | Multi-input 21 wire break detection outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 22 wirefail |  |  | Multi-input 22 wire break detection outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 23 wirefail |  |  | Multi-input 23 wire break detection outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Available power 1 |  |  | -
Limits | Available power 2 |  |  | -
Limits | Available power 3 |  |  | -
Limits | Available power 4 |  |  | -
Limits | Available power 5 |  |  | -
Limits | Volt dep Over Current |  |  | ESS voltage-dependent over-current (menu 1100 and 1110) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Uq<1 |  |  | U and Q < 1 (menu 1960) (ESS voltage is low, with zero or negative kvar from ESS) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Uq<2 |  |  | U and Q < 2 (menu 1970) (ESS voltage is low, with zero or negative kvar from ESS) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | I inverse |  |  | (IEC/IEEE) Inverse time overcurrent (menu 1080) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue1 1 |  |  | Delta analogue1 1 (menu 4610) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue1 2 |  |  | Delta analogue1 2 (menu 4620) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue2 1 |  |  | Delta analogue2 1 (menu 4630) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue2 2 |  |  | Delta analogue2 2 (menu 4640) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue3 1 |  |  | Delta analogue3 1 (menu 4650) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue3 2 |  |  | Delta analogue3 2 (menu 4660) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue4 1 |  |  | Delta analogue4 1 (menu 4680) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue4 2 |  |  | Delta analogue4 2 (menu 4690) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue5 1 |  |  | Delta analogue5 1 (menu 4700) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue5 2 |  |  | Delta analogue5 2 (menu 4710) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue6 1 |  |  | Delta analogue6 1 (menu 4720) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue6 2 |  |  | Delta analogue6 2 (menu 4730) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BB U> Average 1 |  |  | -
Limits | BB U> Average 2 |  |  | -
Limits | M-Logic alarm 1 |  |  | M-Logic alarm 1 (menu 3570) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 2 |  |  | M-Logic alarm 2 (menu 3580) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 3 |  |  | M-Logic alarm 3 (menu 3590) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 4 |  |  | M-Logic alarm 4 (menu 3600) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 5 |  |  | M-Logic alarm 5 (menu 3610) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 10 |  | 1180 | M-Logic alarm 10 (menu 3660) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 11 |  | 1180 | M-Logic alarm 11 (menu 3670) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 12 |  | 1180 | M-Logic alarm 12 (menu 3680) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 13 |  | 1180 | M-Logic alarm 13 (menu 3690) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 14 |  | 1180 | M-Logic alarm 14 (menu 3700) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BTB Ext. Tripped |  |  | -
Limits | BTB sync. failure |  |  | -
Limits | BB meas failure |  |  | -
Limits | M-Logic ext alarm 1 |  | 1061 | M-Logic ext alarm 1 (menu 3621) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic ext alarm 2 |  | 1061 | M-Logic ext alarm 2 (menu 3631) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic ext alarm 3 |  | 1061 | M-Logic ext alarm 3 (menu 3641) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic ext alarm 4 |  | 1061 | M-Logic ext alarm 4 (menu 3651) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits - Battery | ESS Warning |  |  | ESS Warning (menu 7580) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits - Battery | ESS Shutdown |  |  | ESS Shutdown (menu 7590) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits - Battery | BMS Warning |  |  | BMS Warning (menu 7610) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits - Battery | BMS Shutdown |  |  | BMS Shutdown (menu 7620) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits - Battery | PDS Warning |  |  | PDS Warning (menu 7930) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits - Battery | PDS Shutdown |  |  | PDS Shutdown (menu 7940) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits - Battery | SOC Low Alarm |  |  | SOC low alarm (menu 17110) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits - Battery | SOC High Alarm |  |  | DC dU max alarm (menu 17150) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits - Battery | DC dU Max |  |  | BMS-PCS voltage deviation alarm (menu 17150) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits - GEN | Ext. Gen start error |  |  | Ext. DG start error (menu 15170) (a generator start request is active, but no generator is detected on the busbar within the specified time) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits - GEN | Gen reverse power 1 |  |  | Generator reverse power 1 (menu 15070) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits - GEN | Gen reverse power 2 |  |  | Generator reverse power 2 (menu 15080) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits - GEN | Gen spinning reserve 1 |  |  | Spinning reserve 1 (menu 15090) (only generator power is used for the calculation) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits - GEN | Gen spinning reserve 2 |  |  | Spinning reserve 2 (menu 15100) (only generator power is used for the calculation) outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 10 |  |  | CIO 116 No. 1 In. 10 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 11 |  |  | CIO 116 No. 1 In. 11 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 12 |  |  | CIO 116 No. 1 In. 12 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 13 |  |  | CIO 116 No. 1 In. 13 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 14 |  |  | CIO 116 No. 1 In. 14 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 15 |  |  | CIO 116 No. 1 In. 15 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 16 |  |  | CIO 116 No. 1 In. 16 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 17 |  |  | CIO 116 No. 1 In. 17 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 19 |  |  | CIO 116 No. 1 In. 19 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 20 |  |  | CIO 116 No. 1 In. 20 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 21 |  |  | CIO 116 No. 1 In. 21 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 22 |  |  | CIO 116 No. 1 In. 22 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 23 |  |  | CIO 116 No. 1 In. 23 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 24 |  |  | CIO 116 No. 1 In. 24 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 25 |  |  | CIO 116 No. 1 In. 25 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 1 In. 26 |  |  | CIO 116 No. 1 In. 26 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 10 |  |  | CIO 116 No. 2 In. 10 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 11 |  |  | CIO 116 No. 2 In. 11 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 12 |  |  | CIO 116 No. 2 In. 12 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 13 |  |  | CIO 116 No. 2 In. 13 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 14 |  |  | CIO 116 No. 2 In. 14 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 15 |  |  | CIO 116 No. 2 In. 15 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 16 |  |  | CIO 116 No. 2 In. 16 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 17 |  |  | CIO 116 No. 2 In. 17 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 19 |  |  | CIO 116 No. 2 In. 19 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 20 |  |  | CIO 116 No. 2 In. 20 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 21 |  |  | CIO 116 No. 2 In. 21 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 22 |  |  | CIO 116 No. 2 In. 22 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 23 |  |  | CIO 116 No. 2 In. 23 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 24 |  |  | CIO 116 No. 2 In. 24 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 25 |  |  | CIO 116 No. 2 In. 25 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 2 In. 26 |  |  | CIO 116 No. 2 In. 26 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 10 |  |  | CIO 116 No. 3 In. 10 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 11 |  |  | CIO 116 No. 3 In. 11 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 12 |  |  | CIO 116 No. 3 In. 12 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 13 |  |  | CIO 116 No. 3 In. 13 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 14 |  |  | CIO 116 No. 3 In. 14 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 15 |  |  | CIO 116 No. 3 In. 15 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 16 |  |  | CIO 116 No. 3 In. 16 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 17 |  |  | CIO 116 No. 3 In. 17 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 19 |  |  | CIO 116 No. 3 In. 19 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 20 |  |  | CIO 116 No. 3 In. 20 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 21 |  |  | CIO 116 No. 3 In. 21 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 22 |  |  | CIO 116 No. 3 In. 22 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 23 |  |  | CIO 116 No. 3 In. 23 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 24 |  |  | CIO 116 No. 3 In. 24 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 25 |  |  | CIO 116 No. 3 In. 25 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 116 No. 3 In. 26 |  |  | CIO 116 No. 3 In. 26 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 8.1 |  |  | CIO 308 No. 1 In. 8.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 8.2 |  |  | CIO 308 No. 1 In. 8.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 11.1 |  |  | CIO 308 No. 1 In. 11.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 11.2 |  |  | CIO 308 No. 1 In. 11.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 14.1 |  |  | CIO 308 No. 1 In. 14.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 14.2 |  |  | CIO 308 No. 1 In. 14.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 17.1 |  |  | CIO 308 No. 1 In. 17.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 17.2 |  |  | CIO 308 No. 1 In. 17.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 20.1 |  |  | CIO 308 No. 1 In. 20.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 20.2 |  |  | CIO 308 No. 1 In. 20.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 23.1 |  |  | CIO 308 No. 1 In. 23.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 23.2 |  |  | CIO 308 No. 1 In. 23.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 26.1 |  |  | CIO 308 No. 1 In. 26.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 26.2 |  |  | CIO 308 No. 1 In. 26.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 29.1 |  |  | CIO 308 No. 1 In. 29.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 29.2 |  |  | CIO 308 No. 1 In. 29.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 8.1 |  |  | CIO 308 No. 2 In. 8.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 8.2 |  |  | CIO 308 No. 2 In. 8.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 11.1 |  |  | CIO 308 No. 2 In. 11.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 11.2 |  |  | CIO 308 No. 2 In. 11.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 14.1 |  |  | CIO 308 No. 2 In. 14.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 14.2 |  |  | CIO 308 No. 2 In. 14.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 17.1 |  |  | CIO 308 No. 2 In. 17.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 17.2 |  |  | CIO 308 No. 2 In. 17.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 20.1 |  |  | CIO 308 No. 2 In. 20.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 20.2 |  |  | CIO 308 No. 2 In. 20.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 23.1 |  |  | CIO 308 No. 2 In. 23.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 23.2 |  |  | CIO 308 No. 2 In. 23.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 26.1 |  |  | CIO 308 No. 2 In. 26.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 26.2 |  |  | CIO 308 No. 2 In. 26.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 29.1 |  |  | CIO 308 No. 2 In. 29.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 29.2 |  |  | CIO 308 No. 2 In. 29.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 8.1 |  |  | CIO 308 No. 3 In. 8.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 8.2 |  |  | CIO 308 No. 3 In. 8.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 11.1 |  |  | CIO 308 No. 3 In. 11.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 11.2 |  |  | CIO 308 No. 3 In. 11.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 14.1 |  |  | CIO 308 No. 3 In. 14.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 14.2 |  |  | CIO 308 No. 3 In. 14.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 17.1 |  |  | CIO 308 No. 3 In. 17.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 17.2 |  |  | CIO 308 No. 3 In. 17.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 20.1 |  |  | CIO 308 No. 3 In. 20.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 20.2 |  |  | CIO 308 No. 3 In. 20.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 23.1 |  |  | CIO 308 No. 3 In. 23.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 23.2 |  |  | CIO 308 No. 3 In. 23.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 26.1 |  |  | CIO 308 No. 3 In. 26.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 26.2 |  |  | CIO 308 No. 3 In. 26.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 29.1 |  |  | CIO 308 No. 3 In. 29.1 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 29.2 |  |  | CIO 308 No. 3 In. 29.2 outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 8 wire fail |  |  | CIO 308 No. 1 In. 8 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 11 wire fail |  |  | CIO 308 No. 1 In. 11 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 14 wire fail |  |  | CIO 308 No. 1 In. 14 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 17 wire fail |  |  | CIO 308 No. 1 In. 17 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 20 wire fail |  |  | CIO 308 No. 1 In. 20 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 23 wire fail |  |  | CIO 308 No. 1 In. 23 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 26 wire fail |  |  | CIO 308 No. 1 In. 26 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 1 In. 29 wire fail |  |  | CIO 308 No. 1 In. 29 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 8 wire fail |  |  | CIO 308 No. 2 In. 8 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 11 wire fail |  |  | CIO 308 No. 2 In. 11 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 14 wire fail |  |  | CIO 308 No. 2 In. 14 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 17 wire fail |  |  | CIO 308 No. 2 In. 17 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 20 wire fail |  |  | CIO 308 No. 2 In. 20 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 23 wire fail |  |  | CIO 308 No. 2 In. 23 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 26 wire fail |  |  | CIO 308 No. 2 In. 26 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 2 In. 29 wire fail |  |  | CIO 308 No. 2 In. 29 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 8 wire fail |  |  | CIO 308 No. 3 In. 8 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 11 wire fail |  |  | CIO 308 No. 3 In. 11 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 14 wire fail |  |  | CIO 308 No. 3 In. 14 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 17 wire fail |  |  | CIO 308 No. 3 In. 17 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 20 wire fail |  |  | CIO 308 No. 3 In. 20 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 23 wire fail |  |  | CIO 308 No. 3 In. 23 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 26 wire fail |  |  | CIO 308 No. 3 In. 26 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
CIO Limits | CIO 308 No. 3 In. 29 wire fail |  |  | CIO 308 No. 3 In. 29 wire fail outputs A and/or B are set to Limits, and the alarm conditions are met.
Events | Mains-Fail |  |  | There is an active mains failure.
Events | ESS volt/freq Ok |  |  | The voltage and frequency of the ESS are within the limits configured in parameters 2111 to 2114.
Events | Access lock |  |  | The access lock is active.
Events | Emergency stop |  |  | The emergency stop is active.
Events | Lamp test |  |  | The lamp test is active.
Events | Parameter set 1 used |  |  | Nominal parameter set 1 is used.
Events | Parameter set 2 used |  |  | Nominal parameter set 2 is used.
Events | Parameter set 3 used |  |  | Nominal parameter set 3 is used.
Events | Parameter set 4 used |  |  | Nominal parameter set 4 is used.
Events | BB voltage ok |  |  | The voltage and frequency of the busbar are within the limits configured in parameters 2111 to 2114.
Events | Application 1 activated |  |  | The controller is using single-line application drawing 4.
Events | Application 2 activated |  |  | The controller is using single-line application drawing 2.
Events | Application 3 activated |  |  | The controller is using single-line application drawing 3.
Events | Application 4 activated |  |  | The controller is using single-line application drawing 4.
Events | Stand-alone app. selected |  |  | The selected controller application is a stand-alone controller.
Events | Standard app. selected |  |  | The selected controller application is a standard controller (that is, a power management system is possible).
Events | Dynamic section equal static section |  |  | In power management, the bus tie breaker(s) are closed.
Events | Update mode local selected |  |  | Local update mode is selected.
Events | Update mode on all selected |  |  | Update mode on all is selected.
Events | Ack all alarms active |  |  | The controller acknowledges all alarms.
Events | Three phase system |  |  | The AC measurement setup is configured as a three-phase system.
Events | Split L1L3 phase system |  |  | The AC measurement setup is split-phase (L1-L3).
Events | Split L1L2 phase system |  |  | The AC measurement setup is split-phase (L1-L2).
Events | Single phase system |  |  | The AC measurement setup is single-phase.
Events | BB Parameter set 1 used |  |  | The controller is using busbar parameter set 1.
Events | BB Parameter set 2 used |  |  | The controller is using busbar parameter set 2.
Events | BB Unom = ES Unom used |  |  | The controller is using the busbar nominal voltage for the ESS nominal voltage.
Events | 60Hz system |  |  | The system has a nominal frequency of 60 Hz.
Events | L1L2L3 phase rotation active |  |  | The phase rotation used by the controller is L1L2L3.
Events | L1L3L2 phase rotation active |  |  | The phase rotation used by the controller is L1L3L2.
Events | Q ref type off-grid selected: Off |  |  | The reactive power reference for off-grid (parameter 7033) is Off.
Events | Q ref type off-grid selected: Share |  |  | The reactive power reference for off-grid (parameter 7033) is Share.
Events | Q ref type grid-tied selected: Off |  |  | The reactive power reference for grid-tied (parameter 7055) is Off.
Events | Q ref type grid-tied selected: Cosphi fixed |  |  | The reactive power reference for grid-tied (parameter 7055) is Cosphi fixed.
Events | Q ref type grid-tied selected: Cosphi imp/exp |  |  | The reactive power reference for grid-tied (parameter 7055) is Cosphi imp/exp.
Events | Q ref type grid-tied selected: Cosphi superior |  |  | The reactive power reference for grid-tied (parameter 7055) is Cosphi superior.
Events | Q ref type grid-tied selected: Q fixed |  |  | The reactive power reference for grid-tied (parameter 7055) is Q fixed.
Events | Q ref type grid-tied selected: Q imp/ext |  |  | The reactive power reference for grid-tied (parameter 7055) is Q imp/ext.
Events | P/Q limit type selected: Off |  |  | The selected P/Q limit type is Off.
Events | I am over 85 pct loaded |  |  | The ESS SOC is over 85 %.
Events | I am over 90 pct loaded |  |  | The ESS SOC is over 90 %.
Events | I am over 95 pct loaded |  |  | The ESS SOC is over 95 %.
Events | Spinning Reserve Enabled |  |  | Spinning Reserve is enabled.
Events | Any Gen on hybrid busbar |  | 1190 | There is at least one genset connected to the energy management system busbar.
Events | Any MAINS on hybrid busbar |  | 1190 | There is at least one mains connected to the energy management system busbar.
Events | Any other BATTERY on hybrid busbar |  | 1190 | There is at least one other ASC Storage or Battery controller connected to the energy management system busbar.
Events | I am lowest running ESS ID |  | 1190 | The ASC Storage controller ID is the lowest ASC Storage controller ID in the energy management system.
Events | Any alarm active |  | 1190 | At least one alarm is active.
Events - Battery | Power functionality OK |  |  | The power function is activated and the battery is assisting the plant.
Events - Battery | Energy functionality OK |  |  | The energy function is activated and the battery is leading the plant.
Events - Battery | Battery fully charged |  |  | The SOC is at or above the maximum.
Events - Battery | Battery AC coupled selected |  |  | The selection in parameter 17082 is AC-coupled battery.
Events - Battery | Battery DC coupled selected |  |  | The selection in parameter 17082 is DC-coupled battery.
Events - Battery | Battery SOC parameter set 1 selected |  |  | The selection in parameter 17055 is SOC setting 1.
Events - Battery | Battery SOC parameter set 2 selected |  |  | The selection in parameter 17055 is SOC setting 2.
Events - Battery | Battery SOC parameter set 3 selected |  |  | The selection in parameter 17055 is SOC setting 3.
Events - Battery | Battery Energy source selected |  |  | Battery Energy source is selected.
Events - Battery | Battery Power source selected |  |  | Battery Power source is selected.
Events - Battery | P/Q mode active |  |  | The ESS is running in grid-following mode.
Events - Battery | V/f mode active |  |  | The ESS is running in grid-forming mode.
Events - Battery | Droop mode active |  |  | The ESS is running in droop mode.
Events - Battery | Custom output 1 from ESS |  |  | The ESS has activated custom output 1.
Events - Battery | Custom output 2 from ESS |  |  | The ESS has activated custom output 2.
Events - Battery | Custom output 3 from ESS |  |  | The ESS has activated custom output 3.
Events - Battery | Custom output from BMS |  |  | The BMS has activated the custom output.
Events - Battery | Mains charge parameter enabled |  |  | Mains charging (parameter 17022) is Enabled.
Events - Battery | Gen charge parameter enabled |  |  | DG charge mode (parameter 17033) is Enabled.
Events - Battery | PV charge parameter enabled |  |  | PV charging (parameter 17041) is Enabled.
Events - Battery | Boost charging activated |  | 1150 | The ASC is sending a command to the ESS to boost charging.
Events - Battery | PDS spin. res. pct 1 selected |  | 1150 | Parameter 17203 is PDS spinning reserve pct 01.
Events - Battery | PDS spin. res. pct 2 selected |  | 1150 | Parameter 17203 is PDS spinning reserve pct 02.
Events - Battery | SOC Above or Equal to SOC Min |  | 1160 | The state of charge is at or above the minimum for the activated SOC settings (parameter 17051/17061/17071).
Events - Battery | SOC Above or Equal to Threshold 1 |  | 1160 | The stage of charge is at or above threshold 1 for the activated SOC settings (parameter 17053/17063/17073 or 17054/17064/17074).
Events - Battery | SOC Above or Equal to Threshold 2 |  | 1160 | The stage of charge is at or above threshold 2 for the activated SOC settings (parameter 17053/17063/17073 or 17054/17064/17074).
Events - Battery | SOC Above or Equal to SOC Max |  | 1160 | The state of charge is at or above the maximum for the activated SOC settings (parameter 17052/17062/17072).
Events - Battery | ESS isochronous mode active |  | 1180 | ESS isochronous mode is active.
Events - Battery | Maintenance Charge active |  | 1210 | The Maintenance Charge function is active.
Events - Battery | Maintenance Charge fully charged |  | 1210 | The controller used Maintenance Charge and the ESS is now fully charged.
Events - GEN | Min. Gen load set 1 selected |  |  | Min. DG load set 1 (parameter 15013) is selected.
Events - GEN | Min. Gen load set 2 selected |  |  | Min. DG load set 2 (parameter 15013) is selected.
Events - GEN | Request to start ext. Gen active |  |  | The request to start and run and external genset is active.
Events - GEN | Request to stop ext. Gen active |  |  | The request to start and run and external genset is not active.
Events - GEN | Opt. Gen load off selected |  |  | The selection in Opt. DG load set (parameter 15016) is Off.
Events - GEN | Opt. Gen load pct 1 selected |  |  | The selection in Opt. DG load set (parameter 15016) is pct 1.
Events - GEN | Opt. Gen load pct 2 selected |  |  | The selection in Opt. DG load set (parameter 15016) is pct 2.
Events - GEN | DG LS Reverse Q |  | 1210 | The genset load sharing kvar is negative.
Events Breakers | MB-Closed |  |  | The mains breaker is closed.
Events Breakers | MB-Opened |  |  | The mains breaker is opened.
Events Breakers | ESB-Closed |  |  | The ESS breaker is closed.
Events Breakers | ESB-Opened |  |  | The ESS breaker is opened.
Events Breakers | ESB synchronising |  |  | The ESB is synchronising.
Events Breakers | MB synchronising |  |  | The MB is synchronising.
Events Breakers | ESB direct in |  |  | -
Events Breakers | MB synchronisation to ES activated |  |  | Synchronisation of the mains breaker to the ESS is activated.
Events Breakers | MB synchronisation to ES deactivated |  |  | Synchronisation of the mains breaker to the ESS is deactivated.
Events Breakers | ESB synchronisation to mains activated |  |  | Synchronisation of the ESS to the mains connection is activated.
Events Breakers | ESB synchronisation to mains deactivated |  |  | Synchronisation of the ESS to the mains connection is deactivated.
DG power meter inputs | GEN Power meter1 input1 |  |  | Power meter1 input1 (Ext. source 1) is active.
DG power meter inputs | GEN Power meter1 input2 |  |  | Power meter1 input2 (Ext. source 1) is active.
DG power meter inputs | GEN Power meter1 input3 |  |  | Power meter1 input3 (Ext. source 1) is active.
DG power meter inputs | GEN Power meter1 input4 |  |  | Power meter1 input4 (Ext. source 1) is active.
DG power meter inputs | GEN Power meter2 input1 |  |  | Power meter2 input1 (Ext. source 2) is active.
DG power meter inputs | GEN Power meter2 input2 |  |  | Power meter2 input2 (Ext. source 2) is active.
DG power meter inputs | GEN Power meter2 input3 |  |  | Power meter2 input3 (Ext. source 2) is active.
DG power meter inputs | GEN Power meter2 input4 |  |  | Power meter2 input4 (Ext. source 2) is active.
DG power meter inputs | GEN Power meter3 input1 |  |  | Power meter3 input1 (Ext. source 3) is active.
DG power meter inputs | GEN Power meter3 input2 |  |  | Power meter3 input2 (Ext. source 3) is active.
DG power meter inputs | GEN Power meter3 input3 |  |  | Power meter3 input3 (Ext. source 3) is active.
DG power meter inputs | GEN Power meter3 input4 |  |  | Power meter3 input4 (Ext. source 3) is active.
DG power meter inputs | GEN Power meter4 input1 |  |  | Power meter4 input1 (Ext. source 4) is active.
DG power meter inputs | GEN Power meter4 input2 |  |  | Power meter4 input2 (Ext. source 4) is active.
DG power meter inputs | GEN Power meter4 input3 |  |  | Power meter4 input3 (Ext. source 4) is active.
DG power meter inputs | GEN Power meter4 input4 |  |  | Power meter4 input4 (Ext. source 4) is active.
DG power meter inputs | GEN Power meter5 input1 | S4 PREMIUM |  | Power meter5 input1 (Ext. source 5) is active.
DG power meter inputs | GEN Power meter5 input2 | S4 PREMIUM |  | Power meter5 input2 (Ext. source 5) is active.
DG power meter inputs | GEN Power meter5 input3 | S4 PREMIUM |  | Power meter5 input3 (Ext. source 5) is active.
DG power meter inputs | GEN Power meter5 input4 | S4 PREMIUM |  | Power meter5 input4 (Ext. source 5) is active.
DG power meter inputs | GEN Power meter6 input1 | S4 PREMIUM |  | Power meter6 input1 (Ext. source 6) is active.
DG power meter inputs | GEN Power meter6 input2 | S4 PREMIUM |  | Power meter6 input2 (Ext. source 6) is active.
DG power meter inputs | GEN Power meter6 input3 | S4 PREMIUM |  | Power meter6 input3 (Ext. source 6) is active.
DG power meter inputs | GEN Power meter6 input4 | S4 PREMIUM |  | Power meter6 input4 (Ext. source 6) is active.
DG power meter inputs | GEN Power meter7 input1 | S4 PREMIUM |  | Power meter7 input1 (Ext. source 7) is active.
DG power meter inputs | GEN Power meter7 input2 | S4 PREMIUM |  | Power meter7 input2 (Ext. source 7) is active.
DG power meter inputs | GEN Power meter7 input3 | S4 PREMIUM |  | Power meter7 input3 (Ext. source 7) is active.
DG power meter inputs | GEN Power meter7 input4 | S4 PREMIUM |  | Power meter7 input4 (Ext. source 7) is active.
DG power meter inputs | GEN Power meter8 input1 | S4 PREMIUM |  | Power meter8 input1 (Ext. source 8) is active.
DG power meter inputs | GEN Power meter8 input2 | S4 PREMIUM |  | Power meter8 input2 (Ext. source 8) is active.
DG power meter inputs | GEN Power meter8 input3 | S4 PREMIUM |  | Power meter8 input3 (Ext. source 8) is active.
DG power meter inputs | GEN Power meter8 input4 | S4 PREMIUM |  | Power meter8 input4 (Ext. source 8) is active.
DG power meter inputs | GEN Power meter9 input1 | S4 PREMIUM |  | Power meter9 input1 (Ext. source 9) is active.
DG power meter inputs | GEN Power meter9 input2 | S4 PREMIUM |  | Power meter9 input2 (Ext. source 9) is active.
DG power meter inputs | GEN Power meter9 input3 | S4 PREMIUM |  | Power meter9 input3 (Ext. source 9) is active.
DG power meter inputs | GEN Power meter9 input4 | S4 PREMIUM |  | Power meter9 input4 (Ext. source 9) is active.
DG power meter inputs | GEN Power meter10 input1 | S4 PREMIUM |  | Power meter10 input1 (Ext. source 10) is active.
DG power meter inputs | GEN Power meter10 input2 | S4 PREMIUM |  | Power meter10 input2 (Ext. source 10) is active.
DG power meter inputs | GEN Power meter10 input3 | S4 PREMIUM |  | Power meter10 input3 (Ext. source 10) is active.
DG power meter inputs | GEN Power meter10 input4 | S4 PREMIUM |  | Power meter10 input4 (Ext. source 10) is active.
DG power meter inputs | GEN Power meter11 input1 | S4 PREMIUM |  | Power meter11 input1 (Ext. source 11) is active.
DG power meter inputs | GEN Power meter11 input2 | S4 PREMIUM |  | Power meter11 input2 (Ext. source 11) is active.
DG power meter inputs | GEN Power meter11 input3 | S4 PREMIUM |  | Power meter11 input3 (Ext. source 11) is active.
DG power meter inputs | GEN Power meter11 input4 | S4 PREMIUM |  | Power meter11 input4 (Ext. source 11) is active.
DG power meter inputs | GEN Power meter12 input1 | S4 PREMIUM |  | Power meter12 input1 (Ext. source 12) is active.
DG power meter inputs | GEN Power meter12 input2 | S4 PREMIUM |  | Power meter12 input2 (Ext. source 12) is active.
DG power meter inputs | GEN Power meter12 input3 | S4 PREMIUM |  | Power meter12 input3 (Ext. source 12) is active.
DG power meter inputs | GEN Power meter12 input4 | S4 PREMIUM |  | Power meter12 input4 (Ext. source 12) is active.
DG power meter inputs | GEN Power meter13 input1 | S4 PREMIUM |  | Power meter13 input1 (Ext. source 13) is active.
DG power meter inputs | GEN Power meter13 input2 | S4 PREMIUM |  | Power meter13 input2 (Ext. source 13) is active.
DG power meter inputs | GEN Power meter13 input3 | S4 PREMIUM |  | Power meter13 input3 (Ext. source 13) is active.
DG power meter inputs | GEN Power meter13 input4 | S4 PREMIUM |  | Power meter13 input4 (Ext. source 13) is active.
DG power meter inputs | GEN Power meter14 input1 | S4 PREMIUM |  | Power meter14 input1 (Ext. source 14) is active.
DG power meter inputs | GEN Power meter14 input2 | S4 PREMIUM |  | Power meter14 input2 (Ext. source 14) is active.
DG power meter inputs | GEN Power meter14 input3 | S4 PREMIUM |  | Power meter14 input3 (Ext. source 14) is active.
DG power meter inputs | GEN Power meter14 input4 | S4 PREMIUM |  | Power meter14 input4 (Ext. source 14) is active.
DG power meter inputs | GEN Power meter15 input1 | S4 PREMIUM |  | Power meter15 input1 (Ext. source 15) is active.
DG power meter inputs | GEN Power meter15 input2 | S4 PREMIUM |  | Power meter15 input2 (Ext. source 15) is active.
DG power meter inputs | GEN Power meter15 input3 | S4 PREMIUM |  | Power meter15 input3 (Ext. source 15) is active.
DG power meter inputs | GEN Power meter15 input4 | S4 PREMIUM |  | Power meter15 input4 (Ext. source 15) is active.
DG power meter inputs | GEN Power meter16 input1 | S4 PREMIUM |  | Power meter16 input1 (Ext. source 16) is active.
DG power meter inputs | GEN Power meter16 input2 | S4 PREMIUM |  | Power meter16 input2 (Ext. source 16) is active.
DG power meter inputs | GEN Power meter16 input3 | S4 PREMIUM |  | Power meter16 input3 (Ext. source 16) is active.
DG power meter inputs | GEN Power meter16 input4 | S4 PREMIUM |  | Power meter16 input4 (Ext. source 16) is active.
Mains power meter inputs | Mains Power meter1 input1 |  |  | Mains Power meter1 input1 is active.
Mains power meter inputs | Mains Power meter1 input2 |  |  | Mains Power meter1 input2 is active.
Mains power meter inputs | Mains Power meter1 input3 |  |  | Mains Power meter1 input3 is active.
Mains power meter inputs | Mains Power meter1 input4 |  |  | Mains Power meter1 input4 is active.
Cmd Timers | Cmd timer 01 active |  |  | Command timer 1 (parameters 6951, and 6961 to 6966) is active.
Cmd Timers | Cmd timer 02 active |  |  | Command timer 2 (parameters 6952, and 6971 to 6976) is active.
Cmd Timers | Cmd timer 03 active |  |  | Command timer 3 (parameters 6953, and 6981 to 6986) is active.
Cmd Timers | Cmd timer 04 active |  |  | Command timer 4 (parameters 6954, and 6991 to 6996) is active.
Cmd Timers | Any Cmd timer active |  |  | Any command timer (1 to 4) is active.
Cmd Schedulers | Cmd Scheduler 1 active |  |  | Scheduler 1 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 2 active |  |  | Scheduler 2 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 3 active |  |  | Scheduler 3 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 4 active |  |  | Scheduler 4 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 5 active |  |  | Scheduler 5 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 6 active |  |  | Scheduler 6 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 7 active |  |  | Scheduler 7 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 8 active |  |  | Scheduler 8 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 9 active |  |  | Scheduler 9 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 10 active |  |  | Scheduler 10 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 11 active |  |  | Scheduler 11 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 12 active |  |  | Scheduler 12 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 13 active |  |  | Scheduler 13 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 14 active |  |  | Scheduler 14 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 15 active |  |  | Scheduler 15 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 16 active |  |  | Scheduler 16 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 17 active |  |  | Scheduler 17 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 18 active |  |  | Scheduler 18 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 19 active |  |  | Scheduler 19 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 20 active |  |  | Scheduler 20 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 21 active |  |  | Scheduler 21 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 22 active |  |  | Scheduler 22 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 23 active |  |  | Scheduler 23 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 24 active |  |  | Scheduler 24 (configured in the utility software) is active.
CAN Input | CAN Inp 01 active |  |  | M-Logic CAN Inp 01 is active.
CAN Input | CAN Inp 02 active |  |  | M-Logic CAN Inp 02 is active.
CAN Input | CAN Inp 03 active |  |  | M-Logic CAN Inp 03 is active.
CAN Input | CAN Inp 04 active |  |  | M-Logic CAN Inp 04 is active.
CAN Input | CAN Inp 05 active |  |  | M-Logic CAN Inp 05 is active.
CAN Input | CAN Inp 06 active |  |  | M-Logic CAN Inp 06 is active.
CAN Input | CAN Inp 07 active |  |  | M-Logic CAN Inp 07 is active.
CAN Input | CAN Inp 08 active |  |  | M-Logic CAN Inp 08 is active.
CAN Input | CAN Inp 09 active |  |  | M-Logic CAN Inp 09 is active.
CAN Input | CAN Inp 10 active |  |  | M-Logic CAN Inp 10 is active.
CAN Input | CAN Inp 11 active |  |  | M-Logic CAN Inp 11 is active.
CAN Input | CAN Inp 12 active |  |  | M-Logic CAN Inp 12 is active.
CAN Input | CAN Inp 13 active |  |  | M-Logic CAN Inp 13 is active.
CAN Input | CAN Inp 14 active |  |  | M-Logic CAN Inp 14 is active.
CAN Input | CAN Inp 15 active |  |  | M-Logic CAN Inp 15 is active.
CAN Input | CAN Inp 16 active |  |  | M-Logic CAN Inp 16 is active.
PM Compatibility | Digit X compatible |  |  | The power management compatibility X value is the same for all controllers in the plant.
PM Compatibility | Digit Y compatible |  |  | The power management compatibility Y value is the same for all controllers in the plant.
PM Compatibility | Digit Z compatible |  |  | The power management compatibility Z value is the same for all controllers in the plant.
PM Compatibility | Digit W compatible |  |  | The power management compatibility W value is the same for all controllers in the plant.
Logic | Not used |  |  | -
Logic | TRUE |  |  | This event is always TRUE.
Logic | FALSE |  |  | This event is always FALSE.
Inputs | Dig. Input 39 |  |  | Digital input 39 is active.
Inputs | Dig. Input 40 |  |  | Digital input 40 is active.
Inputs | Dig. Input 41 |  |  | Digital input 41 is active.
Inputs | Dig. Input 42 |  |  | Digital input 42 is active.
Inputs | Dig. Input 43 |  |  | Digital input 43 is active.
Inputs | Dig. Input 44 |  |  | Digital input 44 is active.
Inputs | Dig. Input 45 |  |  | Digital input 45 is active.
Inputs | Dig. Input 46 |  |  | Digital input 46 is active.
Inputs | Dig. Input 47 |  |  | Digital input 47 is active.
Inputs | Dig. Input 48 |  |  | Digital input 48 is active.
Inputs | Dig. Input 49 |  |  | Digital input 49 is active.
Inputs | Dig. Input 50 |  |  | Digital input 50 is active.
Inputs | Dig. Input 20 |  |  | Digital input 20 is active.
Inputs | Dig. Input 21 |  |  | Digital input 21 is active.
Inputs | Dig. Input 22 |  |  | Digital input 22 is active.
Inputs | Dig. Input 23 |  |  | Digital input 23 is active.
Inputs | Emergency stop |  |  | The emergency stop input is active.
CIO dig. inputs | CIO 116 no.1 In. 10 |  |  | CIO 116 no.1 In. 10 is active.
CIO dig. inputs | CIO 116 no.1 In. 11 |  |  | CIO 116 no.1 In. 11 is active.
CIO dig. inputs | CIO 116 no.1 In. 12 |  |  | CIO 116 no.1 In. 12 is active.
CIO dig. inputs | CIO 116 no.1 In. 13 |  |  | CIO 116 no.1 In. 13 is active.
CIO dig. inputs | CIO 116 no.1 In. 14 |  |  | CIO 116 no.1 In. 14 is active.
CIO dig. inputs | CIO 116 no.1 In. 15 |  |  | CIO 116 no.1 In. 15 is active.
CIO dig. inputs | CIO 116 no.1 In. 16 |  |  | CIO 116 no.1 In. 16 is active.
CIO dig. inputs | CIO 116 no.1 In. 17 |  |  | CIO 116 no.1 In. 17 is active.
CIO dig. inputs | CIO 116 no.1 In. 19 |  |  | CIO 116 no.1 In. 19 is active.
CIO dig. inputs | CIO 116 no.1 In. 20 |  |  | CIO 116 no.1 In. 20 is active.
CIO dig. inputs | CIO 116 no.1 In. 21 |  |  | CIO 116 no.1 In. 21 is active.
CIO dig. inputs | CIO 116 no.1 In. 22 |  |  | CIO 116 no.1 In. 22 is active.
CIO dig. inputs | CIO 116 no.1 In. 23 |  |  | CIO 116 no.1 In. 23 is active.
CIO dig. inputs | CIO 116 no.1 In. 24 |  |  | CIO 116 no.1 In. 24 is active.
CIO dig. inputs | CIO 116 no.1 In. 25 |  |  | CIO 116 no.1 In. 25 is active.
CIO dig. inputs | CIO 116 no.1 In. 26 |  |  | CIO 116 no.1 In. 26 is active.
CIO dig. inputs | CIO 116 no.2 In. 10 |  |  | CIO 116 no.2 In. 10 is active.
CIO dig. inputs | CIO 116 no.2 In. 11 |  |  | CIO 116 no.2 In. 11 is active.
CIO dig. inputs | CIO 116 no.2 In. 12 |  |  | CIO 116 no.2 In. 12 is active.
CIO dig. inputs | CIO 116 no.2 In. 13 |  |  | CIO 116 no.2 In. 13 is active.
CIO dig. inputs | CIO 116 no.2 In. 14 |  |  | CIO 116 no.2 In. 14 is active.
CIO dig. inputs | CIO 116 no.2 In. 15 |  |  | CIO 116 no.2 In. 15 is active.
CIO dig. inputs | CIO 116 no.2 In. 16 |  |  | CIO 116 no.2 In. 16 is active.
CIO dig. inputs | CIO 116 no.2 In. 17 |  |  | CIO 116 no.2 In. 17 is active.
CIO dig. inputs | CIO 116 no.2 In. 19 |  |  | CIO 116 no.2 In. 19 is active.
CIO dig. inputs | CIO 116 no.2 In. 20 |  |  | CIO 116 no.2 In. 20 is active.
CIO dig. inputs | CIO 116 no.2 In. 21 |  |  | CIO 116 no.2 In. 21 is active.
CIO dig. inputs | CIO 116 no.2 In. 22 |  |  | CIO 116 no.2 In. 22 is active.
CIO dig. inputs | CIO 116 no.2 In. 23 |  |  | CIO 116 no.2 In. 23 is active.
CIO dig. inputs | CIO 116 no.2 In. 24 |  |  | CIO 116 no.2 In. 24 is active.
CIO dig. inputs | CIO 116 no.2 In. 25 |  |  | CIO 116 no.2 In. 25 is active.
CIO dig. inputs | CIO 116 no.2 In. 26 |  |  | CIO 116 no.2 In. 26 is active.
CIO dig. inputs | CIO 116 no.3 In. 10 |  |  | CIO 116 no.3 In. 10 is active.
CIO dig. inputs | CIO 116 no.3 In. 11 |  |  | CIO 116 no.3 In. 11 is active.
CIO dig. inputs | CIO 116 no.3 In. 12 |  |  | CIO 116 no.3 In. 12 is active.
CIO dig. inputs | CIO 116 no.3 In. 13 |  |  | CIO 116 no.3 In. 13 is active.
CIO dig. inputs | CIO 116 no.3 In. 14 |  |  | CIO 116 no.3 In. 14 is active.
CIO dig. inputs | CIO 116 no.3 In. 15 |  |  | CIO 116 no.3 In. 15 is active.
CIO dig. inputs | CIO 116 no.3 In. 16 |  |  | CIO 116 no.3 In. 16 is active.
CIO dig. inputs | CIO 116 no.3 In. 17 |  |  | CIO 116 no.3 In. 17 is active.
CIO dig. inputs | CIO 116 no.3 In. 19 |  |  | CIO 116 no.3 In. 19 is active.
CIO dig. inputs | CIO 116 no.3 In. 20 |  |  | CIO 116 no.3 In. 20 is active.
CIO dig. inputs | CIO 116 no.3 In. 21 |  |  | CIO 116 no.3 In. 21 is active.
CIO dig. inputs | CIO 116 no.3 In. 22 |  |  | CIO 116 no.3 In. 22 is active.
CIO dig. inputs | CIO 116 no.3 In. 23 |  |  | CIO 116 no.3 In. 23 is active.
CIO dig. inputs | CIO 116 no.3 In. 24 |  |  | CIO 116 no.3 In. 24 is active.
CIO dig. inputs | CIO 116 no.3 In. 25 |  |  | CIO 116 no.3 In. 25 is active.
CIO dig. inputs | CIO 116 no.3 In. 26 |  |  | CIO 116 no.3 In. 26 is active.
CIO dig. inputs | CIO 308 no.1 In. 8 |  | 1220 | CIO 308 no.1 In. 8 is active.
CIO dig. inputs | CIO 308 no.1 In. 11 |  | 1220 | CIO 308 no.1 In. 11 is active.
CIO dig. inputs | CIO 308 no.1 In. 14 |  | 1220 | CIO 308 no.1 In. 14 is active.
CIO dig. inputs | CIO 308 no.1 In. 17 |  | 1220 | CIO 308 no.1 In. 17 is active.
CIO dig. inputs | CIO 308 no.1 In. 20 |  | 1220 | CIO 308 no.1 In. 20 is active.
CIO dig. inputs | CIO 308 no.1 In. 23 |  | 1220 | CIO 308 no.1 In. 23 is active.
CIO dig. inputs | CIO 308 no.1 In. 26 |  | 1220 | CIO 308 no.1 In. 26 is active.
CIO dig. inputs | CIO 308 no.1 In. 29 |  | 1220 | CIO 308 no.1 In. 29 is active.
CIO dig. inputs | CIO 308 no.2 In. 8 |  | 1220 | CIO 308 no.2 In. 8 is active.
CIO dig. inputs | CIO 308 no.2 In. 11 |  | 1220 | CIO 308 no.2 In. 11 is active.
CIO dig. inputs | CIO 308 no.2 In. 14 |  | 1220 | CIO 308 no.2 In. 14 is active.
CIO dig. inputs | CIO 308 no.2 In. 17 |  | 1220 | CIO 308 no.2 In. 17 is active.
CIO dig. inputs | CIO 308 no.2 In. 20 |  | 1220 | CIO 308 no.2 In. 20 is active.
CIO dig. inputs | CIO 308 no.2 In. 23 |  | 1220 | CIO 308 no.2 In. 23 is active.
CIO dig. inputs | CIO 308 no.2 In. 26 |  | 1220 | CIO 308 no.2 In. 26 is active.
CIO dig. inputs | CIO 308 no.2 In. 29 |  | 1220 | CIO 308 no.2 In. 29 is active.
CIO dig. inputs | CIO 308 no.3 In. 8 |  | 1220 | CIO 308 no.3 In. 8 is active.
CIO dig. inputs | CIO 308 no.3 In. 11 |  | 1220 | CIO 308 no.3 In. 11 is active.
CIO dig. inputs | CIO 308 no.3 In. 14 |  | 1220 | CIO 308 no.3 In. 14 is active.
CIO dig. inputs | CIO 308 no.3 In. 17 |  | 1220 | CIO 308 no.3 In. 17 is active.
CIO dig. inputs | CIO 308 no.3 In. 20 |  | 1220 | CIO 308 no.3 In. 20 is active.
CIO dig. inputs | CIO 308 no.3 In. 23 |  | 1220 | CIO 308 no.3 In. 23 is active.
CIO dig. inputs | CIO 308 no.3 In. 26 |  | 1220 | CIO 308 no.3 In. 26 is active.
CIO dig. inputs | CIO 308 no.3 In. 29 |  | 1220 | CIO 308 no.3 In. 29 is active.
Modes | Island |  |  | The controller is in island operation.
Modes | AMF |  |  | The controller is in automatic mains failure operation.
Modes | Peak shaving |  |  | The controller is in peak shaving operation.
Modes | Fixed power |  |  | The controller is in fixed power operation.
Modes | Mains power export |  |  | The controller is in mains power export operation.
Modes | Power management |  |  | The controller is in power management operation.
Modes | MANUAL Mode |  |  | The controller is in manual mode (called semi-auto before SW version 1.30).
Modes | AUTO Mode |  |  | The controller is in automatic mode.
Modes | Modeshift or AMF act. |  |  | A mains failure sequence is active.
Relays | Not used |  |  | -
Relays | Relay 5 |  |  | Relay 5 is activated.
Relays | Relay 6 |  |  | Relay 6 is activated.
Relays | Relay 9 |  |  | Relay 9 is activated.
Relays | Relay 10 |  |  | Relay 10 is activated.
Relays | Relay 11 |  |  | Relay 11 is activated.
Relays | Relay 12 |  |  | Relay 12 is activated.
Relays | Relay 13 |  |  | Relay 13 is activated.
Relays | Relay 14 |  |  | Relay 14 is activated.
Relays | Relay 15 |  |  | Relay 15 is activated.
Relays | Relay 16 |  |  | Relay 16 is activated.
Relays | Relay 17 |  |  | Relay 17 is activated.
Relays | Relay 18 |  |  | Relay 18 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 9 |  |  | CIO 208 no.1 Out. 9 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 11 |  |  | CIO 208 no.1 Out. 11 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 13 |  |  | CIO 208 no.1 Out. 13 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 15 |  |  | CIO 208 no.1 Out. 15 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 18 |  |  | CIO 208 no.1 Out. 18 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 21 |  |  | CIO 208 no.1 Out. 21 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 24 |  |  | CIO 208 no.1 Out. 24 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 27 |  |  | CIO 208 no.1 Out. 27 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 9 |  |  | CIO 208 no.2 Out. 9 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 11 |  |  | CIO 208 no.2 Out. 11 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 13 |  |  | CIO 208 no.2 Out. 13 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 15 |  |  | CIO 208 no.2 Out. 15 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 18 |  |  | CIO 208 no.2 Out. 18 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 21 |  |  | CIO 208 no.2 Out. 21 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 24 |  |  | CIO 208 no.2 Out. 24 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 27 |  |  | CIO 208 no.2 Out. 27 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 9 |  |  | CIO 208 no.3 Out. 9 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 11 |  |  | CIO 208 no.3 Out. 11 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 13 |  |  | CIO 208 no.3 Out. 13 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 15 |  |  | CIO 208 no.3 Out. 15 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 18 |  |  | CIO 208 no.3 Out. 18 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 21 |  |  | CIO 208 no.3 Out. 21 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 24 |  |  | CIO 208 no.3 Out. 24 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 27 |  |  | CIO 208 no.3 Out. 27 is activated.
CIO dig. outputs | CIO 116 no.1 conf. status output |  |  | The CIO 116 no.1 conf. status output is activated.
CIO dig. outputs | CIO 116 no.2 conf. status output |  |  | The CIO 116 no.2 conf. status output is activated.
CIO dig. outputs | CIO 116 no.3 conf. status output |  |  | The CIO 116 no.3 conf. status output is activated.
CIO dig. outputs | CIO 208 no.1 conf. status output |  |  | The CIO 208 no.1 conf. status output is activated.
CIO dig. outputs | CIO 208 no.2 conf. status output |  |  | The CIO 208 no.2 conf. status output is activated.
CIO dig. outputs | CIO 208 no.3 conf. status output |  |  | The CIO 208 no.3 conf. status output is activated.
CIO dig. outputs | CIO 308 no.1 conf. status output |  |  | The CIO 308 no.1 conf. status output is activated.
CIO dig. outputs | CIO 308 no.2 conf. status output |  |  | The CIO 308 no.2 conf. status output is activated.
CIO dig. outputs | CIO 308 no.3 conf. status output |  |  | The CIO 308 no.3 conf. status output is activated.
Virtual toggle events | Virtual toggle event 1 |  |  | Virtual toggle event 1 is active.
Virtual toggle events | Virtual toggle event 2 |  |  | Virtual toggle event 2 is active.
Virtual toggle events | Virtual toggle event 3 |  |  | Virtual toggle event 3 is active.
Virtual toggle events | Virtual toggle event 4 |  |  | Virtual toggle event 4 is active.
Virtual toggle events | Virtual toggle event 5 |  |  | Virtual toggle event 5 is active.
Virtual toggle events | Virtual toggle event 6 |  |  | Virtual toggle event 6 is active.
Virtual toggle events | Virtual toggle event 7 |  |  | Virtual toggle event 7 is active.
Virtual toggle events | Virtual toggle event 8 |  |  | Virtual toggle event 8 is active.
Virtual toggle events | Virtual toggle event 9 |  |  | Virtual toggle event 9 is active.
Virtual toggle events | Virtual toggle event 10 |  |  | Virtual toggle event 10 is active.
Virtual toggle events | Virtual toggle event 11 |  |  | Virtual toggle event 11 is active.
Virtual toggle events | Virtual toggle event 12 |  |  | Virtual toggle event 12 is active.
Virtual toggle events | Virtual toggle event 13 |  |  | Virtual toggle event 13 is active.
Virtual toggle events | Virtual toggle event 14 |  |  | Virtual toggle event 14 is active.
Virtual toggle events | Virtual toggle event 15 |  |  | Virtual toggle event 15 is active.
Virtual toggle events | Virtual toggle event 16 |  |  | Virtual toggle event 16 is active.
Virtual toggle events | Virtual toggle event 17 |  |  | Virtual toggle event 17 is active.
Virtual toggle events | Virtual toggle event 18 |  |  | Virtual toggle event 18 is active.
Virtual toggle events | Virtual toggle event 19 |  |  | Virtual toggle event 19 is active.
Virtual toggle events | Virtual toggle event 20 |  |  | Virtual toggle event 20 is active.
Virtual toggle events | Virtual toggle event 21 |  |  | Virtual toggle event 21 is active.
Virtual toggle events | Virtual toggle event 22 |  |  | Virtual toggle event 22 is active.
Virtual toggle events | Virtual toggle event 23 |  |  | Virtual toggle event 23 is active.
Virtual toggle events | Virtual toggle event 24 |  |  | Virtual toggle event 24 is active.
Virtual toggle events | Virtual toggle event 25 |  |  | Virtual toggle event 25 is active.
Virtual toggle events | Virtual toggle event 26 |  |  | Virtual toggle event 26 is active.
Virtual toggle events | Virtual toggle event 27 |  |  | Virtual toggle event 27 is active.
Virtual toggle events | Virtual toggle event 28 |  |  | Virtual toggle event 28 is active.
Virtual toggle events | Virtual toggle event 29 |  |  | Virtual toggle event 29 is active.
Virtual toggle events | Virtual toggle event 30 |  |  | Virtual toggle event 30 is active.
Virtual toggle events | Virtual toggle event 31 |  |  | Virtual toggle event 31 is active.
Virtual toggle events | Virtual toggle event 32 |  |  | Virtual toggle event 32 is active.
Virtual toggle events | Virtual toggle event 33 |  |  | Virtual toggle event 33 is active.
Virtual toggle events | Virtual toggle event 34 |  |  | Virtual toggle event 34 is active.
Virtual toggle events | Virtual toggle event 35 |  |  | Virtual toggle event 35 is active.
Virtual toggle events | Virtual toggle event 36 |  |  | Virtual toggle event 36 is active.
Virtual toggle events | Virtual toggle event 37 |  |  | Virtual toggle event 37 is active.
Virtual toggle events | Virtual toggle event 38 |  |  | Virtual toggle event 38 is active.
Virtual toggle events | Virtual toggle event 39 |  |  | Virtual toggle event 39 is active.
Virtual toggle events | Virtual toggle event 40 |  |  | Virtual toggle event 40 is active.
Virtual toggle events | Virtual toggle event 41 |  |  | Virtual toggle event 41 is active.
Virtual toggle events | Virtual toggle event 42 |  |  | Virtual toggle event 42 is active.
Virtual toggle events | Virtual toggle event 43 |  |  | Virtual toggle event 43 is active.
Virtual toggle events | Virtual toggle event 44 |  |  | Virtual toggle event 44 is active.
Virtual toggle events | Virtual toggle event 45 |  |  | Virtual toggle event 45 is active.
Virtual toggle events | Virtual toggle event 46 |  |  | Virtual toggle event 46 is active.
Virtual toggle events | Virtual toggle event 47 |  |  | Virtual toggle event 47 is active.
Virtual toggle events | Virtual toggle event 48 |  |  | Virtual toggle event 48 is active.
Virtual toggle events | Virtual toggle event 49 |  |  | Virtual toggle event 49 is active.
Virtual toggle events | Virtual toggle event 50 |  |  | Virtual toggle event 50 is active.
Virtual toggle events | Virtual toggle event 51 |  |  | Virtual toggle event 51 is active.
Virtual toggle events | Virtual toggle event 52 |  |  | Virtual toggle event 52 is active.
Virtual toggle events | Virtual toggle event 53 |  |  | Virtual toggle event 53 is active.
Virtual toggle events | Virtual toggle event 54 |  |  | Virtual toggle event 54 is active.
Virtual toggle events | Virtual toggle event 55 |  |  | Virtual toggle event 55 is active.
Virtual toggle events | Virtual toggle event 56 |  |  | Virtual toggle event 56 is active.
Virtual toggle events | Virtual toggle event 57 |  |  | Virtual toggle event 57 is active.
Virtual toggle events | Virtual toggle event 58 |  |  | Virtual toggle event 58 is active.
Virtual toggle events | Virtual toggle event 59 |  |  | Virtual toggle event 59 is active.
Virtual toggle events | Virtual toggle event 60 |  |  | Virtual toggle event 60 is active.
Virtual toggle events | Virtual toggle event 61 |  |  | Virtual toggle event 61 is active.
Virtual toggle events | Virtual toggle event 62 |  |  | Virtual toggle event 62 is active.
Virtual toggle events | Virtual toggle event 63 |  |  | Virtual toggle event 63 is active.
Virtual toggle events | Virtual toggle event 64 |  |  | Virtual toggle event 64 is active.
Virtual toggle events | Virtual toggle event 65 |  |  | Virtual toggle event 65 is active.
Virtual toggle events | Virtual toggle event 66 |  |  | Virtual toggle event 66 is active.
Virtual toggle events | Virtual toggle event 67 |  |  | Virtual toggle event 67 is active.
Virtual toggle events | Virtual toggle event 68 |  |  | Virtual toggle event 68 is active.
Virtual toggle events | Virtual toggle event 69 |  |  | Virtual toggle event 69 is active.
Virtual toggle events | Virtual toggle event 70 |  |  | Virtual toggle event 70 is active.
Virtual toggle events | Virtual toggle event 71 |  |  | Virtual toggle event 71 is active.
Virtual toggle events | Virtual toggle event 72 |  |  | Virtual toggle event 72 is active.
Virtual toggle events | Virtual toggle event 73 |  |  | Virtual toggle event 73 is active.
Virtual toggle events | Virtual toggle event 74 |  |  | Virtual toggle event 74 is active.
Virtual toggle events | Virtual toggle event 75 |  |  | Virtual toggle event 75 is active.
Virtual toggle events | Virtual toggle event 76 |  |  | Virtual toggle event 76 is active.
Virtual toggle events | Virtual toggle event 77 |  |  | Virtual toggle event 77 is active.
Virtual toggle events | Virtual toggle event 78 |  |  | Virtual toggle event 78 is active.
Virtual toggle events | Virtual toggle event 79 |  |  | Virtual toggle event 79 is active.
Virtual toggle events | Virtual toggle event 80 |  |  | Virtual toggle event 80 is active.
Virtual toggle events | Virtual toggle event 81 |  |  | Virtual toggle event 81 is active.
Virtual toggle events | Virtual toggle event 82 |  |  | Virtual toggle event 82 is active.
Virtual toggle events | Virtual toggle event 83 |  |  | Virtual toggle event 83 is active.
Virtual toggle events | Virtual toggle event 84 |  |  | Virtual toggle event 84 is active.
Virtual toggle events | Virtual toggle event 85 |  |  | Virtual toggle event 85 is active.
Virtual toggle events | Virtual toggle event 86 |  |  | Virtual toggle event 86 is active.
Virtual toggle events | Virtual toggle event 87 |  |  | Virtual toggle event 87 is active.
Virtual toggle events | Virtual toggle event 88 |  |  | Virtual toggle event 88 is active.
Virtual toggle events | Virtual toggle event 89 |  |  | Virtual toggle event 89 is active.
Virtual toggle events | Virtual toggle event 90 |  |  | Virtual toggle event 90 is active.
Virtual toggle events | Virtual toggle event 91 |  |  | Virtual toggle event 91 is active.
Virtual toggle events | Virtual toggle event 92 |  |  | Virtual toggle event 92 is active.
Virtual toggle events | Virtual toggle event 93 |  |  | Virtual toggle event 93 is active.
Virtual toggle events | Virtual toggle event 94 |  |  | Virtual toggle event 94 is active.
Virtual toggle events | Virtual toggle event 95 |  |  | Virtual toggle event 95 is active.
Virtual toggle events | Virtual toggle event 96 |  |  | Virtual toggle event 96 is active.
Virtual switch events | Virtual switch event 1 |  |  | Virtual switch event 1 is active.
Virtual switch events | Virtual switch event 2 |  |  | Virtual switch event 2 is active.
Virtual switch events | Virtual switch event 3 |  |  | Virtual switch event 3 is active.
Virtual switch events | Virtual switch event 4 |  |  | Virtual switch event 4 is active.
Virtual switch events | Virtual switch event 5 |  |  | Virtual switch event 5 is active.
Virtual switch events | Virtual switch event 6 |  |  | Virtual switch event 6 is active.
Virtual switch events | Virtual switch event 7 |  |  | Virtual switch event 7 is active.
Virtual switch events | Virtual switch event 8 |  |  | Virtual switch event 8 is active.
Virtual switch events | Virtual switch event 9 |  |  | Virtual switch event 9 is active.
Virtual switch events | Virtual switch event 10 |  |  | Virtual switch event 10 is active.
Virtual switch events | Virtual switch event 11 |  |  | Virtual switch event 11 is active.
Virtual switch events | Virtual switch event 12 |  |  | Virtual switch event 12 is active.
Virtual switch events | Virtual switch event 13 |  |  | Virtual switch event 13 is active.
Virtual switch events | Virtual switch event 14 |  |  | Virtual switch event 14 is active.
Virtual switch events | Virtual switch event 15 |  |  | Virtual switch event 15 is active.
Virtual switch events | Virtual switch event 16 |  |  | Virtual switch event 16 is active.
Virtual switch events | Virtual switch event 17 |  |  | Virtual switch event 17 is active.
Virtual switch events | Virtual switch event 18 |  |  | Virtual switch event 18 is active.
Virtual switch events | Virtual switch event 19 |  |  | Virtual switch event 19 is active.
Virtual switch events | Virtual switch event 20 |  |  | Virtual switch event 20 is active.
Virtual switch events | Virtual switch event 21 |  |  | Virtual switch event 21 is active.
Virtual switch events | Virtual switch event 22 |  |  | Virtual switch event 22 is active.
Virtual switch events | Virtual switch event 23 |  |  | Virtual switch event 23 is active.
Virtual switch events | Virtual switch event 24 |  |  | Virtual switch event 24 is active.
Virtual switch events | Virtual switch event 25 |  |  | Virtual switch event 25 is active.
Virtual switch events | Virtual switch event 26 |  |  | Virtual switch event 26 is active.
Virtual switch events | Virtual switch event 27 |  |  | Virtual switch event 27 is active.
Virtual switch events | Virtual switch event 28 |  |  | Virtual switch event 28 is active.
Virtual switch events | Virtual switch event 29 |  |  | Virtual switch event 29 is active.
Virtual switch events | Virtual switch event 30 |  |  | Virtual switch event 30 is active.
Virtual switch events | Virtual switch event 31 |  |  | Virtual switch event 31 is active.
Virtual switch events | Virtual switch event 32 |  |  | Virtual switch event 32 is active.
AOP Buttons | Button 01 |  |  | AOP button 01 is pushed.
AOP Buttons | Button 02 |  |  | AOP button 02 is pushed.
AOP Buttons | Button 03 |  |  | AOP button 03 is pushed.
AOP Buttons | Button 04 |  |  | AOP button 04 is pushed.
AOP Buttons | Button 05 |  |  | AOP button 05 is pushed.
AOP Buttons | Button 06 |  |  | AOP button 06 is pushed.
AOP Buttons | Button 07 |  |  | AOP button 07 is pushed.
AOP Buttons | Button 08 |  |  | AOP button 08 is pushed.
Fail class | Warning |  |  | At least one alarm with the fail class Warning is active.
Fail class | ESB trip |  |  | At least one alarm with the fail class ESB trip is active.
Fail class | Shutdown |  |  | At least one alarm with the fail class Shutdown is active.
Fail class | MB trip |  |  | At least one alarm with the fail class MB trip is active.
Power management - common | All GB's opened |  |  | All generator breakers are opened.
Power management - common | Any GB closed |  |  | Any generator breaker is closed.
Power management - common | Any MB closed |  |  | Any mains breaker is closed.
Power management - common | Unit has command status |  |  | The controller has command status.
Power management - DG | GEN 1 GB closed |  |  | In the power management system, the generator breaker of genset 1 is closed.
Power management - DG | GEN 2 GB closed |  |  | In the power management system, the generator breaker of genset 2 is closed.
Power management - DG | GEN 3 GB closed |  |  | In the power management system, the generator breaker of genset 3 is closed.
Power management - DG | GEN 4 GB closed |  |  | In the power management system, the generator breaker of genset 4 is closed.
Power management - DG | GEN 5 GB closed |  |  | In the power management system, the generator breaker of genset 5 is closed.
Power management - DG | GEN 6 GB closed |  |  | In the power management system, the generator breaker of genset 6 is closed.
Power management - DG | GEN 7 GB closed |  |  | In the power management system, the generator breaker of genset 7 is closed.
Power management - DG | GEN 8 GB closed |  |  | In the power management system, the generator breaker of genset 8 is closed.
Power management - DG | GEN 9 GB closed |  |  | In the power management system, the generator breaker of genset 9 is closed.
Power management - DG | GEN 10 GB closed |  |  | In the power management system, the generator breaker of genset 10 is closed.
Power management - DG | GEN 11 GB closed |  |  | In the power management system, the generator breaker of genset 11 is closed.
Power management - DG | GEN 12 GB closed |  |  | In the power management system, the generator breaker of genset 12 is closed.
Power management - DG | GEN 13 GB closed |  |  | In the power management system, the generator breaker of genset 13 is closed.
Power management - DG | GEN 14 GB closed |  |  | In the power management system, the generator breaker of genset 14 is closed.
Power management - DG | GEN 15 GB closed |  |  | In the power management system, the generator breaker of genset 15 is closed.
Power management - DG | GEN 16 GB closed |  |  | In the power management system, the generator breaker of genset 16 is closed.
Power management - DG | GEN 17 GB closed |  |  | In the power management system, the generator breaker of genset 17 is closed.
Power management - DG | GEN 18 GB closed |  |  | In the power management system, the generator breaker of genset 18 is closed.
Power management - DG | GEN 19 GB closed |  |  | In the power management system, the generator breaker of genset 19 is closed.
Power management - DG | GEN 20 GB closed |  |  | In the power management system, the generator breaker of genset 20 is closed.
Power management - DG | GEN 21 GB closed |  |  | In the power management system, the generator breaker of genset 21 is closed.
Power management - DG | GEN 22 GB closed |  |  | In the power management system, the generator breaker of genset 22 is closed.
Power management - DG | GEN 23 GB closed |  |  | In the power management system, the generator breaker of genset 23 is closed.
Power management - DG | GEN 24 GB closed |  |  | In the power management system, the generator breaker of genset 24 is closed.
Power management - DG | GEN 25 GB closed |  |  | In the power management system, the generator breaker of genset 25 is closed.
Power management - DG | GEN 26 GB closed |  |  | In the power management system, the generator breaker of genset 26 is closed.
Power management - DG | GEN 27 GB closed |  |  | In the power management system, the generator breaker of genset 27 is closed.
Power management - DG | GEN 28 GB closed |  |  | In the power management system, the generator breaker of genset 28 is closed.
Power management - DG | GEN 29 GB closed |  |  | In the power management system, the generator breaker of genset 29 is closed.
Power management - DG | GEN 30 GB closed |  |  | In the power management system, the generator breaker of genset 30 is closed.
Power management - DG | GEN 31 GB closed |  |  | In the power management system, the generator breaker of genset 31 is closed.
Power management - DG | GEN 32 GB closed |  |  | In the power management system, the generator breaker of genset 32 is closed.
Power management - DG | GEN 1 GB opened |  |  | In the power management system, the generator breaker of genset 1 is opened.
Power management - DG | GEN 2 GB opened |  |  | In the power management system, the generator breaker of genset 2 is opened.
Power management - DG | GEN 3 GB opened |  |  | In the power management system, the generator breaker of genset 3 is opened.
Power management - DG | GEN 4 GB opened |  |  | In the power management system, the generator breaker of genset 4 is opened.
Power management - DG | GEN 5 GB opened |  |  | In the power management system, the generator breaker of genset 5 is opened.
Power management - DG | GEN 6 GB opened |  |  | In the power management system, the generator breaker of genset 6 is opened.
Power management - DG | GEN 7 GB opened |  |  | In the power management system, the generator breaker of genset 7 is opened.
Power management - DG | GEN 8 GB opened |  |  | In the power management system, the generator breaker of genset 8 is opened.
Power management - DG | GEN 9 GB opened |  |  | In the power management system, the generator breaker of genset 9 is opened.
Power management - DG | GEN 10 GB opened |  |  | In the power management system, the generator breaker of genset 10 is opened.
Power management - DG | GEN 11 GB opened |  |  | In the power management system, the generator breaker of genset 11 is opened.
Power management - DG | GEN 12 GB opened |  |  | In the power management system, the generator breaker of genset 12 is opened.
Power management - DG | GEN 13 GB opened |  |  | In the power management system, the generator breaker of genset 13 is opened.
Power management - DG | GEN 14 GB opened |  |  | In the power management system, the generator breaker of genset 14 is opened.
Power management - DG | GEN 15 GB opened |  |  | In the power management system, the generator breaker of genset 15 is opened.
Power management - DG | GEN 16 GB opened |  |  | In the power management system, the generator breaker of genset 16 is opened.
Power management - DG | GEN 17 GB opened |  |  | In the power management system, the generator breaker of genset 17 is opened.
Power management - DG | GEN 18 GB opened |  |  | In the power management system, the generator breaker of genset 18 is opened.
Power management - DG | GEN 19 GB opened |  |  | In the power management system, the generator breaker of genset 19 is opened.
Power management - DG | GEN 20 GB opened |  |  | In the power management system, the generator breaker of genset 20 is opened.
Power management - DG | GEN 21 GB opened |  |  | In the power management system, the generator breaker of genset 21 is opened.
Power management - DG | GEN 22 GB opened |  |  | In the power management system, the generator breaker of genset 22 is opened.
Power management - DG | GEN 23 GB opened |  |  | In the power management system, the generator breaker of genset 23 is opened.
Power management - DG | GEN 24 GB opened |  |  | In the power management system, the generator breaker of genset 24 is opened.
Power management - DG | GEN 25 GB opened |  |  | In the power management system, the generator breaker of genset 25 is opened.
Power management - DG | GEN 26 GB opened |  |  | In the power management system, the generator breaker of genset 26 is opened.
Power management - DG | GEN 27 GB opened |  |  | In the power management system, the generator breaker of genset 27 is opened.
Power management - DG | GEN 28 GB opened |  |  | In the power management system, the generator breaker of genset 28 is opened.
Power management - DG | GEN 29 GB opened |  |  | In the power management system, the generator breaker of genset 29 is opened.
Power management - DG | GEN 30 GB opened |  |  | In the power management system, the generator breaker of genset 30 is opened.
Power management - DG | GEN 31 GB opened |  |  | In the power management system, the generator breaker of genset 31 is opened.
Power management - DG | GEN 32 GB opened |  |  | In the power management system, the generator breaker of genset 32 is opened.
Power management - DG | GEN 1 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 1 are okay.
Power management - DG | GEN 2 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 2 are okay.
Power management - DG | GEN 3 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 3 are okay.
Power management - DG | GEN 4 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 4 are okay.
Power management - DG | GEN 5 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 5 are okay.
Power management - DG | GEN 6 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 6 are okay.
Power management - DG | GEN 7 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 7 are okay.
Power management - DG | GEN 8 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 8 are okay.
Power management - DG | GEN 9 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 9 are okay.
Power management - DG | GEN 10 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 10 are okay.
Power management - DG | GEN 11 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 11 are okay.
Power management - DG | GEN 12 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 12 are okay.
Power management - DG | GEN 13 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 13 are okay.
Power management - DG | GEN 14 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 14 are okay.
Power management - DG | GEN 15 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 15 are okay.
Power management - DG | GEN 16 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 16 are okay.
Power management - DG | GEN 17 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 17 are okay.
Power management - DG | GEN 18 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 18 are okay.
Power management - DG | GEN 19 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 19 are okay.
Power management - DG | GEN 20 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 20 are okay.
Power management - DG | GEN 21 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 21 are okay.
Power management - DG | GEN 22 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 22 are okay.
Power management - DG | GEN 23 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 23 are okay.
Power management - DG | GEN 24 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 24 are okay.
Power management - DG | GEN 25 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 25 are okay.
Power management - DG | GEN 26 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 26 are okay.
Power management - DG | GEN 27 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 27 are okay.
Power management - DG | GEN 28 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 28 are okay.
Power management - DG | GEN 29 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 29 are okay.
Power management - DG | GEN 30 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 30 are okay.
Power management - DG | GEN 31 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 31 are okay.
Power management - DG | GEN 32 volt/freq okay |  |  | In the power management system, the voltage and frequency of genset 32 are okay.
Power management - DG | GEN 1 running |  |  | In the power management system, genset 1 is running.
Power management - DG | GEN 2 running |  |  | In the power management system, genset 2 is running.
Power management - DG | GEN 3 running |  |  | In the power management system, genset 3 is running.
Power management - DG | GEN 4 running |  |  | In the power management system, genset 4 is running.
Power management - DG | GEN 5 running |  |  | In the power management system, genset 5 is running.
Power management - DG | GEN 6 running |  |  | In the power management system, genset 6 is running.
Power management - DG | GEN 7 running |  |  | In the power management system, genset 7 is running.
Power management - DG | GEN 8 running |  |  | In the power management system, genset 8 is running.
Power management - DG | GEN 9 running |  |  | In the power management system, genset 9 is running.
Power management - DG | GEN 10 running |  |  | In the power management system, genset 10 is running.
Power management - DG | GEN 11 running |  |  | In the power management system, genset 11 is running.
Power management - DG | GEN 12 running |  |  | In the power management system, genset 12 is running.
Power management - DG | GEN 13 running |  |  | In the power management system, genset 13 is running.
Power management - DG | GEN 14 running |  |  | In the power management system, genset 14 is running.
Power management - DG | GEN 15 running |  |  | In the power management system, genset 15 is running.
Power management - DG | GEN 16 running |  |  | In the power management system, genset 16 is running.
Power management - DG | GEN 17 running |  |  | In the power management system, genset 17 is running.
Power management - DG | GEN 18 running |  |  | In the power management system, genset 18 is running.
Power management - DG | GEN 19 running |  |  | In the power management system, genset 19 is running.
Power management - DG | GEN 20 running |  |  | In the power management system, genset 20 is running.
Power management - DG | GEN 21 running |  |  | In the power management system, genset 21 is running.
Power management - DG | GEN 22 running |  |  | In the power management system, genset 22 is running.
Power management - DG | GEN 23 running |  |  | In the power management system, genset 23 is running.
Power management - DG | GEN 24 running |  |  | In the power management system, genset 24 is running.
Power management - DG | GEN 25 running |  |  | In the power management system, genset 25 is running.
Power management - DG | GEN 26 running |  |  | In the power management system, genset 26 is running.
Power management - DG | GEN 27 running |  |  | In the power management system, genset 27 is running.
Power management - DG | GEN 28 running |  |  | In the power management system, genset 28 is running.
Power management - DG | GEN 29 running |  |  | In the power management system, genset 29 is running.
Power management - DG | GEN 30 running |  |  | In the power management system, genset 30 is running.
Power management - DG | GEN 31 running |  |  | In the power management system, genset 31 is running.
Power management - DG | GEN 32 running |  |  | In the power management system, genset 32 is running.
Power management - DG | GEN 1 ready to auto start |  |  | In the power management system, genset 1 is ready to auto start.
Power management - DG | GEN 2 ready to auto start |  |  | In the power management system, genset 2 is ready to auto start.
Power management - DG | GEN 3 ready to auto start |  |  | In the power management system, genset 3 is ready to auto start.
Power management - DG | GEN 4 ready to auto start |  |  | In the power management system, genset 4 is ready to auto start.
Power management - DG | GEN 5 ready to auto start |  |  | In the power management system, genset 5 is ready to auto start.
Power management - DG | GEN 6 ready to auto start |  |  | In the power management system, genset 6 is ready to auto start.
Power management - DG | GEN 7 ready to auto start |  |  | In the power management system, genset 7 is ready to auto start.
Power management - DG | GEN 8 ready to auto start |  |  | In the power management system, genset 8 is ready to auto start.
Power management - DG | GEN 9 ready to auto start |  |  | In the power management system, genset 9 is ready to auto start.
Power management - DG | GEN 10 ready to auto start |  |  | In the power management system, genset 10 is ready to auto start.
Power management - DG | GEN 11 ready to auto start |  |  | In the power management system, genset 11 is ready to auto start.
Power management - DG | GEN 12 ready to auto start |  |  | In the power management system, genset 12 is ready to auto start.
Power management - DG | GEN 13 ready to auto start |  |  | In the power management system, genset 13 is ready to auto start.
Power management - DG | GEN 14 ready to auto start |  |  | In the power management system, genset 14 is ready to auto start.
Power management - DG | GEN 15 ready to auto start |  |  | In the power management system, genset 15 is ready to auto start.
Power management - DG | GEN 16 ready to auto start |  |  | In the power management system, genset 16 is ready to auto start.
Power management - DG | GEN 17 ready to auto start |  |  | In the power management system, genset 17 is ready to auto start.
Power management - DG | GEN 18 ready to auto start |  |  | In the power management system, genset 18 is ready to auto start.
Power management - DG | GEN 19 ready to auto start |  |  | In the power management system, genset 19 is ready to auto start.
Power management - DG | GEN 20 ready to auto start |  |  | In the power management system, genset 20 is ready to auto start.
Power management - DG | GEN 21 ready to auto start |  |  | In the power management system, genset 21 is ready to auto start.
Power management - DG | GEN 22 ready to auto start |  |  | In the power management system, genset 22 is ready to auto start.
Power management - DG | GEN 23 ready to auto start |  |  | In the power management system, genset 23 is ready to auto start.
Power management - DG | GEN 24 ready to auto start |  |  | In the power management system, genset 24 is ready to auto start.
Power management - DG | GEN 25 ready to auto start |  |  | In the power management system, genset 25 is ready to auto start.
Power management - DG | GEN 26 ready to auto start |  |  | In the power management system, genset 26 is ready to auto start.
Power management - DG | GEN 27 ready to auto start |  |  | In the power management system, genset 27 is ready to auto start.
Power management - DG | GEN 28 ready to auto start |  |  | In the power management system, genset 28 is ready to auto start.
Power management - DG | GEN 29 ready to auto start |  |  | In the power management system, genset 29 is ready to auto start.
Power management - DG | GEN 30 ready to auto start |  |  | In the power management system, genset 30 is ready to auto start.
Power management - DG | GEN 31 ready to auto start |  |  | In the power management system, genset 31 is ready to auto start.
Power management - DG | GEN 32 ready to auto start |  |  | In the power management system, genset 32 is ready to auto start.
Power management - DG | GEN 1 GB Synchronising |  |  | In the power management system, the generator breaker of genset 1 is synchronising.
Power management - DG | GEN 2 GB Synchronising |  |  | In the power management system, the generator breaker of genset 2 is synchronising.
Power management - DG | GEN 3 GB Synchronising |  |  | In the power management system, the generator breaker of genset 3 is synchronising.
Power management - DG | GEN 4 GB Synchronising |  |  | In the power management system, the generator breaker of genset 4 is synchronising.
Power management - DG | GEN 5 GB Synchronising |  |  | In the power management system, the generator breaker of genset 5 is synchronising.
Power management - DG | GEN 6 GB Synchronising |  |  | In the power management system, the generator breaker of genset 6 is synchronising.
Power management - DG | GEN 7 GB Synchronising |  |  | In the power management system, the generator breaker of genset 7 is synchronising.
Power management - DG | GEN 8 GB Synchronising |  |  | In the power management system, the generator breaker of genset 8 is synchronising.
Power management - DG | GEN 9 GB Synchronising |  |  | In the power management system, the generator breaker of genset 9 is synchronising.
Power management - DG | GEN 10 GB Synchronising |  |  | In the power management system, the generator breaker of genset 10 is synchronising.
Power management - DG | GEN 11 GB Synchronising |  |  | In the power management system, the generator breaker of genset 11 is synchronising.
Power management - DG | GEN 12 GB Synchronising |  |  | In the power management system, the generator breaker of genset 12 is synchronising.
Power management - DG | GEN 13 GB Synchronising |  |  | In the power management system, the generator breaker of genset 13 is synchronising.
Power management - DG | GEN 14 GB Synchronising |  |  | In the power management system, the generator breaker of genset 14 is synchronising.
Power management - DG | GEN 15 GB Synchronising |  |  | In the power management system, the generator breaker of genset 15 is synchronising.
Power management - DG | GEN 16 GB Synchronising |  |  | In the power management system, the generator breaker of genset 16 is synchronising.
Power management - DG | GEN 17 GB Synchronising |  |  | In the power management system, the generator breaker of genset 17 is synchronising.
Power management - DG | GEN 18 GB Synchronising |  |  | In the power management system, the generator breaker of genset 18 is synchronising.
Power management - DG | GEN 19 GB Synchronising |  |  | In the power management system, the generator breaker of genset 19 is synchronising.
Power management - DG | GEN 20 GB Synchronising |  |  | In the power management system, the generator breaker of genset 20 is synchronising.
Power management - DG | GEN 21 GB Synchronising |  |  | In the power management system, the generator breaker of genset 21 is synchronising.
Power management - DG | GEN 22 GB Synchronising |  |  | In the power management system, the generator breaker of genset 22 is synchronising.
Power management - DG | GEN 23 GB Synchronising |  |  | In the power management system, the generator breaker of genset 23 is synchronising.
Power management - DG | GEN 24 GB Synchronising |  |  | In the power management system, the generator breaker of genset 24 is synchronising.
Power management - DG | GEN 25 GB Synchronising |  |  | In the power management system, the generator breaker of genset 25 is synchronising.
Power management - DG | GEN 26 GB Synchronising |  |  | In the power management system, the generator breaker of genset 26 is synchronising.
Power management - DG | GEN 27 GB Synchronising |  |  | In the power management system, the generator breaker of genset 27 is synchronising.
Power management - DG | GEN 28 GB Synchronising |  |  | In the power management system, the generator breaker of genset 28 is synchronising.
Power management - DG | GEN 29 GB Synchronising |  |  | In the power management system, the generator breaker of genset 29 is synchronising.
Power management - DG | GEN 30 GB Synchronising |  |  | In the power management system, the generator breaker of genset 30 is synchronising.
Power management - DG | GEN 31 GB Synchronising |  |  | In the power management system, the generator breaker of genset 31 is synchronising.
Power management - DG | GEN 32 GB Synchronising |  |  | In the power management system, the generator breaker of genset 32 is synchronising.
Power management - ID alarms | PM ID 1 has any alarm present |  |  | The controller with ID 1 has at least one active alarm.
Power management - ID alarms | PM ID 2 has any alarm present |  |  | The controller with ID 2 has at least one active alarm.
Power management - ID alarms | PM ID 3 has any alarm present |  |  | The controller with ID 3 has at least one active alarm.
Power management - ID alarms | PM ID 4 has any alarm present |  |  | The controller with ID 4 has at least one active alarm.
Power management - ID alarms | PM ID 5 has any alarm present |  |  | The controller with ID 5 has at least one active alarm.
Power management - ID alarms | PM ID 6 has any alarm present |  |  | The controller with ID 6 has at least one active alarm.
Power management - ID alarms | PM ID 7 has any alarm present |  |  | The controller with ID 7 has at least one active alarm.
Power management - ID alarms | PM ID 8 has any alarm present |  |  | The controller with ID 8 has at least one active alarm.
Power management - ID alarms | PM ID 9 has any alarm present |  |  | The controller with ID 9 has at least one active alarm.
Power management - ID alarms | PM ID 10 has any alarm present |  |  | The controller with ID 10 has at least one active alarm.
Power management - ID alarms | PM ID 11 has any alarm present |  |  | The controller with ID 11 has at least one active alarm.
Power management - ID alarms | PM ID 12 has any alarm present |  |  | The controller with ID 12 has at least one active alarm.
Power management - ID alarms | PM ID 13 has any alarm present |  |  | The controller with ID 13 has at least one active alarm.
Power management - ID alarms | PM ID 14 has any alarm present |  |  | The controller with ID 14 has at least one active alarm.
Power management - ID alarms | PM ID 15 has any alarm present |  |  | The controller with ID 15 has at least one active alarm.
Power management - ID alarms | PM ID 16 has any alarm present |  |  | The controller with ID 16 has at least one active alarm.
Power management - ID alarms | PM ID 17 has any alarm present |  |  | The controller with ID 17 has at least one active alarm.
Power management - ID alarms | PM ID 18 has any alarm present |  |  | The controller with ID 18 has at least one active alarm.
Power management - ID alarms | PM ID 19 has any alarm present |  |  | The controller with ID 19 has at least one active alarm.
Power management - ID alarms | PM ID 20 has any alarm present |  |  | The controller with ID 20 has at least one active alarm.
Power management - ID alarms | PM ID 21 has any alarm present |  |  | The controller with ID 21 has at least one active alarm.
Power management - ID alarms | PM ID 22 has any alarm present |  |  | The controller with ID 22 has at least one active alarm.
Power management - ID alarms | PM ID 23 has any alarm present |  |  | The controller with ID 23 has at least one active alarm.
Power management - ID alarms | PM ID 24 has any alarm present |  |  | The controller with ID 24 has at least one active alarm.
Power management - ID alarms | PM ID 25 has any alarm present |  |  | The controller with ID 25 has at least one active alarm.
Power management - ID alarms | PM ID 26 has any alarm present |  |  | The controller with ID 26 has at least one active alarm.
Power management - ID alarms | PM ID 27 has any alarm present |  |  | The controller with ID 27 has at least one active alarm.
Power management - ID alarms | PM ID 28 has any alarm present |  |  | The controller with ID 28 has at least one active alarm.
Power management - ID alarms | PM ID 29 has any alarm present |  |  | The controller with ID 29 has at least one active alarm.
Power management - ID alarms | PM ID 30 has any alarm present |  |  | The controller with ID 30 has at least one active alarm.
Power management - ID alarms | PM ID 31 has any alarm present |  |  | The controller with ID 31 has at least one active alarm.
Power management - ID alarms | PM ID 32 has any alarm present |  |  | The controller with ID 32 has at least one active alarm.
Power management - MAINS | Mains 1 MB closed |  |  | In the power management system, the mains breaker of mains 1 is closed.
Power management - MAINS | Mains 2 MB closed |  |  | In the power management system, the mains breaker of mains 2 is closed.
Power management - MAINS | Mains 3 MB closed |  |  | In the power management system, the mains breaker of mains 3 is closed.
Power management - MAINS | Mains 4 MB closed |  |  | In the power management system, the mains breaker of mains 4 is closed.
Power management - MAINS | Mains 5 MB closed |  |  | In the power management system, the mains breaker of mains 5 is closed.
Power management - MAINS | Mains 6 MB closed |  |  | In the power management system, the mains breaker of mains 6 is closed.
Power management - MAINS | Mains 7 MB closed |  |  | In the power management system, the mains breaker of mains 7 is closed.
Power management - MAINS | Mains 8 MB closed |  |  | In the power management system, the mains breaker of mains 8 is closed.
Power management - MAINS | Mains 9 MB closed |  |  | In the power management system, the mains breaker of mains 9 is closed.
Power management - MAINS | Mains 10 MB closed |  |  | In the power management system, the mains breaker of mains 10 is closed.
Power management - MAINS | Mains 11 MB closed |  |  | In the power management system, the mains breaker of mains 11 is closed.
Power management - MAINS | Mains 12 MB closed |  |  | In the power management system, the mains breaker of mains 12 is closed.
Power management - MAINS | Mains 13 MB closed |  |  | In the power management system, the mains breaker of mains 13 is closed.
Power management - MAINS | Mains 14 MB closed |  |  | In the power management system, the mains breaker of mains 14 is closed.
Power management - MAINS | Mains 15 MB closed |  |  | In the power management system, the mains breaker of mains 15 is closed.
Power management - MAINS | Mains 16 MB closed |  |  | In the power management system, the mains breaker of mains 16 is closed.
Power management - MAINS | Mains 17 MB closed |  |  | In the power management system, the mains breaker of mains 17 is closed.
Power management - MAINS | Mains 18 MB closed |  |  | In the power management system, the mains breaker of mains 18 is closed.
Power management - MAINS | Mains 19 MB closed |  |  | In the power management system, the mains breaker of mains 19 is closed.
Power management - MAINS | Mains 20 MB closed |  |  | In the power management system, the mains breaker of mains 20 is closed.
Power management - MAINS | Mains 21 MB closed |  |  | In the power management system, the mains breaker of mains 21 is closed.
Power management - MAINS | Mains 22 MB closed |  |  | In the power management system, the mains breaker of mains 22 is closed.
Power management - MAINS | Mains 23 MB closed |  |  | In the power management system, the mains breaker of mains 23 is closed.
Power management - MAINS | Mains 24 MB closed |  |  | In the power management system, the mains breaker of mains 24 is closed.
Power management - MAINS | Mains 25 MB closed |  |  | In the power management system, the mains breaker of mains 25 is closed.
Power management - MAINS | Mains 26 MB closed |  |  | In the power management system, the mains breaker of mains 26 is closed.
Power management - MAINS | Mains 27 MB closed |  |  | In the power management system, the mains breaker of mains 27 is closed.
Power management - MAINS | Mains 28 MB closed |  |  | In the power management system, the mains breaker of mains 28 is closed.
Power management - MAINS | Mains 29 MB closed |  |  | In the power management system, the mains breaker of mains 29 is closed.
Power management - MAINS | Mains 30 MB closed |  |  | In the power management system, the mains breaker of mains 30 is closed.
Power management - MAINS | Mains 31 MB closed |  |  | In the power management system, the mains breaker of mains 31 is closed.
Power management - MAINS | Mains 32 MB closed |  |  | In the power management system, the mains breaker of mains 32 is closed.
Power management - MAINS | Mains 1 MB opened |  |  | In the power management system, the mains breaker of mains 1 is open.
Power management - MAINS | Mains 2 MB opened |  |  | In the power management system, the mains breaker of mains 2 is open.
Power management - MAINS | Mains 3 MB opened |  |  | In the power management system, the mains breaker of mains 3 is open.
Power management - MAINS | Mains 4 MB opened |  |  | In the power management system, the mains breaker of mains 4 is open.
Power management - MAINS | Mains 5 MB opened |  |  | In the power management system, the mains breaker of mains 5 is open.
Power management - MAINS | Mains 6 MB opened |  |  | In the power management system, the mains breaker of mains 6 is open.
Power management - MAINS | Mains 7 MB opened |  |  | In the power management system, the mains breaker of mains 7 is open.
Power management - MAINS | Mains 8 MB opened |  |  | In the power management system, the mains breaker of mains 8 is open.
Power management - MAINS | Mains 9 MB opened |  |  | In the power management system, the mains breaker of mains 9 is open.
Power management - MAINS | Mains 10 MB opened |  |  | In the power management system, the mains breaker of mains 10 is open.
Power management - MAINS | Mains 11 MB opened |  |  | In the power management system, the mains breaker of mains 11 is open.
Power management - MAINS | Mains 12 MB opened |  |  | In the power management system, the mains breaker of mains 12 is open.
Power management - MAINS | Mains 13 MB opened |  |  | In the power management system, the mains breaker of mains 13 is open.
Power management - MAINS | Mains 14 MB opened |  |  | In the power management system, the mains breaker of mains 14 is open.
Power management - MAINS | Mains 15 MB opened |  |  | In the power management system, the mains breaker of mains 15 is open.
Power management - MAINS | Mains 16 MB opened |  |  | In the power management system, the mains breaker of mains 16 is open.
Power management - MAINS | Mains 17 MB opened |  |  | In the power management system, the mains breaker of mains 17 is open.
Power management - MAINS | Mains 18 MB opened |  |  | In the power management system, the mains breaker of mains 18 is open.
Power management - MAINS | Mains 19 MB opened |  |  | In the power management system, the mains breaker of mains 19 is open.
Power management - MAINS | Mains 20 MB opened |  |  | In the power management system, the mains breaker of mains 20 is open.
Power management - MAINS | Mains 21 MB opened |  |  | In the power management system, the mains breaker of mains 21 is open.
Power management - MAINS | Mains 22 MB opened |  |  | In the power management system, the mains breaker of mains 22 is open.
Power management - MAINS | Mains 23 MB opened |  |  | In the power management system, the mains breaker of mains 23 is open.
Power management - MAINS | Mains 24 MB opened |  |  | In the power management system, the mains breaker of mains 24 is open.
Power management - MAINS | Mains 25 MB opened |  |  | In the power management system, the mains breaker of mains 25 is open.
Power management - MAINS | Mains 26 MB opened |  |  | In the power management system, the mains breaker of mains 26 is open.
Power management - MAINS | Mains 27 MB opened |  |  | In the power management system, the mains breaker of mains 27 is open.
Power management - MAINS | Mains 28 MB opened |  |  | In the power management system, the mains breaker of mains 28 is open.
Power management - MAINS | Mains 29 MB opened |  |  | In the power management system, the mains breaker of mains 29 is open.
Power management - MAINS | Mains 30 MB opened |  |  | In the power management system, the mains breaker of mains 30 is open.
Power management - MAINS | Mains 31 MB opened |  |  | In the power management system, the mains breaker of mains 31 is open.
Power management - MAINS | Mains 32 MB opened |  |  | In the power management system, the mains breaker of mains 32 is open.
Power management - MAINS | Mains 1 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 1.
Power management - MAINS | Mains 2 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 2.
Power management - MAINS | Mains 3 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 3.
Power management - MAINS | Mains 4 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 4.
Power management - MAINS | Mains 5 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 5.
Power management - MAINS | Mains 6 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 6.
Power management - MAINS | Mains 7 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 7.
Power management - MAINS | Mains 8 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 8.
Power management - MAINS | Mains 9 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 9.
Power management - MAINS | Mains 10 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 10.
Power management - MAINS | Mains 11 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 11.
Power management - MAINS | Mains 12 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 12.
Power management - MAINS | Mains 13 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 13.
Power management - MAINS | Mains 14 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 14.
Power management - MAINS | Mains 15 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 15.
Power management - MAINS | Mains 16 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 16.
Power management - MAINS | Mains 17 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 17.
Power management - MAINS | Mains 18 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 18.
Power management - MAINS | Mains 19 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 19.
Power management - MAINS | Mains 20 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 20.
Power management - MAINS | Mains 21 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 21.
Power management - MAINS | Mains 22 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 22.
Power management - MAINS | Mains 23 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 23.
Power management - MAINS | Mains 24 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 24.
Power management - MAINS | Mains 25 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 25.
Power management - MAINS | Mains 26 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 26.
Power management - MAINS | Mains 27 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 27.
Power management - MAINS | Mains 28 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 28.
Power management - MAINS | Mains 29 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 29.
Power management - MAINS | Mains 30 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 30.
Power management - MAINS | Mains 31 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 31.
Power management - MAINS | Mains 32 MB Synchronising |  |  | The power management system is synchronising the mains breaker of mains 32.
Power management - MAINS | Mains 1 TB closed |  |  | In the power management system, the tie breaker of mains 1 is closed.
Power management - MAINS | Mains 2 TB closed |  |  | In the power management system, the tie breaker of mains 2 is closed.
Power management - MAINS | Mains 3 TB closed |  |  | In the power management system, the tie breaker of mains 3 is closed.
Power management - MAINS | Mains 4 TB closed |  |  | In the power management system, the tie breaker of mains 4 is closed.
Power management - MAINS | Mains 5 TB closed |  |  | In the power management system, the tie breaker of mains 5 is closed.
Power management - MAINS | Mains 6 TB closed |  |  | In the power management system, the tie breaker of mains 6 is closed.
Power management - MAINS | Mains 7 TB closed |  |  | In the power management system, the tie breaker of mains 7 is closed.
Power management - MAINS | Mains 8 TB closed |  |  | In the power management system, the tie breaker of mains 8 is closed.
Power management - MAINS | Mains 9 TB closed |  |  | In the power management system, the tie breaker of mains 9 is closed.
Power management - MAINS | Mains 10 TB closed |  |  | In the power management system, the tie breaker of mains 10 is closed.
Power management - MAINS | Mains 11 TB closed |  |  | In the power management system, the tie breaker of mains 11 is closed.
Power management - MAINS | Mains 12 TB closed |  |  | In the power management system, the tie breaker of mains 12 is closed.
Power management - MAINS | Mains 13 TB closed |  |  | In the power management system, the tie breaker of mains 13 is closed.
Power management - MAINS | Mains 14 TB closed |  |  | In the power management system, the tie breaker of mains 14 is closed.
Power management - MAINS | Mains 15 TB closed |  |  | In the power management system, the tie breaker of mains 15 is closed.
Power management - MAINS | Mains 16 TB closed |  |  | In the power management system, the tie breaker of mains 16 is closed.
Power management - MAINS | Mains 17 TB closed |  |  | In the power management system, the tie breaker of mains 17 is closed.
Power management - MAINS | Mains 18 TB closed |  |  | In the power management system, the tie breaker of mains 18 is closed.
Power management - MAINS | Mains 19 TB closed |  |  | In the power management system, the tie breaker of mains 19 is closed.
Power management - MAINS | Mains 20 TB closed |  |  | In the power management system, the tie breaker of mains 20 is closed.
Power management - MAINS | Mains 21 TB closed |  |  | In the power management system, the tie breaker of mains 21 is closed.
Power management - MAINS | Mains 22 TB closed |  |  | In the power management system, the tie breaker of mains 22 is closed.
Power management - MAINS | Mains 23 TB closed |  |  | In the power management system, the tie breaker of mains 23 is closed.
Power management - MAINS | Mains 24 TB closed |  |  | In the power management system, the tie breaker of mains 24 is closed.
Power management - MAINS | Mains 25 TB closed |  |  | In the power management system, the tie breaker of mains 25 is closed.
Power management - MAINS | Mains 26 TB closed |  |  | In the power management system, the tie breaker of mains 26 is closed.
Power management - MAINS | Mains 27 TB closed |  |  | In the power management system, the tie breaker of mains 27 is closed.
Power management - MAINS | Mains 28 TB closed |  |  | In the power management system, the tie breaker of mains 28 is closed.
Power management - MAINS | Mains 29 TB closed |  |  | In the power management system, the tie breaker of mains 29 is closed.
Power management - MAINS | Mains 30 TB closed |  |  | In the power management system, the tie breaker of mains 30 is closed.
Power management - MAINS | Mains 31 TB closed |  |  | In the power management system, the tie breaker of mains 31 is closed.
Power management - MAINS | Mains 32 TB closed |  |  | In the power management system, the tie breaker of mains 32 is closed.
Power management - MAINS | Mains 1 TB opened |  |  | In the power management system, the tie breaker of mains 1 is open.
Power management - MAINS | Mains 2 TB opened |  |  | In the power management system, the tie breaker of mains 2 is open.
Power management - MAINS | Mains 3 TB opened |  |  | In the power management system, the tie breaker of mains 3 is open.
Power management - MAINS | Mains 4 TB opened |  |  | In the power management system, the tie breaker of mains 4 is open.
Power management - MAINS | Mains 5 TB opened |  |  | In the power management system, the tie breaker of mains 5 is open.
Power management - MAINS | Mains 6 TB opened |  |  | In the power management system, the tie breaker of mains 6 is open.
Power management - MAINS | Mains 7 TB opened |  |  | In the power management system, the tie breaker of mains 7 is open.
Power management - MAINS | Mains 8 TB opened |  |  | In the power management system, the tie breaker of mains 8 is open.
Power management - MAINS | Mains 9 TB opened |  |  | In the power management system, the tie breaker of mains 9 is open.
Power management - MAINS | Mains 10 TB opened |  |  | In the power management system, the tie breaker of mains 10 is open.
Power management - MAINS | Mains 11 TB opened |  |  | In the power management system, the tie breaker of mains 11 is open.
Power management - MAINS | Mains 12 TB opened |  |  | In the power management system, the tie breaker of mains 12 is open.
Power management - MAINS | Mains 13 TB opened |  |  | In the power management system, the tie breaker of mains 13 is open.
Power management - MAINS | Mains 14 TB opened |  |  | In the power management system, the tie breaker of mains 14 is open.
Power management - MAINS | Mains 15 TB opened |  |  | In the power management system, the tie breaker of mains 15 is open.
Power management - MAINS | Mains 16 TB opened |  |  | In the power management system, the tie breaker of mains 16 is open.
Power management - MAINS | Mains 17 TB opened |  |  | In the power management system, the tie breaker of mains 17 is open.
Power management - MAINS | Mains 18 TB opened |  |  | In the power management system, the tie breaker of mains 18 is open.
Power management - MAINS | Mains 19 TB opened |  |  | In the power management system, the tie breaker of mains 19 is open.
Power management - MAINS | Mains 20 TB opened |  |  | In the power management system, the tie breaker of mains 20 is open.
Power management - MAINS | Mains 21 TB opened |  |  | In the power management system, the tie breaker of mains 21 is open.
Power management - MAINS | Mains 22 TB opened |  |  | In the power management system, the tie breaker of mains 22 is open.
Power management - MAINS | Mains 23 TB opened |  |  | In the power management system, the tie breaker of mains 23 is open.
Power management - MAINS | Mains 24 TB opened |  |  | In the power management system, the tie breaker of mains 24 is open.
Power management - MAINS | Mains 25 TB opened |  |  | In the power management system, the tie breaker of mains 25 is open.
Power management - MAINS | Mains 26 TB opened |  |  | In the power management system, the tie breaker of mains 26 is open.
Power management - MAINS | Mains 27 TB opened |  |  | In the power management system, the tie breaker of mains 27 is open.
Power management - MAINS | Mains 28 TB opened |  |  | In the power management system, the tie breaker of mains 28 is open.
Power management - MAINS | Mains 29 TB opened |  |  | In the power management system, the tie breaker of mains 29 is open.
Power management - MAINS | Mains 30 TB opened |  |  | In the power management system, the tie breaker of mains 30 is open.
Power management - MAINS | Mains 31 TB opened |  |  | In the power management system, the tie breaker of mains 31 is open.
Power management - MAINS | Mains 32 TB opened |  |  | In the power management system, the tie breaker of mains 32 is open.
Power management - MAINS | Mains 1 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 1.
Power management - MAINS | Mains 2 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 2.
Power management - MAINS | Mains 3 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 3.
Power management - MAINS | Mains 4 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 4.
Power management - MAINS | Mains 5 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 5.
Power management - MAINS | Mains 6 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 6.
Power management - MAINS | Mains 7 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 7.
Power management - MAINS | Mains 8 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 8.
Power management - MAINS | Mains 9 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 9.
Power management - MAINS | Mains 10 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 10.
Power management - MAINS | Mains 11 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 11.
Power management - MAINS | Mains 12 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 12.
Power management - MAINS | Mains 13 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 13.
Power management - MAINS | Mains 14 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 14.
Power management - MAINS | Mains 15 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 15.
Power management - MAINS | Mains 16 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 16.
Power management - MAINS | Mains 17 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 17.
Power management - MAINS | Mains 18 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 18.
Power management - MAINS | Mains 19 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 19.
Power management - MAINS | Mains 20 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 20.
Power management - MAINS | Mains 21 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 21.
Power management - MAINS | Mains 22 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 22.
Power management - MAINS | Mains 23 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 23.
Power management - MAINS | Mains 24 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 24.
Power management - MAINS | Mains 25 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 25.
Power management - MAINS | Mains 26 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 26.
Power management - MAINS | Mains 27 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 27.
Power management - MAINS | Mains 28 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 28.
Power management - MAINS | Mains 29 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 29.
Power management - MAINS | Mains 30 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 30.
Power management - MAINS | Mains 31 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 31.
Power management - MAINS | Mains 32 TB Synchronising |  |  | The power management system is synchronising the tie breaker of mains 32.
Power management - MAINS | Mains 1 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 1 are okay.
Power management - MAINS | Mains 2 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 2 are okay.
Power management - MAINS | Mains 3 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 3 are okay.
Power management - MAINS | Mains 4 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 4 are okay.
Power management - MAINS | Mains 5 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 5 are okay.
Power management - MAINS | Mains 6 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 6 are okay.
Power management - MAINS | Mains 7 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 7 are okay.
Power management - MAINS | Mains 8 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 8 are okay.
Power management - MAINS | Mains 9 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 9 are okay.
Power management - MAINS | Mains 10 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 10 are okay.
Power management - MAINS | Mains 11 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 11 are okay.
Power management - MAINS | Mains 12 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 12 are okay.
Power management - MAINS | Mains 13 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 13 are okay.
Power management - MAINS | Mains 14 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 14 are okay.
Power management - MAINS | Mains 15 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 15 are okay.
Power management - MAINS | Mains 16 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 16 are okay.
Power management - MAINS | Mains 17 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 17 are okay.
Power management - MAINS | Mains 18 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 18 are okay.
Power management - MAINS | Mains 19 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 19 are okay.
Power management - MAINS | Mains 20 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 20 are okay.
Power management - MAINS | Mains 21 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 21 are okay.
Power management - MAINS | Mains 22 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 22 are okay.
Power management - MAINS | Mains 23 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 23 are okay.
Power management - MAINS | Mains 24 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 24 are okay.
Power management - MAINS | Mains 25 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 25 are okay.
Power management - MAINS | Mains 26 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 26 are okay.
Power management - MAINS | Mains 27 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 27 are okay.
Power management - MAINS | Mains 28 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 28 are okay.
Power management - MAINS | Mains 29 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 29 are okay.
Power management - MAINS | Mains 30 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 30 are okay.
Power management - MAINS | Mains 31 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 31 are okay.
Power management - MAINS | Mains 32 mains volt/freq okay |  |  | In the power management system, the voltage and frequency of mains 32 are okay.
Power management - MAINS | Mains 1 mains failure |  |  | Mains failure was detected by the mains 1 controller.
Power management - MAINS | Mains 2 mains failure |  |  | Mains failure was detected by the mains 2 controller.
Power management - MAINS | Mains 3 mains failure |  |  | Mains failure was detected by the mains 3 controller.
Power management - MAINS | Mains 4 mains failure |  |  | Mains failure was detected by the mains 4 controller.
Power management - MAINS | Mains 5 mains failure |  |  | Mains failure was detected by the mains 5 controller.
Power management - MAINS | Mains 6 mains failure |  |  | Mains failure was detected by the mains 6 controller.
Power management - MAINS | Mains 7 mains failure |  |  | Mains failure was detected by the mains 7 controller.
Power management - MAINS | Mains 8 mains failure |  |  | Mains failure was detected by the mains 8 controller.
Power management - MAINS | Mains 9 mains failure |  |  | Mains failure was detected by the mains 9 controller.
Power management - MAINS | Mains 10 mains failure |  |  | Mains failure was detected by the mains 10 controller.
Power management - MAINS | Mains 11 mains failure |  |  | Mains failure was detected by the mains 11 controller.
Power management - MAINS | Mains 12 mains failure |  |  | Mains failure was detected by the mains 12 controller.
Power management - MAINS | Mains 13 mains failure |  |  | Mains failure was detected by the mains 13 controller.
Power management - MAINS | Mains 14 mains failure |  |  | Mains failure was detected by the mains 14 controller.
Power management - MAINS | Mains 15 mains failure |  |  | Mains failure was detected by the mains 15 controller.
Power management - MAINS | Mains 16 mains failure |  |  | Mains failure was detected by the mains 16 controller.
Power management - MAINS | Mains 17 mains failure |  |  | Mains failure was detected by the mains 17 controller.
Power management - MAINS | Mains 18 mains failure |  |  | Mains failure was detected by the mains 18 controller.
Power management - MAINS | Mains 19 mains failure |  |  | Mains failure was detected by the mains 19 controller.
Power management - MAINS | Mains 20 mains failure |  |  | Mains failure was detected by the mains 20 controller.
Power management - MAINS | Mains 21 mains failure |  |  | Mains failure was detected by the mains 21 controller.
Power management - MAINS | Mains 22 mains failure |  |  | Mains failure was detected by the mains 22 controller.
Power management - MAINS | Mains 23 mains failure |  |  | Mains failure was detected by the mains 23 controller.
Power management - MAINS | Mains 24 mains failure |  |  | Mains failure was detected by the mains 24 controller.
Power management - MAINS | Mains 25 mains failure |  |  | Mains failure was detected by the mains 25 controller.
Power management - MAINS | Mains 26 mains failure |  |  | Mains failure was detected by the mains 26 controller.
Power management - MAINS | Mains 27 mains failure |  |  | Mains failure was detected by the mains 27 controller.
Power management - MAINS | Mains 28 mains failure |  |  | Mains failure was detected by the mains 28 controller.
Power management - MAINS | Mains 29 mains failure |  |  | Mains failure was detected by the mains 29 controller.
Power management - MAINS | Mains 30 mains failure |  |  | Mains failure was detected by the mains 30 controller.
Power management - MAINS | Mains 31 mains failure |  |  | Mains failure was detected by the mains 31 controller.
Power management - MAINS | Mains 32 mains failure |  |  | Mains failure was detected by the mains 32 controller.
Power management - MAINS | Mains 1 in auto or test |  |  | The mains 1 controller is in AUTO or test mode.
Power management - MAINS | Mains 2 in auto or test |  |  | The mains 2 controller is in AUTO or test mode.
Power management - MAINS | Mains 3 in auto or test |  |  | The mains 3 controller is in AUTO or test mode.
Power management - MAINS | Mains 4 in auto or test |  |  | The mains 4 controller is in AUTO or test mode.
Power management - MAINS | Mains 5 in auto or test |  |  | The mains 5 controller is in AUTO or test mode.
Power management - MAINS | Mains 6 in auto or test |  |  | The mains 6 controller is in AUTO or test mode.
Power management - MAINS | Mains 7 in auto or test |  |  | The mains 7 controller is in AUTO or test mode.
Power management - MAINS | Mains 8 in auto or test |  |  | The mains 8 controller is in AUTO or test mode.
Power management - MAINS | Mains 9 in auto or test |  |  | The mains 9 controller is in AUTO or test mode.
Power management - MAINS | Mains 10 in auto or test |  |  | The mains 10 controller is in AUTO or test mode.
Power management - MAINS | Mains 11 in auto or test |  |  | The mains 11 controller is in AUTO or test mode.
Power management - MAINS | Mains 12 in auto or test |  |  | The mains 12 controller is in AUTO or test mode.
Power management - MAINS | Mains 13 in auto or test |  |  | The mains 13 controller is in AUTO or test mode.
Power management - MAINS | Mains 14 in auto or test |  |  | The mains 14 controller is in AUTO or test mode.
Power management - MAINS | Mains 15 in auto or test |  |  | The mains 15 controller is in AUTO or test mode.
Power management - MAINS | Mains 16 in auto or test |  |  | The mains 16 controller is in AUTO or test mode.
Power management - MAINS | Mains 17 in auto or test |  |  | The mains 17 controller is in AUTO or test mode.
Power management - MAINS | Mains 18 in auto or test |  |  | The mains 18 controller is in AUTO or test mode.
Power management - MAINS | Mains 19 in auto or test |  |  | The mains 19 controller is in AUTO or test mode.
Power management - MAINS | Mains 20 in auto or test |  |  | The mains 20 controller is in AUTO or test mode.
Power management - MAINS | Mains 21 in auto or test |  |  | The mains 21 controller is in AUTO or test mode.
Power management - MAINS | Mains 22 in auto or test |  |  | The mains 22 controller is in AUTO or test mode.
Power management - MAINS | Mains 23 in auto or test |  |  | The mains 23 controller is in AUTO or test mode.
Power management - MAINS | Mains 24 in auto or test |  |  | The mains 24 controller is in AUTO or test mode.
Power management - MAINS | Mains 25 in auto or test |  |  | The mains 25 controller is in AUTO or test mode.
Power management - MAINS | Mains 26 in auto or test |  |  | The mains 26 controller is in AUTO or test mode.
Power management - MAINS | Mains 27 in auto or test |  |  | The mains 27 controller is in AUTO or test mode.
Power management - MAINS | Mains 28 in auto or test |  |  | The mains 28 controller is in AUTO or test mode.
Power management - MAINS | Mains 29 in auto or test |  |  | The mains 29 controller is in AUTO or test mode.
Power management - MAINS | Mains 30 in auto or test |  |  | The mains 30 controller is in AUTO or test mode.
Power management - MAINS | Mains 31 in auto or test |  |  | The mains 31 controller is in AUTO or test mode.
Power management - MAINS | Mains 32 in auto or test |  |  | The mains 32 controller is in AUTO or test mode.
Power management - MAINS | Mains 1 in BLOCK |  |  | The mains 1 controller is in BLOCK mode.
Power management - MAINS | Mains 2 in BLOCK |  |  | The mains 2 controller is in BLOCK mode.
Power management - MAINS | Mains 3 in BLOCK |  |  | The mains 3 controller is in BLOCK mode.
Power management - MAINS | Mains 4 in BLOCK |  |  | The mains 4 controller is in BLOCK mode.
Power management - MAINS | Mains 5 in BLOCK |  |  | The mains 5 controller is in BLOCK mode.
Power management - MAINS | Mains 6 in BLOCK |  |  | The mains 6 controller is in BLOCK mode.
Power management - MAINS | Mains 7 in BLOCK |  |  | The mains 7 controller is in BLOCK mode.
Power management - MAINS | Mains 8 in BLOCK |  |  | The mains 8 controller is in BLOCK mode.
Power management - MAINS | Mains 9 in BLOCK |  |  | The mains 9 controller is in BLOCK mode.
Power management - MAINS | Mains 10 in BLOCK |  |  | The mains 10 controller is in BLOCK mode.
Power management - MAINS | Mains 11 in BLOCK |  |  | The mains 11 controller is in BLOCK mode.
Power management - MAINS | Mains 12 in BLOCK |  |  | The mains 12 controller is in BLOCK mode.
Power management - MAINS | Mains 13 in BLOCK |  |  | The mains 13 controller is in BLOCK mode.
Power management - MAINS | Mains 14 in BLOCK |  |  | The mains 14 controller is in BLOCK mode.
Power management - MAINS | Mains 15 in BLOCK |  |  | The mains 15 controller is in BLOCK mode.
Power management - MAINS | Mains 16 in BLOCK |  |  | The mains 16 controller is in BLOCK mode.
Power management - MAINS | Mains 17 in BLOCK |  |  | The mains 17 controller is in BLOCK mode.
Power management - MAINS | Mains 18 in BLOCK |  |  | The mains 18 controller is in BLOCK mode.
Power management - MAINS | Mains 19 in BLOCK |  |  | The mains 19 controller is in BLOCK mode.
Power management - MAINS | Mains 20 in BLOCK |  |  | The mains 20 controller is in BLOCK mode.
Power management - MAINS | Mains 21 in BLOCK |  |  | The mains 21 controller is in BLOCK mode.
Power management - MAINS | Mains 22 in BLOCK |  |  | The mains 22 controller is in BLOCK mode.
Power management - MAINS | Mains 23 in BLOCK |  |  | The mains 23 controller is in BLOCK mode.
Power management - MAINS | Mains 24 in BLOCK |  |  | The mains 24 controller is in BLOCK mode.
Power management - MAINS | Mains 25 in BLOCK |  |  | The mains 25 controller is in BLOCK mode.
Power management - MAINS | Mains 26 in BLOCK |  |  | The mains 26 controller is in BLOCK mode.
Power management - MAINS | Mains 27 in BLOCK |  |  | The mains 27 controller is in BLOCK mode.
Power management - MAINS | Mains 28 in BLOCK |  |  | The mains 28 controller is in BLOCK mode.
Power management - MAINS | Mains 29 in BLOCK |  |  | The mains 29 controller is in BLOCK mode.
Power management - MAINS | Mains 30 in BLOCK |  |  | The mains 30 controller is in BLOCK mode.
Power management - MAINS | Mains 31 in BLOCK |  |  | The mains 31 controller is in BLOCK mode.
Power management - MAINS | Mains 32 in BLOCK |  |  | The mains 32 controller is in BLOCK mode.
Power management - BTB | BTB 33 BTB Closed |  |  | In the power management system, the bus tie breaker of mains 33 is closed.
Power management - BTB | BTB 34 BTB Closed |  |  | In the power management system, the bus tie breaker of mains 34 is closed.
Power management - BTB | BTB 35 BTB Closed |  |  | In the power management system, the bus tie breaker of mains 35 is closed.
Power management - BTB | BTB 36 BTB Closed |  |  | In the power management system, the bus tie breaker of mains 36 is closed.
Power management - BTB | BTB 37 BTB Closed |  |  | In the power management system, the bus tie breaker of mains 37 is closed.
Power management - BTB | BTB 38 BTB Closed |  |  | In the power management system, the bus tie breaker of mains 38 is closed.
Power management - BTB | BTB 39 BTB Closed |  |  | In the power management system, the bus tie breaker of mains 39 is closed.
Power management - BTB | BTB 40 BTB Closed |  |  | In the power management system, the bus tie breaker of mains 40 is closed.
Power management - BTB | BTB 33 BTB Opened |  |  | In the power management system, the bus tie breaker of BTB 33 is open.
Power management - BTB | BTB 34 BTB Opened |  |  | In the power management system, the bus tie breaker of BTB 34 is open.
Power management - BTB | BTB 35 BTB Opened |  |  | In the power management system, the bus tie breaker of BTB 35 is open.
Power management - BTB | BTB 36 BTB Opened |  |  | In the power management system, the bus tie breaker of BTB 36 is open.
Power management - BTB | BTB 37 BTB Opened |  |  | In the power management system, the bus tie breaker of BTB 37 is open.
Power management - BTB | BTB 38 BTB Opened |  |  | In the power management system, the bus tie breaker of BTB 38 is open.
Power management - BTB | BTB 39 BTB Opened |  |  | In the power management system, the bus tie breaker of BTB 39 is open.
Power management - BTB | BTB 40 BTB Opened |  |  | In the power management system, the bus tie breaker of BTB 40 is open.
Power management - BTB | BTB 33 BTB Synchronising |  |  | The power management system is synchronising the bus tie breaker of BTB 33.
Power management - BTB | BTB 34 BTB Synchronising |  |  | The power management system is synchronising the bus tie breaker of BTB 34.
Power management - BTB | BTB 35 BTB Synchronising |  |  | The power management system is synchronising the bus tie breaker of BTB 35.
Power management - BTB | BTB 36 BTB Synchronising |  |  | The power management system is synchronising the bus tie breaker of BTB 36.
Power management - BTB | BTB 37 BTB Synchronising |  |  | The power management system is synchronising the bus tie breaker of BTB 37.
Power management - BTB | BTB 38 BTB Synchronising |  |  | The power management system is synchronising the bus tie breaker of BTB 38.
Power management - BTB | BTB 39 BTB Synchronising |  |  | The power management system is synchronising the bus tie breaker of BTB 39.
Power management - BTB | BTB 40 BTB Synchronising |  |  | The power management system is synchronising the bus tie breaker of BTB 40.
General Purpose PID | PID1 active |  | 1190 | PID1 is active.
General Purpose PID | PID1 at min output |  | 1190 | PID1 is at its minimum output.
General Purpose PID | PID1 at max output |  | 1190 | PID1 is at its maximum output.
General Purpose PID | PID1 output frozen |  | 1190 | The PID1 output is frozen.
General Purpose PID | PID2 active |  | 1190 | PID2 is active.
General Purpose PID | PID2 at min output |  | 1190 | PID2 is at its minimum output.
General Purpose PID | PID2 at max output |  | 1190 | PID2 is at its maximum output.
General Purpose PID | PID2 output frozen |  | 1190 | The PID2 output is frozen.
General Purpose PID | PID3 active |  | 1190 | PID3 is active.
General Purpose PID | PID3 at min output |  | 1190 | PID3 is at its minimum output.
General Purpose PID | PID3 at max output |  | 1190 | PID3 is at its maximum output.
General Purpose PID | PID3 output frozen |  | 1190 | The PID3 output is frozen.
General Purpose PID | PID4 active |  | 1190 | PID4 is active.
General Purpose PID | PID4 at min output |  | 1190 | PID4 is at its minimum output.
General Purpose PID | PID4 at max output |  | 1190 | PID4 is at its maximum output.
General Purpose PID | PID4 output frozen |  | 1190 | The PID4 output is frozen.
General Purpose PID | PID1 using input 1 |  | 1190 | PID1 is using input 1.
General Purpose PID | PID1 using input 2 |  | 1190 | PID1 is using input 2.
General Purpose PID | PID1 using input 3 |  | 1190 | PID1 is using input 3.
General Purpose PID | PID2 using input 1 |  | 1190 | PID2 is using input 1.
General Purpose PID | PID2 using input 2 |  | 1190 | PID2 is using input 2.
General Purpose PID | PID2 using input 3 |  | 1190 | PID2 is using input 3.
General Purpose PID | PID3 using input 1 |  | 1190 | PID3 is using input 1.
General Purpose PID | PID3 using input 2 |  | 1190 | PID3 is using input 2.
General Purpose PID | PID3 using input 3 |  | 1190 | PID3 is using input 3.
General Purpose PID | PID4 using input 1 |  | 1190 | PID4 is using input 1.
General Purpose PID | PID4 using input 2 |  | 1190 | PID4 is using input 2.
General Purpose PID | PID4 using input 3 |  | 1190 | PID4 is using input 3.
General Purpose PID | PID1 modbus control |  | 1190 | General purpose PID1 is under Modbus control.
General Purpose PID | PID2 modbus control |  | 1190 | General purpose PID2 is under Modbus control.
General Purpose PID | PID3 modbus control |  | 1190 | General purpose PID3 is under Modbus control.
General Purpose PID | PID4 modbus control |  | 1190 | General purpose PID4 is under Modbus control.
Flip flops | Flip flop output 1 |  |  | M-Logic flip flop 1 is High.
Flip flops | Flip flop output 2 |  |  | M-Logic flip flop 2 is High.
Flip flops | Flip flop output 3 |  |  | M-Logic flip flop 3 is High.
Flip flops | Flip flop output 4 |  |  | M-Logic flip flop 4 is High.
Flip flops | Flip flop output 5 |  |  | M-Logic flip flop 5 is High.
Flip flops | Flip flop output 6 |  |  | M-Logic flip flop 6 is High.
Flip flops | Flip flop output 7 |  |  | M-Logic flip flop 7 is High.
Flip flops | Flip flop output 8 |  |  | M-Logic flip flop 8 is High.
Flip flops | Flip flop output 9 |  |  | M-Logic flip flop 9 is High.
Flip flops | Flip flop output 10 |  |  | M-Logic flip flop 10 is High.
Flip flops | Flip flop output 11 |  |  | M-Logic flip flop 11 is High.
Flip flops | Flip flop output 12 |  |  | M-Logic flip flop 12 is High.
Flip flops | Flip flop output 13 |  |  | M-Logic flip flop 13 is High.
Flip flops | Flip flop output 14 |  |  | M-Logic flip flop 14 is High.
Flip flops | Flip flop output 15 |  |  | M-Logic flip flop 15 is High.
Flip flops | Flip flop output 16 |  |  | M-Logic flip flop 16 is High.
Oneshots | Oneshot output 1 |  | 1120 | M-Logic Oneshot 1 is activated.
Oneshots | Oneshot output 2 |  | 1120 | M-Logic Oneshot 2 is activated.
Oneshots | Oneshot output 3 |  | 1120 | M-Logic Oneshot 3 is activated.
Oneshots | Oneshot output 4 |  | 1120 | M-Logic Oneshot 4 is activated.
Oneshots | Oneshot output 5 |  | 1120 | M-Logic Oneshot 5 is activated.
Oneshots | Oneshot output 6 |  | 1120 | M-Logic Oneshot 6 is activated.
Oneshots | Oneshot output 7 |  | 1120 | M-Logic Oneshot 7 is activated.
Oneshots | Oneshot output 8 |  | 1120 | M-Logic Oneshot 8 is activated.
Oneshots | Oneshot output 9 |  | 1120 | M-Logic Oneshot 9 is activated.
Oneshots | Oneshot output 10 |  | 1120 | M-Logic Oneshot 10 is activated.
Oneshots | Oneshot output 11 |  | 1120 | M-Logic Oneshot 11 is activated.
Oneshots | Oneshot output 12 |  | 1120 | M-Logic Oneshot 12 is activated.
Oneshots | Oneshot output 13 |  | 1120 | M-Logic Oneshot 13 is activated.
Oneshots | Oneshot output 14 |  | 1120 | M-Logic Oneshot 14 is activated.
Oneshots | Oneshot output 15 |  | 1120 | M-Logic Oneshot 15 is activated.
Oneshots | Oneshot output 16 |  | 1120 | M-Logic Oneshot 16 is activated.
Easy connect | Plant active |  |  | The controller has an active single-line application drawing, and you can add generators.
Easy connect | Stand alone |  |  | The single-line application drawing is only one ASC 150 Storage controller.
Power Limit Outputs (RRCR) | Power limit output 01 |  |  | RRCR R1 is active.
Power Limit Outputs (RRCR) | Power limit output 02 |  |  | RRCR R2 is active.
Power Limit Outputs (RRCR) | Power limit output 03 |  |  | RRCR R3 is active.
Power Limit Outputs (RRCR) | Power limit output 04 |  |  | RRCR R4 is active.
Shortcut - Switch | Shortcut - Switch 1 |  |  | M-Logic Shortcut - Switch 1 is active.
Shortcut - Switch | Shortcut - Switch 2 |  |  | M-Logic Shortcut - Switch 2 is active.
Shortcut - Switch | Shortcut - Switch 3 |  |  | M-Logic Shortcut - Switch 3 is active.
Shortcut - Switch | Shortcut - Switch 4 |  |  | M-Logic Shortcut - Switch 4 is active.
Shortcut - Switch | Shortcut - Switch 5 |  |  | M-Logic Shortcut - Switch 5 is active.
Shortcut - Switch | Shortcut - Switch 6 |  |  | M-Logic Shortcut - Switch 6 is active.
Shortcut - Pulse | Shortcut - Pulse 1 |  |  | M-Logic Shortcut - Pulse 1 is active.
Shortcut - Pulse | Shortcut - Pulse 2 |  |  | M-Logic Shortcut - Pulse 2 is active.
Shortcut - Pulse | Shortcut - Pulse 3 |  |  | M-Logic Shortcut - Pulse 3 is active.
Shortcut - Pulse | Shortcut - Pulse 4 |  |  | M-Logic Shortcut - Pulse 4 is active.
Shortcut - Pulse | Shortcut - Pulse 5 |  |  | M-Logic Shortcut - Pulse 5 is active.
Shortcut - Pulse | Shortcut - Pulse 6 |  |  | M-Logic Shortcut - Pulse 6 is active.
M-Logic event counters | M-logic event counter limit 1 |  |  | M-Logic event counter 1 has reached its limit (Counters > M-logic event counters).
M-Logic event counters | M-logic event counter limit 2 |  |  | M-Logic event counter 2 has reached its limit (Counters > M-logic event counters).
M-Logic event counters | M-logic event counter limit 3 |  |  | M-Logic event counter 3 has reached its limit (Counters > M-logic event counters).
M-Logic event counters | M-logic event counter limit 4 |  |  | M-Logic event counter 4 has reached its limit (Counters > M-logic event counters).
M-Logic event counters | M-logic event counter limit 5 |  |  | M-Logic event counter 5 has reached its limit (Counters > M-logic event counters).
M-Logic event counters | M-logic event counter limit 6 |  |  | M-Logic event counter 6 has reached its limit (Counters > M-logic event counters).
M-Logic event counters | M-logic event counter limit 7 |  |  | M-Logic event counter 7 has reached its limit (Counters > M-logic event counters).
M-Logic event counters | M-logic event counter limit 8 |  |  | M-Logic event counter 8 has reached its limit (Counters > M-logic event counters).
M-Logic event counters | M-logic event reset counter 1 |  |  | M-Logic event counter 1 is reset.
M-Logic event counters | M-logic event reset counter 2 |  |  | M-Logic event counter 2 is reset.
M-Logic event counters | M-logic event reset counter 3 |  |  | M-Logic event counter 3 is reset.
M-Logic event counters | M-logic event reset counter 4 |  |  | M-Logic event counter 4 is reset.
M-Logic event counters | M-logic event reset counter 5 |  |  | M-Logic event counter 5 is reset.
M-Logic event counters | M-logic event reset counter 6 |  |  | M-Logic event counter 6 is reset.
M-Logic event counters | M-logic event reset counter 7 |  |  | M-Logic event counter 7 is reset.
M-Logic event counters | M-logic event reset counter 8 |  |  | M-Logic event counter 8 is reset.
Display keypress events | Up |  |  | The Up button on the display folio is pushed.
Display keypress events | Down |  |  | The Down button on the display folio is pushed.
Display keypress events | Left |  |  | The Left button on the display folio is pushed.
Display keypress events | Right |  |  | The Right button on the display folio is pushed.
Display keypress events | Escape |  |  | The Back button on the display folio is pushed.
Display keypress events | Select |  |  | The OK button on the display folio is pushed.
Display keypress events | Start |  |  | The Start button on the display mimic is pushed.
Display keypress events | Stop |  |  | The Stop button on the display mimic is pushed.
Display keypress events | ESB close |  |  | The ESB close button on the display mimic is pushed.
Display keypress events | ESB open |  |  | The ESB open button on the display mimic is pushed.
Display keypress events | MB close |  |  | The MB close button on the display mimic is pushed.
Display keypress events | MB open |  |  | The MB open button on the display mimic is pushed.
Display keypress events | AUTO mode |  |  | The Auto button on the display folio is pushed.
Display keypress events | MANUAL mode |  |  | The Manual button on the display folio is pushed.
Display keypress events | Alarm list |  |  | The Alarm button on the display folio is pushed.
Display keypress events | Command menu |  |  | The Menu button on the display folio is pushed.
Synchronisation | Phase OK |  |  | The phases are synchronised.
Synchronisation | Frequency OK |  |  | The frequencies are inside the synchronisation window.
Synchronisation | Voltage OK |  |  | The voltages are inside the synchronisation window.

## ASC_150_Storage_M-Logic_Outputs
Category | Name | Options | From SW version | Controller action when the output is activated
Command | Auto start/stop |  |  | Start and run the ESS.
Command | Remote start |  |  | Start the ESS.
Command | Remote stop |  |  | Stop the ESS.
Command | Lamp test |  |  | Activate the lamp test.
Command | Force backlight and LEDs OFF |  | 1090 | Turn off the display backlight and LEDs.
Command | Ack. all alarms |  |  | Acknowledge all alarms.
Command | Set clock to 4 AM |  |  | Set the controller clock to 04h00.
Command | Reset horn |  |  | Reset the alarm horn function.
Command | Access lock |  |  | Display button access is locked.
Command | Q ref type off-grid: Off |  |  | Change Q type off-grid (parameter 7033) to Off.
Command | Q ref type off-grid: Share |  |  | Change Q type off-grid (parameter 7033) to Q share.
Command | Q ref type grid-tied: Off |  |  | Change Q-type grid-tie (parameter 7055) to Off.
Command | Q ref type grid-tied: Cosphi fixed |  |  | Change Q-type grid-tie (parameter 7055) to Cosphi fixed.
Command | Q ref type grid-tied: Cosphi imp/exp |  |  | Change Q-type grid-tie (parameter 7055) to Cosphi imp/exp.
Command | Q ref type grid-tied: Cosphi superior |  |  | Change Q-type grid-tie (parameter 7055) to Cosphi superior.
Command | Q ref type grid-tied: Q fixed |  |  | Change Q-type grid-tie (parameter 7055) to Q fixed.
Command | Q ref type grid-tied: Q imp/ext |  |  | Change Q-type grid-tie (parameter 7055) to Q imp/ext.
Command | P/Q limit type: Off |  |  | Turns off P/Q limitation.
Command | Freeze P ramp |  |  | Freeze the ESS power ramp.
Command | Freeze Q ramp |  |  | Freeze the ESS reactive power ramp.
Command | Activate active power control via comm |  | 1220 | Activate active power control via communication (parameter 7501).
Command | Activate cosphi control via comm |  | 1220 | Activate cosphi control via communication (parameter 7502).
Command | Activate reactive power control via comm |  | 1220 | Activate reactive power control via communication (parameter 7503).
Command | Deactivate active power control via comm |  | 1220 | Deactivate active power control via communication (parameter 7501).
Command | Deactivate cosphi control via comm |  | 1220 | Deactivate cosphi control via communication (parameter 7502).
Command | Deactivate reactive power control via comm |  | 1220 | Deactivate reactive power control via communication (parameter 7503).
Command AC | Select three phase system |  |  | Select 3-phase system (parameter 9131).
Command AC | Select split L1L3 phase system |  |  | Select split-phase (L1L3) system (parameter 9131).
Command AC | Select split L1L2 phase system |  |  | Select split-phase (L1L2) system (parameter 9131).
Command AC | Select single phase system |  |  | Select single-phase system (parameter 9131).
Command AC | Select L1L2L3 phase rotation |  |  | Select L1L2L3 phase rotation (parameter 2154).
Command AC | Select L1L3L2 phase rotation |  |  | Select L1L3L2 phase rotation (parameter 2154).
Command Battery | Custom input to ESS |  |  | Activate a custom function in the ESS protocol. For example, this command could activate a low ripple current charging mode.
Command Battery | Reset Power Functionality |  |  | The ASC resets its use of the power function.
Command Battery | Set Power Functionality |  |  | The ASC ignores the SOC thresholds history and uses the power function.
Command Battery | Reset Energy Functionality |  |  | The ASC resets its use of the energy function.
Command Battery | Set Energy Functionality |  |  | The ASC ignores the SOC thresholds history and uses the energy function.
Command Battery | Set AC Coupling |  |  | Use an AC-coupled battery (parameter 17082).
Command Battery | Set DC Coupling |  |  | Use a DC-coupled battery (parameter 17082).
Command Battery | Set SOC setting 1 |  |  | Use SOC setting 1 (parameter 17055).
Command Battery | Set SOC setting 2 |  |  | Use SOC setting 2 (parameter 17055).
Command Battery | Set SOC setting 3 |  |  | Use SOC setting 3 (parameter 17055).
Command Battery | Set Battery mode - Energy Source |  |  | The battery is the energy source (parameter 17081).
Command Battery | Set Battery mode - Power Source |  |  | The battery is the power source (parameter 17081).
Command Battery | Request ESS to Sync MB (Tesla) |  |  | For the Tesla protocol, the ASC requests the ESS to synchronise to the mains breaker.
Command Battery | Request ESS to Open MB (Tesla) |  |  | For the Tesla protocol, the ASC requests the ESS to open the mains breaker.
Command Battery | Enable mains charge parameter |  |  | Mains charging (parameter 17022) is changed to Enabled.
Command Battery | Disable mains charge parameter |  |  | Mains charging (parameter 17022) is changed to Not enabled.
Command Battery | Enable Gen charge parameter |  |  | DG charge mode (parameter 17033) is changed to Enabled.
Command Battery | Disable Gen charge parameter |  |  | DG charge mode (parameter 17033) is changed to Not enabled.
Command Battery | Enable PV charge parameter |  |  | PV charging (parameter 17041) is changed to Enabled.
Command Battery | Disable PV charge parameter |  |  | PV charging (parameter 17041) is changed to Not enabled.
Command Battery | Force BMS Shutdown |  |  | The ASC sends a command to the BMS to shut down.
Command Battery | Set mode to Droop |  |  | The ESS runs in droop mode.
Command Battery | Set mode to P/Q |  |  | The ESS runs in grid-following mode.
Command Battery | Set mode to V/f |  |  | The ESS runs in grid-forming mode.
Command Battery | Freeze charging |  |  | Freeze the ESS charging.
Command Battery | Freeze discharging |  |  | Freeze the ESS discharging.
Command Battery | Force charging |  |  | Force the ESS to charge.
Command Battery | Force discharging |  |  | Force the ESS to discharge.
Command Battery | Ack. alarms on ESS |  | 1150 | Acknowledge all the alarms on the ESS.
Command Battery | Ack. alarms on BMS |  | 1150 | Acknowledge all the alarms on the BMS.
Command Battery | Ack. alarms on PDS |  | 1150 | Acknowledge all the alarms on the PDS.
Command Battery | Request boost charging |  | 1150 | For supported systems, send a command to the ESS to activate boost charging while this command is active.
Command Battery | PDS spin. res. set pct 1 |  | 1150 | Parameter 17203 is changed to PDS Spinning reserve pct 01.
Command Battery | PDS spin. res. set pct 2 |  | 1150 | Parameter 17203 is changed to PDS Spinning reserve pct 02.
Command Battery | Disable PDS |  | 1180 | Disable the PDS.
Command Battery | Enable ESS isochronous mode |  | 1180 | Change ESS isochronous mode (parameter 8042) to enabled.
Command Battery | Disable ESS isochronous mode |  | 1180 | Change ESS isochronous mode (parameter 8042) to not enabled.
Command Battery | Disable ESS send grid mode |  | 1200
Command Battery | Disable Maintenance Charge |  | 1210 | Change Maintenance charge (parameter 17400) to not enabled.
Command Battery | Enable Maintenance Charge |  | 1210 | Change Maintenance charge (parameter 17400) to enabled.
Command Battery | Skip Q ramp down |  | 1210 | Change the kvar reference without a ramp down.
Command Battery | Skip Q ramp up |  | 1210 | Change the kvar reference without a ramp up.
Command GEN | Min. Gen load set 1 |  |  | Change Min DG load set (parameter 15013) to Min. DG load set 1.
Command GEN | Min. Gen load set 2 |  |  | Change Min DG load set (parameter 15013) to Min. DG load set 2.
Command GEN | Request ext. Gen to start |  |  | Activate the Start/Stop Ext. DG output.
Command GEN | Request ext. Gen to stop |  |  | Deactivate the Start/Stop Ext. DG output.
Command GEN | Opt. Gen load set off |  |  | Charge Opt DG load set (parameter 15016) to Optimal DG load set off.
Command GEN | Opt. Gen load set pct 1 |  |  | Charge Opt DG load set (parameter 15016) to Optimal DG load set pct 1.
Command GEN | Opt. Gen load set pct 2 |  |  | Charge Opt DG load set (parameter 15016) to Optimal DG load set pct 2.
Command Parameter set | Set parameter 1 |  |  | Use nominal parameters set 1 (parameters 6001 to 6008).
Command Parameter set | Set parameter 2 |  |  | Use nominal parameters set 2 (parameters 6011 to 6017).
Command Parameter set | Set parameter 3 |  |  | Use nominal parameters set 3 (parameters 6021 to 6027).
Command Parameter set | Set parameter 4 |  |  | Use nominal parameters set 4 (parameters 6031 to 6037).
Command Parameter set | Set BB parameter 1 |  |  | Use the busbar nominal parameters set 1 (parameters 6051 to 6055).
Command Parameter set | Set BB parameter 2 |  |  | Use the busbar nominal parameters set 2 (parameters 6061 to 6064).
Command Parameter set | Set BB Unom = ES Unom |  |  | For the busbar nominal voltage, use the ESS nominal voltage.
Command Breakers | ESB close inhibit |  |  | Inhibit any ESS breaker close command.
Command Breakers | Open ESB |  |  | Open the ESS breaker.
Command Breakers | Close ESB |  |  | Close the ESS breaker.
Command Breakers | Open MB | S4 PREMIUM |  | Close the mains breaker.
Command Breakers | Close MB | S4 PREMIUM |  | Open the mains breaker.
Command Breakers | MB close inhibit | S4 PREMIUM |  | Inhibit any mains breaker close command.
Command Plant | Select application 1 |  |  | Use the single-line drawing for application 1.
Command Plant | Select application 2 |  |  | Use the single-line drawing for application 2.
Command Plant | Select application 3 |  |  | Use the single-line drawing for application 3.
Command Plant | Select application 4 |  |  | Use the single-line drawing for application 4.
Command M-Logic and AOP | M-Logic alarm 1 |  |  | Activate M-Logic alarm 1 (menu 3570).
Command M-Logic and AOP | M-Logic alarm 2 |  |  | Activate M-Logic alarm 2 (menu 3580).
Command M-Logic and AOP | M-Logic alarm 3 |  |  | Activate M-Logic alarm 3 (menu 3590).
Command M-Logic and AOP | M-Logic alarm 4 |  |  | Activate M-Logic alarm 4 (menu 3600).
Command M-Logic and AOP | M-Logic alarm 5 |  |  | Activate M-Logic alarm 5 (menu 3610).
Command M-Logic and AOP | M-Logic alarm 10 |  | 1180 | Activate M-Logic alarm 10 (menu 3660).
Command M-Logic and AOP | M-Logic alarm 11 |  | 1180 | Activate M-Logic alarm 11 (menu 3670).
Command M-Logic and AOP | M-Logic alarm 12 |  | 1180 | Activate M-Logic alarm 12 (menu 3680).
Command M-Logic and AOP | M-Logic alarm 13 |  | 1180 | Activate M-Logic alarm 13 (menu 3690).
Command M-Logic and AOP | M-Logic alarm 14 |  | 1180 | Activate M-Logic alarm 14 (menu 3700).
Command M-Logic and AOP | M-Logic ext alarm 1: Start extended timer |  | 1060 | Start the timer for M-Logic ext alarm 1 (parameter 3621 and menu 3622).
Command M-Logic and AOP | M-Logic ext alarm 2: Start extended timer |  | 1060 | Start the timer for M-Logic ext alarm 2 (parameter 3631 and menu 3632).
Command M-Logic and AOP | M-Logic ext alarm 3: Start extended timer |  | 1060 | Start the timer for M-Logic ext alarm 3 (parameter 3641 and menu 3642).
Command M-Logic and AOP | M-Logic ext alarm 4: Start extended timer |  | 1060 | Start the timer for M-Logic ext alarm 4 (parameter 3651 and menu 3652).
Command M-Logic and AOP | M-Logic ext alarm 1: Reset extended timer |  | 1060 | Reset the timer for M-Logic ext alarm 1.
Command M-Logic and AOP | M-Logic ext alarm 2: Reset extended timer |  | 1060 | Reset the timer for M-Logic ext alarm 2.
Command M-Logic and AOP | M-Logic ext alarm 3: Reset extended timer |  | 1060 | Reset the timer for M-Logic ext alarm 3.
Command M-Logic and AOP | M-Logic ext alarm 4: Reset extended timer |  | 1060 | Reset the timer for M-Logic ext alarm 4.
Command M-Logic and AOP | Activate relay on AOP2 ID 1 |  |  | Activate the relay on the AOP2 with ID 1.
Command M-Logic and AOP | Activate relay on AOP2 ID 2 | S4 PREMIUM |  | Activate the relay on the AOP2 with ID 2.
Command M-Logic and AOP | Activate buzzer on AOP2 ID 1 |  |  | Activate the buzzer on the AOP2 with ID 1.
Command M-Logic and AOP | Activate buzzer on AOP2 ID 2 | S4 PREMIUM |  | Activate the buzzer on the AOP2 with ID 2.
Command M-Logic and AOP | Activate All AOP2 buzzers |  |  | Activate the buzzers on all AOP2s.
Command M-Logic and AOP | Activate All AOP2 relays |  |  | Activate the relays on all AOP2s.
Modes | Island |  |  | Change the ASC mode to island.
Modes | AMF |  |  | Change the ASC mode to automatic mains failure.
Modes | Peak shaving |  |  | Change the ASC mode to peak shaving.
Modes | Fixed power |  |  | Change the ASC mode to fixed power.
Modes | Mains power export |  |  | Change the ASC mode to mains power export.
Modes | Power management |  |  | Change the ASC mode to power management.
Modes | MANUAL Mode |  |  | Change the ASC mode to manual (some manual control).
Modes | AUTO Mode |  |  | Change the ASC mode to automatic (no manual control).
Virtual toggle events | Virtual toggle event 1 |  |  | Activate virtual toggle event 1.
Virtual toggle events | Virtual toggle event 2 |  |  | Activate virtual toggle event 2.
Virtual toggle events | Virtual toggle event 3 |  |  | Activate virtual toggle event 3.
Virtual toggle events | Virtual toggle event 4 |  |  | Activate virtual toggle event 4.
Virtual toggle events | Virtual toggle event 5 |  |  | Activate virtual toggle event 5.
Virtual toggle events | Virtual toggle event 6 |  |  | Activate virtual toggle event 6.
Virtual toggle events | Virtual toggle event 7 |  |  | Activate virtual toggle event 7.
Virtual toggle events | Virtual toggle event 8 |  |  | Activate virtual toggle event 8.
Virtual toggle events | Virtual toggle event 9 |  |  | Activate virtual toggle event 9.
Virtual toggle events | Virtual toggle event 10 |  |  | Activate virtual toggle event 10.
Virtual toggle events | Virtual toggle event 11 |  |  | Activate virtual toggle event 11.
Virtual toggle events | Virtual toggle event 12 |  |  | Activate virtual toggle event 12.
Virtual toggle events | Virtual toggle event 13 |  |  | Activate virtual toggle event 13.
Virtual toggle events | Virtual toggle event 14 |  |  | Activate virtual toggle event 14.
Virtual toggle events | Virtual toggle event 15 |  |  | Activate virtual toggle event 15.
Virtual toggle events | Virtual toggle event 16 |  |  | Activate virtual toggle event 16.
Virtual toggle events | Virtual toggle event 17 |  |  | Activate virtual toggle event 17.
Virtual toggle events | Virtual toggle event 18 |  |  | Activate virtual toggle event 18.
Virtual toggle events | Virtual toggle event 19 |  |  | Activate virtual toggle event 19.
Virtual toggle events | Virtual toggle event 20 |  |  | Activate virtual toggle event 20.
Virtual toggle events | Virtual toggle event 21 |  |  | Activate virtual toggle event 21.
Virtual toggle events | Virtual toggle event 22 |  |  | Activate virtual toggle event 22.
Virtual toggle events | Virtual toggle event 23 |  |  | Activate virtual toggle event 23.
Virtual toggle events | Virtual toggle event 24 |  |  | Activate virtual toggle event 24.
Virtual toggle events | Virtual toggle event 25 |  |  | Activate virtual toggle event 25.
Virtual toggle events | Virtual toggle event 26 |  |  | Activate virtual toggle event 26.
Virtual toggle events | Virtual toggle event 27 |  |  | Activate virtual toggle event 27.
Virtual toggle events | Virtual toggle event 28 |  |  | Activate virtual toggle event 28.
Virtual toggle events | Virtual toggle event 29 |  |  | Activate virtual toggle event 29.
Virtual toggle events | Virtual toggle event 30 |  |  | Activate virtual toggle event 30.
Virtual toggle events | Virtual toggle event 31 |  |  | Activate virtual toggle event 31.
Virtual toggle events | Virtual toggle event 32 |  |  | Activate virtual toggle event 32.
Virtual toggle events | Virtual toggle event 33 |  |  | Activate virtual toggle event 33.
Virtual toggle events | Virtual toggle event 34 |  |  | Activate virtual toggle event 34.
Virtual toggle events | Virtual toggle event 35 |  |  | Activate virtual toggle event 35.
Virtual toggle events | Virtual toggle event 36 |  |  | Activate virtual toggle event 36.
Virtual toggle events | Virtual toggle event 37 |  |  | Activate virtual toggle event 37.
Virtual toggle events | Virtual toggle event 38 |  |  | Activate virtual toggle event 38.
Virtual toggle events | Virtual toggle event 39 |  |  | Activate virtual toggle event 39.
Virtual toggle events | Virtual toggle event 40 |  |  | Activate virtual toggle event 40.
Virtual toggle events | Virtual toggle event 41 |  |  | Activate virtual toggle event 41.
Virtual toggle events | Virtual toggle event 42 |  |  | Activate virtual toggle event 42.
Virtual toggle events | Virtual toggle event 43 |  |  | Activate virtual toggle event 43.
Virtual toggle events | Virtual toggle event 44 |  |  | Activate virtual toggle event 44.
Virtual toggle events | Virtual toggle event 45 |  |  | Activate virtual toggle event 45.
Virtual toggle events | Virtual toggle event 46 |  |  | Activate virtual toggle event 46.
Virtual toggle events | Virtual toggle event 47 |  |  | Activate virtual toggle event 47.
Virtual toggle events | Virtual toggle event 48 |  |  | Activate virtual toggle event 48.
Virtual toggle events | Virtual toggle event 49 |  |  | Activate virtual toggle event 49.
Virtual toggle events | Virtual toggle event 50 |  |  | Activate virtual toggle event 50.
Virtual toggle events | Virtual toggle event 51 |  |  | Activate virtual toggle event 51.
Virtual toggle events | Virtual toggle event 52 |  |  | Activate virtual toggle event 52.
Virtual toggle events | Virtual toggle event 53 |  |  | Activate virtual toggle event 53.
Virtual toggle events | Virtual toggle event 54 |  |  | Activate virtual toggle event 54.
Virtual toggle events | Virtual toggle event 55 |  |  | Activate virtual toggle event 55.
Virtual toggle events | Virtual toggle event 56 |  |  | Activate virtual toggle event 56.
Virtual toggle events | Virtual toggle event 57 |  |  | Activate virtual toggle event 57.
Virtual toggle events | Virtual toggle event 58 |  |  | Activate virtual toggle event 58.
Virtual toggle events | Virtual toggle event 59 |  |  | Activate virtual toggle event 59.
Virtual toggle events | Virtual toggle event 60 |  |  | Activate virtual toggle event 60.
Virtual toggle events | Virtual toggle event 61 |  |  | Activate virtual toggle event 61.
Virtual toggle events | Virtual toggle event 62 |  |  | Activate virtual toggle event 62.
Virtual toggle events | Virtual toggle event 63 |  |  | Activate virtual toggle event 63.
Virtual toggle events | Virtual toggle event 64 |  |  | Activate virtual toggle event 64.
Virtual toggle events | Virtual toggle event 65 |  |  | Activate virtual toggle event 65.
Virtual toggle events | Virtual toggle event 66 |  |  | Activate virtual toggle event 66.
Virtual toggle events | Virtual toggle event 67 |  |  | Activate virtual toggle event 67.
Virtual toggle events | Virtual toggle event 68 |  |  | Activate virtual toggle event 68.
Virtual toggle events | Virtual toggle event 69 |  |  | Activate virtual toggle event 69.
Virtual toggle events | Virtual toggle event 70 |  |  | Activate virtual toggle event 70.
Virtual toggle events | Virtual toggle event 71 |  |  | Activate virtual toggle event 71.
Virtual toggle events | Virtual toggle event 72 |  |  | Activate virtual toggle event 72.
Virtual toggle events | Virtual toggle event 73 |  |  | Activate virtual toggle event 73.
Virtual toggle events | Virtual toggle event 74 |  |  | Activate virtual toggle event 74.
Virtual toggle events | Virtual toggle event 75 |  |  | Activate virtual toggle event 75.
Virtual toggle events | Virtual toggle event 76 |  |  | Activate virtual toggle event 76.
Virtual toggle events | Virtual toggle event 77 |  |  | Activate virtual toggle event 77.
Virtual toggle events | Virtual toggle event 78 |  |  | Activate virtual toggle event 78.
Virtual toggle events | Virtual toggle event 79 |  |  | Activate virtual toggle event 79.
Virtual toggle events | Virtual toggle event 80 |  |  | Activate virtual toggle event 80.
Virtual toggle events | Virtual toggle event 81 |  |  | Activate virtual toggle event 81.
Virtual toggle events | Virtual toggle event 82 |  |  | Activate virtual toggle event 82.
Virtual toggle events | Virtual toggle event 83 |  |  | Activate virtual toggle event 83.
Virtual toggle events | Virtual toggle event 84 |  |  | Activate virtual toggle event 84.
Virtual toggle events | Virtual toggle event 85 |  |  | Activate virtual toggle event 85.
Virtual toggle events | Virtual toggle event 86 |  |  | Activate virtual toggle event 86.
Virtual toggle events | Virtual toggle event 87 |  |  | Activate virtual toggle event 87.
Virtual toggle events | Virtual toggle event 88 |  |  | Activate virtual toggle event 88.
Virtual toggle events | Virtual toggle event 89 |  |  | Activate virtual toggle event 89.
Virtual toggle events | Virtual toggle event 90 |  |  | Activate virtual toggle event 90.
Virtual toggle events | Virtual toggle event 91 |  |  | Activate virtual toggle event 91.
Virtual toggle events | Virtual toggle event 92 |  |  | Activate virtual toggle event 92.
Virtual toggle events | Virtual toggle event 93 |  |  | Activate virtual toggle event 93.
Virtual toggle events | Virtual toggle event 94 |  |  | Activate virtual toggle event 94.
Virtual toggle events | Virtual toggle event 95 |  |  | Activate virtual toggle event 95.
Virtual toggle events | Virtual toggle event 96 |  |  | Activate virtual toggle event 96.
Virtual switch events | Virtual switch event 1 |  |  | Activate virtual switch event 1.
Virtual switch events | Virtual switch event 2 |  |  | Activate virtual switch event 2.
Virtual switch events | Virtual switch event 3 |  |  | Activate virtual switch event 3.
Virtual switch events | Virtual switch event 4 |  |  | Activate virtual switch event 4.
Virtual switch events | Virtual switch event 5 |  |  | Activate virtual switch event 5.
Virtual switch events | Virtual switch event 6 |  |  | Activate virtual switch event 6.
Virtual switch events | Virtual switch event 7 |  |  | Activate virtual switch event 7.
Virtual switch events | Virtual switch event 8 |  |  | Activate virtual switch event 8.
Virtual switch events | Virtual switch event 9 |  |  | Activate virtual switch event 9.
Virtual switch events | Virtual switch event 10 |  |  | Activate virtual switch event 10.
Virtual switch events | Virtual switch event 11 |  |  | Activate virtual switch event 11.
Virtual switch events | Virtual switch event 12 |  |  | Activate virtual switch event 12.
Virtual switch events | Virtual switch event 13 |  |  | Activate virtual switch event 13.
Virtual switch events | Virtual switch event 14 |  |  | Activate virtual switch event 14.
Virtual switch events | Virtual switch event 15 |  |  | Activate virtual switch event 15.
Virtual switch events | Virtual switch event 16 |  |  | Activate virtual switch event 16.
Virtual switch events | Virtual switch event 17 |  |  | Activate virtual switch event 17.
Virtual switch events | Virtual switch event 18 |  |  | Activate virtual switch event 18.
Virtual switch events | Virtual switch event 19 |  |  | Activate virtual switch event 19.
Virtual switch events | Virtual switch event 20 |  |  | Activate virtual switch event 20.
Virtual switch events | Virtual switch event 21 |  |  | Activate virtual switch event 21.
Virtual switch events | Virtual switch event 22 |  |  | Activate virtual switch event 22.
Virtual switch events | Virtual switch event 23 |  |  | Activate virtual switch event 23.
Virtual switch events | Virtual switch event 24 |  |  | Activate virtual switch event 24.
Virtual switch events | Virtual switch event 25 |  |  | Activate virtual switch event 25.
Virtual switch events | Virtual switch event 26 |  |  | Activate virtual switch event 26.
Virtual switch events | Virtual switch event 27 |  |  | Activate virtual switch event 27.
Virtual switch events | Virtual switch event 28 |  |  | Activate virtual switch event 28.
Virtual switch events | Virtual switch event 29 |  |  | Activate virtual switch event 29.
Virtual switch events | Virtual switch event 30 |  |  | Activate virtual switch event 30.
Virtual switch events | Virtual switch event 31 |  |  | Activate virtual switch event 31.
Virtual switch events | Virtual switch event 32 |  |  | Activate virtual switch event 32.
Relays | Not used |  |  | -
Relays | Relay 5 |  |  | Activate Relay 5.
Relays | Relay 6 |  |  | Activate Relay 6.
Relays | Relay 9 |  |  | Activate Relay 9.
Relays | Relay 10 |  |  | Activate Relay 10.
Relays | Relay 11 |  |  | Activate Relay 11.
Relays | Relay 12 |  |  | Activate Relay 12.
Relays | Relay 13 |  |  | Activate Relay 13.
Relays | Relay 14 |  |  | Activate Relay 14.
Relays | Relay 15 |  |  | Activate Relay 15.
Relays | Relay 16 |  |  | Activate Relay 16.
Relays | Relay 17 |  |  | Activate Relay 17.
Relays | Relay 18 |  |  | Activate Relay 18.
CIO outputs | CIO 208 no.1 Out. 9 |  |  | Activate CIO 208 no.1 Out. 9.
CIO outputs | CIO 208 no.1 Out. 11 |  |  | Activate CIO 208 no.1 Out. 11.
CIO outputs | CIO 208 no.1 Out. 13 |  |  | Activate CIO 208 no.1 Out. 13.
CIO outputs | CIO 208 no.1 Out. 15 |  |  | Activate CIO 208 no.1 Out. 15.
CIO outputs | CIO 208 no.1 Out. 18 |  |  | Activate CIO 208 no.1 Out. 18.
CIO outputs | CIO 208 no.1 Out. 21 |  |  | Activate CIO 208 no.1 Out. 21.
CIO outputs | CIO 208 no.1 Out. 24 |  |  | Activate CIO 208 no.1 Out. 24.
CIO outputs | CIO 208 no.1 Out. 27 |  |  | Activate CIO 208 no.1 Out. 27.
CIO outputs | CIO 208 no.2 Out. 9 |  |  | Activate CIO 208 no.2 Out. 9.
CIO outputs | CIO 208 no.2 Out. 11 |  |  | Activate CIO 208 no.2 Out. 11.
CIO outputs | CIO 208 no.2 Out. 13 |  |  | Activate CIO 208 no.2 Out. 13.
CIO outputs | CIO 208 no.2 Out. 15 |  |  | Activate CIO 208 no.2 Out. 15.
CIO outputs | CIO 208 no.2 Out. 18 |  |  | Activate CIO 208 no.2 Out. 18.
CIO outputs | CIO 208 no.2 Out. 21 |  |  | Activate CIO 208 no.2 Out. 21.
CIO outputs | CIO 208 no.2 Out. 24 |  |  | Activate CIO 208 no.2 Out. 24.
CIO outputs | CIO 208 no.2 Out. 27 |  |  | Activate CIO 208 no.2 Out. 27.
CIO outputs | CIO 208 no.3 Out. 9 |  |  | Activate CIO 208 no.3 Out. 9.
CIO outputs | CIO 208 no.3 Out. 11 |  |  | Activate CIO 208 no.3 Out. 11.
CIO outputs | CIO 208 no.3 Out. 13 |  |  | Activate CIO 208 no.3 Out. 13.
CIO outputs | CIO 208 no.3 Out. 15 |  |  | Activate CIO 208 no.3 Out. 15.
CIO outputs | CIO 208 no.3 Out. 18 |  |  | Activate CIO 208 no.3 Out. 18.
CIO outputs | CIO 208 no.3 Out. 21 |  |  | Activate CIO 208 no.3 Out. 21.
CIO outputs | CIO 208 no.3 Out. 24 |  |  | Activate CIO 208 no.3 Out. 24.
CIO outputs | CIO 208 no.3 Out. 27 |  |  | Activate CIO 208 no.3 Out. 27.
CIO outputs | CIO 116 no.1 conf. status output |  |  | Activate CIO 116 no.1 conf. status output.
CIO outputs | CIO 116 no.2 conf. status output |  |  | Activate CIO 116 no.2 conf. status output.
CIO outputs | CIO 116 no.3 conf. status output |  |  | Activate CIO 116 no.3 conf. status output.
CIO outputs | CIO 208 no.1 conf. status output |  |  | Activate CIO 208 no.1 conf. status output.
CIO outputs | CIO 208 no.2 conf. status output |  |  | Activate CIO 208 no.2 conf. status output.
CIO outputs | CIO 208 no.3 conf. status output |  |  | Activate CIO 208 no.3 conf. status output.
CIO outputs | CIO 308 no.1 conf. status output |  |  | Activate CIO 308 no.1 conf. status output.
CIO outputs | CIO 308 no.2 conf. status output |  |  | Activate CIO 308 no.2 conf. status output.
CIO outputs | CIO 308 no.3 conf. status output |  |  | Activate CIO 308 no.3 conf. status output.
Inhibits/Activate/Deactivate | Not used |  |  | -
Inhibits/Activate/Deactivate | Deactivate Mode change via Mode Cmd |  |  | Deactivate the AUTO and MANUAL mode buttons on the display.
Inhibits/Activate/Deactivate | Deactivate OFF selection via Mode Cmd
Inhibits/Activate/Deactivate | Inh. start button |  |  | Deactivate the start button on the display.
Inhibits/Activate/Deactivate | Inh. stop button |  |  | Deactivate the stop button on the display.
Inhibits/Activate/Deactivate | Inh. inverter start |  |  | Inhibit the inverter start.
Inhibits/Activate/Deactivate | Inh. ESB buttons |  |  | Deactivate the ESB open and close buttons on the display.
Inhibits/Activate/Deactivate | Inh. MB buttons |  |  | Deactivate the MB open and close buttons on the display.
Inhibits/Activate/Deactivate | Inh. ESB black close |  |  | Inhibit ESB black closing.
Inhibits/Activate/Deactivate | Inh. regulation |  |  | Deactivate regulation.
Inhibits/Activate/Deactivate | Inh. acknowledge in AUTO |  |  | Inhibit alarm acknowledge in AUTO mode.
Inhibits/Activate/Deactivate | Inh. modbus commands |  |  | Inhibit Modbus commands to this controller.
Inhibits/Activate/Deactivate | Inhibit 1 |  |  | Activate User configurable alarm inhibit 1 (to inhibit alarms with this inhibit).
Inhibits/Activate/Deactivate | Inhibit 2 |  |  | Activate User configurable alarm inhibit 2 (to inhibit alarms with this inhibit).
Inhibits/Activate/Deactivate | Inhibit 3 |  |  | Activate User configurable alarm inhibit 3 (to inhibit alarms with this inhibit).
Inhibits/Activate/Deactivate | Inh. AOP2_1 buttons |  |  | Deactivate all the buttons on AOP2 number 1.
Inhibits/Activate/Deactivate | Inh. AOP2_2 buttons | S4 PREMIUM |  | Deactivate all the buttons on AOP2 number 2.
Inhibits/Activate/Deactivate | Activate modeshift |  |  | Activate AMF mode automatically.
Inhibits/Activate/Deactivate | Deactivate modeshift |  |  | Deactivate AMF mode automatically.
External DG ena/dis | Enable DG1 |  |  | Include DG1 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 1" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Enable DG2 |  |  | Include DG2 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 2" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Enable DG3 |  |  | Include DG3 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 3" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Enable DG4 |  |  | Include DG4 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 4" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Enable DG5 | S4 PREMIUM |  | Include DG5 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 5" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Enable DG6 | S4 PREMIUM |  | Include DG6 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 6" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Enable DG7 | S4 PREMIUM |  | Include DG7 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 7" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Enable DG8 | S4 PREMIUM |  | Include DG8 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 8" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Enable DG9 | S4 PREMIUM |  | Include DG9 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 9" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Enable DG10 | S4 PREMIUM |  | Include DG10 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 10" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Enable DG11 | S4 PREMIUM |  | Include DG11 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 11" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Enable DG12 | S4 PREMIUM |  | Include DG12 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 12" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Enable DG13 | S4 PREMIUM |  | Include DG13 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 13" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Enable DG14 | S4 PREMIUM |  | Include DG14 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 14" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Enable DG15 | S4 PREMIUM |  | Include DG15 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 15" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Enable DG16 | S4 PREMIUM |  | Include DG16 in the Open PMS application. This has the same effect as selecting "DG" for "Ext. source 16" under I/O & Hardware setup > Ext. P/Q sources > Type.
External DG ena/dis | Disable DG1 |  |  | Do not include DG1 in the Open PMS application.
External DG ena/dis | Disable DG2 |  |  | Do not include DG2 in the Open PMS application.
External DG ena/dis | Disable DG3 |  |  | Do not include DG3 in the Open PMS application.
External DG ena/dis | Disable DG4 |  |  | Do not include DG4 in the Open PMS application.
External DG ena/dis | Disable DG5 | S4 PREMIUM |  | Do not include DG5 in the Open PMS application.
External DG ena/dis | Disable DG6 | S4 PREMIUM |  | Do not include DG6 in the Open PMS application.
External DG ena/dis | Disable DG7 | S4 PREMIUM |  | Do not include DG7 in the Open PMS application.
External DG ena/dis | Disable DG8 | S4 PREMIUM |  | Do not include DG8 in the Open PMS application.
External DG ena/dis | Disable DG9 | S4 PREMIUM |  | Do not include DG9 in the Open PMS application.
External DG ena/dis | Disable DG10 | S4 PREMIUM |  | Do not include DG10 in the Open PMS application.
External DG ena/dis | Disable DG11 | S4 PREMIUM |  | Do not include DG11 in the Open PMS application.
External DG ena/dis | Disable DG12 | S4 PREMIUM |  | Do not include DG12 in the Open PMS application.
External DG ena/dis | Disable DG13 | S4 PREMIUM |  | Do not include DG13 in the Open PMS application.
External DG ena/dis | Disable DG14 | S4 PREMIUM |  | Do not include DG14 in the Open PMS application.
External DG ena/dis | Disable DG15 | S4 PREMIUM |  | Do not include DG15 in the Open PMS application.
External DG ena/dis | Disable DG16 | S4 PREMIUM |  | Do not include DG16 in the Open PMS application.
External GB feedbacks | GB1 closed feedback |  |  | Treats GB1 as closed (used for feedback from power meters).
External GB feedbacks | GB2 closed feedback |  |  | Treats GB2 as closed (used for feedback from power meters).
External GB feedbacks | GB3 closed feedback |  |  | Treats GB3 as closed (used for feedback from power meters).
External GB feedbacks | GB4 closed feedback |  |  | Treats GB4 as closed (used for feedback from power meters).
External GB feedbacks | GB5 closed feedback | S4 PREMIUM |  | Treats GB5 as closed (used for feedback from power meters).
External GB feedbacks | GB6 closed feedback | S4 PREMIUM |  | Treats GB6 as closed (used for feedback from power meters).
External GB feedbacks | GB7 closed feedback | S4 PREMIUM |  | Treats GB7 as closed (used for feedback from power meters).
External GB feedbacks | GB8 closed feedback | S4 PREMIUM |  | Treats GB8 as closed (used for feedback from power meters).
External GB feedbacks | GB9 closed feedback | S4 PREMIUM |  | Treats GB9 as closed (used for feedback from power meters).
External GB feedbacks | GB10 closed feedback | S4 PREMIUM |  | Treats GB10 as closed (used for feedback from power meters).
External GB feedbacks | GB11 closed feedback | S4 PREMIUM |  | Treats GB11 as closed (used for feedback from power meters).
External GB feedbacks | GB12 closed feedback | S4 PREMIUM |  | Treats GB12 as closed (used for feedback from power meters).
External GB feedbacks | GB13 closed feedback | S4 PREMIUM |  | Treats GB13 as closed (used for feedback from power meters).
External GB feedbacks | GB14 closed feedback | S4 PREMIUM |  | Treats GB14 as closed (used for feedback from power meters).
External GB feedbacks | GB15 closed feedback | S4 PREMIUM |  | Treats GB15 as closed (used for feedback from power meters).
External GB feedbacks | GB16 closed feedback | S4 PREMIUM |  | Treats GB16 as closed (used for feedback from power meters).
External MB feedbacks | MB closed feedback |  |  | Treats MB as closed (used for feedback from power meters).
External MB feedbacks | MB open feedback |  |  | Treats MB as closed (used for feedback from power meters).
External ESB feedbacks | ESB closed feedback |  |  | Treats ESB as closed (used for feedback from power meters).
External ESB feedbacks | ESB open feedback |  |  | Treats ESB as closed (used for feedback from power meters).
CAN Cmd | CAN Cmd 01 active |  |  | Keep M-Logic CAN Cmd 01 active.
CAN Cmd | CAN Cmd 02 active |  |  | Keep M-Logic CAN Cmd 02 active.
CAN Cmd | CAN Cmd 03 active |  |  | Keep M-Logic CAN Cmd 03 active.
CAN Cmd | CAN Cmd 04 active |  |  | Keep M-Logic CAN Cmd 04 active.
CAN Cmd | CAN Cmd 05 active |  |  | Keep M-Logic CAN Cmd 05 active.
CAN Cmd | CAN Cmd 06 active |  |  | Keep M-Logic CAN Cmd 06 active.
CAN Cmd | CAN Cmd 07 active |  |  | Keep M-Logic CAN Cmd 07 active.
CAN Cmd | CAN Cmd 08 active |  |  | Keep M-Logic CAN Cmd 08 active.
CAN Cmd | CAN Cmd 09 active |  |  | Keep M-Logic CAN Cmd 09 active.
CAN Cmd | CAN Cmd 10 active |  |  | Keep M-Logic CAN Cmd 10 active.
CAN Cmd | CAN Cmd 11 active |  |  | Keep M-Logic CAN Cmd 11 active.
CAN Cmd | CAN Cmd 12 active |  |  | Keep M-Logic CAN Cmd 12 active.
CAN Cmd | CAN Cmd 13 active |  |  | Keep M-Logic CAN Cmd 13 active.
CAN Cmd | CAN Cmd 14 active |  |  | Keep M-Logic CAN Cmd 14 active.
CAN Cmd | CAN Cmd 15 active |  |  | Keep M-Logic CAN Cmd 15 active.
CAN Cmd | CAN Cmd 16 active |  |  | Keep M-Logic CAN Cmd 16 active.
Display - View control | Act. view 1 on display |  |  | Show view 1 on the display (Device display > Views)
Display - View control | Act. view 2 on display |  |  | Show view 2 on the display (Device display > Views)
Display - View control | Act. view 3 on display |  |  | Show view 3 on the display (Device display > Views)
Display - View control | Act. view 4 on display |  |  | Show view 4 on the display (Device display > Views)
Display - View control | Act. view 5 on display |  |  | Show view 5 on the display (Device display > Views)
Display - View control | Act. view 6 on display |  |  | Show view 6 on the display (Device display > Views)
Display - View control | Act. view 7 on display |  |  | Show view 7 on the display (Device display > Views)
Display - View control | Act. view 8 on display |  |  | Show view 8 on the display (Device display > Views)
Display - View control | Act. view 9 on display |  |  | Show view 9 on the display (Device display > Views)
Display - View control | Act. view 10 on display |  |  | Show view 10 on the display (Device display > Views)
Display - View control | Act. view 11 on display |  |  | Show view 11 on the display (Device display > Views)
Display - View control | Act. view 12 on display |  |  | Show view 12 on the display (Device display > Views)
Display - View control | Act. view 13 on display |  |  | Show view 13 on the display (Device display > Views)
Display - View control | Act. view 14 on display |  |  | Show view 14 on the display (Device display > Views)
Display - View control | Act. view 15 on display |  |  | Show view 15 on the display (Device display > Views)
Display - View control | Act. view 16 on display |  |  | Show view 16 on the display (Device display > Views)
Display - View control | Act. view 17 on display |  |  | Show view 17 on the display (Device display > Views)
Display - View control | Act. view 18 on display |  |  | Show view 18 on the display (Device display > Views)
Display - View control | Act. view 19 on display |  |  | Show view 19 on the display (Device display > Views)
Display - View control | Act. view 20 on display |  |  | Show view 20 on the display (Device display > Views)
Display - View-line control | Activate view-line 1_1 |  |  | On display view 1, show the view line 1 configured in the USW.
Display - View-line control | Activate view-line 1_2 |  |  | On display view 1, show the view line 2 configured in the USW.
Display - View-line control | Activate view-line 1_3 |  |  | On display view 1, show the view line 3 configured in the USW.
Display - View-line control | Activate view-line 1_4 |  |  | On display view 1, show the view line 4 configured in the USW.
Display - View-line control | Activate view-line 1_5 |  |  | On display view 1, show the view line 5 configured in the USW.
Display - View-line control | Activate view-line 2_1 |  |  | On display view 2, show the view line 1 configured in the USW.
Display - View-line control | Activate view-line 2_2 |  |  | On display view 2, show the view line 2 configured in the USW.
Display - View-line control | Activate view-line 2_3 |  |  | On display view 2, show the view line 3 configured in the USW.
Display - View-line control | Activate view-line 2_4 |  |  | On display view 2, show the view line 4 configured in the USW.
Display - View-line control | Activate view-line 2_5 |  |  | On display view 2, show the view line 5 configured in the USW.
Display - View-line control | Activate view-line 3_1 |  |  | On display view 3, show the view line 1 configured in the USW.
Display - View-line control | Activate view-line 3_2 |  |  | On display view 3, show the view line 2 configured in the USW.
Display - View-line control | Activate view-line 3_3 |  |  | On display view 3, show the view line 3 configured in the USW.
Display - View-line control | Activate view-line 3_4 |  |  | On display view 3, show the view line 4 configured in the USW.
Display - View-line control | Activate view-line 3_5 |  |  | On display view 3, show the view line 5 configured in the USW.
Display - View-line control | Activate view-line 4_1 |  |  | On display view 4, show the view line 1 configured in the USW.
Display - View-line control | Activate view-line 4_2 |  |  | On display view 4, show the view line 2 configured in the USW.
Display - View-line control | Activate view-line 4_3 |  |  | On display view 4, show the view line 3 configured in the USW.
Display - View-line control | Activate view-line 4_4 |  |  | On display view 4, show the view line 4 configured in the USW.
Display - View-line control | Activate view-line 4_5 |  |  | On display view 4, show the view line 5 configured in the USW.
Display - View-line control | Activate view-line 5_1 |  |  | On display view 5, show the view line 1 configured in the USW.
Display - View-line control | Activate view-line 5_2 |  |  | On display view 5, show the view line 2 configured in the USW.
Display - View-line control | Activate view-line 5_3 |  |  | On display view 5, show the view line 3 configured in the USW.
Display - View-line control | Activate view-line 5_4 |  |  | On display view 5, show the view line 4 configured in the USW.
Display - View-line control | Activate view-line 5_5 |  |  | On display view 5, show the view line 5 configured in the USW.
Display - Remote display setup | OFF |  |  | Select the function of the remote display: OFF (non-functional, no alarms from remote display).
Display - Remote display setup | ON: View only |  |  | Select the function of the remote display: ON: View only.
Display - Remote display setup | ON: View and control |  |  | Select the function of the remote display: ON: View and control.
Display - Keyboard commands | Start |  |  | Start the ESS (that is, as if the Start button was pushed on the display).
Display - Keyboard commands | Stop |  |  | Stop the ESS (that is, as if the Stop button was pushed on the display).
Display - Keyboard commands | ESB close |  |  | Close the ESB (that is, as if the ESB close button was pushed on the display).
Display - Keyboard commands | ESB open |  |  | Open the ESB (that is, as if the ESB open button was pushed on the display).
Display - Keyboard commands | MB close |  |  | Close the MB (that is, as if the MB close button was pushed on the display).
Display - Keyboard commands | MB open |  |  | Open the MB (that is, as if the MB open button was pushed on the display).
Display - Keyboard commands | AUTO mode |  |  | Change the controller mode to Auto (that is, as if the Auto button was pushed on the display).
Display - Keyboard commands | MANUAL mode |  |  | Change the controller mode to Manual (that is, as if the Manual button was pushed on the display).
Display - Keyboard commands | Alarm list |  |  | Show the alarm list on the display (that is, as if the Alarm button was pushed on the display).
AOP Led 01 | Not used |  |  | Deactivate AOP LED 01.
AOP Led 01 | Red + Blink |  |  | AOP LED 01 is red and flashes.
AOP Led 01 | Red |  |  | AOP LED 01 is red continuously.
AOP Led 01 | Yellow + Blink |  |  | AOP LED 01 is yellow and flashes.
AOP Led 01 | Yellow |  |  | AOP LED 01 is yellow continuously.
AOP Led 01 | Green + Blink |  |  | AOP LED 01 is green and flashes.
AOP Led 01 | Green |  |  | AOP LED 01 is green continuously.
AOP Led 02 | Not used |  |  | Deactivate AOP LED 02.
AOP Led 02 | Red + Blink |  |  | AOP LED 02 is red and flashes.
AOP Led 02 | Red |  |  | AOP LED 02 is red continuously.
AOP Led 02 | Yellow + Blink |  |  | AOP LED 02 is yellow and flashes.
AOP Led 02 | Yellow |  |  | AOP LED 02 is yellow continuously.
AOP Led 02 | Green + Blink |  |  | AOP LED 02 is green and flashes.
AOP Led 02 | Green |  |  | AOP LED 02 is green continuously.
AOP Led 03 | Not used |  |  | Deactivate AOP LED 03.
AOP Led 03 | Red + Blink |  |  | AOP LED 03 is red and flashes.
AOP Led 03 | Red |  |  | AOP LED 03 is red continuously.
AOP Led 03 | Yellow + Blink |  |  | AOP LED 03 is yellow and flashes.
AOP Led 03 | Yellow |  |  | AOP LED 03 is yellow continuously.
AOP Led 03 | Green + Blink |  |  | AOP LED 03 is green and flashes.
AOP Led 03 | Green |  |  | AOP LED 03 is green continuously.
AOP Led 04 | Not used |  |  | Deactivate AOP LED 04.
AOP Led 04 | Red + Blink |  |  | AOP LED 04 is red and flashes.
AOP Led 04 | Red |  |  | AOP LED 04 is red continuously.
AOP Led 04 | Yellow + Blink |  |  | AOP LED 04 is yellow and flashes.
AOP Led 04 | Yellow |  |  | AOP LED 04 is yellow continuously.
AOP Led 04 | Green + Blink |  |  | AOP LED 04 is green and flashes.
AOP Led 04 | Green |  |  | AOP LED 04 is green continuously.
AOP Led 05 | Not used |  |  | Deactivate AOP LED 05.
AOP Led 05 | Red + Blink |  |  | AOP LED 05 is red and flashes.
AOP Led 05 | Red |  |  | AOP LED 05 is red continuously.
AOP Led 05 | Yellow + Blink |  |  | AOP LED 05 is yellow and flashes.
AOP Led 05 | Yellow |  |  | AOP LED 05 is yellow continuously.
AOP Led 05 | Green + Blink |  |  | AOP LED 05 is green and flashes.
AOP Led 05 | Green |  |  | AOP LED 05 is green continuously.
AOP Led 06 | Not used |  |  | Deactivate AOP LED 06.
AOP Led 06 | Red + Blink |  |  | AOP LED 06 is red and flashes.
AOP Led 06 | Red |  |  | AOP LED 06 is red continuously.
AOP Led 06 | Yellow + Blink |  |  | AOP LED 06 is yellow and flashes.
AOP Led 06 | Yellow |  |  | AOP LED 06 is yellow continuously.
AOP Led 06 | Green + Blink |  |  | AOP LED 06 is green and flashes.
AOP Led 06 | Green |  |  | AOP LED 06 is green continuously.
AOP Led 07 | Not used |  |  | Deactivate AOP LED 07.
AOP Led 07 | Red + Blink |  |  | AOP LED 07 is red and flashes.
AOP Led 07 | Red |  |  | AOP LED 07 is red continuously.
AOP Led 07 | Yellow + Blink |  |  | AOP LED 07 is yellow and flashes.
AOP Led 07 | Yellow |  |  | AOP LED 07 is yellow continuously.
AOP Led 07 | Green + Blink |  |  | AOP LED 07 is green and flashes.
AOP Led 07 | Green |  |  | AOP LED 07 is green continuously.
AOP Led 08 | Not used |  |  | Deactivate AOP LED 08.
AOP Led 08 | Red + Blink |  |  | AOP LED 08 is red and flashes.
AOP Led 08 | Red |  |  | AOP LED 08 is red continuously.
AOP Led 08 | Yellow + Blink |  |  | AOP LED 08 is yellow and flashes.
AOP Led 08 | Yellow |  |  | AOP LED 08 is yellow continuously.
AOP Led 08 | Green + Blink |  |  | AOP LED 08 is green and flashes.
AOP Led 08 | Green |  |  | AOP LED 08 is green continuously.
AOP Led 09 | Not used |  |  | Deactivate AOP LED 09.
AOP Led 09 | Red + Blink |  |  | AOP LED 09 is red and flashes.
AOP Led 09 | Red |  |  | AOP LED 09 is red continuously.
AOP Led 09 | Yellow + Blink |  |  | AOP LED 09 is yellow and flashes.
AOP Led 09 | Yellow |  |  | AOP LED 09 is yellow continuously.
AOP Led 09 | Green + Blink |  |  | AOP LED 09 is green and flashes.
AOP Led 09 | Green |  |  | AOP LED 09 is green continuously.
AOP Led 10 | Not used |  |  | Deactivate AOP LED 10.
AOP Led 10 | Red + Blink |  |  | AOP LED 10 is red and flashes.
AOP Led 10 | Red |  |  | AOP LED 10 is red continuously.
AOP Led 10 | Yellow + Blink |  |  | AOP LED 10 is yellow and flashes.
AOP Led 10 | Yellow |  |  | AOP LED 10 is yellow continuously.
AOP Led 10 | Green + Blink |  |  | AOP LED 10 is green and flashes.
AOP Led 10 | Green |  |  | AOP LED 10 is green continuously.
AOP Led 11 | Not used |  |  | Deactivate AOP LED 11.
AOP Led 11 | Red + Blink |  |  | AOP LED 11 is red and flashes.
AOP Led 11 | Red |  |  | AOP LED 11 is red continuously.
AOP Led 11 | Yellow + Blink |  |  | AOP LED 11 is yellow and flashes.
AOP Led 11 | Yellow |  |  | AOP LED 11 is yellow continuously.
AOP Led 11 | Green + Blink |  |  | AOP LED 11 is green and flashes.
AOP Led 11 | Green |  |  | AOP LED 11 is green continuously.
AOP Led 12 | Not used |  |  | Deactivate AOP LED 12.
AOP Led 12 | Red + Blink |  |  | AOP LED 12 is red and flashes.
AOP Led 12 | Red |  |  | AOP LED 12 is red continuously.
AOP Led 12 | Yellow + Blink |  |  | AOP LED 12 is yellow and flashes.
AOP Led 12 | Yellow |  |  | AOP LED 12 is yellow continuously.
AOP Led 12 | Green + Blink |  |  | AOP LED 12 is green and flashes.
AOP Led 12 | Green |  |  | AOP LED 12 is green continuously.
AOP Led 13 | Not used |  |  | Deactivate AOP LED 13.
AOP Led 13 | Red + Blink |  |  | AOP LED 13 is red and flashes.
AOP Led 13 | Red |  |  | AOP LED 13 is red continuously.
AOP Led 13 | Yellow + Blink |  |  | AOP LED 13 is yellow and flashes.
AOP Led 13 | Yellow |  |  | AOP LED 13 is yellow continuously.
AOP Led 13 | Green + Blink |  |  | AOP LED 13 is green and flashes.
AOP Led 13 | Green |  |  | AOP LED 13 is green continuously.
AOP Led 14 | Not used |  |  | Deactivate AOP LED 14.
AOP Led 14 | Red + Blink |  |  | AOP LED 14 is red and flashes.
AOP Led 14 | Red |  |  | AOP LED 14 is red continuously.
AOP Led 14 | Yellow + Blink |  |  | AOP LED 14 is yellow and flashes.
AOP Led 14 | Yellow |  |  | AOP LED 14 is yellow continuously.
AOP Led 14 | Green + Blink |  |  | AOP LED 14 is green and flashes.
AOP Led 14 | Green |  |  | AOP LED 14 is green continuously.
AOP Led 15 | Not used |  |  | Deactivate AOP LED 15.
AOP Led 15 | Red + Blink |  |  | AOP LED 15 is red and flashes.
AOP Led 15 | Red |  |  | AOP LED 15 is red continuously.
AOP Led 15 | Yellow + Blink |  |  | AOP LED 15 is yellow and flashes.
AOP Led 15 | Yellow |  |  | AOP LED 15 is yellow continuously.
AOP Led 15 | Green + Blink |  |  | AOP LED 15 is green and flashes.
AOP Led 15 | Green |  |  | AOP LED 15 is green continuously.
AOP Led 16 | Not used |  |  | Deactivate AOP LED 16.
AOP Led 16 | Red + Blink |  |  | AOP LED 16 is red and flashes.
AOP Led 16 | Red |  |  | AOP LED 16 is red continuously.
AOP Led 16 | Yellow + Blink |  |  | AOP LED 16 is yellow and flashes.
AOP Led 16 | Yellow |  |  | AOP LED 16 is yellow continuously.
AOP Led 16 | Green + Blink |  |  | AOP LED 16 is green and flashes.
AOP Led 16 | Green |  |  | AOP LED 16 is green continuously.
General Purpose PID commands | PID1 Activate |  | 1190 | Activate general purpose PID1.
General Purpose PID commands | PID1 force min. outp. |  | 1190 | Force the output of PID1 to the value in PID1 outp. > M-logic min event setpoint.
General Purpose PID commands | PID1 force max. outp. |  | 1190 | Force the output of PID1 to the value in PID1 outp. > M-logic max event setpoint.
General Purpose PID commands | PID1 reset |  | 1190 | Force the output of PID1 to the value in PID1 outp. > Analogue offset.
General Purpose PID commands | PID1 freeze output |  | 1190 | Freeze the output of PID1 at its current value.
General Purpose PID commands | PID2 Activate |  | 1190 | Activate general purpose PID2.
General Purpose PID commands | PID2 force min. outp. |  | 1190 | Force the output of PID2 to the value in PID2 outp. > M-logic min event setpoint.
General Purpose PID commands | PID2 force max. outp. |  | 1190 | Force the output of PID2 to the value in PID2 outp. > M-logic max event setpoint.
General Purpose PID commands | PID2 reset |  | 1190 | Force the output of PID2 to the value in PID2 outp. > Analogue offset.
General Purpose PID commands | PID2 freeze output |  | 1190 | Freeze the output of PID2 at its current value.
General Purpose PID commands | PID3 Activate |  | 1190 | Activate general purpose PID3.
General Purpose PID commands | PID3 force min. outp. |  | 1190 | Force the output of PID3 to the value in PID3 outp. > M-logic min event setpoint.
General Purpose PID commands | PID3 force max. outp. |  | 1190 | Force the output of PID3 to the value in PID3 outp. > M-logic max event setpoint.
General Purpose PID commands | PID3 reset |  | 1190 | Force the output of PID3 to the value in PID3 outp. > Analogue offset.
General Purpose PID commands | PID3 freeze output |  | 1190 | Freeze the output of PID3 at its current value.
General Purpose PID commands | PID4 Activate |  | 1190 | Activate general purpose PID4.
General Purpose PID commands | PID4 force min. outp. |  | 1190 | Force the output of PID4 to the value in PID4 outp. > M-logic min event setpoint.
General Purpose PID commands | PID4 force max. outp. |  | 1190 | Force the output of PID4 to the value in PID4 outp. > M-logic max event setpoint.
General Purpose PID commands | PID4 reset |  | 1190 | Force the output of PID4 to the value in PID4 outp. > Analogue offset.
General Purpose PID commands | PID4 freeze output |  | 1190 | Freeze the output of PID4 at its current value.
General Purpose PID commands | PID1 activate input 1 |  | 1190 | For PID1, change PID1 inp. > Enable 1 to On.
General Purpose PID commands | PID1 activate input 2 |  | 1190 | For PID1, change PID1 inp. > Enable 2 to On.
General Purpose PID commands | PID1 activate input 3 |  | 1190 | For PID1, change PID1 inp. > Enable 3 to On.
General Purpose PID commands | PID2 activate input 1 |  | 1190 | For PID2, change PID2 inp. > Enable 1 to On.
General Purpose PID commands | PID2 activate input 2 |  | 1190 | For PID2, change PID2 inp. > Enable 2 to On.
General Purpose PID commands | PID2 activate input 3 |  | 1190 | For PID2, change PID2 inp. > Enable 3 to On.
General Purpose PID commands | PID3 activate input 1 |  | 1190 | For PID3, change PID3 inp. > Enable 1 to On.
General Purpose PID commands | PID3 activate input 2 |  | 1190 | For PID3, change PID3 inp. > Enable 2 to On.
General Purpose PID commands | PID3 activate input 3 |  | 1190 | For PID3, change PID3 inp. > Enable 3 to On.
General Purpose PID commands | PID4 activate input 1 |  | 1190 | For PID4, change PID4 inp. > Enable 1 to On.
General Purpose PID commands | PID4 activate input 2 |  | 1190 | For PID4, change PID4 inp. > Enable 2 to On.
General Purpose PID commands | PID4 activate input 3 |  | 1190 | For PID4, change PID4 inp. > Enable 3 to On.
General Purpose PID commands | PID1 deactivate input 1 |  | 1190 | For PID1, change PID1 inp. > Enable 1 to Off.
General Purpose PID commands | PID1 deactivate input 2 |  | 1190 | For PID1, change PID1 inp. > Enable 2 to Off.
General Purpose PID commands | PID1 deactivate input 3 |  | 1190 | For PID1, change PID1 inp. > Enable 3 to Off.
General Purpose PID commands | PID2 deactivate input 1 |  | 1190 | For PID2, change PID2 inp. > Enable 1 to Off.
General Purpose PID commands | PID2 deactivate input 2 |  | 1190 | For PID2, change PID2 inp. > Enable 2 to Off.
General Purpose PID commands | PID2 deactivate input 3 |  | 1190 | For PID2, change PID2 inp. > Enable 3 to Off.
General Purpose PID commands | PID3 deactivate input 1 |  | 1190 | For PID3, change PID3 inp. > Enable 1 to Off.
General Purpose PID commands | PID3 deactivate input 2 |  | 1190 | For PID3, change PID3 inp. > Enable 2 to Off.
General Purpose PID commands | PID3 deactivate input 3 |  | 1190 | For PID3, change PID3 inp. > Enable 3 to Off.
General Purpose PID commands | PID4 deactivate input 1 |  | 1190 | For PID4, change PID4 inp. > Enable 1 to Off.
General Purpose PID commands | PID4 deactivate input 2 |  | 1190 | For PID4, change PID4 inp. > Enable 2 to Off.
General Purpose PID commands | PID4 deactivate input 3 |  | 1190 | For PID4, change PID4 inp. > Enable 3 to Off.
Flip flops | Flip flop set 1 |  |  | Change the output state of M-Logic flip flop 1 to High.
Flip flops | Flip flop set 2 |  |  | Change the output state of M-Logic flip flop 2 to High.
Flip flops | Flip flop set 3 |  |  | Change the output state of M-Logic flip flop 3 to High.
Flip flops | Flip flop set 4 |  |  | Change the output state of M-Logic flip flop 4 to High.
Flip flops | Flip flop set 5 |  |  | Change the output state of M-Logic flip flop 5 to High.
Flip flops | Flip flop set 6 |  |  | Change the output state of M-Logic flip flop 6 to High.
Flip flops | Flip flop set 7 |  |  | Change the output state of M-Logic flip flop 7 to High.
Flip flops | Flip flop set 8 |  |  | Change the output state of M-Logic flip flop 8 to High.
Flip flops | Flip flop set 9 |  |  | Change the output state of M-Logic flip flop 9 to High.
Flip flops | Flip flop set 10 |  |  | Change the output state of M-Logic flip flop 10 to High.
Flip flops | Flip flop set 11 |  |  | Change the output state of M-Logic flip flop 11 to High.
Flip flops | Flip flop set 12 |  |  | Change the output state of M-Logic flip flop 12 to High.
Flip flops | Flip flop set 13 |  |  | Change the output state of M-Logic flip flop 13 to High.
Flip flops | Flip flop set 14 |  |  | Change the output state of M-Logic flip flop 14 to High.
Flip flops | Flip flop set 15 |  |  | Change the output state of M-Logic flip flop 15 to High.
Flip flops | Flip flop set 16 |  |  | Change the output state of M-Logic flip flop 16 to High.
Flip flops | Flip flop reset 1 |  |  | Change the output state of M-Logic flip flop 1 to Low.
Flip flops | Flip flop reset 2 |  |  | Change the output state of M-Logic flip flop 2 to Low.
Flip flops | Flip flop reset 3 |  |  | Change the output state of M-Logic flip flop 3 to Low.
Flip flops | Flip flop reset 4 |  |  | Change the output state of M-Logic flip flop 4 to Low.
Flip flops | Flip flop reset 5 |  |  | Change the output state of M-Logic flip flop 5 to Low.
Flip flops | Flip flop reset 6 |  |  | Change the output state of M-Logic flip flop 6 to Low.
Flip flops | Flip flop reset 7 |  |  | Change the output state of M-Logic flip flop 7 to Low.
Flip flops | Flip flop reset 8 |  |  | Change the output state of M-Logic flip flop 8 to Low.
Flip flops | Flip flop reset 9 |  |  | Change the output state of M-Logic flip flop 9 to Low.
Flip flops | Flip flop reset 10 |  |  | Change the output state of M-Logic flip flop 10 to Low.
Flip flops | Flip flop reset 11 |  |  | Change the output state of M-Logic flip flop 11 to Low.
Flip flops | Flip flop reset 12 |  |  | Change the output state of M-Logic flip flop 12 to Low.
Flip flops | Flip flop reset 13 |  |  | Change the output state of M-Logic flip flop 13 to Low.
Flip flops | Flip flop reset 14 |  |  | Change the output state of M-Logic flip flop 14 to Low.
Flip flops | Flip flop reset 15 |  |  | Change the output state of M-Logic flip flop 15 to Low.
Flip flops | Flip flop reset 16 |  |  | Change the output state of M-Logic flip flop 16 to Low.
Flip flops | Flip flop toggle 1 |  |  | Change the output state of M-Logic flip flop 1 from Low to High, or from High to Low.
Flip flops | Flip flop toggle 2 |  |  | Change the output state of M-Logic flip flop 2 from Low to High, or from High to Low.
Flip flops | Flip flop toggle 3 |  |  | Change the output state of M-Logic flip flop 3 from Low to High, or from High to Low.
Flip flops | Flip flop toggle 4 |  |  | Change the output state of M-Logic flip flop 4 from Low to High, or from High to Low.
Flip flops | Flip flop toggle 5 |  |  | Change the output state of M-Logic flip flop 5 from Low to High, or from High to Low.
Flip flops | Flip flop toggle 6 |  |  | Change the output state of M-Logic flip flop 6 from Low to High, or from High to Low.
Flip flops | Flip flop toggle 7 |  |  | Change the output state of M-Logic flip flop 7 from Low to High, or from High to Low.
Flip flops | Flip flop toggle 8 |  |  | Change the output state of M-Logic flip flop 8 from Low to High, or from High to Low.
Flip flops | Flip flop toggle 9 |  |  | Change the output state of M-Logic flip flop 9 from Low to High, or from High to Low.
Flip flops | Flip flop toggle 10 |  |  | Change the output state of M-Logic flip flop 10 from Low to High, or from High to Low.
Flip flops | Flip flop toggle 11 |  |  | Change the output state of M-Logic flip flop 11 from Low to High, or from High to Low.
Flip flops | Flip flop toggle 12 |  |  | Change the output state of M-Logic flip flop 12 from Low to High, or from High to Low.
Flip flops | Flip flop toggle 13 |  |  | Change the output state of M-Logic flip flop 13 from Low to High, or from High to Low.
Flip flops | Flip flop toggle 14 |  |  | Change the output state of M-Logic flip flop 14 from Low to High, or from High to Low.
Flip flops | Flip flop toggle 15 |  |  | Change the output state of M-Logic flip flop 15 from Low to High, or from High to Low.
Flip flops | Flip flop toggle 16 |  |  | Change the output state of M-Logic flip flop 16 from Low to High, or from High to Low.
Oneshots | Oneshot set 1 |  | 1120 | Activate M-Logic Oneshot 1 for a short time (about 100 ms), then deactivate.
Oneshots | Oneshot set 2 |  | 1120 | Activate M-Logic Oneshot 2 for a short time (about 100 ms), then deactivate.
Oneshots | Oneshot set 3 |  | 1120 | Activate M-Logic Oneshot 3 for a short time (about 100 ms), then deactivate.
Oneshots | Oneshot set 4 |  | 1120 | Activate M-Logic Oneshot 4 for a short time (about 100 ms), then deactivate.
Oneshots | Oneshot set 5 |  | 1120 | Activate M-Logic Oneshot 5 for a short time (about 100 ms), then deactivate.
Oneshots | Oneshot set 6 |  | 1120 | Activate M-Logic Oneshot 6 for a short time (about 100 ms), then deactivate.
Oneshots | Oneshot set 7 |  | 1120 | Activate M-Logic Oneshot 7 for a short time (about 100 ms), then deactivate.
Oneshots | Oneshot set 8 |  | 1120 | Activate M-Logic Oneshot 8 for a short time (about 100 ms), then deactivate.
Oneshots | Oneshot set 9 |  | 1120 | Activate M-Logic Oneshot 9 for a short time (about 100 ms), then deactivate.
Oneshots | Oneshot set 10 |  | 1120 | Activate M-Logic Oneshot 10 for a short time (about 100 ms), then deactivate.
Oneshots | Oneshot set 11 |  | 1120 | Activate M-Logic Oneshot 11 for a short time (about 100 ms), then deactivate.
Oneshots | Oneshot set 12 |  | 1120 | Activate M-Logic Oneshot 12 for a short time (about 100 ms), then deactivate.
Oneshots | Oneshot set 13 |  | 1120 | Activate M-Logic Oneshot 13 for a short time (about 100 ms), then deactivate.
Oneshots | Oneshot set 14 |  | 1120 | Activate M-Logic Oneshot 14 for a short time (about 100 ms), then deactivate.
Oneshots | Oneshot set 15 |  | 1120 | Activate M-Logic Oneshot 15 for a short time (about 100 ms), then deactivate.
Oneshots | Oneshot set 16 |  | 1120 | Activate M-Logic Oneshot 16 for a short time (about 100 ms), then deactivate.
Power Limit Inputs (RRCR) | Power limit input 01 |  |  | For RRCR, the power set point input I1 from the system operator is ON.
Power Limit Inputs (RRCR) | Power limit input 02 |  |  | For RRCR, the power set point input I2 from the system operator is ON.
Power Limit Inputs (RRCR) | Power limit input 03 |  |  | For RRCR, the power set point input I3 from the system operator is ON.
Power Limit Inputs (RRCR) | Power limit input 04 |  |  | For RRCR, the power set point input I4 from the system operator is ON.
Easy connect | Add ESS |  |  | Use Easy connect to add an ESS to the application drawing.
Easy connect | Remove ESS |  |  | Use Easy connect to remove an ESS from the application drawing.
Easy connect | Select yes on display |  |  | During Easy connect, this has the same effect as the operator selecting Yes on the display.
Easy connect | Select no on display |  |  | During Easy connect, this has the same effect as the operator selecting No on the display.
Easy connect | Enable Easy connect |  | 1160 | Enable Easy connect (parameter 8023).
Easy connect | Disable Easy connect |  | 1160 | Disable Easy connect (parameter 8023).
Viewline LED Lamps | LED 1 On |  | 1130 | Show LED 1 (a function in display view configuration) as ON.
Viewline LED Lamps | LED 1 Blink |  | 1130 | Show LED 1 (a function in display view configuration) as blinking.
Viewline LED Lamps | LED 2 On |  | 1130 | Show LED 2 (a function in display view configuration) as ON.
Viewline LED Lamps | LED 2 Blink |  | 1130 | Show LED 2 (a function in display view configuration) as blinking.
Viewline LED Lamps | LED 3 On |  | 1130 | Show LED 3 (a function in display view configuration) as ON.
Viewline LED Lamps | LED 3 Blink |  | 1130 | Show LED 3 (a function in display view configuration) as blinking.
Viewline LED Lamps | LED 4 On |  | 1130 | Show LED 4 (a function in display view configuration) as ON.
Viewline LED Lamps | LED 4 Blink |  | 1130 | Show LED 4 (a function in display view configuration) as blinking.
Viewline LED Lamps | LED 5 On |  | 1130 | Show LED 5 (a function in display view configuration) as ON.
Viewline LED Lamps | LED 5 Blink |  | 1130 | Show LED 5 (a function in display view configuration) as blinking.
M-Logic event counters | M-logic event counter 1 |  |  | Add 1 to M-Logic event counter 1 (Counters > M-logic event counters).
M-Logic event counters | M-logic event counter 2 |  |  | Add 1 to M-Logic event counter 2 (Counters > M-logic event counters).
M-Logic event counters | M-logic event counter 3 |  |  | Add 1 to M-Logic event counter 3 (Counters > M-logic event counters).
M-Logic event counters | M-logic event counter 4 |  |  | Add 1 to M-Logic event counter 4 (Counters > M-logic event counters).
M-Logic event counters | M-logic event counter 5 |  |  | Add 1 to M-Logic event counter 5 (Counters > M-logic event counters).
M-Logic event counters | M-logic event counter 6 |  |  | Add 1 to M-Logic event counter 6 (Counters > M-logic event counters).
M-Logic event counters | M-logic event counter 7 |  |  | Add 1 to M-Logic event counter 7 (Counters > M-logic event counters).
M-Logic event counters | M-logic event counter 8 |  |  | Add 1 to M-Logic event counter 8 (Counters > M-logic event counters).
M-Logic event counters | M-logic event reset counter 1 |  |  | Reset M-Logic event counter 1.
M-Logic event counters | M-logic event reset counter 2 |  |  | Reset M-Logic event counter 2.
M-Logic event counters | M-logic event reset counter 3 |  |  | Reset M-Logic event counter 3.
M-Logic event counters | M-logic event reset counter 4 |  |  | Reset M-Logic event counter 4.
M-Logic event counters | M-logic event reset counter 5 |  |  | Reset M-Logic event counter 5.
M-Logic event counters | M-logic event reset counter 6 |  |  | Reset M-Logic event counter 6.
M-Logic event counters | M-logic event reset counter 7 |  |  | Reset M-Logic event counter 7.
M-Logic event counters | M-logic event reset counter 8 |  |  | Reset M-Logic event counter 8.