## Description
SGC 120 Mk II Modbus descriptions
Software version
The information contained in these tables (Revision C) is applicable to software version R18.0 of the SGC 120 Mk II.
Row | Hyperlink index
11 | Modbus function codes
19 | Holding_Read_register
43 | Enum_list
Back to index | Modbus function codes
| Function code | Description
| 03 | Reads one or more 16‑bit holding registers.
| 04 | Reads one or more 16‑bit input registers.
| 16 | Writes values to one or more 16‑bit holding registers.
Back to index | Holding & Read register
| Function code | Effect
| 03 or 04 | Read
| 16 | Write
| Function group | Description
| AC measurement | Read the operating value of the associated AC measurement.
| Energy counter | Read the counter value.
| Engine measurement | Read the operating value of the associated engine measurement.
| Running hours | Read the running hours value.
| Alarm status | Read the alarm status.
| Input and output diagnostics | Read the state of a digital input or output on the controller.
| DG status | Read the status of the genset.
| CPCB IV+ Alarm Status | Read the CPCB IV alarm status.
| EGR Modbus | Read EGR related data via Modbus communication.
| DTC status | Read the DTC status.
| DTC Value | Read the DTC value reported by the engine.
| Custom Sensor | Read the Custom Sensor value.
| EIC Data Over Modbus | Read EIC data via Modbus communication.
| DG mode change | Write the controller changes the state of the genset if a valid value is entered.
| DTC status | Write the DTC status.
Back to index | ENUM list
Register 65 to 76, 110 and 111 ( 03; 04)
| Decimal value | Interpretation
| 00 | Alarm disabled
| 01 | Alarm not active
| 02 | Warning alarm active
| 03 | Shutdown alarm active
| 04 | Electrical trip alarm active
| 05 | Notification

## Holding & Read (03;04;16)
Function group | Modbus address | Bit | Modbus function code | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | Enum
Protocol revision | 0 |  | 03; 04 | Protocol revision | - | - | - | - | -
AC measurement | 1 |  | 03; 04 | Generator L1-n voltage | INT16u | - | 0.1 | V | -
AC measurement | 2 |  | 03; 04 | Generator L2-n voltage | INT16u | - | 0.1 | V | -
AC measurement | 3 |  | 03; 04 | Generator L3-n voltage | INT16u | - | 0.1 | V | -
AC measurement | 4 |  | 03; 04 | Generator L1-L2 voltage | INT16u | - | 0.1 | V | -
AC measurement | 5 |  | 03; 04 | Generator L2-L3 voltage | INT16u | - | 0.1 | V | -
AC measurement | 6 |  | 03; 04 | Generator L3-L1 voltage | INT16u | - | 0.1 | V | -
AC measurement | 7 |  | 03; 04 | Generator R frequency | INT16u | - | 0.1 | Hz | -
AC measurement | 8 |  | 03; 04 | Generator Y frequency | INT16u | - | 0.1 | Hz | -
AC measurement | 9 |  | 03; 04 | Generator B frequency | INT16u | - | 0.1 | Hz | -
AC measurement | 10 |  | 03; 04 | Generator power factor L1 | INT16s | - | 0.01 | - | -
AC measurement | 11 |  | 03; 04 | Generator power factor L2 | INT16s | - | 0.01 | - | -
AC measurement | 12 |  | 03; 04 | Generator power factor L3 | INT16s | - | 0.01 | - | -
AC measurement | 13 |  | 03; 04 | Generator average power factor | INT16s | - | 0.01 | - | -
AC measurement | 14 |  | 03; 04 | Mains L1-n voltage | INT16u | - | 0.1 | V | -
AC measurement | 15 |  | 03; 04 | Mains L2-n voltage | INT16u | - | 0.1 | V | -
AC measurement | 16 |  | 03; 04 | Mains L3-n voltage | INT16u | - | 0.1 | V | -
AC measurement | 17 |  | 03; 04 | Mains L1-L2 voltage | INT16u | - | 0.1 | V | -
AC measurement | 18 |  | 03; 04 | Mains L2-L3 voltage | INT16u | - | 0.1 | V | -
AC measurement | 19 |  | 03; 04 | Mains L3-L1 voltage | INT16u | - | 0.1 | V | -
AC measurement | 20 |  | 03; 04 | Mains R frequency | INT16u | - | 0.1 | Hz | -
AC measurement | 21 |  | 03; 04 | Mains Y frequency | INT16u | - | 0.1 | Hz | -
AC measurement | 22 |  | 03; 04 | Mains B frequency | INT16u | - | 0.1 | Hz | -
AC measurement | 23 |  | 03; 04 | Load L1 current | INT16u | - | 0.1 | A | -
AC measurement | 24 |  | 03; 04 | Load L2 current | INT16u | - | 0.1 | A | -
AC measurement | 25 |  | 03; 04 | Load L3 current | INT16u | - | 0.1 | A | -
AC measurement | 26 |  | 03; 04 | Load L1 power | INT16s | - | 0.1 | kW | -
AC measurement | 27 |  | 03; 04 | Load L2 power | INT16s | - | 0.1 | kW | -
AC measurement | 28 |  | 03; 04 | Load L3 power | INT16s | - | 0.1 | kW | -
AC measurement | 29 |  | 03; 04 | Load total power | INT16s | - | 0.1 | kW | -
AC measurement | 30 |  | 03; 04 | Percentage Load | INT16s | - | 1 | kW | -
AC measurement | 31 |  | 03; 04 | Load L1 apparent power | INT16u | - | 0.1 | kVA | -
AC measurement | 32 |  | 03; 04 | Load L2 apparent power | INT16u | - | 0.1 | kVA | -
AC measurement | 33 |  | 03; 04 | Load L3 apparent power | INT16u | - | 0.1 | kVA | -
AC measurement | 34 |  | 03; 04 | Load total apparent power | INT16u | - | 0.1 | kVA | -
AC measurement | 35 |  | 03; 04 | Load L1 reactive power | INT16u | - | 0.1 | kVAR | -
AC measurement | 36 |  | 03; 04 | Load L2 reactive power | INT16u | - | 0.1 | kVAR | -
AC measurement | 37 |  | 03; 04 | Load L3 reactive power | INT16u | - | 0.1 | kVAR | -
AC measurement | 38 |  | 03; 04 | Load total reactive power | INT16u | - | 0.1 | kVAR | -
Energy counter | 39 |  | 03; 04 | Generator cumulative energy | FLOAT32 | CDAB | 0.1 | kWh | -
Energy counter | 41 |  | 03; 04 | Generator cumulative apparent energy | FLOAT32 | CDAB | 0.1 | kVAh | -
Energy counter | 43 |  | 03; 04 | Generator cumulative reactive energy | FLOAT32 | CDAB | 0.1 | kVARh | -
Energy counter | 45 |  | 03; 04 | Mains cumulative energy | FLOAT32 | CDAB | 0.1 | kWh | -
Energy counter | 47 |  | 03; 04 | Mains cumulative apparent energy | FLOAT32 | CDAB | 0.1 | kVAh | -
Energy counter | 49 |  | 03; 04 | Mains cumulative reactive energy | FLOAT32 | CDAB | 0.1 | kVARh | -
Engine measurement | 51 |  | 03; 04 | Oil pressure & LOP From ECU | INT16u | - | 0.1 | bar | -
Engine measurement | 52 |  | 03; 04 | Coolant temperature & CLNT Temp from ECU | INT16s | - | 0.1 | °C | -
Engine measurement | 53 |  | 03; 04 | Fuel level | INT16u | - | 1 | % | -
Engine measurement | 54 |  | 03; 04 | Fuel Level in litres | INT16u | - | 0.1 | L | -
Engine measurement | 55 |  | 03; 04 | Charge alternator voltage | INT16u | - | 0.1 | V | -
Engine measurement | 56 |  | 03; 04 | Battery voltage & Battery Vtg from ECU | INT16u | - | 0.1 | V | -
Engine measurement | 57 |  | 03; 04 | Engine speed & Speed from ECU | INT16u | - | 1 | RPM | -
Engine measurement | 58 |  | 03; 04 | No of starts | INT16u | - | 1 | - | -
Engine measurement | 59 |  | 03; 04 | No of trips | INT16u | - | 1 | - | -
Running hours | 60 |  | 03; 04 | Engine run hours from ECU (more than 65535 from ECU) | INT32u | - | 1 | hr | -
Running hours | 62 |  | 03; 04 | Engine run minutes | INT16u | - | 1 | min | -
Running hours | 63 |  | 03; 04 | Mains run hrs | INT16u | - | 1 | hr | -
Running hours | 64 |  | 03; 04 | Mains run minutes | INT16u | - | 1 | min | -
Alarm Status for Alarm 1 | 65 | 1 | 03; 04 | Water level switch | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 1 | 65 | 2 | 03; 04 | Water level switch | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 1 | 65 | 3 | 03; 04 | Water level switch | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 1 | 65 | 4 | 03; 04 | Water level switch | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 1 | 65 | 5 | 03; 04 | Low fuel level | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 1 | 65 | 6 | 03; 04 | Low fuel level | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 1 | 65 | 7 | 03; 04 | Low fuel level | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 1 | 65 | 8 | 03; 04 | Low fuel level | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 1 | 65 | 9 | 03; 04 | High coolant temperature | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 1 | 65 | 10 | 03; 04 | High coolant temperature | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 1 | 65 | 11 | 03; 04 | High coolant temperature | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 1 | 65 | 12 | 03; 04 | High coolant temperature | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 1 | 65 | 13 | 03; 04 | Low oil pressure | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 1 | 65 | 14 | 03; 04 | Low oil pressure | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 1 | 65 | 15 | 03; 04 | Low oil pressure | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 1 | 65 | 16 | 03; 04 | Low oil pressure | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 66 | 16 | 03; 04 | Under speed | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 67 | 1 | 03; 04 | Fail to stop | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 67 | 2 | 03; 04 | Fail to stop | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 67 | 3 | 03; 04 | Fail to stop | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 67 | 4 | 03; 04 | Fail to stop | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 67 | 5 | 03; 04 | Fail to start | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 67 | 6 | 03; 04 | Fail to start | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 67 | 7 | 03; 04 | Fail to start | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 67 | 8 | 03; 04 | Fail to start | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 67 | 9 | 03; 04 | Over speed | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 67 | 10 | 03; 04 | Over speed | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 67 | 11 | 03; 04 | Over speed | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 67 | 12 | 03; 04 | Over speed | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 67 | 13 | 03; 04 | Under speed | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 67 | 14 | 03; 04 | Under speed | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 2 | 67 | 15 | 03; 04 | Under speed | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 1 | 03; 04 | Generator high Frequency | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 1 | 03; 04 | Emergency stop | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 2 | 03; 04 | Generator high Frequency | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 2 | 03; 04 | Emergency stop | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 3 | 03; 04 | Generator high Frequency | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 3 | 03; 04 | Emergency stop | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 4 | 03; 04 | Generator high Frequency | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 4 | 03; 04 | Emergency stop | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 5 | 03; 04 | Generator low frequency | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 5 | 03; 04 | Unbalanced load | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 6 | 03; 04 | Generator low frequency | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 6 | 03; 04 | Unbalanced load | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 7 | 03; 04 | Generator low frequency | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 7 | 03; 04 | Unbalanced load | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 8 | 03; 04 | Generator low frequency | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 8 | 03; 04 | Unbalanced load | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 9 | 03; 04 | High shelter temp | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 9 | 03; 04 | Generator overload | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 10 | 03; 04 | High shelter temp | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 10 | 03; 04 | Generator overload | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 11 | 03; 04 | High shelter temp | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 11 | 03; 04 | Generator overload | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 12 | 03; 04 | High shelter temp | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 12 | 03; 04 | Generator overload | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 13 | 03; 04 | Shelter temperature open circuit | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 13 | 03; 04 | Generator high current | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 14 | 03; 04 | Shelter temperature open circuit | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 14 | 03; 04 | Generator high current | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 15 | 03; 04 | Shelter temperature open circuit | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 15 | 03; 04 | Generator high current | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 3 | 68 | 16 | 03; 04 | Shelter temperature open circuit | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 4 | 68 | 16 | 03; 04 | Generator high current | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 1 | 03; 04 | Red lamp (Automation) | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 2 | 03; 04 | Red lamp (Automation) | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 3 | 03; 04 | Red lamp (Automation) | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 4 | 03; 04 | Red lamp (Automation) | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 5 | 03; 04 | MIL lamp (Automation) | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 6 | 03; 04 | MIL lamp (Automation) | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 7 | 03; 04 | MIL lamp (Automation) | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 8 | 03; 04 | MIL lamp (Automation) | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 9 | 03; 04 | Oil filter maintenance / filter maintenance | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 10 | 03; 04 | Oil filter maintenance / filter maintenance | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 11 | 03; 04 | Oil filter maintenance / filter maintenance | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 12 | 03; 04 | Oil filter maintenance / filter maintenance | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 13 | 03; 04 | Charge alternator failure | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 14 | 03; 04 | Charge alternator failure | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 15 | 03; 04 | Charge alternator failure | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 5 | 69 | 16 | 03; 04 | Charge alternator failure | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 1 | 03; 04 | Reverse Power Detected | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 2 | 03; 04 | Reverse Power Detected | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 3 | 03; 04 | Reverse Power Detected | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 4 | 03; 04 | Reverse Power Detected | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 5 | 03; 04 | Engine Temperature Circuit open | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 6 | 03; 04 | Engine Temperature Circuit open | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 7 | 03; 04 | Engine Temperature Circuit open | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 8 | 03; 04 | Engine Temperature Circuit open | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 9 | 03; 04 | Battery high voltage | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 10 | 03; 04 | Battery high voltage | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 11 | 03; 04 | Battery high voltage | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 12 | 03; 04 | Battery high voltage | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 13 | 03; 04 | Battery low voltage | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 14 | 03; 04 | Battery low voltage | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 15 | 03; 04 | Battery low voltage | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 6 | 70 | 16 | 03; 04 | Battery low voltage | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 1 | 03; 04 | Reserved | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 2 | 03; 04 | Reserved | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 3 | 03; 04 | Reserved | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 4 | 03; 04 | Reserved | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 5 | 03; 04 | Oil pressure circuit open | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 6 | 03; 04 | Oil pressure circuit open | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 7 | 03; 04 | Oil pressure circuit open | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 8 | 03; 04 | Oil pressure circuit open | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 9 | 03; 04 | Magnetic pick up fault | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 10 | 03; 04 | Magnetic pick up fault | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 11 | 03; 04 | Magnetic pick up fault | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 12 | 03; 04 | Magnetic pick up fault | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 13 | 03; 04 | Fuel theft | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 14 | 03; 04 | Fuel theft | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 15 | 03; 04 | Fuel theft | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 7 | 71 | 16 | 03; 04 | Fuel theft | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 1 | 03; 04 | Auxiliary input D | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 2 | 03; 04 | Auxiliary input D | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 3 | 03; 04 | Auxiliary input D | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 4 | 03; 04 | Auxiliary input D | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 5 | 03; 04 | Auxiliary input C | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 6 | 03; 04 | Auxiliary input C | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 7 | 03; 04 | Auxiliary input C | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 8 | 03; 04 | Auxiliary input C | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 9 | 03; 04 | Auxiliary input B | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 10 | 03; 04 | Auxiliary input B | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 11 | 03; 04 | Auxiliary input B | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 12 | 03; 04 | Auxiliary input B | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 13 | 03; 04 | Auxiliary input A | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 14 | 03; 04 | Auxiliary input A | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 15 | 03; 04 | Auxiliary input A | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 8 | 72 | 16 | 03; 04 | Auxiliary input A | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 1 | 03; 04 | Auxiliary input H | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 2 | 03; 04 | Auxiliary input H | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 3 | 03; 04 | Auxiliary input H | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 4 | 03; 04 | Auxiliary input H | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 5 | 03; 04 | Auxiliary input G | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 6 | 03; 04 | Auxiliary input G | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 7 | 03; 04 | Auxiliary input G | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 8 | 03; 04 | Auxiliary input G | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 9 | 03; 04 | Auxiliary input F | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 10 | 03; 04 | Auxiliary input F | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 11 | 03; 04 | Auxiliary input F | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 12 | 03; 04 | Auxiliary input F | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 13 | 03; 04 | Auxiliary input E | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 14 | 03; 04 | Auxiliary input E | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 15 | 03; 04 | Auxiliary input E | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 9 | 73 | 16 | 03; 04 | Auxiliary input E | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 1 | 03; 04 | Auxiliary input L | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 2 | 03; 04 | Auxiliary input L | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 3 | 03; 04 | Auxiliary input L | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 4 | 03; 04 | Auxiliary input L | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 5 | 03; 04 | Auxiliary input K | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 6 | 03; 04 | Auxiliary input K | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 7 | 03; 04 | Auxiliary input K | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 8 | 03; 04 | Auxiliary input K | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 9 | 03; 04 | Auxiliary input J | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 10 | 03; 04 | Auxiliary input J | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 11 | 03; 04 | Auxiliary input J | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 12 | 03; 04 | Auxiliary input J | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 13 | 03; 04 | Auxiliary input I | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 14 | 03; 04 | Auxiliary input I | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 15 | 03; 04 | Auxiliary input I | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 10 | 74 | 16 | 03; 04 | Auxiliary input I | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 1 | 03; 04 | Auxiliary input P | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 2 | 03; 04 | Auxiliary input P | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 3 | 03; 04 | Auxiliary input P | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 4 | 03; 04 | Auxiliary input P | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 5 | 03; 04 | Auxiliary input O | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 6 | 03; 04 | Auxiliary input O | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 7 | 03; 04 | Auxiliary input O | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 8 | 03; 04 | Auxiliary input O | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 9 | 03; 04 | Auxiliary input N | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 10 | 03; 04 | Auxiliary input N | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 11 | 03; 04 | Auxiliary input N | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 12 | 03; 04 | Auxiliary input N | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 13 | 03; 04 | Auxiliary input M | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 14 | 03; 04 | Auxiliary input M | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 15 | 03; 04 | Auxiliary input M | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 11 | 75 | 16 | 03; 04 | Auxiliary input M | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 1 | 03; 04 | Gen L2 phase high volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 2 | 03; 04 | Gen L2 phase high volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 3 | 03; 04 | Gen L2 phase high volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 4 | 03; 04 | Gen L2 phase high volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 5 | 03; 04 | Gen L2 phase low volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 6 | 03; 04 | Gen L2 phase low volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 7 | 03; 04 | Gen L2 phase low volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 8 | 03; 04 | Gen L2 phase low volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 9 | 03; 04 | Gen L1 phase high volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 10 | 03; 04 | Gen L1 phase high volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 11 | 03; 04 | Gen L1 phase high volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 12 | 03; 04 | Gen L1 phase high volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 13 | 03; 04 | Gen L1 phase low volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 14 | 03; 04 | Gen L1 phase low volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 15 | 03; 04 | Gen L1 phase low volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 12 | 76 | 16 | 03; 04 | Gen L1 phase low volt | INT16u | - | 1 | - | See Enum list on Description worksheet
Output diagnostics | 77 | 1 | 03; 04 | Reserved | BOOL | - | 1 | - | 0:Disable, 1:Enable
Output diagnostics | 77 | 2 | 03; 04 | Digital output F | BOOL | - | 1 | - | 0:Disable, 1:Enable
Output diagnostics | 77 | 3 | 03; 04 | Digital output E | BOOL | - | 1 | - | 0:Disable, 1:Enable
Output diagnostics | 77 | 4 | 03; 04 | Digital output D | BOOL | - | 1 | - | 0:Disable, 1:Enable
Output diagnostics | 77 | 5 | 03; 04 | Digital output C | BOOL | - | 1 | - | 0:Disable, 1:Enable
Output diagnostics | 77 | 6 | 03; 04 | Digital output B | BOOL | - | 1 | - | 0:Disable, 1:Enable
Output diagnostics | 77 | 7 | 03; 04 | Digital output A | BOOL | - | 1 | - | 0:Disable, 1:Enable
Input diagnostics | 77 | 8 | 03; 04 | Digital input I | BOOL | - | 1 | - | 0:Disable, 1:Enable
Input diagnostics | 77 | 9 | 03; 04 | Digital input H | BOOL | - | 1 | - | 0:Disable, 1:Enable
Input diagnostics | 77 | 10 | 03; 04 | Digital input G | BOOL | - | 1 | - | 0:Disable, 1:Enable
Input diagnostics | 77 | 11 | 03; 04 | Digital input F | BOOL | - | 1 | - | 0:Disable, 1:Enable
Input diagnostics | 77 | 12 | 03; 04 | Digital input E | BOOL | - | 1 | - | 0:Disable, 1:Enable
Input diagnostics | 77 | 13 | 03; 04 | Digital input D | BOOL | - | 1 | - | 0:Disable, 1:Enable
Input diagnostics | 77 | 14 | 03; 04 | Digital input C | BOOL | - | 1 | - | 0:Disable, 1:Enable
Input diagnostics | 77 | 15 | 03; 04 | Digital input B | BOOL | - | 1 | - | 0:Disable, 1:Enable
Input diagnostics | 77 | 16 | 03; 04 | Digital input A | BOOL | - | 1 | - | 0:Disable, 1:Enable
DG status | 78 | 1 | 03; 04 | Common notification | BOOL | - | 1 | - | 0:False, 1:True
DG status | 78 | 2 | 03; 04 | Common warning | BOOL | - | 1 | - | 0:False, 1:True
DG status | 78 | 3 | 03; 04 | Common electric trip | BOOL | - | 1 | - | 0:False, 1:True
DG status | 78 | 4 | 03; 04 | Common shut down | BOOL | - | 1 | - | 0:False, 1:True
DG status | 78 | 5 | 03; 04 | Gen available | BOOL | - | 1 | - | 0:False, 1:True
DG status | 78 | 6 | 03; 04 | DG fail to start | BOOL | - | 1 | - | 0:False, 1:True
DG status | 78 | 7 | 03; 04 | DG stopped with fault | BOOL | - | 1 | - | 0:False, 1:True
DG status | 78 | 8 | 03; 04 | DG stopped normally | BOOL | - | 1 | - | 0:False, 1:True
DG status | 78 | 9 | 03; 04 | Current DG status | BOOL | - | 1 | - | 0:Stopped, 1:Running
DG status | 78 | 10 | 03; 04 | Load on DG | BOOL | - | 1 | - | 0:False, 1:True
DG status | 78 | 11 | 03; 04 | Load on Mains | BOOL | - | 1 | - | 0:False, 1:True
DG status | 78 | 12 | 03; 04 | DG operation mode | INT16u | - | 1 | - | [Bits 12–14] 100:Manual,101:Auto,110:Scheduler
DG status | 78 | 13 | 03; 04 | DG operation mode | INT16u | - | 1 | - | [Bits 12–14] 100:Manual,101:Auto,110:Scheduler
DG status | 78 | 14 | 03; 04 | DG operation mode | INT16u | - | 1 | - | [Bits 12–14] 100:Manual,101:Auto,110:Scheduler
DG status | 78 | 15 | 03; 04 | Mains healthy / unhealthy | BOOL | - | 1 | - | 0:False, 1:True
DG status | 78 | 16 | 03; 04 | SGC Mode | BOOL | - | 1 | - | 0:Other states, 1:Configuration, event log, or password screen
DG status | 79 | 1 | 03; 04 | Current time stamp | INT16u | - | 1 | min | -
DG status | 79 | 2 | 03; 04 | Current time stamp | INT16u | - | 1 | min | -
DG status | 79 | 3 | 03; 04 | Current time stamp | INT16u | - | 1 | min | -
DG status | 79 | 4 | 03; 04 | Current time stamp | INT16u | - | 1 | min | -
DG status | 79 | 5 | 03; 04 | Current time stamp | INT16u | - | 1 | min | -
DG status | 79 | 6 | 03; 04 | Current time stamp | INT16u | - | 1 | min | -
DG status | 79 | 7 | 03; 04 | Current time stamp | INT16u | - | 1 | min | -
DG status | 79 | 8 | 03; 04 | Current time stamp | INT16u | - | 1 | min | -
DG status | 79 | 9 | 03; 04 | Current time stamp | INT16u | - | 1 | sec | -
DG status | 79 | 10 | 03; 04 | Current time stamp | INT16u | - | 1 | sec | -
DG status | 79 | 11 | 03; 04 | Current time stamp | INT16u | - | 1 | sec | -
DG status | 79 | 12 | 03; 04 | Current time stamp | INT16u | - | 1 | sec | -
DG status | 79 | 13 | 03; 04 | Current time stamp | INT16u | - | 1 | sec | -
DG status | 79 | 14 | 03; 04 | Current time stamp | INT16u | - | 1 | sec | -
DG status | 79 | 15 | 03; 04 | Current time stamp | INT16u | - | 1 | sec | -
DG status | 79 | 16 | 03; 04 | Current time stamp | INT16u | - | 1 | sec | -
DG status | 80 | 1 | 03; 04 | Current time stamp | INT16u | - | 1 | hr | -
DG status | 80 | 2 | 03; 04 | Current time stamp | INT16u | - | 1 | hr | -
DG status | 80 | 3 | 03; 04 | Current time stamp | INT16u | - | 1 | hr | -
DG status | 80 | 4 | 03; 04 | Current time stamp | INT16u | - | 1 | hr | -
DG status | 80 | 5 | 03; 04 | Current time stamp | INT16u | - | 1 | hr | -
DG status | 80 | 6 | 03; 04 | Current time stamp | INT16u | - | 1 | hr | -
DG status | 80 | 7 | 03; 04 | Current time stamp | INT16u | - | 1 | hr | -
DG status | 80 | 8 | 03; 04 | Current time stamp | INT16u | - | 1 | hr | -
DG status | 80 | 9 | 03; 04 | Current time stamp | INT16u | - | 1 | day | -
DG status | 80 | 10 | 03; 04 | Current time stamp | INT16u | - | 1 | day | -
DG status | 80 | 11 | 03; 04 | Current time stamp | INT16u | - | 1 | day | -
DG status | 80 | 12 | 03; 04 | Current time stamp | INT16u | - | 1 | day | -
DG status | 80 | 13 | 03; 04 | Current time stamp | INT16u | - | 1 | day | -
DG status | 80 | 14 | 03; 04 | Current time stamp | INT16u | - | 1 | day | -
DG status | 80 | 15 | 03; 04 | Current time stamp | INT16u | - | 1 | day | -
DG status | 80 | 16 | 03; 04 | Current time stamp | INT16u | - | 1 | day | -
DG status | 81 | 1 | 03; 04 | Current time stamp | INT16u | - | 1 | dd | -
DG status | 81 | 2 | 03; 04 | Current time stamp | INT16u | - | 1 | dd | -
DG status | 81 | 3 | 03; 04 | Current time stamp | INT16u | - | 1 | dd | -
DG status | 81 | 4 | 03; 04 | Current time stamp | INT16u | - | 1 | dd | -
DG status | 81 | 5 | 03; 04 | Current time stamp | INT16u | - | 1 | dd | -
DG status | 81 | 6 | 03; 04 | Current time stamp | INT16u | - | 1 | dd | -
DG status | 81 | 7 | 03; 04 | Current time stamp | INT16u | - | 1 | dd | -
DG status | 81 | 8 | 03; 04 | Current time stamp | INT16u | - | 1 | dd | -
DG status | 81 | 9 | 03; 04 | Current time stamp | INT16u | - | 1 | mm | -
DG status | 81 | 10 | 03; 04 | Current time stamp | INT16u | - | 1 | mm | -
DG status | 81 | 11 | 03; 04 | Current time stamp | INT16u | - | 1 | mm | -
DG status | 81 | 12 | 03; 04 | Current time stamp | INT16u | - | 1 | mm | -
DG status | 81 | 13 | 03; 04 | Current time stamp | INT16u | - | 1 | mm | -
DG status | 81 | 14 | 03; 04 | Current time stamp | INT16u | - | 1 | mm | -
DG status | 81 | 15 | 03; 04 | Current time stamp | INT16u | - | 1 | mm | -
DG status | 81 | 16 | 03; 04 | Current time stamp | INT16u | - | 1 | mm | -
DG status | 82 |  | 03; 04 | Current time stamp | INT16u | - | 1 | yy | -
CPCB IV+ alarm status | 83 | 1 | 03; 04 | Common Alarm | BOOL | - | 1 | - | 0:False, 1:True
CPCB IV+ alarm status | 83 | 2 | 03; 04 | Inducement buzzer | BOOL | - | 1 | - | 0:False, 1:True
CPCB IV+ alarm status | 83 | 3 | 03; 04 | Urea level low | BOOL | - | 1 | - | 0:False, 1:True
CPCB IV+ alarm status | 83 | 4 | 03; 04 | Impeded EGR valve | BOOL | - | 1 | - | 0:False, 1:True
CPCB IV+ alarm status | 83 | 5 | 03; 04 | Incorrect urea detected | BOOL | - | 1 | - | 0:False, 1:True
CPCB IV+ alarm status | 83 | 6 | 03; 04 | Critical emission failure | BOOL | - | 1 | - | 0:False, 1:True
CPCB IV+ alarm status | 83 | 7 | 03; 04 | Urea dosing malfunction | BOOL | - | 1 | - | 0:False, 1:True
CPCB IV+ alarm status | 83 | 8 | 03; 04 | SPN 3326 FMI 20 DTC status over Modbus | BOOL | - | 1 | - | 0:False, 1:True
EGR Modbus | 84 | 1 | 03; 04 | ECU Healthy | BOOL | - | 1 | - | 0:False, 1:True
EGR Modbus | 84 | 2 | 03; 04 | ECU Faulty | BOOL | - | 1 | - | 0:False, 1:True
EGR Modbus | 84 | 3 | 03; 04 | Temperature Sensor Open or Faulty | BOOL | - | 1 | - | 0:False, 1:True
EGR Modbus | 84 | 4 | 03; 04 | Temperature Sensor Out | BOOL | - | 1 | - | 0:False, 1:True
EGR Modbus | 84 | 5 | 03; 04 | EGR Valve Wire Open | BOOL | - | 1 | - | 0:False, 1:True
EGR Modbus | 84 | 6 | 03; 04 | EGR Valve Sensor Not Connected or Faulty | BOOL | - | 1 | - | 0:False, 1:True
EGR Modbus | 84 | 7 | 03; 04 | EGR Valve Not Lifting | BOOL | - | 1 | - | 0:False, 1:True
EGR Modbus | 84 | 8 | 03; 04 | EGR Valve Not Closing | BOOL | - | 1 | - | 0:False, 1:True
EGR Modbus | 85 |  | 03; 04 | EGR Fault time | INT16u | - | 1 | min | -
EGR Modbus | 86 |  | 03; 04 | EGR Heal Time | INT16u | - | 1 | min | -
EGR Modbus | 87 |  | 03; 04 | Engine Shutdown due to EGR Fault | INT16u | - | 1 | - | -
DTC status | 88 |  | 03; 04 | DTC Parent Specifier | INT16u | - | 1 | - | Decimal value: 0: DTC DM1 parent, 1: DTC DM1 child1, 16: DTC DM2 parent, 17: DTC DM2 child1
DTC Value | 89 |  | 03; 04 | SPN of 5th DTC Received over CAN | INT32u | CDAB | 1 | - | -
DTC Value | 91 |  | 03; 04 | FMI of 5th DTC Received over CAN | INT16u | - | 1 | - | -
DTC Value | 92 |  | 03; 04 | OC of 5th DTC Received over CAN | INT16u | - | 1 | - | -
DTC Value | 93 |  | 03; 04 | SPN of 4th DTC Received over CAN | INT32u | CDAB | 1 | - | -
DTC Value | 95 |  | 03; 04 | FMI of 4th DTC Received over CAN | INT16u | - | 1 | - | -
DTC Value | 96 |  | 03; 04 | OC of 4th DTC Received over CAN | INT16u | - | 1 | - | -
DTC Value | 97 |  | 03; 04 | SPN of 3rd DTC Received over CAN | INT32u | CDAB | 1 | - | -
DTC Value | 99 |  | 03; 04 | FMI of 3rd DTC Received over CAN | INT16u | - | 1 | - | -
DTC Value | 100 |  | 03; 04 | OC of 3rd DTC Received over CAN | INT16u | - | 1 | - | -
DTC Value | 101 |  | 03; 04 | SPN of 2nd DTC Received over CAN | INT32u | CDAB | 1 | - | -
DTC Value | 103 |  | 03; 04 | FMI of 2nd DTC Received over CAN | INT16u | - | 1 | - | -
DTC Value | 104 |  | 03; 04 | OC of 2nd DTC Received over CAN | INT16u | - | 1 | - | -
DTC Value | 105 |  | 03; 04 | SPN of 1st DTC Received over CAN | INT32u | CDAB | 1 | - | -
DTC Value | 107 |  | 03; 04 | FMI of 1st DTC Received over CAN | INT16u | - | 1 | - | -
DTC Value | 108 |  | 03; 04 | OC of 1 st DTC Received over CAN | INT16u | - | 1 | - | -
Custom Sensor | 109 |  | 03; 04 | Custom Sensor Value | INT16s | - | 10 | - | -
Alarm Status for Alarm 13 | 110 | 1 | 03; 04 | Custom sensor Shutdown Alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 13 | 110 | 2 | 03; 04 | Custom sensor Shutdown Alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 13 | 110 | 3 | 03; 04 | Custom sensor Shutdown Alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 13 | 110 | 4 | 03; 04 | Custom sensor Shutdown Alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 13 | 110 | 5 | 03; 04 | Custom sensor Open CKT Fault | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 13 | 110 | 6 | 03; 04 | Custom sensor Open CKT Fault | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 13 | 110 | 7 | 03; 04 | Custom sensor Open CKT Fault | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 13 | 110 | 8 | 03; 04 | Custom sensor Open CKT Fault | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 13 | 110 | 9 | 03; 04 | Reserved | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 13 | 110 | 10 | 03; 04 | Reserved | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 13 | 110 | 11 | 03; 04 | Reserved | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 13 | 110 | 12 | 03; 04 | Reserved | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 13 | 110 | 13 | 03; 04 | Reserved | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 13 | 110 | 14 | 03; 04 | Reserved | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 13 | 110 | 15 | 03; 04 | Reserved | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 13 | 110 | 16 | 03; 04 | Reserved | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 1 | 03; 04 | Fail to Close Gen alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 2 | 03; 04 | Fail to Close Gen alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 3 | 03; 04 | Fail to Close Gen alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 4 | 03; 04 | Fail to Close Gen alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 5 | 03; 04 | Fail to Open Gen continuous alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 6 | 03; 04 | Fail to Open Gen continuous alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 7 | 03; 04 | Fail to Open Gen continuous alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 8 | 03; 04 | Fail to Open Gen continuous alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 9 | 03; 04 | Fail to Latch Mains alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 10 | 03; 04 | Fail to Latch Mains alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 11 | 03; 04 | Fail to Latch Mains alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 12 | 03; 04 | Fail to Latch Mains alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 13 | 03; 04 | Fail to Open Mains continuous alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 14 | 03; 04 | Fail to Open Mains continuous alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 15 | 03; 04 | Fail to Open Mains continuous alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
Alarm Status for Alarm 14 | 111 | 16 | 03; 04 | Fail to Open Mains continuous alarm | INT16u | - | 1 | - | See Enum list on Description worksheet
EIC Data Over Modbus | 112 |  | 03; 04 | Urea Level SPN:1761 PGN:65110 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 113 |  | 03; 04 | Urea concentration SPN:3516 PGN:64923 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 114 |  | 03; 04 | Lub oil temperature SPN:175 PGN:65262 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 115 |  | 03; 04 | Aftertreatment 2 Diesel Exhaust Fluid Actual Dosing Quantity SPN:4384 PGN:61478 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 116 |  | 03; 04 | Aftertreatment 2 Diesel Exhaust Fluid Dosing Absolute Pressure SPN:4387 PGN:61478 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 117 |  | 03; 04 | Aftertreatment 2 SCR Dosing Air Assist Valve SPN:4389 PGN:64827 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 118 | 1 | 03; 04 | Exhaust system high temperature OFF SPN:3698 PGN:64892 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 118 | 2 | 03; 04 | Exhaust system high temperature ON SPN:3698 PGN:64892 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 118 | 3 | 03; 04 | Alarm Yellow lamp OFF SPN:624 PGN:65226 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 118 | 4 | 03; 04 | Alarm Yellow lamp ON SPN:624 PGN:65226 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 118 | 5 | 03; 04 | Alarm Red lamp OFF SPN:623 PGN:65226 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 118 | 6 | 03; 04 | Alarm Red lamp ON SPN:623 PGN:65226 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 118 | 7 | 03; 04 | DPF lamp OFF SPN:3697 PGN:64892 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 118 | 8 | 03; 04 | DPF lamp ON solid SPN:3697 PGN:64892 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 118 | 9 | 03; 04 | DPF lamp ON blink SPN:3697 PGN:64892 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 118 | 10 | 03; 04 | DPF Active Regeneration not activated SPN:3700 PGN:64892 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 118 | 11 | 03; 04 | DPF Active Regeneration activated SPN:3700 PGN:64892 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 118 | 12 | 03; 04 | DPF Active Regeneration needed SPN:3700 PGN:64892 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 118 | 13 | 03; 04 | DPF Regeneration not needed SPN:3701 PGN:64892 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 118 | 14 | 03; 04 | DPF Regeneration needed Lowest SPN:3701 PGN:64892 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 118 | 15 | 03; 04 | DPF Regeneration needed Moderate SPN:3701 PGN:64892 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 118 | 16 | 03; 04 | DPF Regeneration needed Highest SPN:3701 PGN:64892 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 119 | 1 | 03; 04 | DPF Regeneration Not Inhibit SPN:3703 PGN:64892 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 119 | 2 | 03; 04 | DPF Regeneration Inhibit SPN:3703 PGN:64892 | BOOL | - | 1 | - | 0:False, 1:True
EIC Data Over Modbus | 120 |  | 03; 04 | Fuel rail pressure SPN:3.1(65329) PGN:65329 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 121 |  | 03; 04 | Fuel consumption by CAN SPN:250 PGN:65257 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 122 |  | 03; 04 | Fuel consumption by CAN SPN:250 PGN:65257 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 123 |  | 03; 04 | Aftertreatment 1 Intake Nox SPN:3216 PGN:61454 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 124 |  | 03; 04 | Aftertreatment 1 Outlet NOx SPN:3226 PGN:61455 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 125 |  | 03; 04 | Aftertreatment 1 Diesel Exhaust Fluid Actual Dosing Quantity SPN:4331 PGN:61475 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 126 |  | 03; 04 | Aftertreatment 1 Diesel Exhaust Fluid Doser Absolute Pressure SPN:4334 PGN:61475 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 127 |  | 03; 04 | Aftertreatment 1 SCR Dosing Air Assist Valve SPN:4336 PGN:64833 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 128 |  | 03; 04 | Aftertreatment 1 Diesel Exhaust Fluid Dosing Requested Quantity SPN:4348 PGN:61476 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 129 |  | 03; 04 | Aftertreatment 1 SCR Catalyst Intake Gas Temperature SPN:4765 PGN:64800 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 130 |  | 03; 04 | Aftertreatment 2 Intake Nox SPN:3255 PGN:61456 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 131 |  | 03; 04 | Aftertreatment 2 Outlet NOx SPN:3265 PGN:61457 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 132 |  | 03; 04 | ECU temperature SPN:1136 PGN:65188 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 133 |  | 03; 04 | Boot pressure SPN:102 PGN:65270 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 134 |  | 03; 04 | Engine Percentage torques SPN:2432 PGN:61444 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 135 |  | 03; 04 | Inducement timer-1 SPN:7426 PGN:64554 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 136 |  | 03; 04 | Inducement timer-2 SPN:7719 PGN:64554 | INT16u | - | 1 | - | -
EIC Data Over Modbus | 137 |  | 03; 04 | Ambient temperature SPN:171 PGN:65269 | INT16u | - | 1 | - | -
DG mode change | 0 |  | 16 | DG mode change command | INT16u | - | 1 | - | Decimal value: 1: STOP, 2: START, 4: AUTO, 64: ACK
DTC Status | 1 |  | 16 | DTC Parent Specifier | INT16u | - | 1 | - | Decimal value: 0: DTC DM1 parent, 1: DTC DM1 child1, 16: DTC DM2 parent, 17: DTC DM2 child1