## Descriptions
iE 150 Marine Modbus descriptions
Software version
The information contained in these tables (Revision D) is applicable to software version 1.35.0 of the iE 150.
| Name | Controller
| BTB-M | Bus tie breaker (marine)
| Shore | Shore connection
| GEN-M | Genset (marine)
| ENG-M | Engine drive (marine)
See the iE 150 AGC 150 Modbus server User manual for more information.
Row | Hyperlink index
21 | Modbus function codes
32 | Discrete output coil
40 | Discrete input contact
49 | Output holding register
58 | Input register
Back to index | Modbus function codes
| Function code | Description
| 01 | Read a single or multiple discrete output coils.
| 02 | Read a single or multiple discrete input contacts.
| 03 | Read a single or multiple output holding registers.
| 04 | Read a single or multiple input registers.
| 05 | Write a value to a single discrete output coil.
| 06 | Write a value to a single output holding register.
| 15 | Write a value to multiple consecutive discrete output coils.
| 16 | Write a value to multiple consecutive output holding registers.
Back to index | Discrete output coil
| Function code | Effect
| 01 | Read
| 05 or 15 | Write
| Function group | Description
| Command flag | Activate a command in the controller. Read: The controller always returns 0 (false). Write: The controller executes the command if you write 1 (true).
Back to index | Discrete input contact
| Function code | Effect
| 02 | Read
| Function group | Description
| Digital input | Read the state of a digital input on the controller. The controller returns 0 (false) when the digital input is inactive. The controller returns 1 (true) when the digital input is active.
| Digital output | Read the state of a digital output on the controller. The controller returns 0 (false) when the digital output is inactive. The controller returns 1 (true) when the digital output is active.
| Status flag | Read whether a status flag is activated. The controller returns 0 (false) when the status flag is not activated. The controller returns 1 (true) when the status flag is activated.
Back to index | Output holding register
| Function code | Effect
| 03 | Read
| 06 or 16 | Write
| Function group | Description
| Control command | Activate a command in the controller. Read: The controller always returns 0 (false) from the bits. Write: The controller executes the command if you write 1 (true) to the address bit.
| Control time command | Read and write the time and date values of the controller. Read: The controller returns the value of the associated function. Write: The controller changes the value of the associated function if a valid value is entered.
Back to index | Input register
| Function code | Effect
| 04 | Read
| Function group | Description
| AC alarm | Read one bit to see whether the AC alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| AC measurement | Read the operating value of the associated AC measurement.
| Alarm | Read one bit to see whether the alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| Alarm list monitoring | Read the Address for each active alarm. Use the Parameters tab in the utility software to look up which alarm corresponds to each Address. The alarm list monitoring is in Modbus addresses 28000 to 28099. These addresses are not listed in the Input register (04) worksheet.
| APPL version | Read the controller application version.
| Control command state | Read the state of all the bits in the control command address.
| Counter | Read the counter value.
| DAVR alarm | Read one bit to see whether the digital AVR alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| DAVR measurement | Read the operating value of the associated digital AVR measurement.
| DC measurement | Read the operating value of the associated measurement.
| Digital input state | Read one bit to see whether the digital input is activated. The controller returns 0 (false) when the digital input is not activated. The controller returns 1 (true) when the digital input is activated.
| Digital output state | Read one bit to see whether the digital output is activated. The controller returns 0 (false) when the digital output is not activated. The controller returns 1 (true) when the digital output is activated.
| EIC alarm | Read one bit to see whether the alarm from engine communication is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| EIC measurement | Read the operating value of the associated engine communication measurement.
| EIC measurements validity | Read one bit to see whether the measurement from engine communication is valid. The controller returns 0 (false) when the measurement is not valid. The controller returns 1 (true) when the measurement is valid.
| EIC measurements value | Read the operating value of the associated engine communication measurement. Note: The offsets can be different for EIC measurement and EIC measurements value.
| EIC state | Read one bit to see whether the engine communication state is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| M-Logic state | Read one bit to see whether the M-Logic virtual event or flip-flop is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| Modbus configurable area | Read the value of the function assigned to the address using the Modbus configurator. Additional information about the assigned address should be completed by the user. Modbus addresses 0 to 499 are available for configurable Modbus. These addresses are not listed in the Input register (04) worksheet.
| Modes | Read one bit to see whether the mode is activated. The controller returns 0 (false) when the mode is not activated. The controller returns 1 (true) when the mode is activated.
| Plant config | Read the value of the plant configuration.
| Plant logic state | Read one bit to see whether the plant state is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| PM AC measurement | Read the operating value of the associated Power Management measurements and settings.
| PM alarm | Read one bit to see whether the Power Management alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| PM Plant logic state | Read one bit to see whether the Power Management state is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| Profibus configurable area | Read the value of the function assigned to the address using the Modbus configurator. Additional information about the assigned address should be completed by the user. Modbus addresses 0 to 62 are available for configurable Profibus. These addresses are not listed in the Input register (04) worksheet.
| Relay state | Read one bit to see the relay state. The controller returns 0 (false) when the relay is de-energised. The controller returns 1 (true) when the relay is energised.

## Discrete output coil (01;05;15)
Discrete output coil (01;05;15)
Function group | Modbus address | PLC address | Modbus function code | Controller function name | BTB-M | SHORE | GEN-M | ENG-M
Command flag | 0 | 1 | 01; 05; 15 | Remote start |  |  | X | X
Command flag | 1 | 2 | 01; 05; 15 | Remote GB ON |  |  | X
Command flag | 1 | 2 | 01; 05; 15 | Remote BTB ON | X
Command flag | 2 | 3 | 01; 05; 15 | Remote GB OFF |  |  | X
Command flag | 2 | 3 | 01; 05; 15 | Remote BTB OFF | X
Command flag | 3 | 4 | 01; 05; 15 | Remote stop |  |  | X | X
Command flag | 4 | 5 | 01; 05; 15 | Alarm inhibit 1 | X | X | X | X
Command flag | 5 | 6 | 01; 05; 15 | Alarm inhibit 2 | X | X | X | X
Command flag | 6 | 7 | 01; 05; 15 | Alarm inhibit 3 | X | X | X | X
Command flag | 7 | 8 | 01; 05; 15 | Reset GOV/AVR regulation output to offset |  |  | X
Command flag | 9 | 10 | 01; 05; 15 | Alarm ack. | X | X | X | X
Command flag | 10 | 11 | 01; 05; 15 | Nominal setting 1 | X | X | X
Command flag | 11 | 12 | 01; 05; 15 | Nominal setting 2 | X | X | X
Command flag | 12 | 13 | 01; 05; 15 | Nominal setting 3 | X | X | X
Command flag | 13 | 14 | 01; 05; 15 | Nominal setting 4 | X | X | X
Command flag | 14 | 15 | 01; 05; 15 | Start+sync. (MANUAL) |  |  | X
Command flag | 15 | 16 | 01; 05; 15 | Deload/stop (MANUAL) |  |  | X
Command flag | 16 | 17 | 01; 05; 15 | Island |  |  | X
Command flag | 17 | 18 | 01; 05; 15 | EDG |  |  | X
Command flag | 24 | 25 | 01; 05; 15 | TB ON (EDG) |  |  | X
Command flag | 24 | 25 | 01; 05; 15 | SCB ON |  | X
Command flag | 25 | 26 | 01; 05; 15 | TB OFF (EDG) |  |  | X
Command flag | 25 | 26 | 01; 05; 15 | SCB OFF |  | X
Command flag | 26 | 27 | 01; 05; 15 | AUTO start/stop |  | X | X
Command flag | 28 | 29 | 01; 05; 15 | Local mode |  |  | X | X
Command flag | 28 | 29 | 01; 05; 15 | MANUAL mode |  | X
Command flag | 29 | 30 | 01; 05; 15 | REMOTE mode |  |  | X | X
Command flag | 29 | 30 | 01; 05; 15 | AUTO mode |  | X
Command flag | 30 | 31 | 01; 05; 15 | TEST mode |  | X | X | X
Command flag | 31 | 32 | 01; 05; 15 | External frequency control |  |  | X
Command flag | 32 | 33 | 01; 05; 15 | External voltage control |  |  | X
Command flag | 33 | 34 | 01; 05; 15 | External power control |  | X | X
Command flag | 34 | 35 | 01; 05; 15 | External reactive power control |  |  | X
Command flag | 35 | 36 | 01; 05; 15 | External power factor control |  |  | X
Command flag | 36 | 37 | 01; 05; 15 | Capacitive PF |  |  | X
Command flag | 40 | 41 | 01; 05; 15 | Application 1 | X | X | X
Command flag | 41 | 42 | 01; 05; 15 | Application 2 | X | X | X
Command flag | 42 | 43 | 01; 05; 15 | Application 3 | X | X | X
Command flag | 43 | 44 | 01; 05; 15 | Application 4 | X | X | X
Command flag | 44 | 45 | 01; 05; 15 | Battery test |  |  | X | X
Command flag | 46 | 47 | 01; 05; 15 | Synchronise clock to 4:00 a.m. | X | X | X | X
Command flag | 48 | 49 | 01; 05; 15 | Virtual event set 1 | X | X | X | X
Command flag | 49 | 50 | 01; 05; 15 | Virtual event set 2 | X | X | X | X
Command flag | 50 | 51 | 01; 05; 15 | Virtual event set 3 | X | X | X | X
Command flag | 51 | 52 | 01; 05; 15 | Virtual event set 4 | X | X | X | X
Command flag | 52 | 53 | 01; 05; 15 | Virtual event set 5 | X | X | X | X
Command flag | 53 | 54 | 01; 05; 15 | Virtual event set 6 | X | X | X | X
Command flag | 54 | 55 | 01; 05; 15 | Virtual event set 7 | X | X | X | X
Command flag | 55 | 56 | 01; 05; 15 | Virtual event set 8 | X | X | X | X
Command flag | 56 | 57 | 01; 05; 15 | Virtual event set 9 | X | X | X | X
Command flag | 57 | 58 | 01; 05; 15 | Virtual event set 10 | X | X | X | X
Command flag | 58 | 59 | 01; 05; 15 | Virtual event set 11 | X | X | X | X
Command flag | 59 | 60 | 01; 05; 15 | Virtual event set 12 | X | X | X | X
Command flag | 60 | 61 | 01; 05; 15 | Virtual event set 13 | X | X | X | X
Command flag | 61 | 62 | 01; 05; 15 | Virtual event set 14 | X | X | X | X
Command flag | 62 | 63 | 01; 05; 15 | Virtual event set 15 | X | X | X | X
Command flag | 63 | 64 | 01; 05; 15 | Virtual event set 16 | X | X | X | X
Command flag | 64 | 65 | 01; 05; 15 | Virtual event set 17 | X | X | X | X
Command flag | 65 | 66 | 01; 05; 15 | Virtual event set 18 | X | X | X | X
Command flag | 66 | 67 | 01; 05; 15 | Virtual event set 19 | X | X | X | X
Command flag | 67 | 68 | 01; 05; 15 | Virtual event set 20 | X | X | X | X
Command flag | 68 | 69 | 01; 05; 15 | Virtual event set 21 | X | X | X | X
Command flag | 69 | 70 | 01; 05; 15 | Virtual event set 22 | X | X | X | X
Command flag | 70 | 71 | 01; 05; 15 | Virtual event set 23 | X | X | X | X
Command flag | 71 | 72 | 01; 05; 15 | Virtual event set 24 | X | X | X | X
Command flag | 72 | 73 | 01; 05; 15 | Virtual event set 25 | X | X | X | X
Command flag | 73 | 74 | 01; 05; 15 | Virtual event set 26 | X | X | X | X
Command flag | 74 | 75 | 01; 05; 15 | Virtual event set 27 | X | X | X | X
Command flag | 75 | 76 | 01; 05; 15 | Virtual event set 28 | X | X | X | X
Command flag | 76 | 77 | 01; 05; 15 | Virtual event set 29 | X | X | X | X
Command flag | 77 | 78 | 01; 05; 15 | Virtual event set 30 | X | X | X | X
Command flag | 78 | 79 | 01; 05; 15 | Virtual event set 31 | X | X | X | X
Command flag | 79 | 80 | 01; 05; 15 | Virtual event set 32 | X | X | X | X
Command flag | 98 | 99 | 01; 05; 15 | PID1 manual regulation ON |  |  |  | X
Command flag | 99 | 100 | 01; 05; 15 | PID1 manual regulation OFF |  |  |  | X
Command flag | 121 | 122 | 01; 05; 15 | Clear log | X | X | X | X
Command flag | 122 | 123 | 01; 05; 15 | Clear Parameter edits | X | X | X | X
Command flag | 123 | 124 | 01; 05; 15 | Enable external frequency control |  |  | X
Command flag | 124 | 125 | 01; 05; 15 | Disable external frequency control |  |  | X
Command flag | 125 | 126 | 01; 05; 15 | Enable external voltage control |  |  | X
Command flag | 126 | 127 | 01; 05; 15 | Disable external voltage control |  |  | X
Command flag | 127 | 128 | 01; 05; 15 | Enable external power control |  | X | X
Command flag | 128 | 129 | 01; 05; 15 | Disable external power control |  | X | X
Command flag | 129 | 130 | 01; 05; 15 | Enable external VAr control |  |  | X
Command flag | 130 | 131 | 01; 05; 15 | Disable external VAr control |  |  | X
Command flag | 131 | 132 | 01; 05; 15 | Enable external CosPhi control |  |  | X
Command flag | 132 | 133 | 01; 05; 15 | Disable external CosPhi control |  |  | X
Command flag | 135 | 136 | 01; 05; 15 | Reset horn | X | X | X | X
Command flag | 142 | 143 | 01; 05; 15 | Virtual event set 33 | X | X | X | X
Command flag | 143 | 144 | 01; 05; 15 | Virtual event set 34 | X | X | X | X
Command flag | 144 | 145 | 01; 05; 15 | Virtual event set 35 | X | X | X | X
Command flag | 145 | 146 | 01; 05; 15 | Virtual event set 36 | X | X | X | X
Command flag | 146 | 147 | 01; 05; 15 | Virtual event set 37 | X | X | X | X
Command flag | 147 | 148 | 01; 05; 15 | Virtual event set 38 | X | X | X | X
Command flag | 148 | 149 | 01; 05; 15 | Virtual event set 39 | X | X | X | X
Command flag | 149 | 150 | 01; 05; 15 | Virtual event set 40 | X | X | X | X
Command flag | 150 | 151 | 01; 05; 15 | Virtual event set 41 | X | X | X | X
Command flag | 151 | 152 | 01; 05; 15 | Virtual event set 42 | X | X | X | X
Command flag | 152 | 153 | 01; 05; 15 | Virtual event set 43 | X | X | X | X
Command flag | 153 | 154 | 01; 05; 15 | Virtual event set 44 | X | X | X | X
Command flag | 154 | 155 | 01; 05; 15 | Virtual event set 45 | X | X | X | X
Command flag | 155 | 156 | 01; 05; 15 | Virtual event set 46 | X | X | X | X
Command flag | 156 | 157 | 01; 05; 15 | Virtual event set 47 | X | X | X | X
Command flag | 157 | 158 | 01; 05; 15 | Virtual event set 48 | X | X | X | X
Command flag | 158 | 159 | 01; 05; 15 | Virtual event set 49 | X | X | X | X
Command flag | 159 | 160 | 01; 05; 15 | Virtual event set 50 | X | X | X | X
Command flag | 160 | 161 | 01; 05; 15 | Virtual event set 51 | X | X | X | X
Command flag | 161 | 162 | 01; 05; 15 | Virtual event set 52 | X | X | X | X
Command flag | 162 | 163 | 01; 05; 15 | Virtual event set 53 | X | X | X | X
Command flag | 163 | 164 | 01; 05; 15 | Virtual event set 54 | X | X | X | X
Command flag | 164 | 165 | 01; 05; 15 | Virtual event set 55 | X | X | X | X
Command flag | 165 | 166 | 01; 05; 15 | Virtual event set 56 | X | X | X | X
Command flag | 166 | 167 | 01; 05; 15 | Virtual event set 57 | X | X | X | X
Command flag | 167 | 168 | 01; 05; 15 | Virtual event set 58 | X | X | X | X
Command flag | 168 | 169 | 01; 05; 15 | Virtual event set 59 | X | X | X | X
Command flag | 169 | 170 | 01; 05; 15 | Virtual event set 60 | X | X | X | X
Command flag | 170 | 171 | 01; 05; 15 | Virtual event set 61 | X | X | X | X
Command flag | 171 | 172 | 01; 05; 15 | Virtual event set 62 | X | X | X | X
Command flag | 172 | 173 | 01; 05; 15 | Virtual event set 63 | X | X | X | X
Command flag | 173 | 174 | 01; 05; 15 | Virtual event set 64 | X | X | X | X
Command flag | 174 | 175 | 01; 05; 15 | Virtual event set 65 | X | X | X | X
Command flag | 175 | 176 | 01; 05; 15 | Virtual event set 66 | X | X | X | X
Command flag | 176 | 177 | 01; 05; 15 | Virtual event set 67 | X | X | X | X
Command flag | 177 | 178 | 01; 05; 15 | Virtual event set 68 | X | X | X | X
Command flag | 178 | 179 | 01; 05; 15 | Virtual event set 69 | X | X | X | X
Command flag | 179 | 180 | 01; 05; 15 | Virtual event set 70 | X | X | X | X
Command flag | 180 | 181 | 01; 05; 15 | Virtual event set 71 | X | X | X | X
Command flag | 181 | 182 | 01; 05; 15 | Virtual event set 72 | X | X | X | X
Command flag | 182 | 183 | 01; 05; 15 | Virtual event set 73 | X | X | X | X
Command flag | 183 | 184 | 01; 05; 15 | Virtual event set 74 | X | X | X | X
Command flag | 184 | 185 | 01; 05; 15 | Virtual event set 75 | X | X | X | X
Command flag | 185 | 186 | 01; 05; 15 | Virtual event set 76 | X | X | X | X
Command flag | 186 | 187 | 01; 05; 15 | Virtual event set 77 | X | X | X | X
Command flag | 187 | 188 | 01; 05; 15 | Virtual event set 78 | X | X | X | X
Command flag | 188 | 189 | 01; 05; 15 | Virtual event set 79 | X | X | X | X
Command flag | 189 | 190 | 01; 05; 15 | Virtual event set 80 | X | X | X | X
Command flag | 190 | 191 | 01; 05; 15 | Virtual event set 81 | X | X | X | X
Command flag | 191 | 192 | 01; 05; 15 | Virtual event set 82 | X | X | X | X
Command flag | 192 | 193 | 01; 05; 15 | Virtual event set 83 | X | X | X | X
Command flag | 193 | 194 | 01; 05; 15 | Virtual event set 84 | X | X | X | X
Command flag | 194 | 195 | 01; 05; 15 | Virtual event set 85 | X | X | X | X
Command flag | 195 | 196 | 01; 05; 15 | Virtual event set 86 | X | X | X | X
Command flag | 196 | 197 | 01; 05; 15 | Virtual event set 87 | X | X | X | X
Command flag | 197 | 198 | 01; 05; 15 | Virtual event set 88 | X | X | X | X
Command flag | 198 | 199 | 01; 05; 15 | Virtual event set 89 | X | X | X | X
Command flag | 199 | 200 | 01; 05; 15 | Virtual event set 90 | X | X | X | X
Command flag | 200 | 201 | 01; 05; 15 | Virtual event set 91 | X | X | X | X
Command flag | 201 | 202 | 01; 05; 15 | Virtual event set 92 | X | X | X | X
Command flag | 202 | 203 | 01; 05; 15 | Virtual event set 93 | X | X | X | X
Command flag | 203 | 204 | 01; 05; 15 | Virtual event set 94 | X | X | X | X
Command flag | 204 | 205 | 01; 05; 15 | Virtual event set 95 | X | X | X | X
Command flag | 205 | 206 | 01; 05; 15 | Virtual event set 96 | X | X | X | X
Command flag | 206 | 207 | 01; 05; 15 | Set flipflop 01 | X | X | X | X
Command flag | 207 | 208 | 01; 05; 15 | Set flipflop 02 | X | X | X | X
Command flag | 208 | 209 | 01; 05; 15 | Set flipflop 03 | X | X | X | X
Command flag | 209 | 210 | 01; 05; 15 | Set flipflop 04 | X | X | X | X
Command flag | 210 | 211 | 01; 05; 15 | Set flipflop 05 | X | X | X | X
Command flag | 211 | 212 | 01; 05; 15 | Set flipflop 06 | X | X | X | X
Command flag | 212 | 213 | 01; 05; 15 | Set flipflop 07 | X | X | X | X
Command flag | 213 | 214 | 01; 05; 15 | Set flipflop 08 | X | X | X | X
Command flag | 214 | 215 | 01; 05; 15 | Set flipflop 09 | X | X | X | X
Command flag | 215 | 216 | 01; 05; 15 | Set flipflop 10 | X | X | X | X
Command flag | 216 | 217 | 01; 05; 15 | Set flipflop 11 | X | X | X | X
Command flag | 217 | 218 | 01; 05; 15 | Set flipflop 12 | X | X | X | X
Command flag | 218 | 219 | 01; 05; 15 | Set flipflop 13 | X | X | X | X
Command flag | 219 | 220 | 01; 05; 15 | Set flipflop 14 | X | X | X | X
Command flag | 220 | 221 | 01; 05; 15 | Set flipflop 15 | X | X | X | X
Command flag | 221 | 222 | 01; 05; 15 | Set flipflop 16 | X | X | X | X
Command flag | 222 | 223 | 01; 05; 15 | Reset flipflop 01 | X | X | X | X
Command flag | 223 | 224 | 01; 05; 15 | Reset flipflop 02 | X | X | X | X
Command flag | 224 | 225 | 01; 05; 15 | Reset flipflop 03 | X | X | X | X
Command flag | 225 | 226 | 01; 05; 15 | Reset flipflop 04 | X | X | X | X
Command flag | 226 | 227 | 01; 05; 15 | Reset flipflop 05 | X | X | X | X
Command flag | 227 | 228 | 01; 05; 15 | Reset flipflop 06 | X | X | X | X
Command flag | 228 | 229 | 01; 05; 15 | Reset flipflop 07 | X | X | X | X
Command flag | 229 | 230 | 01; 05; 15 | Reset flipflop 08 | X | X | X | X
Command flag | 230 | 231 | 01; 05; 15 | Reset flipflop 09 | X | X | X | X
Command flag | 231 | 232 | 01; 05; 15 | Reset flipflop 10 | X | X | X | X
Command flag | 232 | 233 | 01; 05; 15 | Reset flipflop 11 | X | X | X | X
Command flag | 233 | 234 | 01; 05; 15 | Reset flipflop 12 | X | X | X | X
Command flag | 234 | 235 | 01; 05; 15 | Reset flipflop 13 | X | X | X | X
Command flag | 235 | 236 | 01; 05; 15 | Reset flipflop 14 | X | X | X | X
Command flag | 236 | 237 | 01; 05; 15 | Reset flipflop 15 | X | X | X | X
Command flag | 237 | 238 | 01; 05; 15 | Reset flipflop 16 | X | X | X | X
Command flag | 238 | 239 | 01; 05; 15 | Toggle flipflop 01 | X | X | X | X
Command flag | 239 | 240 | 01; 05; 15 | Toggle flipflop 02 | X | X | X | X
Command flag | 240 | 241 | 01; 05; 15 | Toggle flipflop 03 | X | X | X | X
Command flag | 241 | 242 | 01; 05; 15 | Toggle flipflop 04 | X | X | X | X
Command flag | 242 | 243 | 01; 05; 15 | Toggle flipflop 05 | X | X | X | X
Command flag | 243 | 244 | 01; 05; 15 | Toggle flipflop 06 | X | X | X | X
Command flag | 244 | 245 | 01; 05; 15 | Toggle flipflop 07 | X | X | X | X
Command flag | 245 | 246 | 01; 05; 15 | Toggle flipflop 08 | X | X | X | X
Command flag | 246 | 247 | 01; 05; 15 | Toggle flipflop 09 | X | X | X | X
Command flag | 247 | 248 | 01; 05; 15 | Toggle flipflop 10 | X | X | X | X
Command flag | 248 | 249 | 01; 05; 15 | Toggle flipflop 11 | X | X | X | X
Command flag | 249 | 250 | 01; 05; 15 | Toggle flipflop 12 | X | X | X | X
Command flag | 250 | 251 | 01; 05; 15 | Toggle flipflop 13 | X | X | X | X
Command flag | 251 | 252 | 01; 05; 15 | Toggle flipflop 14 | X | X | X | X
Command flag | 252 | 253 | 01; 05; 15 | Toggle flipflop 15 | X | X | X | X
Command flag | 253 | 254 | 01; 05; 15 | Toggle flipflop 16 | X | X | X | X
Command flag | 291 | 292 | 01; 05; 15 | Set oneshot 01 | X | X | X | X
Command flag | 292 | 293 | 01; 05; 15 | Set oneshot 02 | X | X | X | X
Command flag | 293 | 294 | 01; 05; 15 | Set oneshot 03 | X | X | X | X
Command flag | 294 | 295 | 01; 05; 15 | Set oneshot 04 | X | X | X | X
Command flag | 295 | 296 | 01; 05; 15 | Set oneshot 05 | X | X | X | X
Command flag | 296 | 297 | 01; 05; 15 | Set oneshot 06 | X | X | X | X
Command flag | 297 | 298 | 01; 05; 15 | Set oneshot 07 | X | X | X | X
Command flag | 298 | 299 | 01; 05; 15 | Set oneshot 08 | X | X | X | X
Command flag | 299 | 300 | 01; 05; 15 | Set oneshot 09 | X | X | X | X
Command flag | 300 | 301 | 01; 05; 15 | Set oneshot 10 | X | X | X | X
Command flag | 301 | 302 | 01; 05; 15 | Set oneshot 11 | X | X | X | X
Command flag | 302 | 303 | 01; 05; 15 | Set oneshot 12 | X | X | X | X
Command flag | 303 | 304 | 01; 05; 15 | Set oneshot 13 | X | X | X | X
Command flag | 304 | 305 | 01; 05; 15 | Set oneshot 14 | X | X | X | X
Command flag | 305 | 306 | 01; 05; 15 | Set oneshot 15 | X | X | X | X
Command flag | 306 | 307 | 01; 05; 15 | Set oneshot 16 | X | X | X | X
Command flag | 307 | 308 | 01; 05; 15 | Virtual toggle set 1 | X | X | X | X
Command flag | 308 | 309 | 01; 05; 15 | Virtual toggle set 2 | X | X | X | X
Command flag | 309 | 310 | 01; 05; 15 | Virtual toggle set 3 | X | X | X | X
Command flag | 310 | 311 | 01; 05; 15 | Virtual toggle set 4 | X | X | X | X
Command flag | 311 | 312 | 01; 05; 15 | Virtual toggle set 5 | X | X | X | X
Command flag | 312 | 313 | 01; 05; 15 | Virtual toggle set 6 | X | X | X | X
Command flag | 313 | 314 | 01; 05; 15 | Virtual toggle set 7 | X | X | X | X
Command flag | 314 | 315 | 01; 05; 15 | Virtual toggle set 8 | X | X | X | X
Command flag | 315 | 316 | 01; 05; 15 | Virtual toggle set 9 | X | X | X | X
Command flag | 316 | 317 | 01; 05; 15 | Virtual toggle set 10 | X | X | X | X
Command flag | 317 | 318 | 01; 05; 15 | Virtual toggle set 11 | X | X | X | X
Command flag | 318 | 319 | 01; 05; 15 | Virtual toggle set 12 | X | X | X | X
Command flag | 319 | 320 | 01; 05; 15 | Virtual toggle set 13 | X | X | X | X
Command flag | 320 | 321 | 01; 05; 15 | Virtual toggle set 14 | X | X | X | X
Command flag | 321 | 322 | 01; 05; 15 | Virtual toggle set 15 | X | X | X | X
Command flag | 322 | 323 | 01; 05; 15 | Virtual toggle set 16 | X | X | X | X
Command flag | 323 | 324 | 01; 05; 15 | Virtual toggle set 17 | X | X | X | X
Command flag | 324 | 325 | 01; 05; 15 | Virtual toggle set 18 | X | X | X | X
Command flag | 325 | 326 | 01; 05; 15 | Virtual toggle set 19 | X | X | X | X
Command flag | 326 | 327 | 01; 05; 15 | Virtual toggle set 20 | X | X | X | X
Command flag | 327 | 328 | 01; 05; 15 | Virtual toggle set 21 | X | X | X | X
Command flag | 328 | 329 | 01; 05; 15 | Virtual toggle set 22 | X | X | X | X
Command flag | 329 | 330 | 01; 05; 15 | Virtual toggle set 23 | X | X | X | X
Command flag | 330 | 331 | 01; 05; 15 | Virtual toggle set 24 | X | X | X | X
Command flag | 331 | 332 | 01; 05; 15 | Virtual toggle set 25 | X | X | X | X
Command flag | 332 | 333 | 01; 05; 15 | Virtual toggle set 26 | X | X | X | X
Command flag | 333 | 334 | 01; 05; 15 | Virtual toggle set 27 | X | X | X | X
Command flag | 334 | 335 | 01; 05; 15 | Virtual toggle set 28 | X | X | X | X
Command flag | 335 | 336 | 01; 05; 15 | Virtual toggle set 29 | X | X | X | X
Command flag | 336 | 337 | 01; 05; 15 | Virtual toggle set 30 | X | X | X | X
Command flag | 337 | 338 | 01; 05; 15 | Virtual toggle set 31 | X | X | X | X
Command flag | 338 | 339 | 01; 05; 15 | Virtual toggle set 32 | X | X | X | X
Command flag | 340 | 341 | 01; 05; 15 | CAT C7.1 aftertreatment system - enable/disable |  |  | X | X
Command flag | 341 | 342 | 01; 05; 15 | CAT C7.1 aftertreatment dosing - standard/reduced |  |  | X | X

## Discrete input contact (02)
Discrete input contact (02)
Function group | Modbus address | PLC address | Modbus function code | Controller function name | BTB-M | SHORE | GEN-M | ENG-M
Status flag | 0 | 100001 | 02 | GB position ON |  |  | X
Status flag | 0 | 100001 | 02 | BTB position ON | X
Status flag | 1 | 100002 | 02 | TB position ON (EDG) |  |  | X
Status flag | 1 | 100002 | 02 | SCB position ON |  | X
Status flag | 3 | 100004 | 02 | Running |  |  | X | X
Status flag | 4 | 100005 | 02 | Generator voltage/frequency OK |  |  | X
Status flag | 4 | 100005 | 02 | Busbar voltage/frequency OK |  | X
Status flag | 4 | 100005 | 02 | Busbar B voltage/frequency OK | X
Status flag | 5 | 100006 | 02 | EDG bus failure (Single DG) |  |  | X
Status flag | 5 | 100006 | 02 | Shore failure |  | X
Status flag | 6 | 100007 | 02 | BLOCK mode |  |  | X | X
Status flag | 7 | 100008 | 02 | No Regulation mode |  |  | X | X
Status flag | 8 | 100009 | 02 | MANUAL mode | X | X | X | X
Status flag | 9 | 100010 | 02 | AUTO mode | X | X | X | X
Status flag | 10 | 100011 | 02 | TEST mode |  | X | X | X
Status flag | 11 | 100012 | 02 | GB position OFF |  |  | X
Status flag | 11 | 100012 | 02 | BTB position OFF | X
Status flag | 12 | 100013 | 02 | TB position OFF (EDG) |  |  | X
Status flag | 12 | 100013 | 02 | SCB position OFF |  | X
Status flag | 13 | 100014 | 02 | Island |  |  | X | X
Status flag | 14 | 100015 | 02 | EDG |  |  | X
Status flag | 20 | 100021 | 02 | Any alarm on PMS ID1 | X | X | X
Status flag | 21 | 100022 | 02 | Any alarm on PMS ID2 | X | X | X
Status flag | 28 | 100029 | 02 | Any alarm shore (Command Unit) | X | X | X
Status flag | 29 | 100030 | 02 | Battery test |  |  | X | X
Status flag | 31 | 100032 | 02 | Ready AUTO-start GEN1 | X | X | X
Status flag | 32 | 100033 | 02 | Ready AUTO-start GEN2 | X | X | X
Digital input | 22500 | 122501 | 02 | Digital input 39 | X | X | X | X
Digital input | 22501 | 122502 | 02 | Digital input 40 | X | X | X | X
Digital input | 22502 | 122503 | 02 | Digital input 41 | X | X | X | X
Digital input | 22503 | 122504 | 02 | Digital input 42 | X | X | X | X
Digital input | 22504 | 122505 | 02 | Digital input 43 | X | X | X | X
Digital input | 22505 | 122506 | 02 | Digital input 44 | X | X | X | X
Digital input | 22506 | 122507 | 02 | Digital input 45 | X | X | X | X
Digital input | 22507 | 122508 | 02 | Digital input 46 | X | X | X | X
Digital input | 22512 | 122513 | 02 | Dplus input 7 |  |  | X | X
Digital input | 22513 | 122514 | 02 | Emergency stop input 4 | X | X | X | X
Digital input | 22590 | 122591 | 02 | Binary in 23 | X | X | X | X
Digital input | 22591 | 122592 | 02 | Binary in 22 | X | X | X | X
Digital input | 22592 | 122593 | 02 | Binary in 21 | X | X | X | X
Digital input | 22593 | 122594 | 02 | Binary in 20 | X | X | X | X
Digital input | 22594 | 122595 | 02 | CIO 116 no. 1. Input 10 | X | X | X | X
Digital input | 22595 | 122596 | 02 | CIO 116 no. 1. Input 11 | X | X | X | X
Digital input | 22596 | 122597 | 02 | CIO 116 no. 1. Input 12 | X | X | X | X
Digital input | 22597 | 122598 | 02 | CIO 116 no. 1. Input 13 | X | X | X | X
Digital input | 22598 | 122599 | 02 | CIO 116 no. 1. Input 14 | X | X | X | X
Digital input | 22599 | 122600 | 02 | CIO 116 no. 1. Input 15 | X | X | X | X
Digital input | 22600 | 122601 | 02 | CIO 116 no. 1. Input 16 | X | X | X | X
Digital input | 22601 | 122602 | 02 | CIO 116 no. 1. Input 17 | X | X | X | X
Digital input | 22602 | 122603 | 02 | CIO 116 no. 1. Input 19 | X | X | X | X
Digital input | 22603 | 122604 | 02 | CIO 116 no. 1. Input 20 | X | X | X | X
Digital input | 22604 | 122605 | 02 | CIO 116 no. 1. Input 21 | X | X | X | X
Digital input | 22605 | 122606 | 02 | CIO 116 no. 1. Input 22 | X | X | X | X
Digital input | 22606 | 122607 | 02 | CIO 116 no. 1. Input 23 | X | X | X | X
Digital input | 22607 | 122608 | 02 | CIO 116 no. 1. Input 24 | X | X | X | X
Digital input | 22608 | 122609 | 02 | CIO 116 no. 1. Input 25 | X | X | X | X
Digital input | 22609 | 122610 | 02 | CIO 116 no. 1. Input 26 | X | X | X | X
Digital input | 22610 | 122611 | 02 | CIO 116 no. 2. Input 10 | X | X | X | X
Digital input | 22611 | 122612 | 02 | CIO 116 no. 2. Input 11 | X | X | X | X
Digital input | 22612 | 122613 | 02 | CIO 116 no. 2. Input 12 | X | X | X | X
Digital input | 22613 | 122614 | 02 | CIO 116 no. 2. Input 13 | X | X | X | X
Digital input | 22614 | 122615 | 02 | CIO 116 no. 2. Input 14 | X | X | X | X
Digital input | 22615 | 122616 | 02 | CIO 116 no. 2. Input 15 | X | X | X | X
Digital input | 22616 | 122617 | 02 | CIO 116 no. 2. Input 16 | X | X | X | X
Digital input | 22617 | 122618 | 02 | CIO 116 no. 2. Input 17 | X | X | X | X
Digital input | 22618 | 122619 | 02 | CIO 116 no. 2. Input 19 | X | X | X | X
Digital input | 22619 | 122620 | 02 | CIO 116 no. 2. Input 20 | X | X | X | X
Digital input | 22620 | 122621 | 02 | CIO 116 no. 2. Input 21 | X | X | X | X
Digital input | 22621 | 122622 | 02 | CIO 116 no. 2. Input 22 | X | X | X | X
Digital input | 22622 | 122623 | 02 | CIO 116 no. 2. Input 23 | X | X | X | X
Digital input | 22623 | 122624 | 02 | CIO 116 no. 2. Input 24 | X | X | X | X
Digital input | 22624 | 122625 | 02 | CIO 116 no. 2. Input 25 | X | X | X | X
Digital input | 22625 | 122626 | 02 | CIO 116 no. 2. Input 26 | X | X | X | X
Digital input | 22626 | 122627 | 02 | CIO 116 no. 3. Input 10 | X | X | X | X
Digital input | 22627 | 122628 | 02 | CIO 116 no. 3. Input 11 | X | X | X | X
Digital input | 22628 | 122629 | 02 | CIO 116 no. 3. Input 12 | X | X | X | X
Digital input | 22629 | 122630 | 02 | CIO 116 no. 3. Input 13 | X | X | X | X
Digital input | 22630 | 122631 | 02 | CIO 116 no. 3. Input 14 | X | X | X | X
Digital input | 22631 | 122632 | 02 | CIO 116 no. 3. Input 15 | X | X | X | X
Digital input | 22632 | 122633 | 02 | CIO 116 no. 3. Input 16 | X | X | X | X
Digital input | 22633 | 122634 | 02 | CIO 116 no. 3. Input 17 | X | X | X | X
Digital input | 22634 | 122635 | 02 | CIO 116 no. 3. Input 19 | X | X | X | X
Digital input | 22635 | 122636 | 02 | CIO 116 no. 3. Input 20 | X | X | X | X
Digital input | 22636 | 122637 | 02 | CIO 116 no. 3. Input 21 | X | X | X | X
Digital input | 22637 | 122638 | 02 | CIO 116 no. 3. Input 22 | X | X | X | X
Digital input | 22638 | 122639 | 02 | CIO 116 no. 3. Input 23 | X | X | X | X
Digital input | 22639 | 122640 | 02 | CIO 116 no. 3. Input 24 | X | X | X | X
Digital input | 22640 | 122641 | 02 | CIO 116 no. 3. Input 25 | X | X | X | X
Digital input | 22641 | 122642 | 02 | CIO 116 no. 3. Input 26 | X | X | X | X
Digital input | 22674 | 122675 | 02 | CIO 308 no. 1. Input 8 | X | X | X | X
Digital input | 22675 | 122676 | 02 | CIO 308 no. 1. Input 11 | X | X | X | X
Digital input | 22676 | 122677 | 02 | CIO 308 no. 1. Input 14 | X | X | X | X
Digital input | 22677 | 122678 | 02 | CIO 308 no. 1. Input 17 | X | X | X | X
Digital input | 22678 | 122679 | 02 | CIO 308 no. 1. Input 20 | X | X | X | X
Digital input | 22679 | 122680 | 02 | CIO 308 no. 1. Input 23 | X | X | X | X
Digital input | 22680 | 122681 | 02 | CIO 308 no. 1. Input 26 | X | X | X | X
Digital input | 22681 | 122682 | 02 | CIO 308 no. 1. Input 29 | X | X | X | X
Digital input | 22682 | 122683 | 02 | CIO 308 no. 2. Input 8 | X | X | X | X
Digital input | 22683 | 122684 | 02 | CIO 308 no. 2. Input 11 | X | X | X | X
Digital input | 22684 | 122685 | 02 | CIO 308 no. 2. Input 14 | X | X | X | X
Digital input | 22685 | 122686 | 02 | CIO 308 no. 2. Input 17 | X | X | X | X
Digital input | 22686 | 122687 | 02 | CIO 308 no. 2. Input 20 | X | X | X | X
Digital input | 22687 | 122688 | 02 | CIO 308 no. 2. Input 23 | X | X | X | X
Digital input | 22688 | 122689 | 02 | CIO 308 no. 2. Input 26 | X | X | X | X
Digital input | 22689 | 122690 | 02 | CIO 308 no. 2. Input 29 | X | X | X | X
Digital input | 22690 | 122691 | 02 | CIO 308 no. 3. Input 8 | X | X | X | X
Digital input | 22691 | 122692 | 02 | CIO 308 no. 3. Input 11 | X | X | X | X
Digital input | 22692 | 122693 | 02 | CIO 308 no. 3. Input 14 | X | X | X | X
Digital input | 22693 | 122694 | 02 | CIO 308 no. 3. Input 17 | X | X | X | X
Digital input | 22694 | 122695 | 02 | CIO 308 no. 3. Input 20 | X | X | X | X
Digital input | 22695 | 122696 | 02 | CIO 308 no. 3. Input 23 | X | X | X | X
Digital input | 22696 | 122697 | 02 | CIO 308 no. 3. Input 26 | X | X | X | X
Digital input | 22697 | 122698 | 02 | CIO 308 no. 3. Input 29 | X | X | X | X
Digital output | 23003 | 123004 | 02 | Relay 9 | X | X | X | X
Digital output | 23004 | 123005 | 02 | Relay 10 | X | X | X | X
Digital output | 23005 | 123006 | 02 | Relay 11 | X | X | X | X
Digital output | 23006 | 123007 | 02 | Relay 12 | X | X | X | X
Digital output | 23007 | 123008 | 02 | Relay 13 | X | X | X | X
Digital output | 23008 | 123009 | 02 | Relay 14 | X | X | X | X
Digital output | 23026 | 123027 | 02 | Relay 16 | X | X | X | X
Digital output | 23027 | 123028 | 02 | Relay 15 | X | X | X | X
Digital output | 23028 | 123029 | 02 | Relay 18 | X | X | X | X
Digital output | 23029 | 123030 | 02 | Relay 17 | X | X | X | X
Digital output | 23030 | 123031 | 02 | Relay 5 | X | X | X | X
Digital output | 23031 | 123032 | 02 | Relay 6 | X | X | X | X
Digital output | 23056 | 123057 | 02 | CIO 208 no. 1. Output 9 | X | X | X | X
Digital output | 23057 | 123058 | 02 | CIO 208 no. 1. Output 11 | X | X | X | X
Digital output | 23058 | 123059 | 02 | CIO 208 no. 1. Output 13 | X | X | X | X
Digital output | 23059 | 123060 | 02 | CIO 208 no. 1. Output 15 | X | X | X | X
Digital output | 23060 | 123061 | 02 | CIO 208 no. 1. Output 18 | X | X | X | X
Digital output | 23061 | 123062 | 02 | CIO 208 no. 1. Output 21 | X | X | X | X
Digital output | 23062 | 123063 | 02 | CIO 208 no. 1. Output 24 | X | X | X | X
Digital output | 23063 | 123064 | 02 | CIO 208 no. 1. Output 27 | X | X | X | X
Digital output | 23064 | 123065 | 02 | CIO 208 no. 2. Output 9 | X | X | X | X
Digital output | 23065 | 123066 | 02 | CIO 208 no. 2. Output 11 | X | X | X | X
Digital output | 23066 | 123067 | 02 | CIO 208 no. 2. Output 13 | X | X | X | X
Digital output | 23067 | 123068 | 02 | CIO 208 no. 2. Output 15 | X | X | X | X
Digital output | 23068 | 123069 | 02 | CIO 208 no. 2. Output 18 | X | X | X | X
Digital output | 23069 | 123070 | 02 | CIO 208 no. 2. Output 21 | X | X | X | X
Digital output | 23070 | 123071 | 02 | CIO 208 no. 2. Output 24 | X | X | X | X
Digital output | 23071 | 123072 | 02 | CIO 208 no. 2. Output 27 | X | X | X | X
Digital output | 23072 | 123073 | 02 | CIO 208 no. 3. Output 9 | X | X | X | X
Digital output | 23073 | 123074 | 02 | CIO 208 no. 3. Output 11 | X | X | X | X
Digital output | 23074 | 123075 | 02 | CIO 208 no. 3. Output 13 | X | X | X | X
Digital output | 23075 | 123076 | 02 | CIO 208 no. 3. Output 15 | X | X | X | X
Digital output | 23076 | 123077 | 02 | CIO 208 no. 3. Output 18 | X | X | X | X
Digital output | 23077 | 123078 | 02 | CIO 208 no. 3. Output 21 | X | X | X | X
Digital output | 23078 | 123079 | 02 | CIO 208 no. 3. Output 24 | X | X | X | X
Digital output | 23079 | 123080 | 02 | CIO 208 no. 3. Output 27 | X | X | X | X
Digital output | 23080 | 123081 | 02 | CIO 116 no. 1 conf. status out | X | X | X | X
Digital output | 23081 | 123082 | 02 | CIO 116 no. 2 conf. status out | X | X | X | X
Digital output | 23082 | 123083 | 02 | CIO 116 no. 3 conf. status out | X | X | X | X
Digital output | 23083 | 123084 | 02 | CIO 208 no. 1 conf. status out | X | X | X | X
Digital output | 23084 | 123085 | 02 | CIO 208 no. 2 conf. status out | X | X | X | X
Digital output | 23085 | 123086 | 02 | CIO 208 no. 3 conf. status out | X | X | X | X
Digital output | 23086 | 123087 | 02 | CIO 308 no. 1 conf. status out | X | X | X | X
Digital output | 23087 | 123088 | 02 | CIO 308 no. 2 conf. status out | X | X | X | X
Digital output | 23088 | 123089 | 02 | CIO 308 no. 3 conf. status out | X | X | X | X

## Holding register (03;06;16)
Holding register (03;06;16)
Function group | Modbus address | Bit | PLC address | Modbus function code | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | BTB-M | SHORE | GEN-M | ENG-M
Control command | 0 |  | 400001 | 03; 06; 16 | Power regulator setpoint - 0...100% of nominal power. Activated in menu 7501 | INT16s | AB | 0 |  |  | X | X
Control command | 1 |  | 400002 | 03; 06; 16 | cosPhi regulator setpoint - 60...100 stated as cosPhi value/100. The value 100 means cosPhi = 1.00 Activated in menu 7504 | INT16s | AB | 0 |  |  |  | X
Control command | 2 |  | 400003 | 03; 06; 16 | Reactive power regulator setpoint - +/-100% of nominal power. A negative value means capacitive reactive power, and a positive value means inductive reactive power. Activated in menu 7505 | INT16s | AB | 0 |  |  |  | X
Control command | 3 |  | 400004 | 03; 06; 16 | Frequency regulator setpoint - +/-100% corresponding to +/10.0% of nominal frequency. Activated in menu 7502 | INT16s | AB | 0 |  |  |  | X
Control command | 4 |  | 400005 | 03; 06; 16 | Voltage regulator setpoint - +/-100% corresponding to +/10.0% of nominal voltage. Activated in menu 7503 | INT16s | AB | 0 |  |  |  | X
Control command | 5 | 0 | 400006 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X | X
Control command | 5 | 1 | 400006 | 03; 06; 16 | Remote start | BOOL | [5 empty] | X | X
Control command | 5 | 2 | 400006 | 03; 06; 16 | Remote GB ON | BOOL | [5 empty] | X
Control command | 5 | 2 | 400006 | 03; 06; 16 | Remote BTB ON | BOOL |  |  |  | X
Control command | 5 | 3 | 400006 | 03; 06; 16 | Remote GB OFF | BOOL | [5 empty] | X
Control command | 5 | 3 | 400006 | 03; 06; 16 | Remote BTB OFF | BOOL |  |  |  | X
Control command | 5 | 4 | 400006 | 03; 06; 16 | Remote stop | BOOL | [5 empty] | X | X
Control command | 5 | 5 | 400006 | 03; 06; 16 | Reset GOV/AVR regulation output to offset | BOOL | [5 empty] | X
Control command | 5 | 6 | 400006 | 03; 06; 16 | Remotely start + GB on | BOOL | [5 empty] | X
Control command | 5 | 7 | 400006 | 03; 06; 16 | Alarm inhibit 1 | BOOL | [5 empty] | X | X
Control command | 5 | 8 | 400006 | 03; 06; 16 | Alarm inhibit 2 | BOOL | [5 empty] | X | X
Control command | 5 | 9 | 400006 | 03; 06; 16 | Alarm inhibit 3 | BOOL | [5 empty] | X | X
Control command | 5 | 10 | 400006 | 03; 06; 16 | Alarm ack. | BOOL |  |  |  | X | X | X | X
Control command | 5 | 11 | 400006 | 03; 06; 16 | Nominal setting 1 | BOOL |  |  |  | X | X | X
Control command | 5 | 12 | 400006 | 03; 06; 16 | Nominal setting 2 | BOOL |  |  |  | X | X | X
Control command | 5 | 13 | 400006 | 03; 06; 16 | Nominal setting 3 | BOOL |  |  |  | X | X | X
Control command | 5 | 14 | 400006 | 03; 06; 16 | Nominal setting 4 | BOOL |  |  |  | X | X | X
Control command | 5 | 15 | 400006 | 03; 06; 16 | Remotely GB off + stop | BOOL | [5 empty] | X
Control command | 6 | 0 | 400007 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X | X
Control command | 6 | 1 | 400007 | 03; 06; 16 | Island | BOOL | [5 empty] | X
Control command | 6 | 2 | 400007 | 03; 06; 16 | EDG | BOOL | [5 empty] | X
Control command | 6 | 9 | 400007 | 03; 06; 16 | TB ON (EDG) | BOOL | [5 empty] | X
Control command | 6 | 9 | 400007 | 03; 06; 16 | SCB ON | BOOL |  |  |  |  | X
Control command | 6 | 10 | 400007 | 03; 06; 16 | TB OFF (EDG) | BOOL | [5 empty] | X
Control command | 6 | 10 | 400007 | 03; 06; 16 | SCB OFF | BOOL |  |  |  |  | X
Control command | 6 | 11 | 400007 | 03; 06; 16 | Auto start/stop (EDG) | BOOL | [5 empty] | X
Control command | 6 | 13 | 400007 | 03; 06; 16 | REMOTE mode | BOOL | [5 empty] | X | X
Control command | 6 | 13 | 400007 | 03; 06; 16 | AUTO mode | BOOL |  |  |  | X | X
Control command | 6 | 14 | 400007 | 03; 06; 16 | LOCAL mode | BOOL | [5 empty] | X | X
Control command | 6 | 14 | 400007 | 03; 06; 16 | MANUAL mode | BOOL |  |  |  | X | X
Control command | 6 | 15 | 400007 | 03; 06; 16 | TEST mode | BOOL |  |  |  |  | X | X | X
Control command | 7 | 0 | 400008 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X | X
Control command | 7 | 1 | 400008 | 03; 06; 16 | External frequency control | BOOL | [5 empty] | X
Control command | 7 | 2 | 400008 | 03; 06; 16 | External voltage control | BOOL | [5 empty] | X
Control command | 7 | 3 | 400008 | 03; 06; 16 | External power control | BOOL | [5 empty] | X
Control command | 7 | 4 | 400008 | 03; 06; 16 | External reactive power control | BOOL | [5 empty] | X
Control command | 7 | 5 | 400008 | 03; 06; 16 | External power factor control | BOOL | [5 empty] | X
Control command | 7 | 6 | 400008 | 03; 06; 16 | Capacitive PF | BOOL | [5 empty] | X
Control command | 7 | 9 | 400008 | 03; 06; 16 | Application 1 | BOOL |  |  |  | X | X | X
Control command | 7 | 10 | 400008 | 03; 06; 16 | Application 2 | BOOL |  |  |  | X | X | X
Control command | 7 | 11 | 400008 | 03; 06; 16 | Application 3 | BOOL |  |  |  | X | X | X
Control command | 7 | 12 | 400008 | 03; 06; 16 | Application 4 | BOOL |  |  |  | X | X | X
Control command | 7 | 13 | 400008 | 03; 06; 16 | Battery test | BOOL | [5 empty] | X | X
Control command | 7 | 15 | 400008 | 03; 06; 16 | Synchronise clock to 4:00 a.m. | BOOL |  |  |  | X | X | X | X
Control command | 8 | 0 | 400009 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X | X
Control command | 8 | 1 | 400009 | 03; 06; 16 | Virtual toggle event 1 | BOOL |  |  |  | X | X | X | X
Control command | 8 | 2 | 400009 | 03; 06; 16 | Virtual toggle event 2 | BOOL |  |  |  | X | X | X | X
Control command | 8 | 3 | 400009 | 03; 06; 16 | Virtual toggle event 3 | BOOL |  |  |  | X | X | X | X
Control command | 8 | 4 | 400009 | 03; 06; 16 | Virtual toggle event 4 | BOOL |  |  |  | X | X | X | X
Control command | 8 | 5 | 400009 | 03; 06; 16 | Virtual toggle event 5 | BOOL |  |  |  | X | X | X | X
Control command | 8 | 6 | 400009 | 03; 06; 16 | Virtual toggle event 6 | BOOL |  |  |  | X | X | X | X
Control command | 8 | 7 | 400009 | 03; 06; 16 | Virtual toggle event 7 | BOOL |  |  |  | X | X | X | X
Control command | 8 | 8 | 400009 | 03; 06; 16 | Virtual toggle event 8 | BOOL |  |  |  | X | X | X | X
Control command | 8 | 9 | 400009 | 03; 06; 16 | Virtual toggle event 9 | BOOL |  |  |  | X | X | X | X
Control command | 8 | 10 | 400009 | 03; 06; 16 | Virtual toggle event 10 | BOOL |  |  |  | X | X | X | X
Control command | 8 | 11 | 400009 | 03; 06; 16 | Virtual toggle event 11 | BOOL |  |  |  | X | X | X | X
Control command | 8 | 12 | 400009 | 03; 06; 16 | Virtual toggle event 12 | BOOL |  |  |  | X | X | X | X
Control command | 8 | 13 | 400009 | 03; 06; 16 | Virtual toggle event 13 | BOOL |  |  |  | X | X | X | X
Control command | 8 | 14 | 400009 | 03; 06; 16 | Virtual toggle event 14 | BOOL |  |  |  | X | X | X | X
Control command | 8 | 15 | 400009 | 03; 06; 16 | Virtual toggle event 15 | BOOL |  |  |  | X | X | X | X
Control command | 9 | 0 | 400010 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X | X
Control command | 9 | 1 | 400010 | 03; 06; 16 | Virtual toggle event 16 | BOOL |  |  |  | X | X | X | X
Control command | 9 | 2 | 400010 | 03; 06; 16 | Virtual toggle event 17 | BOOL |  |  |  | X | X | X | X
Control command | 9 | 3 | 400010 | 03; 06; 16 | Virtual toggle event 18 | BOOL |  |  |  | X | X | X | X
Control command | 9 | 4 | 400010 | 03; 06; 16 | Virtual toggle event 19 | BOOL |  |  |  | X | X | X | X
Control command | 9 | 5 | 400010 | 03; 06; 16 | Virtual toggle event 20 | BOOL |  |  |  | X | X | X | X
Control command | 9 | 6 | 400010 | 03; 06; 16 | Virtual toggle event 21 | BOOL |  |  |  | X | X | X | X
Control command | 9 | 7 | 400010 | 03; 06; 16 | Virtual toggle event 22 | BOOL |  |  |  | X | X | X | X
Control command | 9 | 8 | 400010 | 03; 06; 16 | Virtual toggle event 23 | BOOL |  |  |  | X | X | X | X
Control command | 9 | 9 | 400010 | 03; 06; 16 | Virtual toggle event 24 | BOOL |  |  |  | X | X | X | X
Control command | 9 | 10 | 400010 | 03; 06; 16 | Virtual toggle event 25 | BOOL |  |  |  | X | X | X | X
Control command | 9 | 11 | 400010 | 03; 06; 16 | Virtual toggle event 26 | BOOL |  |  |  | X | X | X | X
Control command | 9 | 12 | 400010 | 03; 06; 16 | Virtual toggle event 27 | BOOL |  |  |  | X | X | X | X
Control command | 9 | 13 | 400010 | 03; 06; 16 | Virtual toggle event 28 | BOOL |  |  |  | X | X | X | X
Control command | 9 | 14 | 400010 | 03; 06; 16 | Virtual toggle event 29 | BOOL |  |  |  | X | X | X | X
Control command | 9 | 15 | 400010 | 03; 06; 16 | Virtual toggle event 30 | BOOL |  |  |  | X | X | X | X
Control command | 10 | 0 | 400011 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X | X
Control command | 10 | 1 | 400011 | 03; 06; 16 | Virtual event 31 | BOOL |  |  |  | X | X | X | X
Control command | 10 | 2 | 400011 | 03; 06; 16 | Virtual event 32 | BOOL |  |  |  | X | X | X | X
Control command | 10 | 4 | 400011 | 03; 06; 16 | Clear log | BOOL |  |  |  | X | X | X | X
Control command | 10 | 5 | 400011 | 03; 06; 16 | Clear Parameter edits | BOOL |  |  |  | X | X | X | X
Control command | 10 | 6 | 400011 | 03; 06; 16 | PID1 activate manual regulation | BOOL | [6 empty] | X
Control command | 10 | 7 | 400011 | 03; 06; 16 | PID1 de-activate manual regulation | BOOL | [6 empty] | X
Control command | 13 | 0 | 400014 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X | X
Control command | 13 | 1 | 400014 | 03; 06; 16 | Enable external frequency control | BOOL | [5 empty] | X
Control command | 13 | 2 | 400014 | 03; 06; 16 | Disable external frequency control | BOOL | [5 empty] | X
Control command | 13 | 3 | 400014 | 03; 06; 16 | Enable external voltage control | BOOL | [5 empty] | X
Control command | 13 | 4 | 400014 | 03; 06; 16 | Disable external voltage control | BOOL | [5 empty] | X
Control command | 13 | 5 | 400014 | 03; 06; 16 | Enable external power control | BOOL | [5 empty] | X
Control command | 13 | 6 | 400014 | 03; 06; 16 | Disable external power control | BOOL | [5 empty] | X
Control command | 13 | 7 | 400014 | 03; 06; 16 | Enable external VAr control | BOOL | [5 empty] | X
Control command | 13 | 8 | 400014 | 03; 06; 16 | Disable external VAr control | BOOL | [5 empty] | X
Control command | 13 | 9 | 400014 | 03; 06; 16 | Enable external CosPhi control | BOOL | [5 empty] | X
Control command | 13 | 10 | 400014 | 03; 06; 16 | Disable external CosPhi control | BOOL | [5 empty] | X
Control command | 13 | 13 | 400014 | 03; 06; 16 | Reset horn | BOOL |  |  |  | X | X | X | X
Control time command | 58000 |  | 458001 | 03; 06; 16 | Year (2003-2099) | INT16s | AB | 0 |  | X | X | X | X
Control time command | 58001 |  | 458002 | 03; 06; 16 | Month (1-12) | INT16s | AB | 0 |  | X | X | X | X
Control time command | 58002 |  | 458003 | 03; 06; 16 | Date (1-31) | INT16s | AB | 0 |  | X | X | X | X
Control time command | 58003 |  | 458004 | 03; 06; 16 | Day (1-7, Monday - Sunday) | INT16s | AB | 0 |  | X | X | X | X
Control time command | 58004 |  | 458005 | 03; 06; 16 | Hour (0-23) | INT16s | AB | 0 |  | X | X | X | X
Control time command | 58005 |  | 458006 | 03; 06; 16 | Min (0-59) | INT16s | AB | 0 |  | X | X | X | X
Control time command | 58006 |  | 458007 | 03; 06; 16 | Sec (0-59) | INT16s | AB | 0 |  | X | X | X | X

## Input register (04)
Input register (04)
Function group | Modbus address | Bit | PLC address | Modbus function code | Channel | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | BTB-M | SHORE | GEN-M | ENG-M
APPL version | 500 |  | 300501 | 04 |  | Application version | INT16s | AB | 0 |  | X | X | X | X
AC measurement | 501 |  | 300502 | 04 |  | Generator voltage L1-L2 | INT16s | AB | 0 | V |  |  | X
AC measurement | 501 |  | 300502 | 04 |  | Shore voltage L1-L2 | INT16s | AB | 0 | V |  | X
AC measurement | 501 |  | 300502 | 04 |  | Bus A voltage L1-L2 | INT16s | AB | 0 | V | X
AC measurement | 502 |  | 300503 | 04 |  | Generator voltage L2-L3 | INT16s | AB | 0 | V |  |  | X
AC measurement | 502 |  | 300503 | 04 |  | Shore voltage L2-L3 | INT16s | AB | 0 | V |  | X
AC measurement | 502 |  | 300503 | 04 |  | Bus A voltage L2-L3 | INT16s | AB | 0 | V | X
AC measurement | 503 |  | 300504 | 04 |  | Generator voltage L3-L1 | INT16s | AB | 0 | V |  |  | X
AC measurement | 503 |  | 300504 | 04 |  | Shore voltage L3-L1 | INT16s | AB | 0 | V |  | X
AC measurement | 503 |  | 300504 | 04 |  | Bus A voltage L3-L1 | INT16s | AB | 0 | V | X
AC measurement | 504 |  | 300505 | 04 |  | Generator voltage L1-N | INT16s | AB | 0 | V |  |  | X
AC measurement | 504 |  | 300505 | 04 |  | Shore voltage L1-N | INT16s | AB | 0 | V |  | X
AC measurement | 504 |  | 300505 | 04 |  | Bus A voltage L1-N | INT16s | AB | 0 | V | X
AC measurement | 505 |  | 300506 | 04 |  | Generator voltage L2-N | INT16s | AB | 0 | V |  |  | X
AC measurement | 505 |  | 300506 | 04 |  | Shore voltage L2-N | INT16s | AB | 0 | V |  | X
AC measurement | 505 |  | 300506 | 04 |  | Bus A voltage L2-N | INT16s | AB | 0 | V | X
AC measurement | 506 |  | 300507 | 04 |  | Generator voltage L3-N | INT16s | AB | 0 | V |  |  | X
AC measurement | 506 |  | 300507 | 04 |  | Shore voltage L3-N | INT16s | AB | 0 | V |  | X
AC measurement | 506 |  | 300507 | 04 |  | Bus A voltage L3-N | INT16s | AB | 0 | V | X
AC measurement | 507 |  | 300508 | 04 |  | Generator frequency L1 | INT16s | AB | 2 | Hz |  |  | X
AC measurement | 507 |  | 300508 | 04 |  | Shore frequency L1 | INT16s | AB | 2 | Hz |  | X
AC measurement | 507 |  | 300508 | 04 |  | Bus A frequency L1 | INT16s | AB | 2 | Hz | X
AC measurement | 508 |  | 300509 | 04 |  | Generator frequency L2 | INT16s | AB | 2 | Hz |  |  | X
AC measurement | 508 |  | 300509 | 04 |  | Shore frequency L2 | INT16s | AB | 2 | Hz |  | X
AC measurement | 508 |  | 300509 | 04 |  | Bus A frequency L2 | INT16s | AB | 2 | Hz | X
AC measurement | 509 |  | 300510 | 04 |  | Generator frequency L3 | INT16s | AB | 2 | Hz |  |  | X
AC measurement | 509 |  | 300510 | 04 |  | Shore frequency L3 | INT16s | AB | 2 | Hz |  | X
AC measurement | 509 |  | 300510 | 04 |  | Bus A frequency L3 | INT16s | AB | 2 | Hz | X
AC measurement | 510 |  | 300511 | 04 |  | Generator voltage phase angle L1-L2 | INT16s | AB | 1 | Deg |  |  | X
AC measurement | 510 |  | 300511 | 04 |  | Shore voltage phase angle L1-L2 | INT16s | AB | 1 | Deg |  | X
AC measurement | 510 |  | 300511 | 04 |  | Bus A voltage phase angle L1-L2 | INT16s | AB | 1 | Deg | X
AC measurement | 511 |  | 300512 | 04 |  | Generator voltage phase angle L2-L3 | INT16s | AB | 1 | Deg |  |  | X
AC measurement | 511 |  | 300512 | 04 |  | Shore voltage phase angle L2-L3 | INT16s | AB | 1 | Deg |  | X
AC measurement | 511 |  | 300512 | 04 |  | Bus A voltage phase angle L2-L3 | INT16s | AB | 1 | Deg | X
AC measurement | 512 |  | 300513 | 04 |  | Generator voltage phase angle L3-L1 | INT16s | AB | 1 | Deg |  |  | X
AC measurement | 512 |  | 300513 | 04 |  | Shore voltage phase angle L3-L1 | INT16s | AB | 1 | Deg |  | X
AC measurement | 512 |  | 300513 | 04 |  | Bus A voltage phase angle L3-L1 | INT16s | AB | 1 | Deg | X
AC measurement | 513 |  | 300514 | 04 |  | Generator current L1 | INT16s | AB | 0 | A |  |  | X
AC measurement | 513 |  | 300514 | 04 |  | Shore current L1 | INT16s | AB | 0 | A |  | X
AC measurement | 513 |  | 300514 | 04 |  | Bus A current L1 | INT16s | AB | 0 | A | X
AC measurement | 514 |  | 300515 | 04 |  | Generator current L2 | INT16s | AB | 0 | A |  |  | X
AC measurement | 514 |  | 300515 | 04 |  | Shore current L2 | INT16s | AB | 0 | A |  | X
AC measurement | 514 |  | 300515 | 04 |  | Bus A current L2 | INT16s | AB | 0 | A | X
AC measurement | 515 |  | 300516 | 04 |  | Generator current L3 | INT16s | AB | 0 | A |  |  | X
AC measurement | 515 |  | 300516 | 04 |  | Shore current L3 | INT16s | AB | 0 | A |  | X
AC measurement | 515 |  | 300516 | 04 |  | Bus A current L3 | INT16s | AB | 0 | A | X
AC measurement | 516 |  | 300517 | 04 |  | Generator power L1 | INT16s | AB | 0 | kW |  |  | X
AC measurement | 516 |  | 300517 | 04 |  | Shore power L1 | INT16s | AB | 0 | kW |  | X
AC measurement | 516 |  | 300517 | 04 |  | Bus A power L1 | INT16s | AB | 0 | kW | X
AC measurement | 517 |  | 300518 | 04 |  | Generator power L2 | INT16s | AB | 0 | kW |  |  | X
AC measurement | 517 |  | 300518 | 04 |  | Shore power L2 | INT16s | AB | 0 | kW |  | X
AC measurement | 517 |  | 300518 | 04 |  | Bus A power L2 | INT16s | AB | 0 | kW | X
AC measurement | 518 |  | 300519 | 04 |  | Generator power L3 | INT16s | AB | 0 | kW |  |  | X
AC measurement | 518 |  | 300519 | 04 |  | Shore power L3 | INT16s | AB | 0 | kW |  | X
AC measurement | 518 |  | 300519 | 04 |  | Bus A power L3 | INT16s | AB | 0 | kW | X
AC measurement | 519 |  | 300520 | 04 |  | Generator power | INT16s | AB | 0 | kW |  |  | X
AC measurement | 519 |  | 300520 | 04 |  | Shore power | INT16s | AB | 0 | kW |  | X
AC measurement | 519 |  | 300520 | 04 |  | Bus A power | INT16s | AB | 0 | kW | X
AC measurement | 520 |  | 300521 | 04 |  | Shore reactive power L1 | INT16s | AB | 0 | kVAr |  | X
AC measurement | 520 |  | 300521 | 04 |  | Generator reactive power L1 | INT16s | AB | 0 | kVAr |  |  | X
AC measurement | 520 |  | 300521 | 04 |  | Bus A reactive power L1 | INT16s | AB | 0 | kVAr | X
AC measurement | 521 |  | 300522 | 04 |  | Generator reactive power L2 | INT16s | AB | 0 | kVAr |  |  | X
AC measurement | 521 |  | 300522 | 04 |  | Shore reactive power L2 | INT16s | AB | 0 | kVAr |  | X
AC measurement | 521 |  | 300522 | 04 |  | Bus A reactive power L2 | INT16s | AB | 0 | kVAr | X
AC measurement | 522 |  | 300523 | 04 |  | Generator reactive power L3 | INT16s | AB | 0 | kVAr |  |  | X
AC measurement | 522 |  | 300523 | 04 |  | Shore reactive power L3 | INT16s | AB | 0 | kVAr |  | X
AC measurement | 522 |  | 300523 | 04 |  | Bus A reactive power L3 | INT16s | AB | 0 | kVAr | X
AC measurement | 523 |  | 300524 | 04 |  | Generator reactive power | INT16s | AB | 0 | kVAr |  |  | X
AC measurement | 523 |  | 300524 | 04 |  | Shore reactive power | INT16s | AB | 0 | kVAr |  | X
AC measurement | 523 |  | 300524 | 04 |  | Bus A reactive power | INT16s | AB | 0 | kVAr | X
AC measurement | 524 |  | 300525 | 04 |  | Generator apparent power L1 | INT16s | AB | 0 | kVA |  |  | X
AC measurement | 524 |  | 300525 | 04 |  | Shore apparent power L1 | INT16s | AB | 0 | kVA |  | X
AC measurement | 524 |  | 300525 | 04 |  | Bus A apparent power L1 | INT16s | AB | 0 | kVA | X
AC measurement | 525 |  | 300526 | 04 |  | Generator apparent power L2 | INT16s | AB | 0 | kVA |  |  | X
AC measurement | 525 |  | 300526 | 04 |  | Shore apparent power L2 | INT16s | AB | 0 | kVA |  | X
AC measurement | 525 |  | 300526 | 04 |  | Bus A apparent power L2 | INT16s | AB | 0 | kVA | X
AC measurement | 526 |  | 300527 | 04 |  | Shore apparent power L3 | INT16s | AB | 0 | kVA |  | X
AC measurement | 526 |  | 300527 | 04 |  | Generator apparent power L3 | INT16s | AB | 0 | kVA |  |  | X
AC measurement | 526 |  | 300527 | 04 |  | Bus A apparent power L3 | INT16s | AB | 0 | kVA | X
AC measurement | 527 |  | 300528 | 04 |  | Generator apparent power | INT16s | AB | 0 | kVA |  |  | X
AC measurement | 527 |  | 300528 | 04 |  | Shore apparent power | INT16s | AB | 0 | kVA |  | X
AC measurement | 527 |  | 300528 | 04 |  | Bus A apparent power | INT16s | AB | 0 | kVA | X
Counter | 528 |  | 300529 | 04 |  | Generator Export reactive energy counter, total | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 528 |  | 300529 | 04 |  | Bus A Export reactive energy counter, total | INT32s | ABCD | 0 | kVArh | X
Counter | 530 |  | 300531 | 04 |  | Generator Export, active energy counter, day | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 530 |  | 300531 | 04 |  | Bus A Export, active energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 532 |  | 300533 | 04 |  | Generator Export, active energy counter, week | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 532 |  | 300533 | 04 |  | Bus A Export, active energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 534 |  | 300535 | 04 |  | Generator Export, active energy counter, month | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 534 |  | 300535 | 04 |  | Bus A Export, active energy counter, month | INT32s | ABCD | 0 | kWh | X
Counter | 536 |  | 300537 | 04 |  | Generator Export, active energy counter, total | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 536 |  | 300537 | 04 |  | Bus A Export, active energy counter, total | INT32s | ABCD | 0 | kWh | X
AC measurement | 538 |  | 300539 | 04 |  | Generator PF | INT16s | AB | 2 | PF |  |  | X
AC measurement | 538 |  | 300539 | 04 |  | Shore PF | INT16s | AB | 2 | PF |  | X
AC measurement | 538 |  | 300539 | 04 |  | Bus A PF | INT16s | AB | 2 | PF | X
AC measurement | 539 |  | 300540 | 04 |  | Bus B voltage L1-L2 | INT16s | AB | 0 | V | X | X | X
AC measurement | 540 |  | 300541 | 04 |  | Bus B voltage L2-L3 | INT16s | AB | 0 | V | X | X | X
AC measurement | 541 |  | 300542 | 04 |  | Bus B voltage L3-L1 | INT16s | AB | 0 | V | X | X | X
AC measurement | 542 |  | 300543 | 04 |  | Bus B voltage L1-N | INT16s | AB | 0 | V | X | X | X
AC measurement | 543 |  | 300544 | 04 |  | Bus B voltage L2-N | INT16s | AB | 0 | V | X | X | X
AC measurement | 544 |  | 300545 | 04 |  | Bus B voltage L3-N | INT16s | AB | 0 | V | X | X | X
AC measurement | 545 |  | 300546 | 04 |  | Bus B frequency L1 | INT16s | AB | 2 | Hz | X | X | X
AC measurement | 546 |  | 300547 | 04 |  | Bus B frequency L2 | INT16s | AB | 2 | Hz | X | X | X
AC measurement | 547 |  | 300548 | 04 |  | Bus B frequency L3 | INT16s | AB | 2 | Hz | X | X | X
AC measurement | 548 |  | 300549 | 04 |  | Bus B voltage phase angle L1-L2 | INT16s | AB | 1 | Deg | X | X | X
AC measurement | 549 |  | 300550 | 04 |  | Bus B voltage phase angle L2-L3 | INT16s | AB | 1 | Deg | X | X | X
AC measurement | 550 |  | 300551 | 04 |  | Bus B voltage phase angle L3-L1 | INT16s | AB | 1 | Deg | X | X | X
AC measurement | 551 |  | 300552 | 04 |  | U BB L1 - U GEN L1 phase angle | INT16s | AB | 1 | Deg |  |  | X
AC measurement | 551 |  | 300552 | 04 |  | U BB L1 - U Shore L1 phase angle | INT16s | AB | 1 | Deg |  | X
AC measurement | 551 |  | 300552 | 04 |  | U BB A L1 - U BB B L1 phase angle | INT16s | AB | 1 | Deg | X
AC measurement | 552 |  | 300553 | 04 |  | U BB L2 - U GEN L2 phase angle | INT16s | AB | 1 | Deg |  |  | X
AC measurement | 552 |  | 300553 | 04 |  | U BB L2 - U Shore L2 phase angle | INT16s | AB | 1 | Deg |  | X
AC measurement | 552 |  | 300553 | 04 |  | U BB A L2 - U BB B L2 phase angle | INT16s | AB | 1 | Deg | X
AC measurement | 553 |  | 300554 | 04 |  | U BB L3 - U GEN L3 phase angle | INT16s | AB | 1 | Deg |  |  | X
AC measurement | 553 |  | 300554 | 04 |  | U BB L3 - U Shore L3 phase angle | INT16s | AB | 1 | Deg |  | X
AC measurement | 553 |  | 300554 | 04 |  | U BB A L3 - U BB B L3 phase angle | INT16s | AB | 1 | Deg | X
Counter | 554 |  | 300555 | 04 |  | Absolute running hours | INT32s | ABCD | 0 |  |  |  | X | X
Counter | 556 |  | 300557 | 04 |  | Relative running hours | INT32s | ABCD | 0 |  |  |  | X | X
Counter | 558 |  | 300559 | 04 |  | No. of alarms | INT16s | AB | 0 |  | X | X | X | X
Counter | 559 |  | 300560 | 04 |  | No. of unacknowledged alarms | INT16s | AB | 0 |  | X | X | X | X
Counter | 560 |  | 300561 | 04 |  | No. of active acknowledged alarms | INT16s | AB | 0 |  | X | X | X | X
Counter | 561 |  | 300562 | 04 |  | Running minute counter, shutdown override | INT16s | AB | 0 |  |  |  | X | X
Counter | 562 |  | 300563 | 04 |  | Running hour counter, shutdown override | INT16s | AB | 0 |  |  |  | X | X
Counter | 563 |  | 300564 | 04 |  | No. of GB operations | INT16s | AB | 0 |  |  |  | X
Counter | 563 |  | 300564 | 04 |  | No. of BTB operations | INT16s | AB | 0 |  | X
Counter | 564 |  | 300565 | 04 |  | No. of TB operations (EDG) | INT16s | AB | 0 |  |  |  | X
Counter | 564 |  | 300565 | 04 |  | No. of SCB operations | INT16s | AB | 0 |  |  | X
Counter | 566 |  | 300567 | 04 |  | Start attempts | INT16s | AB | 0 |  |  |  | X | X
DC measurement | 567 |  | 300568 | 04 |  | DC supply term. 1-2 | INT16s | AB | 1 | V | X | X | X | X
Counter | 569 |  | 300570 | 04 |  | Service timer 1 running hours | INT16s | AB | 0 |  |  |  | X | X
Counter | 570 |  | 300571 | 04 |  | Service timer 1 running days | INT16s | AB | 0 |  |  |  | X | X
Counter | 571 |  | 300572 | 04 |  | Service timer 2 running hours | INT16s | AB | 0 |  |  |  | X | X
Counter | 572 |  | 300573 | 04 |  | Service timer 2 running days | INT16s | AB | 0 |  |  |  | X | X
AC measurement | 573 |  | 300574 | 04 |  | Cos-phi | INT16s | AB | 2 | cosPhi | X | X | X
AC measurement | 574 |  | 300575 | 04 |  | Cos-phi Inductive/Capacitive 0=Inductive, 1=Capacitive | INT16s | AB | 0 |  | X | X | X
DC measurement | 576 |  | 300577 | 04 |  | RPM (revolutions per minute) | INT16s | AB | 0 | rpm |  |  | X | X
Counter | 577 |  | 300578 | 04 |  | Running hours load profile | INT32s | ABCD | 0 |  |  |  | X | X
DC measurement | 583 |  | 300584 | 04 |  | Multi-input 20 | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 584 |  | 300585 | 04 |  | Multi-input 21 | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 585 |  | 300586 | 04 |  | Multi-input 22 | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 587 |  | 300588 | 04 |  | Multi-input 23 | INT16s | AB | 0 |  | X | X | X | X
AC measurement | 591 |  | 300592 | 04 |  | Busbar power, Multi-input 21 | INT16s | AB | 0 | kW |  | X
AC measurement | 591 |  | 300592 | 04 |  | Bus A power, Multi-input 21 | INT16s | AB | 0 | kW | X
AC measurement | 592 |  | 300593 | 04 |  | Shore power: Multi-input 20 or 4th CT input | INT16s | AB | 0 | kW |  | X
EIC measurement | 593 |  | 300594 | 04 |  | Engine Speed | INT16s | AB | 0 | rpm |  |  | X | X
EIC measurement | 594 |  | 300595 | 04 |  | Engine Coolant Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 595 |  | 300596 | 04 |  | Engine Oil Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 596 |  | 300597 | 04 |  | Number of Actual Faults | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 597 |  | 300598 | 04 |  | Engine Oil Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 598 |  | 300599 | 04 |  | Fuel temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 599 |  | 300600 | 04 |  | Intake manifold #1 pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 600 |  | 300601 | 04 |  | Air inlet temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 601 |  | 300602 | 04 |  | Coolant level | INT16s | AB | 1 | perc |  |  | X | X
EIC measurement | 602 |  | 300603 | 04 |  | Fuel rate | INT16s | AB | 1 | L/h |  |  | X | X
EIC measurement | 603 |  | 300604 | 04 |  | Charge air pressure | INT16s | AB | 0 | bar/psi |  |  | X | X
EIC measurement | 604 |  | 300605 | 04 |  | Intake manifold #1 temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 605 |  | 300606 | 04 |  | Drivers demand engine - percent torque | INT16s | AB | 0 | perc |  |  | X | X
EIC measurement | 606 |  | 300607 | 04 |  | Actual engine - percent torque | INT16s | AB | 0 | perc |  |  | X | X
EIC measurement | 607 |  | 300608 | 04 |  | Accelerator pedal position | INT16s | AB | 0 | perc |  |  | X | X
EIC measurement | 608 |  | 300609 | 04 |  | Percent load at current speed | INT16s | AB | 0 | perc |  |  | X | X
EIC measurement | 609 |  | 300610 | 04 |  | Air inlet pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 610 |  | 300611 | 04 |  | Exhaust gas temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 611 |  | 300612 | 04 |  | Engine hours | INT16s | AB | 0 | h |  |  | X | X
EIC measurement | 612 |  | 300613 | 04 |  | Engine oil filter differential pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 613 |  | 300614 | 04 |  | Keyswitch battery potential | INT16s | AB | 1 | V |  |  | X | X
EIC measurement | 614 |  | 300615 | 04 |  | Fuel delivery pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 615 |  | 300616 | 04 |  | Engine oil level | INT16s | AB | 1 | perc |  |  | X | X
EIC measurement | 616 |  | 300617 | 04 |  | Crankcase pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 617 |  | 300618 | 04 |  | Coolant pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 618 |  | 300619 | 04 |  | Water in fuel 1 (1 = Yes, 0 = No) | INT16s | AB | 0 | 2 bits |  |  | X | X
EIC measurement | 619 |  | 300620 | 04 |  | Blowby flow | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 620 |  | 300621 | 04 |  | Fuel rail pressure | INT16s | AB | 0 | bar/psi |  |  | X | X
EIC measurement | 621 |  | 300622 | 04 |  | Timing rail pressure | INT16s | AB | 0 | bar/psi |  |  | X | X
EIC measurement | 622 |  | 300623 | 04 |  | Aftercooler water inlet temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 623 |  | 300624 | 04 |  | Turbo oil temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 624 |  | 300625 | 04 |  | Particulate trap inlet pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 625 |  | 300626 | 04 |  | Air filter differential pressure | INT16s | AB | 3 | bar/psi |  |  | X | X
EIC measurement | 626 |  | 300627 | 04 |  | Coolant filter differential pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 627 |  | 300628 | 04 |  | Atmospheric pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 628 |  | 300629 | 04 |  | Ambient air temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 629 |  | 300630 | 04 |  | Exhaust temperature - right | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 630 |  | 300631 | 04 |  | Exhaust temperature - left | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 631 |  | 300632 | 04 |  | Winding 1 temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 632 |  | 300633 | 04 |  | Winding 2 temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 633 |  | 300634 | 04 |  | Winding 3 temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 634 |  | 300635 | 04 |  | Auxiliary_Analog_Info | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 635 |  | 300636 | 04 |  | Auxiliary_Analog_Info | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 636 |  | 300637 | 04 |  | Engine turbocharger 1 compressor outlet temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 637 |  | 300638 | 04 |  | Engine intercooler temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 638 |  | 300639 | 04 |  | Engine trip fuel | INT16s | AB | 0 | L |  |  | X | X
EIC measurement | 639 |  | 300640 | 04 |  | Engine total fuel used | INT16s | AB | 1 | kL |  |  | X | X
EIC measurement | 640 |  | 300641 | 04 |  | Trip fuel, gaseous | INT16s | AB | 0 | kg |  |  | X | X
EIC measurement | 641 |  | 300642 | 04 |  | Total fuel used, gaseous | INT16s | AB | 1 | ton |  |  | X | X
Control command state | 642 |  | 300643 | 04 |  | Control command address 0 | INT16s | AB | 0 |  | X | X | X | X
Control command state | 643 |  | 300644 | 04 |  | Control command address 1 | INT16s | AB | 0 |  | X | X | X | X
Control command state | 644 |  | 300645 | 04 |  | Control command address 2 | INT16s | AB | 0 |  | X | X | X | X
Control command state | 645 |  | 300646 | 04 |  | Control command address 3 | INT16s | AB | 0 |  | X | X | X | X
Control command state | 646 |  | 300647 | 04 |  | Control command address 4 | INT16s | AB | 0 |  | X | X | X | X
Control command state | 647 |  | 300648 | 04 |  | Control command address 5 | INT16s | AB | 0 |  | X | X | X | X
Control command state | 648 |  | 300649 | 04 |  | Control command address 6 | INT16s | AB | 0 |  | X | X | X | X
Control command state | 649 |  | 300650 | 04 |  | Control command address 7 | INT16s | AB | 0 |  | X | X | X | X
Control command state | 650 |  | 300651 | 04 |  | Control command address 8 | INT16s | AB | 0 |  | X | X | X | X
Control command state | 651 |  | 300652 | 04 |  | Control command address 9 | INT16s | AB | 0 |  | X | X | X | X
Control command state | 652 |  | 300653 | 04 |  | Control command address 10 | INT16s | AB | 0 |  | X | X | X | X
Control command state | 653 |  | 300654 | 04 |  | Control command address 11 | INT16s | AB | 0 |  | X | X | X | X
Control command state | 654 |  | 300655 | 04 |  | Control command address 12 | INT16s | AB | 0 |  | X | X | X | X
Control command state | 655 |  | 300656 | 04 |  | Control command address 13 | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 660 |  | 300661 | 04 |  | CIO 308 no. 1. Input 8 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 661 |  | 300662 | 04 |  | CIO 308 no. 1. Input 11 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 662 |  | 300663 | 04 |  | CIO 308 no. 1. Input 14 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 663 |  | 300664 | 04 |  | CIO 308 no. 1. Input 17 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 664 |  | 300665 | 04 |  | CIO 308 no. 1. Input 20 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 665 |  | 300666 | 04 |  | CIO 308 no. 1. Input 23 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 666 |  | 300667 | 04 |  | CIO 308 no. 1. Input 26 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 667 |  | 300668 | 04 |  | CIO 308 no. 1. Input 29 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 668 |  | 300669 | 04 |  | CIO 308 no. 2. Input 8 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 669 |  | 300670 | 04 |  | CIO 308 no. 2. Input 11 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 670 |  | 300671 | 04 |  | CIO 308 no. 2. Input 14 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 671 |  | 300672 | 04 |  | CIO 308 no. 2. Input 17 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 672 |  | 300673 | 04 |  | CIO 308 no. 2. Input 20 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 673 |  | 300674 | 04 |  | CIO 308 no. 2. Input 23 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 674 |  | 300675 | 04 |  | CIO 308 no. 2. Input 26 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 675 |  | 300676 | 04 |  | CIO 308 no. 2. Input 29 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 676 |  | 300677 | 04 |  | CIO 308 no. 3. Input 8 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 677 |  | 300678 | 04 |  | CIO 308 no. 3. Input 11 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 678 |  | 300679 | 04 |  | CIO 308 no. 3. Input 14 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 679 |  | 300680 | 04 |  | CIO 308 no. 3. Input 17 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 680 |  | 300681 | 04 |  | CIO 308 no. 3. Input 20 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 681 |  | 300682 | 04 |  | CIO 308 no. 3. Input 23 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 682 |  | 300683 | 04 |  | CIO 308 no. 3. Input 26 [Config] | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 683 |  | 300684 | 04 |  | CIO 308 no. 3. Input 29 [Config] | INT16s | AB | 0 |  | X | X | X | X
AC measurement | 689 |  | 300690 | 04 |  | Power derate value | INT16s | AB | 1 | perc |  |  | X
Plant logic state | 690 |  | 300691 | 04 |  | Power derate function active: 0: No derate. 1: P derate 1. 2: P derate 2. 3: Pderate3. 4: EIC derate | INT16s | AB | 0 |  |  |  | X
Alarm | 691 |  | 300692 | 04 |  | M-Logic extended timer alarm 1 value | INT16s | AB | 0 | min/day/hrs | X | X | X | X
Alarm | 692 |  | 300693 | 04 |  | M-Logic extended timer alarm 2 value | INT16s | AB | 0 | min/day/hrs | X | X | X | X
Alarm | 693 |  | 300694 | 04 |  | M-Logic extended timer alarm 3 value | INT16s | AB | 0 | min/day/hrs | X | X | X | X
Alarm | 694 |  | 300695 | 04 |  | M-Logic extended timer alarm 4 value | INT16s | AB | 0 | min/day/hrs | X | X | X | X
EIC measurement | 696 |  | 300697 | 04 |  | Lowest Cylinder Exhaust temperature | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 697 |  | 300698 | 04 |  | Highest Cylinder Exhaust temperature | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 698 |  | 300699 | 04 |  | Average Cylinder Exhaust temperature | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 699 |  | 300700 | 04 |  | Cylinder Exhaust temperature: Max or Min most deviated from Average | INT16s | AB | 0 |  |  |  | X | X
AC measurement | 700 |  | 300701 | 04 |  | Actual nominal power (Includes derate etc.) | INT16s | AB | 0 |  | X |  | X
Plant logic state | 701 |  | 300702 | 04 |  | Shore power transducer used or Mains power 4th CT used | INT16s | AB | 0 |  |  | X
Counter | 702 |  | 300703 | 04 |  | Fan A running hours | INT32s | ABCD | 0 |  |  |  | X
Counter | 704 |  | 300705 | 04 |  | Fan B running hours | INT32s | ABCD | 0 |  |  |  | X
Counter | 706 |  | 300707 | 04 |  | Fan C running hours | INT32s | ABCD | 0 |  |  |  | X
Counter | 708 |  | 300709 | 04 |  | Fan D running hours | INT32s | ABCD | 0 |  |  |  | X
AC measurement | 750 |  | 300751 | 04 |  | 4th current input: I neutral (true RMS) | INT16s | AB | 0 | A | X | X | X
AC measurement | 751 |  | 300752 | 04 |  | 4th current input: I ground (3rd harmonic filter) | INT16s | AB | 0 | A | X | X | X
AC measurement | 752 |  | 300753 | 04 |  | 4th current input: Apparent power | INT16s | AB | 0 | kVA | X | X | X
AC measurement | 753 |  | 300754 | 04 |  | 4th current input: Active power | INT16s | AB | 0 | kW | X | X | X
AC measurement | 754 |  | 300755 | 04 |  | 4th current input: Reactive power | INT16s | AB | 0 | kvar | X | X | X
AC measurement | 755 |  | 300756 | 04 |  | 4th current input: Cos-phi | INT16s | AB | 2 | cosPhi | X | X | X
AC measurement | 756 |  | 300757 | 04 |  | 4th current input: Cos-phi Inductive/Capacitive 0=Inductive, 1=Capacitive | INT16s | AB | 0 |  | X | X | X
AC measurement | 757 |  | 300758 | 04 |  | 4th current input: Power factor | INT16s | AB | 2 | PF | X | X | X
Plant logic state | 758 |  | 300759 | 04 |  | Shore Q transducer used or Shore Q 4th CT used | INT16s | AB | 0 |  |  | X
AC measurement | 759 |  | 300760 | 04 |  | Shore Q, Multi-input 20 or 4th CT | INT16s | AB | 0 | kW |  | X
Counter | 760 |  | 300761 | 04 |  | Absolute running minutes | INT16s | AB | 0 | min |  |  | X | X
PM Plant logic state | 763 |  | 300764 | 04 |  | Power management: Active application | INT16s | AB | 0 |  | X | X | X | X
AC measurement | 764 |  | 300765 | 04 |  | 4th current input: I busbar (true RMS) | INT16s | AB | 0 | A | X | X | X
AC measurement | 765 |  | 300766 | 04 |  | Active Power Load | INT32s | ABCD | 0 | kW | X | X | X | X
Counter | 770 |  | 300771 | 04 |  | Controller name letter 1 + 2. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X | X | X
Counter | 771 |  | 300772 | 04 |  | Controller name letter 3 + 4. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X | X | X
Counter | 772 |  | 300773 | 04 |  | Controller name letter 5 + 6. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X | X | X
Counter | 773 |  | 300774 | 04 |  | Controller name letter 7 + 7. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X | X | X
Counter | 774 |  | 300775 | 04 |  | Controller name letter 9 + 10. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X | X | X
Counter | 775 |  | 300776 | 04 |  | Controller name letter 11 + 12. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X | X | X
Counter | 776 |  | 300777 | 04 |  | Multi-input 20 configuration | INT16s | AB | 0 |  | X | X | X | X
Counter | 777 |  | 300778 | 04 |  | Multi-input 21 configuration | INT16s | AB | 0 |  | X | X | X | X
Counter | 778 |  | 300779 | 04 |  | Multi-input 22 configuration | INT16s | AB | 0 |  | X | X | X | X
Counter | 779 |  | 300780 | 04 |  | Multi-input 23 configuration | INT16s | AB | 0 |  | X | X | X | X
Counter | 790 |  | 300791 | 04 |  | Generator Export reactive energy counter, month | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 790 |  | 300791 | 04 |  | Shore Export reactive energy counter, month | INT32s | ABCD | 0 | kWh |  | X
Counter | 790 |  | 300791 | 04 |  | Bus A Export reactive energy counter, month | INT32s | ABCD | 0 | kWh | X
Counter | 792 |  | 300793 | 04 |  | Generator Export reactive energy counter, week | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 792 |  | 300793 | 04 |  | Shore Export reactive energy counter, week | INT32s | ABCD | 0 | kWh |  | X
Counter | 792 |  | 300793 | 04 |  | Bus A Export reactive energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 794 |  | 300795 | 04 |  | Generator Export reactive energy counter, day | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 794 |  | 300795 | 04 |  | Shore Export reactive energy counter, day | INT32s | ABCD | 0 | kWh |  | X
Counter | 794 |  | 300795 | 04 |  | Bus A Export reactive energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 796 |  | 300797 | 04 |  | Generator Import active energy counter, total | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 796 |  | 300797 | 04 |  | Shore Import active energy counter, total | INT32s | ABCD | 0 | kWh |  | X
Counter | 796 |  | 300797 | 04 |  | Bus A Import active energy counter, total | INT32s | ABCD | 0 | kWh | X
Counter | 798 |  | 300799 | 04 |  | Generator Import active energy counter, month | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 798 |  | 300799 | 04 |  | Shore Import active energy counter, month | INT32s | ABCD | 0 | kWh |  | X
Counter | 798 |  | 300799 | 04 |  | Bus A Import active energy counter, month | INT32s | ABCD | 0 | kWh | X
Counter | 800 |  | 300801 | 04 |  | Generator Import active energy counter, week | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 800 |  | 300801 | 04 |  | Shore Import active energy counter, week | INT32s | ABCD | 0 | kWh |  | X
Counter | 800 |  | 300801 | 04 |  | Bus A Import active energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 802 |  | 300803 | 04 |  | Generator Import active energy counter, day | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 802 |  | 300803 | 04 |  | Shore Import active energy counter, day | INT32s | ABCD | 0 | kWh |  | X
Counter | 802 |  | 300803 | 04 |  | Bus A Import active energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 804 |  | 300805 | 04 |  | Generator Import reactive energy counter, total | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 804 |  | 300805 | 04 |  | Shore Import reactive energy counter, total | INT32s | ABCD | 0 | kWh |  | X
Counter | 804 |  | 300805 | 04 |  | Bus A Import reactive energy counter, total | INT32s | ABCD | 0 | kWh | X
Counter | 806 |  | 300807 | 04 |  | Generator Import reactive energy counter, month | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 806 |  | 300807 | 04 |  | Shore Import reactive energy counter, month | INT32s | ABCD | 0 | kWh |  | X
Counter | 806 |  | 300807 | 04 |  | Bus A Import reactive energy counter, month | INT32s | ABCD | 0 | kWh | X
Counter | 808 |  | 300809 | 04 |  | Generator Import reactive energy counter, week | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 808 |  | 300809 | 04 |  | Shore Import reactive energy counter, week | INT32s | ABCD | 0 | kWh |  | X
Counter | 808 |  | 300809 | 04 |  | Bus A Import reactive energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 810 |  | 300811 | 04 |  | Generator Import reactive energy counter, day | INT32s | ABCD | 0 | kVArh |  |  | X
Counter | 810 |  | 300811 | 04 |  | Shore Import reactive energy counter, day | INT32s | ABCD | 0 | kWh |  | X
Counter | 810 |  | 300811 | 04 |  | Bus A Import reactive energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 822 |  | 300823 | 04 |  | Start attempts standard | INT16s | AB | 0 |  |  |  | X | X
Counter | 823 |  | 300824 | 04 |  | Start attempts double starter | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 840 |  | 300841 | 04 |  | Battery Potential / Power Input 1 | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 841 |  | 300842 | 04 |  | Engine Turbocharger 2 Boost Pressure | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 842 |  | 300843 | 04 |  | Engine Intake Manifold 3 Temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 843 |  | 300844 | 04 |  | Engine Intake Manifold 4 Temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 844 |  | 300845 | 04 |  | Engine Fuel 1 Injector Metering Rail 1 Pressure | INT16s | AB | 0 | bar/psi |  |  | X | X
EIC measurement | 845 |  | 300846 | 04 |  | Engine Pre-filter Oil Pressure | INT16s | AB | 0 | bar/psi |  |  | X | X
EIC measurement | 846 |  | 300847 | 04 |  | Water in fuel 2 (1 = Yes, 0 = No) | INT16s | AB | 0 | 2 bits |  |  | X | X
EIC measurement | 850 |  | 300851 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Dosing Requested Quantity | INT16s | AB | 1 | g/h |  |  | X | X
EIC measurement | 851 |  | 300852 | 04 |  | Aftertreatment 2 SCR Catalyst Intake Gas Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 852 |  | 300853 | 04 |  | Aftertreatment 2 SCR Catalyst Outlet Gas Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 853 |  | 300854 | 04 |  | Engine Oil-Filter Outlet Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 854 |  | 300855 | 04 |  | Engine Operating State | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 855 |  | 300856 | 04 |  | Source Address of Controlling Device | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 856 |  | 300857 | 04 |  | Engine Rated Speed | INT16s | AB | 0 | rpm |  |  | X | X
EIC measurement | 857 |  | 300858 | 04 |  | Engine Speed At Idle, Point 1 | INT16s | AB | 0 | rpm |  |  | X | X
EIC measurement | 858 |  | 300859 | 04 |  | MTU only: Fuel Consumption g/KWh | INT16s | AB | 0 | g/kWh |  |  | X | X
EIC measurement | 859 |  | 300860 | 04 |  | MTU only: Engine Status of Start procedure | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 860 |  | 300861 | 04 |  | UREA Level (Scania and Isuzu) | INT16s | AB | 1 | perc |  |  | X | X
EIC measurement | 861 |  | 300862 | 04 |  | Severity status of the operator inducement system | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 862 |  | 300863 | 04 |  | Temperature of engine combustion byproducts leaving the diesel particulate filter exhaust in exhaust bank 1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 863 |  | 300864 | 04 |  | Time to activate next regeneration for diesel particulate filter | INT16s | AB | 1 | h |  |  | X | X
EIC measurement | 864 |  | 300865 | 04 |  | Temperature of combustion air after it exits from the Charge Air Cooler 1 but before any mixing of recirculated exhaust gas. | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 865 |  | 300866 | 04 |  | Aftertreatment 1 Diesel Particulate Filter 1 Soot Load Percent | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 866 |  | 300867 | 04 |  | Battery Charger 1 Output Voltage | INT16s | AB | 0 | V |  |  | X | X
EIC measurement | 867 |  | 300868 | 04 |  | Battery Charger 1 Output Current | INT16s | AB | 0 | A |  |  | X | X
EIC state | 868 | 0 | 300869 | 04 |  | DPF lamp OFF | BOOL | [5 empty] | X | X
EIC state | 868 | 1 | 300869 | 04 |  | DPF lamp ON solid | BOOL | [5 empty] | X | X
EIC state | 868 | 2 | 300869 | 04 |  | DPF lamp ON blink | BOOL | [5 empty] | X | X
EIC state | 868 | 3 | 300869 | 04 |  | DPF Active Regeneration not activated | BOOL | [5 empty] | X | X
EIC state | 868 | 4 | 300869 | 04 |  | DPF Active Regeneration activated | BOOL | [5 empty] | X | X
EIC state | 868 | 5 | 300869 | 04 |  | DPF Active Regeneration needed | BOOL | [5 empty] | X | X
EIC state | 868 | 6 | 300869 | 04 |  | DPF Regeneration not needed | BOOL | [5 empty] | X | X
EIC state | 868 | 7 | 300869 | 04 |  | DPF Regeneration needed Lowest | BOOL | [5 empty] | X | X
EIC state | 868 | 8 | 300869 | 04 |  | DPF Regeneration needed Moderate | BOOL | [5 empty] | X | X
EIC state | 868 | 9 | 300869 | 04 |  | DPF Regeneration needed Highest | BOOL | [5 empty] | X | X
EIC state | 868 | 10 | 300869 | 04 |  | DPF Regeneration Not Inhibit | BOOL | [5 empty] | X | X
EIC state | 868 | 11 | 300869 | 04 |  | DPF Regeneration Inhibit | BOOL | [5 empty] | X | X
EIC state | 868 | 12 | 300869 | 04 |  | Exhaust system high temperature OFF | BOOL | [5 empty] | X | X
EIC state | 868 | 13 | 300869 | 04 |  | Exhaust system high temperature ON | BOOL | [5 empty] | X | X
EIC state | 868 | 14 | 300869 | 04 |  | After run status | BOOL | [5 empty] | X | X
EIC state | 869 | 0 | 300870 | 04 |  | MTU limit lamp OFF | BOOL | [5 empty] | X | X
EIC state | 869 | 1 | 300870 | 04 |  | MTU limit lamp ON solid | BOOL | [5 empty] | X | X
EIC state | 869 | 2 | 300870 | 04 |  | MTU limit lamp ON blink 1Hz | BOOL | [5 empty] | X | X
EIC state | 869 | 3 | 300870 | 04 |  | DEF level low lamp OFF | BOOL | [5 empty] | X | X
EIC state | 869 | 4 | 300870 | 04 |  | DEF level low lamp ON solid | BOOL | [5 empty] | X | X
EIC state | 869 | 5 | 300870 | 04 |  | DEF level low lamp ON blink | BOOL | [5 empty] | X | X
EIC state | 869 | 6 | 300870 | 04 |  | Volvo Penta Scr Inducement not ACTIVE | BOOL | [5 empty] | X | X
EIC state | 869 | 7 | 300870 | 04 |  | Volvo Penta Scr Inducement WARNING | BOOL | [5 empty] | X | X
EIC state | 869 | 8 | 300870 | 04 |  | Volvo Penta Scr Derate ACTIVE | BOOL | [5 empty] | X | X
EIC state | 869 | 9 | 300870 | 04 |  | Volvo Penta Pre severe Derate WARNING | BOOL | [5 empty] | X | X
EIC state | 869 | 10 | 300870 | 04 |  | Volvo Penta Severe Derate | BOOL | [5 empty] | X | X
EIC state | 869 | 11 | 300870 | 04 |  | Volvo Penta Temperature Override Derate | BOOL | [5 empty] | X | X
EIC state | 869 | 12 | 300870 | 04 |  | Volvo Penta Scr Inducement Reason OK | BOOL | [5 empty] | X | X
EIC state | 869 | 13 | 300870 | 04 |  | Volvo Penta Reagent Tank low | BOOL | [5 empty] | X | X
EIC state | 869 | 14 | 300870 | 04 |  | Volvo Penta Incorrect Reagent Quality | BOOL | [5 empty] | X | X
EIC state | 869 | 15 | 300870 | 04 |  | Volvo Penta Absence of Reagent Dosing | BOOL | [5 empty] | X | X
EIC state | 870 | 0 | 300871 | 04 |  | MTU limit lamp ON blink 2Hz | BOOL | [5 empty] | X | X
EIC state | 870 | 1 | 300871 | 04 |  | MTU TIER4 lamp ON blink 2Hz | BOOL | [5 empty] | X | X
EIC state | 870 | 2 | 300871 | 04 |  | MTU buzzer lamp OFF | BOOL | [5 empty] | X | X
EIC state | 870 | 3 | 300871 | 04 |  | MTU buzzer lamp ON solid | BOOL | [5 empty] | X | X
EIC state | 870 | 4 | 300871 | 04 |  | MTU buzzer lamp ON blink 1Hz | BOOL | [5 empty] | X | X
EIC state | 870 | 5 | 300871 | 04 |  | MTU buzzer lamp ON blink 2Hz | BOOL | [5 empty] | X | X
EIC state | 870 | 6 | 300871 | 04 |  | Alarm Yellow lamp OFF | BOOL | [5 empty] | X | X
EIC state | 870 | 7 | 300871 | 04 |  | Alarm Yellow lamp ON | BOOL | [5 empty] | X | X
EIC state | 870 | 8 | 300871 | 04 |  | Alarm Red lamp OFF | BOOL | [5 empty] | X | X
EIC state | 870 | 9 | 300871 | 04 |  | Alarm Red lamp ON | BOOL | [5 empty] | X | X
EIC state | 870 | 10 | 300871 | 04 |  | Engine protect system SHUTDOWN | BOOL | [5 empty] | X | X
EIC state | 870 | 11 | 300871 | 04 |  | Engine over-speed test | BOOL | [5 empty] | X | X
EIC state | 870 | 12 | 300871 | 04 |  | Engine Alarm acknowledge | BOOL | [5 empty] | X | X
EIC state | 870 | 13 | 300871 | 04 |  | Manual purge ECU | BOOL | [5 empty] | X | X
EIC state | 870 | 14 | 300871 | 04 |  | Manual purge EIDSS | BOOL | [5 empty] | X | X
EIC state | 870 | 15 | 300871 | 04 |  | Force purge | BOOL | [5 empty] | X | X
EIC measurement | 871 |  | 300872 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Average Consumption | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 872 |  | 300873 | 04 |  | Volvo Penta Time left to torque reduction | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 873 |  | 300874 | 04 |  | Volvo Penta Time left to severe torque reduction | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 874 |  | 300875 | 04 |  | Volvo Penta SCR inducement severity | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 875 |  | 300876 | 04 |  | Volvo Penta SCR inducement reason | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 876 |  | 300877 | 04 |  | Engine Operating Derate Request | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 877 |  | 300878 | 04 |  | Engine Demand - Percent Torque | INT16s | AB | 0 | perc |  |  | X | X
EIC measurement | 878 |  | 300879 | 04 |  | Engine Throttle Actuator 1 Control Command | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 879 |  | 300880 | 04 |  | Long-term Fuel Trim | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 880 |  | 300881 | 04 |  | Short-term Fuel Trim | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 881 |  | 300882 | 04 |  | Engine Exhaust Gas Oxygen Sensor Closed Loop Operation | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 882 |  | 300883 | 04 |  | Engine Desired Ignition Timing #1 | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 883 |  | 300884 | 04 |  | Engine Actual Ignition Timing | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 884 |  | 300885 | 04 |  | Aftertreatment 1 Intake Percent Oxygen 1 | INT16s | AB | 0 | perc |  |  | X | X
EIC measurement | 885 |  | 300886 | 04 |  | Aftertreatment 1 Intake Percent Oxygen 2 | INT16s | AB | 0 | perc |  |  | X | X
EIC measurement | 886 |  | 300887 | 04 |  | Engine Starter Mode | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 887 |  | 300888 | 04 |  | Actual Maximum Available Engine-Percent Torque | INT16s | AB | 0 | perc |  |  | X | X
EIC measurement | 888 |  | 300889 | 04 |  | Engine Coolant Preheated State | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 889 |  | 300890 | 04 |  | Engine Safety and Protection Override Status | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 890 |  | 300891 | 04 |  | Engine Cylinder Cut-off | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 891 |  | 300892 | 04 |  | MTU Engine Running State | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 892 |  | 300893 | 04 |  | External Stop State | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 893 |  | 300894 | 04 |  | MTU Requested Absolute Torque | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 894 |  | 300895 | 04 |  | Source of Current Speed Demand | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 895 |  | 300896 | 04 |  | Engine Demanded Operating Speed (Speed Demand Effective) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 896 |  | 300897 | 04 |  | Feedback of Speed Demand CAN | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 897 |  | 300898 | 04 |  | Feedback of Speed Demand Analogue Input | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 898 |  | 300899 | 04 |  | Speed Demand Fail Mode | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 899 |  | 300900 | 04 |  | Inducement Timer | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 900 |  | 300901 | 04 |  | Mean Trip Fuel consumption | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 901 |  | 300902 | 04 |  | Nominal power | INT16s | AB | 0 | kWm |  |  | X | X
EIC measurement | 902 |  | 300903 | 04 |  | Engine Trip Fuel (not scaled) | INT32s | ABCD | 0 | L |  |  | X | X
EIC measurement | 904 |  | 300905 | 04 |  | Engine Total Fuel Used (not scaled) | INT32s | ABCD | 0 | L |  |  | X | X
EIC measurement | 906 |  | 300907 | 04 |  | Mean Trip Fuel consumption (not scaled) | INT32s | ABCD | 0 | L |  |  | X | X
EIC measurement | 908 |  | 300909 | 04 |  | Engine power | INT16s | AB | 0 | kW |  |  | X | X
EIC measurement | 909 |  | 300910 | 04 |  | Engine Hours (not scaled) | INT32s | ABCD | 0 | h |  |  | X | X
EIC measurement | 911 |  | 300912 | 04 |  | Engine intake Manifold #1 Absolute pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 912 |  | 300913 | 04 |  | Air Filter Differential pressure 2 | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 913 |  | 300914 | 04 |  | Fuel Supply Pump Inlet Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 914 |  | 300915 | 04 |  | Fuel Filter (suction side) Differential Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 915 |  | 300916 | 04 |  | Engine Fuel Filter Differential Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
DAVR measurement | 916 |  | 300917 | 04 |  | DAVR Generator voltage L1L2 | INT16s | AB | 0 | V |  |  | X
DAVR measurement | 917 |  | 300918 | 04 |  | DAVR Generator frequency L1 | INT16s | AB | 0 | Hz |  |  | X
DAVR measurement | 918 |  | 300919 | 04 |  | DAVR Generator current L1 | INT16s | AB | 0 | A |  |  | X
DAVR measurement | 919 |  | 300920 | 04 |  | DAVR Generator excitation field current | INT16s | AB | 0 |  |  |  | X
DAVR measurement | 921 |  | 300922 | 04 |  | DAVR Generator total reactive power | INT16s | AB | 0 | kvar |  |  | X
DAVR measurement | 922 |  | 300923 | 04 |  | DAVR Generator overall power factor | INT16s | AB | 0 |  |  |  | X
DAVR measurement | 925 |  | 300926 | 04 |  | DAVR Generator total active power | INT16s | AB | 0 | kW |  |  | X
DAVR measurement | 927 |  | 300928 | 04 |  | DAVR Generator total apparent power | INT16s | AB | 0 | kVA |  |  | X
DAVR measurement | 928 |  | 300929 | 04 |  | DAVR Pt100 #1 | INT16s | AB | 0 | Deg C/F |  |  | X
DAVR measurement | 929 |  | 300930 | 04 |  | DAVR Pt100 #2 | INT16s | AB | 0 | Deg C/F |  |  | X
DAVR measurement | 930 |  | 300931 | 04 |  | DAVR Pt100 #3 | INT16s | AB | 0 | Deg C/F |  |  | X
DAVR measurement | 931 |  | 300932 | 04 |  | DAVR Trip alarm | INT16s | AB | 0 |  |  |  | X
EIC measurement | 932 |  | 300933 | 04 |  | Speed demand switch | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 933 |  | 300934 | 04 |  | Pressure: Lube Oil Limit LO | INT16s | AB | 0 | bar/psi |  |  | X | X
EIC measurement | 934 |  | 300935 | 04 |  | Pressure: Lube Oil Limit LOLO | INT16s | AB | 0 | bar/psi |  |  | X | X
EIC measurement | 935 |  | 300936 | 04 |  | Pressure: Fuel | INT16s | AB | 0 | bar/psi |  |  | X | X
EIC measurement | 936 |  | 300937 | 04 |  | Temperature: Coolant Limit HI | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 937 |  | 300938 | 04 |  | Temperature: Coolant Limit HIHI | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 938 |  | 300939 | 04 |  | Temperature: Coolant Intercooler | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 939 |  | 300940 | 04 |  | ECU temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 940 |  | 300941 | 04 |  | Actual Droop | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 941 |  | 300942 | 04 |  | Injection Quantity Act.DBR | INT16s | AB | 0 | perc |  |  | X | X
EIC measurement | 942 |  | 300943 | 04 |  | Engine Speed Camshaft | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 943 |  | 300944 | 04 |  | Temperature: Lube Oil Limit HI | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 944 |  | 300945 | 04 |  | Temperature: Lube Oil Limit HIHI | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 945 |  | 300946 | 04 |  | Feedback Speed Demand analog | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 946 |  | 300947 | 04 |  | Stop signal activated | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 947 |  | 300948 | 04 |  | Exhaust Port Temperature 01 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 948 |  | 300949 | 04 |  | Exhaust Port Temperature 02 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 949 |  | 300950 | 04 |  | Exhaust Port Temperature 03 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 950 |  | 300951 | 04 |  | Exhaust Port Temperature 04 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 951 |  | 300952 | 04 |  | Exhaust Port Temperature 05 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 952 |  | 300953 | 04 |  | Exhaust Port Temperature 06 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 953 |  | 300954 | 04 |  | Exhaust Port Temperature 07 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 954 |  | 300955 | 04 |  | Exhaust Port Temperature 08 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 955 |  | 300956 | 04 |  | Exhaust Port Temperature 09 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 956 |  | 300957 | 04 |  | Exhaust Port Temperature 10 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 957 |  | 300958 | 04 |  | Exhaust Port Temperature 11 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 958 |  | 300959 | 04 |  | Exhaust Port Temperature 12 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 959 |  | 300960 | 04 |  | Exhaust Port Temperature 13 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 960 |  | 300961 | 04 |  | Exhaust Port Temperature 14 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 961 |  | 300962 | 04 |  | Exhaust Port Temperature 15 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 962 |  | 300963 | 04 |  | Exhaust Port Temperature 16 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 963 |  | 300964 | 04 |  | Exhaust Port Temperature 17 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 964 |  | 300965 | 04 |  | Exhaust Port Temperature 18 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 965 |  | 300966 | 04 |  | Exhaust Port Temperature 19 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 966 |  | 300967 | 04 |  | Exhaust Port Temperature 20 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 967 |  | 300968 | 04 |  | Engine Filtered Fuel Delivery Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 968 |  | 300969 | 04 |  | Engine Coolant Temperature 2 | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 969 |  | 300970 | 04 |  | Engine Coolant Temperature 3 | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 970 |  | 300971 | 04 |  | Engine Coolant Pump Outlet Temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 971 |  | 300972 | 04 |  | Engine Auxiliary Coolant Temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 972 |  | 300973 | 04 |  | Engine Turbocharger 1 Turbine Intake Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 973 |  | 300974 | 04 |  | Engine Turbocharger 2 Turbine Intake Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 974 |  | 300975 | 04 |  | Engine Auxiliary Coolant Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 975 |  | 300976 | 04 |  | Ambient Conditions 2 Specific Humidity | INT16s | AB | 1 | g/kg |  |  | X | X
EIC measurement | 976 |  | 300977 | 04 |  | Engine Turbocharger 2 Speed | INT16s | AB | 0 | rpm |  |  | X | X
EIC measurement | 977 |  | 300978 | 04 |  | Engine Turbocharger 3 Speed | INT16s | AB | 0 | rpm |  |  | X | X
EIC measurement | 978 |  | 300979 | 04 |  | Trip Engine Running Time | INT16s | AB | 0 | h |  |  | X | X
EIC measurement | 979 |  | 300980 | 04 |  | Trip Idle Time | INT16s | AB | 0 | h |  |  | X | X
EIC measurement | 980 |  | 300981 | 04 |  | Estimated Percent Fan Speed | INT16s | AB | 1 | perc |  |  | X | X
EIC measurement | 981 |  | 300982 | 04 |  | Engine Turbocharger 1 Speed | INT16s | AB | 0 | rpm |  |  | X | X
EIC measurement | 982 |  | 300983 | 04 |  | Nominal Friction - Percent Torque | INT16s | AB | 0 | perc |  |  | X | X
EIC measurement | 983 |  | 300984 | 04 |  | Engine's Desired Operating Speed | INT16s | AB | 0 | rpm |  |  | X | X
EIC measurement | 984 |  | 300985 | 04 |  | Temperature of pre-combustion air found in intake manifold of engine air supply system | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 985 |  | 300986 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Level | INT16s | AB | 1 | perc |  |  | X | X
EIC measurement | 986 |  | 300987 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 987 |  | 300988 | 04 |  | Aftertreatment 1 Intake NOx | INT16s | AB | 1 | ppm |  |  | X | X
EIC measurement | 988 |  | 300989 | 04 |  | Aftertreatment 1 Outlet NOx | INT16s | AB | 1 | ppm |  |  | X | X
EIC measurement | 989 |  | 300990 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Actual Dosing Quantity | INT16s | AB | 1 | g/h |  |  | X | X
EIC measurement | 990 |  | 300991 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Doser Absolute Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 991 |  | 300992 | 04 |  | Aftertreatment 1 SCR Dosing Air Assist Valve | INT16s | AB | 0 | Deg C/F |  |  | X | X
EIC measurement | 992 |  | 300993 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Dosing Requested Quantity | INT16s | AB | 0 | g/h |  |  | X | X
EIC measurement | 993 |  | 300994 | 04 |  | Aftertreatment 1 SCR Catalyst Intake Gas Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 994 |  | 300995 | 04 |  | Aftertreatment 1 SCR Catalyst Outlet Gas Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 995 |  | 300996 | 04 |  | Aftertreatment 2 Intake NOx | INT16s | AB | 1 | ppm |  |  | X | X
EIC measurement | 996 |  | 300997 | 04 |  | Aftertreatment 2 Outlet NOx | INT16s | AB | 1 | ppm |  |  | X | X
EIC measurement | 997 |  | 300998 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Actual Dosing Quantity | INT16s | AB | 1 | Deg C/F |  |  | X | X
EIC measurement | 998 |  | 300999 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Dosing Absolute Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X
EIC measurement | 999 |  | 301000 | 04 |  | Aftertreatment 2 SCR Dosing Air Assist Valve | INT16s | AB | 0 | Deg C/F |  |  | X | X
AC alarm | 1000 | 0 | 301001 | 04 | 1000 | G -P> 1 | BOOL | [5 empty] | X
AC alarm | 1000 | 0 | 301001 | 04 | 1000 | BA -P> 1 | BOOL |  |  |  | X
AC alarm | 1000 | 1 | 301001 | 04 | 1010 | G -P> 2 | BOOL | [5 empty] | X
AC alarm | 1000 | 1 | 301001 | 04 | 1010 | BA -P> 2 | BOOL |  |  |  | X
AC alarm | 1000 | 2 | 301001 | 04 | 1070 | G -P> 3 | BOOL | [5 empty] | X
AC alarm | 1000 | 2 | 301001 | 04 | 1070 | BA -P> 3 | BOOL |  |  |  | X
AC alarm | 1000 | 3 | 301001 | 04 | 1030 | G I> 1 | BOOL | [5 empty] | X
AC alarm | 1000 | 3 | 301001 | 04 | 1030 | SC I> 1 | BOOL |  |  |  |  | X
AC alarm | 1000 | 3 | 301001 | 04 | 1030 | BA I> 1 | BOOL |  |  |  | X
AC alarm | 1000 | 4 | 301001 | 04 | 1040 | G I> 2 | BOOL | [5 empty] | X
AC alarm | 1000 | 4 | 301001 | 04 | 1040 | SC I> 2 | BOOL |  |  |  |  | X
AC alarm | 1000 | 4 | 301001 | 04 | 1040 | BA I> 2 | BOOL |  |  |  | X
AC alarm | 1000 | 5 | 301001 | 04 | 1050 | G I> 3 | BOOL | [5 empty] | X
AC alarm | 1000 | 5 | 301001 | 04 | 1050 | SC I> 3 | BOOL |  |  |  |  | X
AC alarm | 1000 | 5 | 301001 | 04 | 1050 | BA I> 3 | BOOL |  |  |  | X
AC alarm | 1000 | 6 | 301001 | 04 | 1060 | G I> 4 | BOOL | [5 empty] | X
AC alarm | 1000 | 6 | 301001 | 04 | 1060 | SC I> 4 | BOOL |  |  |  |  | X
AC alarm | 1000 | 6 | 301001 | 04 | 1060 | BA I> 4 | BOOL |  |  |  | X
AC alarm | 1000 | 7 | 301001 | 04 | 1087 | G I> inv. | BOOL | [5 empty] | X
AC alarm | 1000 | 8 | 301001 | 04 | 1110 | G Iv> | BOOL | [5 empty] | X
AC alarm | 1000 | 8 | 301001 | 04 | 1110 | SC Iv> | BOOL |  |  |  |  | X
AC alarm | 1000 | 9 | 301001 | 04 | 1130 | G I>> 1 | BOOL | [5 empty] | X
AC alarm | 1000 | 9 | 301001 | 04 | 1130 | SC I>> 1 | BOOL |  |  |  |  | X
AC alarm | 1000 | 9 | 301001 | 04 | 1130 | BA I>> 1 | BOOL |  |  |  | X
AC alarm | 1000 | 10 | 301001 | 04 | 1140 | G I>> 2 | BOOL | [5 empty] | X
AC alarm | 1000 | 10 | 301001 | 04 | 1140 | SC I>> 2 | BOOL |  |  |  |  | X
AC alarm | 1000 | 10 | 301001 | 04 | 1140 | BA I>> 2 | BOOL |  |  |  | X
AC alarm | 1000 | 11 | 301001 | 04 | 1150 | G U> 1 | BOOL | [5 empty] | X
AC alarm | 1000 | 11 | 301001 | 04 | 1150 | SC U> 1 | BOOL |  |  |  |  | X
AC alarm | 1000 | 11 | 301001 | 04 | 1150 | BA U> 1 | BOOL |  |  |  | X
AC alarm | 1000 | 12 | 301001 | 04 | 1160 | SC U> 2 | BOOL |  |  |  |  | X
AC alarm | 1000 | 12 | 301001 | 04 | 1160 | G U> 2 | BOOL | [5 empty] | X
AC alarm | 1000 | 12 | 301001 | 04 | 1160 | BA U> 2 | BOOL |  |  |  | X
AC alarm | 1000 | 13 | 301001 | 04 | 1170 | G U< 1 | BOOL | [5 empty] | X
AC alarm | 1000 | 13 | 301001 | 04 | 1170 | SC U< 1 | BOOL |  |  |  |  | X
AC alarm | 1000 | 13 | 301001 | 04 | 1170 | BA U< 1 | BOOL |  |  |  | X
AC alarm | 1000 | 14 | 301001 | 04 | 1180 | G U< 2 | BOOL | [5 empty] | X
AC alarm | 1000 | 14 | 301001 | 04 | 1180 | SC U< 2 | BOOL |  |  |  |  | X
AC alarm | 1000 | 14 | 301001 | 04 | 1180 | BA U< 2 | BOOL |  |  |  | X
AC alarm | 1000 | 15 | 301001 | 04 | 1190 | G U< 3 | BOOL | [5 empty] | X
AC alarm | 1000 | 15 | 301001 | 04 | 1190 | SC U< 3 | BOOL |  |  |  |  | X
AC alarm | 1000 | 15 | 301001 | 04 | 1190 | BA U< 3 | BOOL |  |  |  | X
AC alarm | 1001 | 0 | 301002 | 04 | 1210 | G f> 1 | BOOL | [5 empty] | X
AC alarm | 1001 | 0 | 301002 | 04 | 1210 | SC f> 1 | BOOL |  |  |  |  | X
AC alarm | 1001 | 0 | 301002 | 04 | 1210 | BA f> 1 | BOOL |  |  |  | X
AC alarm | 1001 | 1 | 301002 | 04 | 1220 | G f> 2 | BOOL | [5 empty] | X
AC alarm | 1001 | 1 | 301002 | 04 | 1220 | SC f> 2 | BOOL |  |  |  |  | X
AC alarm | 1001 | 1 | 301002 | 04 | 1220 | BA f> 2 | BOOL |  |  |  | X
AC alarm | 1001 | 2 | 301002 | 04 | 1230 | G f> 3 | BOOL | [5 empty] | X
AC alarm | 1001 | 2 | 301002 | 04 | 1230 | SC f> 3 | BOOL |  |  |  |  | X
AC alarm | 1001 | 2 | 301002 | 04 | 1230 | BA f> 3 | BOOL |  |  |  | X
AC alarm | 1001 | 3 | 301002 | 04 | 1240 | G f< 1 | BOOL | [5 empty] | X
AC alarm | 1001 | 3 | 301002 | 04 | 1240 | SC f< 1 | BOOL |  |  |  |  | X
AC alarm | 1001 | 3 | 301002 | 04 | 1240 | BA f< 1 | BOOL |  |  |  | X
AC alarm | 1001 | 4 | 301002 | 04 | 1250 | G f< 2 | BOOL | [5 empty] | X
AC alarm | 1001 | 4 | 301002 | 04 | 1250 | SC f< 2 | BOOL |  |  |  |  | X
AC alarm | 1001 | 4 | 301002 | 04 | 1250 | BA f< 2 | BOOL |  |  |  | X
AC alarm | 1001 | 5 | 301002 | 04 | 1260 | G f< 3 | BOOL | [5 empty] | X
AC alarm | 1001 | 5 | 301002 | 04 | 1260 | SC f< 3 | BOOL |  |  |  |  | X
AC alarm | 1001 | 5 | 301002 | 04 | 1260 | BA f< 3 | BOOL |  |  |  | X
AC alarm | 1001 | 6 | 301002 | 04 | 1270 | BB U> 1 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 7 | 301002 | 04 | 1280 | BB U> 2 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 8 | 301002 | 04 | 1290 | BB U> 3 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 9 | 301002 | 04 | 1300 | BB U< 1 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 10 | 301002 | 04 | 1310 | BB U< 2 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 11 | 301002 | 04 | 1320 | BB U< 3 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 12 | 301002 | 04 | 1330 | BB U< 4 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 13 | 301002 | 04 | 1350 | BB f> 1 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 14 | 301002 | 04 | 1360 | BB f> 2 | BOOL |  |  |  | X | X | X
AC alarm | 1001 | 15 | 301002 | 04 | 1370 | BB f> 3 | BOOL |  |  |  | X | X | X
AC alarm | 1002 | 0 | 301003 | 04 | 1380 | BB f< 1 | BOOL |  |  |  | X | X | X
AC alarm | 1002 | 1 | 301003 | 04 | 1390 | BB f< 2 | BOOL |  |  |  | X | X | X
AC alarm | 1002 | 2 | 301003 | 04 | 1400 | BB f< 3 | BOOL |  |  |  | X | X | X
AC alarm | 1002 | 3 | 301003 | 04 | 1410 | BB f< 4 | BOOL |  |  |  | X | X | X
AC alarm | 1002 | 4 | 301003 | 04 | 1420 | df/dt (ROCOF) | BOOL | [5 empty] | X
AC alarm | 1002 | 5 | 301003 | 04 | 1430 | Vector jump | BOOL | [5 empty] | X
AC alarm | 1002 | 6 | 301003 | 04 | 1440 | BB pos. seq. volt. low | BOOL | [5 empty] | X
AC alarm | 1002 | 7 | 301003 | 04 | 1450 | G P> 1 | BOOL | [5 empty] | X
AC alarm | 1002 | 7 | 301003 | 04 | 1450 | SC P> 1 | BOOL |  |  |  |  | X
AC alarm | 1002 | 7 | 301003 | 04 | 1450 | BA P> 1 | BOOL |  |  |  | X
AC alarm | 1002 | 8 | 301003 | 04 | 1460 | G P> 2 | BOOL | [5 empty] | X
AC alarm | 1002 | 8 | 301003 | 04 | 1460 | SC P> 2 | BOOL |  |  |  |  | X
AC alarm | 1002 | 8 | 301003 | 04 | 1460 | BA P> 2 | BOOL |  |  |  | X
AC alarm | 1002 | 9 | 301003 | 04 | 1470 | G P> 3 | BOOL | [5 empty] | X
AC alarm | 1002 | 9 | 301003 | 04 | 1470 | SC P> 3 | BOOL |  |  |  |  | X
AC alarm | 1002 | 9 | 301003 | 04 | 1470 | BA P> 3 | BOOL |  |  |  | X
AC alarm | 1002 | 10 | 301003 | 04 | 1480 | G P> 4 | BOOL | [5 empty] | X
AC alarm | 1002 | 10 | 301003 | 04 | 1480 | SC P> 4 | BOOL |  |  |  |  | X
AC alarm | 1002 | 10 | 301003 | 04 | 1480 | BA P> 4 | BOOL |  |  |  | X
AC alarm | 1002 | 11 | 301003 | 04 | 1490 | G P> 5 | BOOL | [5 empty] | X
AC alarm | 1002 | 11 | 301003 | 04 | 1490 | SC P> 5 | BOOL |  |  |  |  | X
AC alarm | 1002 | 11 | 301003 | 04 | 1490 | BA P> 5 | BOOL |  |  |  | X
AC alarm | 1002 | 12 | 301003 | 04 | 1500 | Unbalance curr. 1 | BOOL |  |  |  |  | X
AC alarm | 1002 | 13 | 301003 | 04 | 1510 | Unbalance volt. | BOOL |  |  |  |  | X
AC alarm | 1002 | 14 | 301003 | 04 | 1520 | G -Q> | BOOL | [5 empty] | X
AC alarm | 1002 | 14 | 301003 | 04 | 1520 | SC -Q> | BOOL |  |  |  |  | X
AC alarm | 1002 | 14 | 301003 | 04 | 1520 | BA -Q> | BOOL |  |  |  | X
AC alarm | 1002 | 15 | 301003 | 04 | 1530 | G Q> | BOOL | [5 empty] | X
AC alarm | 1002 | 15 | 301003 | 04 | 1530 | SC Q> | BOOL |  |  |  |  | X
AC alarm | 1002 | 15 | 301003 | 04 | 1530 | BA Q> | BOOL |  |  |  | X
AC alarm | 1003 | 0 | 301004 | 04 | 1540 | Gen. neg. seq. I | BOOL | [5 empty] | X
AC alarm | 1003 | 1 | 301004 | 04 | 1550 | Generator neg. seq. U | BOOL | [5 empty] | X
AC alarm | 1003 | 1 | 301004 | 04 | 1550 | Bus A neg. seq. U | BOOL |  |  |  | X
AC alarm | 1003 | 2 | 301004 | 04 | 1570 | Gen. zero seq. I | BOOL | [5 empty] | X
AC alarm | 1003 | 2 | 301004 | 04 | 1570 | Bus A zero seq. I | BOOL |  |  |  | X
AC alarm | 1003 | 3 | 301004 | 04 | 1580 | Zero seq. U | BOOL | [5 empty] | X
AC alarm | 1003 | 3 | 301004 | 04 | 1580 | Bus A zero seq. U | BOOL |  |  |  | X
AC alarm | 1003 | 4 | 301004 | 04 | 1600 | Directional overcurrent 1 | BOOL |  |  |  |  | X | X
AC alarm | 1003 | 5 | 301004 | 04 | 1610 | Directional overcurrent 2 | BOOL |  |  |  |  | X | X
AC alarm | 1003 | 6 | 301004 | 04 | 1620 | BB unbalance U | BOOL |  |  |  | X | X | X
AC alarm | 1003 | 7 | 301004 | 04 | 1800 | NEL 1 I> | BOOL |  |  |  |  | X | X
AC alarm | 1003 | 8 | 301004 | 04 | 1810 | NEL 2 I> | BOOL |  |  |  |  | X | X
AC alarm | 1003 | 9 | 301004 | 04 | 1820 | NEL 3 I> | BOOL |  |  |  |  | X | X
AC alarm | 1003 | 10 | 301004 | 04 | 1830 | NEL 1 BB f< | BOOL |  |  |  |  | X | X
AC alarm | 1003 | 11 | 301004 | 04 | 1840 | NEL 2 BB f< | BOOL |  |  |  |  | X | X
AC alarm | 1003 | 12 | 301004 | 04 | 1850 | NEL 3 BB f< | BOOL |  |  |  |  | X | X
AC alarm | 1003 | 13 | 301004 | 04 | 1860 | NEL 1 P> | BOOL |  |  |  |  | X | X
AC alarm | 1003 | 14 | 301004 | 04 | 1870 | NEL 2 P> | BOOL |  |  |  |  | X | X
AC alarm | 1003 | 15 | 301004 | 04 | 1880 | NEL 3 P> | BOOL |  |  |  |  | X | X
AC alarm | 1004 | 0 | 301005 | 04 | 1890 | NEL 1 P>> | BOOL |  |  |  |  | X | X
AC alarm | 1004 | 1 | 301005 | 04 | 1900 | NEL 2 P>> | BOOL |  |  |  |  | X | X
AC alarm | 1004 | 2 | 301005 | 04 | 1910 | NEL 3 P>> | BOOL |  |  |  |  | X | X
AC alarm | 1004 | 6 | 301005 | 04 | 1960 | U and Q< 1 | BOOL | [5 empty] | X
AC alarm | 1004 | 7 | 301005 | 04 | 1970 | U and Q< 2 | BOOL | [5 empty] | X
AC alarm | 1004 | 8 | 301005 | 04 | 1981 | GB ext. trip | BOOL | [5 empty] | X
AC alarm | 1004 | 8 | 301005 | 04 | 1981 | BTB ext. trip | BOOL |  |  |  | X
AC alarm | 1004 | 9 | 301005 | 04 | 1983 | TB ext. trip (EDG) | BOOL | [5 empty] | X
AC alarm | 1004 | 9 | 301005 | 04 | 1983 | SCB ext. trip | BOOL |  |  |  |  | X
Alarm | 1005 | 0 | 301006 | 04 | 2120 | Synchronising window | BOOL |  |  |  | X | X | X
Alarm | 1005 | 1 | 301006 | 04 | 2130 | Synchronising failure GB | BOOL | [5 empty] | X
Alarm | 1005 | 1 | 301006 | 04 | 2130 | Synchronising failure BTB | BOOL |  |  |  | X
Alarm | 1005 | 2 | 301006 | 04 | 2140 | Synchronising failure SCB | BOOL |  |  |  |  | X
AC alarm | 1005 | 3 | 301006 | 04 | 2150 | Phase seq. failure A | BOOL |  |  |  | X | X | X
Alarm | 1005 | 4 | 301006 | 04 | 2160 | GB open failure | BOOL | [5 empty] | X
Alarm | 1005 | 4 | 301006 | 04 | 2160 | BTB open failure | BOOL |  |  |  | X
Alarm | 1005 | 5 | 301006 | 04 | 2170 | GB close failure | BOOL | [5 empty] | X
Alarm | 1005 | 5 | 301006 | 04 | 2170 | BTB close failure | BOOL |  |  |  | X
Alarm | 1005 | 6 | 301006 | 04 | 2180 | GB pos. failure | BOOL | [5 empty] | X
Alarm | 1005 | 6 | 301006 | 04 | 2180 | BTB pos. failure | BOOL |  |  |  | X
Alarm | 1005 | 7 | 301006 | 04 | 2200 | SCB open failure | BOOL |  |  |  |  | X
Alarm | 1005 | 8 | 301006 | 04 | 2210 | SCB close failure | BOOL |  |  |  |  | X
Alarm | 1005 | 9 | 301006 | 04 | 2220 | SCB pos. failure | BOOL |  |  |  |  | X
AC alarm | 1005 | 11 | 301006 | 04 | 2155 | Phase seq. failure B | BOOL |  |  |  | X | X | X
Alarm | 1006 | 0 | 301007 | 04 | 2560 | GOVERNOR regulation fail. | BOOL | [5 empty] | X
Alarm | 1006 | 1 | 301007 | 04 | 2630 | Deload error | BOOL | [5 empty] | X
Alarm | 1006 | 2 | 301007 | 04 | 2680 | AVR regulation fail. | BOOL | [5 empty] | X
Alarm | 1007 | 0 | 301008 | 04 | 3000 | Digital alarm input 39 | BOOL |  |  |  | X | X | X | X
Alarm | 1007 | 1 | 301008 | 04 | 3010 | Digital alarm input 40 | BOOL |  |  |  | X | X | X | X
Alarm | 1007 | 2 | 301008 | 04 | 3020 | Digital alarm input 41 | BOOL |  |  |  | X | X | X | X
Alarm | 1007 | 3 | 301008 | 04 | 3030 | Digital alarm input 42 | BOOL |  |  |  | X | X | X | X
Alarm | 1007 | 4 | 301008 | 04 | 3040 | Digital alarm input 43 | BOOL |  |  |  | X | X | X | X
Alarm | 1007 | 5 | 301008 | 04 | 3050 | Digital alarm input 44 | BOOL |  |  |  | X | X | X | X
Alarm | 1007 | 6 | 301008 | 04 | 3060 | Digital alarm input 45 | BOOL |  |  |  | X | X | X | X
Alarm | 1007 | 7 | 301008 | 04 | 3070 | Digital alarm input 46 | BOOL |  |  |  | X | X | X | X
Alarm | 1007 | 8 | 301008 | 04 | 3080 | Digital alarm input 47 | BOOL |  |  |  | X | X | X | X
Alarm | 1007 | 9 | 301008 | 04 | 3090 | Digital alarm input 48 | BOOL |  |  |  | X | X | X | X
Alarm | 1007 | 10 | 301008 | 04 | 3100 | Digital alarm input 49 | BOOL |  |  |  | X | X | X | X
Alarm | 1007 | 11 | 301008 | 04 | 3110 | Digital alarm input 50 | BOOL |  |  |  | X | X | X | X
Alarm | 1010 | 12 | 301011 | 04 | 3490 | Digital alarm input 4 (Emergency stop) | BOOL |  |  |  | X | X | X | X
Alarm | 1011 | 7 | 301012 | 04 | 3570 | M-Logic alarm 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1011 | 8 | 301012 | 04 | 3580 | M-Logic alarm 2 | BOOL |  |  |  | X | X | X | X
Alarm | 1011 | 9 | 301012 | 04 | 3590 | M-Logic alarm 3 | BOOL |  |  |  | X | X | X | X
Alarm | 1011 | 10 | 301012 | 04 | 3600 | M-Logic alarm 4 | BOOL |  |  |  | X | X | X | X
Alarm | 1011 | 11 | 301012 | 04 | 3610 | M-Logic alarm 5 | BOOL |  |  |  | X | X | X | X
Alarm | 1011 | 12 | 301012 | 04 | 3620 | M-Logic extended alarm 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1011 | 13 | 301012 | 04 | 3630 | M-Logic extended alarm 2 | BOOL |  |  |  | X | X | X | X
Alarm | 1011 | 14 | 301012 | 04 | 3640 | M-Logic extended alarm 3 | BOOL |  |  |  | X | X | X | X
Alarm | 1011 | 15 | 301012 | 04 | 3650 | M-Logic extended alarm 4 | BOOL |  |  |  | X | X | X | X
Alarm | 1013 | 0 | 301014 | 04 | 4120 | Multi input terminal 20.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1013 | 1 | 301014 | 04 | 4130 | Multi input terminal 20.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1013 | 2 | 301014 | 04 | 4140 | W. fail. 20 | BOOL |  |  |  | X | X | X | X
Alarm | 1013 | 3 | 301014 | 04 | 4150 | Multi input terminal 21.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1013 | 4 | 301014 | 04 | 4160 | Multi input terminal 21.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1013 | 5 | 301014 | 04 | 4170 | W. fail. 21 | BOOL |  |  |  | X | X | X | X
Alarm | 1013 | 6 | 301014 | 04 | 4180 | Multi input terminal 22.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1013 | 7 | 301014 | 04 | 4190 | Multi input terminal 22.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1013 | 8 | 301014 | 04 | 4200 | W. fail. 22 | BOOL |  |  |  | X | X | X | X
Alarm | 1013 | 9 | 301014 | 04 | 4510 | Overspeed 1 | BOOL | [5 empty] | X | X
Alarm | 1013 | 10 | 301014 | 04 | 4520 | Overspeed 2 | BOOL | [5 empty] | X | X
Alarm | 1013 | 11 | 301014 | 04 | 4530 | Crank failure | BOOL | [5 empty] | X | X
Alarm | 1013 | 12 | 301014 | 04 | 4540 | Running feedback failure | BOOL | [5 empty] | X | X
Alarm | 1013 | 13 | 301014 | 04 | 4550 | MPU wire failure | BOOL | [5 empty] | X | X
Alarm | 1013 | 14 | 301014 | 04 | 4560 | Hz/V failure | BOOL | [5 empty] | X
Alarm | 1013 | 15 | 301014 | 04 | 4570 | Start failure | BOOL | [5 empty] | X | X
Alarm | 1014 | 0 | 301015 | 04 | 4580 | Stop failure | BOOL | [5 empty] | X | X
Alarm | 1014 | 1 | 301015 | 04 | 4960 | U< aux. term. 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1014 | 2 | 301015 | 04 | 4970 | U> aux. term. 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1014 | 5 | 301015 | 04 | 4590 | Underspeed 1 | BOOL | [5 empty] | X | X
Alarm | 1014 | 6 | 301015 | 04 | 4210 | Multi input terminal 23.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1014 | 7 | 301015 | 04 | 4220 | Multi input terminal 23.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1014 | 8 | 301015 | 04 | 4230 | W. fail. 23 | BOOL |  |  |  | X | X | X | X
Alarm | 1015 | 0 | 301016 | 04 | 6110 | Service timer 1 | BOOL | [5 empty] | X | X
Alarm | 1015 | 1 | 301016 | 04 | 6120 | Service timer 2 | BOOL | [5 empty] | X | X
Alarm | 1015 | 2 | 301016 | 04 | 6270 | Stop coil wire break | BOOL | [5 empty] | X | X
Alarm | 1015 | 4 | 301016 | 04 | 6330 | Engine heater 1 | BOOL | [5 empty] | X | X
Alarm | 1015 | 5 | 301016 | 04 | 6410 | Battery test | BOOL | [5 empty] | X | X
Alarm | 1015 | 6 | 301016 | 04 | 6440 | Battery asymmetry 1 | BOOL | [5 empty] | X | X
Alarm | 1015 | 7 | 301016 | 04 | 6450 | Battery asymmetry 2 | BOOL | [5 empty] | X | X
Alarm | 1015 | 8 | 301016 | 04 | 6470 | Max. ventilation 1 | BOOL | [5 empty] | X | X
Alarm | 1015 | 9 | 301016 | 04 | 6480 | Max. ventilation 2 | BOOL | [5 empty] | X | X
Alarm | 1015 | 10 | 301016 | 04 | 6500 | Block switchboard error | BOOL | [5 empty] | X
Alarm | 1015 | 11 | 301016 | 04 | 6510 | Stop switchboard error | BOOL | [5 empty] | X
Alarm | 1015 | 12 | 301016 | 04 | 6540 | Unit not in auto | BOOL |  |  |  | X | X | X | X
Alarm | 1015 | 13 | 301016 | 04 | 6550 | Fuel pump logic | BOOL | [5 empty] | X | X
Relay state | 1016 | 0 | 301017 | 04 | 5000 | Relay 5 | BOOL |  |  |  | X | X | X | X
Relay state | 1016 | 1 | 301017 | 04 | 5000 | Relay 6 | BOOL |  |  |  | X | X | X | X
Relay state | 1016 | 2 | 301017 | 04 | 5000 | Relay 9 | BOOL |  |  |  | X | X | X | X
Relay state | 1016 | 3 | 301017 | 04 | 5000 | Relay 10 | BOOL |  |  |  | X | X | X | X
Relay state | 1016 | 4 | 301017 | 04 | 5000 | Relay 11 | BOOL |  |  |  | X | X | X | X
Relay state | 1016 | 5 | 301017 | 04 | 5000 | Relay 12 | BOOL |  |  |  | X | X | X | X
Relay state | 1016 | 6 | 301017 | 04 | 5000 | Relay 13 | BOOL |  |  |  | X | X | X | X
Relay state | 1016 | 7 | 301017 | 04 | 5000 | Relay 14 | BOOL |  |  |  | X | X | X | X
Relay state | 1016 | 8 | 301017 | 04 | 5080 | Relay 15 | BOOL |  |  |  | X | X | X | X
Relay state | 1016 | 9 | 301017 | 04 | 8090 | Relay 16 | BOOL |  |  |  | X | X | X | X
Relay state | 1016 | 10 | 301017 | 04 | 5100 | Relay 17 | BOOL |  |  |  | X | X | X | X
Relay state | 1016 | 11 | 301017 | 04 | 5110 | Relay 18 | BOOL |  |  |  | X | X | X | X
Relay state | 1017 | 12 | 301018 | 04 |  | Run. coil relay | BOOL | [5 empty] | X | X
Relay state | 1017 | 13 | 301018 | 04 |  | Start prepare | BOOL | [5 empty] | X | X
Relay state | 1017 | 14 | 301018 | 04 |  | Start relay | BOOL | [5 empty] | X | X
Relay state | 1017 | 15 | 301018 | 04 |  | Stop coil relay | BOOL | [5 empty] | X | X
Plant logic state | 1018 | 0 | 301019 | 04 |  | EDG bus failure | BOOL | [5 empty] | X
Plant logic state | 1018 | 0 | 301019 | 04 |  | Shore failure | BOOL |  |  |  |  | X
Plant logic state | 1018 | 1 | 301019 | 04 |  | TB position ON (EDG) | BOOL | [5 empty] | X
Plant logic state | 1018 | 1 | 301019 | 04 |  | SCB position ON | BOOL |  |  |  |  | X
Plant logic state | 1018 | 3 | 301019 | 04 |  | Start GOV regulation | BOOL | [5 empty] | X
Plant logic state | 1018 | 4 | 301019 | 04 |  | GB position ON | BOOL | [5 empty] | X
Plant logic state | 1018 | 4 | 301019 | 04 |  | BTB position ON | BOOL |  |  |  | X
Plant logic state | 1018 | 5 | 301019 | 04 |  | GB synchronising | BOOL | [5 empty] | X
Plant logic state | 1018 | 5 | 301019 | 04 |  | BTB synchronising | BOOL |  |  |  | X
Plant logic state | 1018 | 6 | 301019 | 04 |  | Engine running | BOOL | [5 empty] | X | X
Plant logic state | 1018 | 7 | 301019 | 04 | 6173 | Running detected, timer expired | BOOL | [5 empty] | X | X
Plant logic state | 1018 | 8 | 301019 | 04 | 6220 | DG Hz/V OK, timer expired | BOOL | [5 empty] | X
Plant logic state | 1018 | 8 | 301019 | 04 | 6220 | BB Hz/V OK, timer expired | BOOL |  |  |  | X
Plant logic state | 1018 | 9 | 301019 | 04 | 6410 | Battery test ongoing | BOOL | [5 empty] | X | X
Plant logic state | 1018 | 10 | 301019 | 04 |  | Shutdown override active | BOOL | [5 empty] | X | X
Plant logic state | 1018 | 11 | 301019 | 04 |  | GB position OFF | BOOL | [5 empty] | X
Plant logic state | 1018 | 11 | 301019 | 04 |  | BTB position OFF | BOOL |  |  |  | X
Plant logic state | 1018 | 12 | 301019 | 04 |  | TB position OFF | BOOL | [5 empty] | X
Plant logic state | 1018 | 12 | 301019 | 04 |  | SCB position OFF | BOOL |  |  |  |  | X
Plant logic state | 1018 | 13 | 301019 | 04 |  | BB Hz/V OK | BOOL |  |  |  | X | X | X
Plant logic state | 1018 | 14 | 301019 | 04 |  | EDG, TB synchronising | BOOL | [5 empty] | X
Plant logic state | 1018 | 14 | 301019 | 04 |  | Shore, SCB synchronising | BOOL |  |  |  |  | X
Modes | 1019 | 0 | 301020 | 04 |  | BLOCK mode | BOOL |  |  |  | X | X | X | X
Modes | 1019 | 1 | 301020 | 04 |  | SWBD mode | BOOL |  |  |  | X | X | X | X
Modes | 1019 | 2 | 301020 | 04 |  | MANUAL mode | BOOL |  |  |  | X | X | X | X
Modes | 1019 | 3 | 301020 | 04 |  | Remote mode | BOOL | [5 empty] | X | X
Modes | 1019 | 3 | 301020 | 04 |  | AUTO mode | BOOL |  |  |  | X | X
Modes | 1019 | 4 | 301020 | 04 |  | TEST | BOOL |  |  |  |  | X | X | X
Modes | 1019 | 5 | 301020 | 04 |  | Island | BOOL | [5 empty] | X | X
Modes | 1019 | 6 | 301020 | 04 |  | EDG | BOOL | [5 empty] | X
Modes | 1019 | 15 | 301020 | 04 |  | EDG active | BOOL | [5 empty] | X
EIC alarm | 1020 | 0 | 301021 | 04 | 7570 | Communication Error | BOOL | [5 empty] | X | X
EIC alarm | 1020 | 1 | 301021 | 04 | 7580 | Warning / Yellow alarm | BOOL | [5 empty] | X | X
EIC alarm | 1020 | 2 | 301021 | 04 | 7590 | Shutdown / Red alarm | BOOL | [5 empty] | X | X
EIC alarm | 1020 | 3 | 301021 | 04 | 7600 | Over-speed | BOOL | [5 empty] | X | X
EIC alarm | 1020 | 4 | 301021 | 04 | 7610 | Coolant water temperature 1 | BOOL | [5 empty] | X | X
EIC alarm | 1020 | 5 | 301021 | 04 | 7620 | Coolant water temperature 2 | BOOL | [5 empty] | X | X
EIC alarm | 1020 | 6 | 301021 | 04 | 7630 | Oil pressure 1 | BOOL | [5 empty] | X | X
EIC alarm | 1020 | 7 | 301021 | 04 | 7640 | Oil pressure 2 | BOOL | [5 empty] | X | X
EIC alarm | 1020 | 8 | 301021 | 04 | 7650 | Oil temperature 1 | BOOL | [5 empty] | X | X
EIC alarm | 1020 | 9 | 301021 | 04 | 7660 | Oil temperature 2 | BOOL | [5 empty] | X | X
EIC alarm | 1020 | 10 | 301021 | 04 | 7670 | Coolant water level 1 | BOOL | [5 empty] | X | X
EIC alarm | 1020 | 11 | 301021 | 04 | 7680 | Coolant water level 2 | BOOL | [5 empty] | X | X
EIC alarm | 1020 | 12 | 301021 | 04 | 7690 | Cylinder exhaust difference 1 | BOOL | [5 empty] | X | X
EIC alarm | 1020 | 13 | 301021 | 04 | 7700 | Cylinder exhaust difference 2 | BOOL | [5 empty] | X | X
EIC alarm | 1021 | 0 | 301022 | 04 |  | ECU alarm bit 49 | BOOL | [5 empty] | X | X
EIC alarm | 1021 | 1 | 301022 | 04 |  | ECU alarm bit 50 | BOOL | [5 empty] | X | X
EIC alarm | 1021 | 12 | 301022 | 04 |  | Protection lamp | BOOL | [5 empty] | X | X
EIC alarm | 1021 | 13 | 301022 | 04 |  | Malfunction lamp | BOOL | [5 empty] | X | X
EIC alarm | 1021 | 14 | 301022 | 04 |  | Yellow lamp | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 0 | 301023 | 04 |  | ECU alarm bit 33 | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 1 | 301023 | 04 |  | ECU alarm bit 34 | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 2 | 301023 | 04 |  | ECU alarm bit 35 | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 3 | 301023 | 04 |  | ECU alarm bit 36 | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 4 | 301023 | 04 |  | ECU alarm bit 37 | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 5 | 301023 | 04 |  | ECU alarm bit 38 | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 6 | 301023 | 04 |  | ECU alarm bit 39 | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 7 | 301023 | 04 |  | ECU alarm bit 40 | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 8 | 301023 | 04 |  | ECU alarm bit 41 | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 9 | 301023 | 04 |  | ECU alarm bit 42 | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 10 | 301023 | 04 |  | ECU alarm bit 43 | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 11 | 301023 | 04 |  | ECU alarm bit 44 | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 12 | 301023 | 04 |  | ECU alarm bit 45 | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 13 | 301023 | 04 |  | ECU alarm bit 46 | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 14 | 301023 | 04 |  | ECU alarm bit 47 | BOOL | [5 empty] | X | X
EIC alarm | 1022 | 15 | 301023 | 04 |  | ECU alarm bit 48 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 0 | 301024 | 04 |  | ECU alarm bit 17 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 1 | 301024 | 04 |  | ECU alarm bit 18 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 2 | 301024 | 04 |  | ECU alarm bit 19 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 3 | 301024 | 04 |  | ECU alarm bit 20 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 4 | 301024 | 04 |  | ECU alarm bit 21 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 5 | 301024 | 04 |  | ECU alarm bit 22 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 6 | 301024 | 04 |  | ECU alarm bit 23 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 7 | 301024 | 04 |  | ECU alarm bit 24 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 8 | 301024 | 04 |  | ECU alarm bit 25 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 9 | 301024 | 04 |  | ECU alarm bit 26 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 10 | 301024 | 04 |  | ECU alarm bit 27 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 11 | 301024 | 04 |  | ECU alarm bit 28 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 12 | 301024 | 04 |  | ECU alarm bit 29 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 13 | 301024 | 04 |  | ECU alarm bit 30 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 14 | 301024 | 04 |  | ECU alarm bit 31 | BOOL | [5 empty] | X | X
EIC alarm | 1023 | 15 | 301024 | 04 |  | ECU alarm bit 32 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 0 | 301025 | 04 |  | ECU alarm bit 1 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 1 | 301025 | 04 |  | ECU alarm bit 2 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 2 | 301025 | 04 |  | ECU alarm bit 3 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 3 | 301025 | 04 |  | ECU alarm bit 4 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 4 | 301025 | 04 |  | ECU alarm bit 5 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 5 | 301025 | 04 |  | ECU alarm bit 6 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 6 | 301025 | 04 |  | ECU alarm bit 7 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 7 | 301025 | 04 |  | ECU alarm bit 8 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 8 | 301025 | 04 |  | ECU alarm bit 9 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 9 | 301025 | 04 |  | ECU alarm bit 10 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 10 | 301025 | 04 |  | ECU alarm bit 11 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 11 | 301025 | 04 |  | ECU alarm bit 12 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 12 | 301025 | 04 |  | ECU alarm bit 13 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 13 | 301025 | 04 |  | ECU alarm bit 14 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 14 | 301025 | 04 |  | ECU alarm bit 15 | BOOL | [5 empty] | X | X
EIC alarm | 1024 | 15 | 301025 | 04 |  | ECU alarm bit 16 | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 0 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Overreving | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 1 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Speed sensor 1 | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 2 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Speed sensor 2 | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 3 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Water temperature sensor | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 4 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Charge air temperature sensor | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 5 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Charge air pressure sensor | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 6 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Oil temperature sensor | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 7 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Oil pressure sensor | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 8 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Fault in cor. | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 9 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Throttle pedal | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 10 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Emergency stop o.r | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 11 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Oil pressure protection | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 12 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Wrong parameter | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 13 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Battery voltage | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 14 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Oil pressure protection | BOOL | [5 empty] | X | X
EIC alarm | 1026 | 15 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Emergency stop cor | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 0 | 301028 | 04 |  | Scania EMS 2 KWP2000 - CAN-circuit defect | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 1 | 301028 | 04 |  | Scania EMS 2 KWP2000 - CAN message DLN1 | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 2 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Wrong CAN version | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 3 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 1 | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 4 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 2 | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 5 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 3 | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 6 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 4 | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 7 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 5 | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 8 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 6 | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 9 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 7 | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 10 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 8 | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 11 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Extra analogue input | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 12 | 301028 | 04 |  | Scania EMS 2 KWP2000 - System shutdown | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 13 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Coolant l. protection | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 14 | 301028 | 04 |  | Scania EMS 2 KWP2000 - hardware watchdog | BOOL | [5 empty] | X | X
EIC alarm | 1027 | 15 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Fault in RAM | BOOL | [5 empty] | X | X
EIC alarm | 1028 | 0 | 301029 | 04 |  | Scania EMS 2 KWP2000 - Seal | BOOL | [5 empty] | X | X
EIC alarm | 1028 | 1 | 301029 | 04 |  | Scania EMS 2 KWP2000 - Coolant shut off | BOOL | [5 empty] | X | X
EIC alarm | 1028 | 2 | 301029 | 04 |  | Scania EMS 2 KWP2000 - Over heat protection | BOOL | [5 empty] | X | X
EIC alarm | 1028 | 3 | 301029 | 04 |  | Scania EMS 2 KWP2000 - Fault in TPU | BOOL | [5 empty] | X | X
PM alarm | 1031 | 1 | 301032 | 04 |  | CAN 1 missing ID 1 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 2 | 301032 | 04 |  | CAN 1 missing ID 2 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 2 | 301033 | 04 |  | CAN 2 missing ID 1 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 3 | 301033 | 04 |  | CAN 2 missing ID 2 | BOOL |  |  |  | X | X | X
Alarm | 1033 | 2 | 301034 | 04 | 7520 | Communication error ext. | BOOL |  |  |  | X | X | X | X
PM alarm | 1034 | 1 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 1 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 2 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 2 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 0 | 301037 | 04 | 12000 | Ext. Analogue in. 1.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1036 | 1 | 301037 | 04 | 12010 | Ext. Analogue in. 1.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1036 | 3 | 301037 | 04 | 12030 | Ext. Analogue in. 2.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1036 | 4 | 301037 | 04 | 12040 | Ext. Analogue in. 2.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1036 | 6 | 301037 | 04 | 12060 | Ext. Analogue in. 3.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1036 | 7 | 301037 | 04 | 12070 | Ext. Analogue in. 3.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1036 | 9 | 301037 | 04 | 12090 | Ext. Analogue in. 4.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1036 | 10 | 301037 | 04 | 12100 | Ext. Analogue in. 4.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1036 | 12 | 301037 | 04 | 12120 | Ext. Analogue in. 5.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1036 | 13 | 301037 | 04 | 12130 | Ext. Analogue in. 5.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1036 | 15 | 301037 | 04 | 12150 | Ext. Analogue in. 6.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1037 | 0 | 301038 | 04 | 12160 | Ext. Analogue in. 6.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1037 | 2 | 301038 | 04 | 12180 | Ext. Analogue in. 7.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1037 | 3 | 301038 | 04 | 12190 | Ext. Analogue in. 7.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1037 | 5 | 301038 | 04 | 12210 | Ext. Analogue in. 8.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1037 | 6 | 301038 | 04 | 12220 | Ext. Analogue in. 8.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 0 | 301039 | 04 | 12540 | External digital input 1/CIO 116-1 digital input 10 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 1 | 301039 | 04 | 12550 | External digital input 2/CIO 116-1 digital input 11 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 2 | 301039 | 04 | 12560 | External digital input 3/CIO 116-1 digital input 12 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 3 | 301039 | 04 | 12570 | External digital input 4/CIO 116-1 digital input 13 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 4 | 301039 | 04 | 12580 | External digital input 5/CIO 116-1 digital input 14 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 5 | 301039 | 04 | 12590 | External digital input 6/CIO 116-1 digital input 15 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 6 | 301039 | 04 | 12600 | External digital input 7/CIO 116-1 digital input 16 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 7 | 301039 | 04 | 12610 | External digital input 8/CIO 116-1 digital input 17 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 8 | 301039 | 04 | 12620 | External digital input 9/CIO 116-1 digital input 19 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 9 | 301039 | 04 | 12630 | External digital input 10/CIO 116-1 digital input 20 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 10 | 301039 | 04 | 12640 | External digital input 11/CIO 116-1 digital input 21 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 11 | 301039 | 04 | 12650 | External digital input 12/CIO 116-1 digital input 22 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 12 | 301039 | 04 | 12660 | External digital input 13/CIO 116-1 digital input 23 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 13 | 301039 | 04 | 12670 | External digital input 14/CIO 116-1 digital input 24 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 14 | 301039 | 04 | 12680 | External digital input 15/CIO 116-1 digital input 25 | BOOL |  |  |  | X | X | X | X
Alarm | 1038 | 15 | 301039 | 04 | 12690 | External digital input 16/CIO 116 no.1 digital input 26 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 0 | 301040 | 04 | 12790 | External digital output 1/CIO 208-1 digital output 9 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 1 | 301040 | 04 | 12800 | External digital output 2/CIO 208-1 digital output 11 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 2 | 301040 | 04 | 12810 | External digital output 3/CIO 208-1 digital output 13 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 3 | 301040 | 04 | 12820 | External digital output 4/CIO 208-1 digital output 15 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 4 | 301040 | 04 | 12830 | External digital output 5/CIO 208-1 digital output 18 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 5 | 301040 | 04 | 12840 | External digital output 6/CIO 208-1 digital output 21 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 6 | 301040 | 04 | 12850 | External digital output 7/CIO 208-1 digital output 24 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 7 | 301040 | 04 | 12860 | External digital output 8/CIO 208-1 digital output 27 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 8 | 301040 | 04 | 12870 | External digital output 9/CIO 208-2 digital output 9 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 9 | 301040 | 04 | 12880 | External digital output 10/CIO 208-2 digital output 11 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 10 | 301040 | 04 | 12890 | External digital output 11/CIO 208-2 digital output 13 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 11 | 301040 | 04 | 12900 | External digital output 12/CIO 208-2 digital output 15 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 12 | 301040 | 04 | 12910 | External digital output 13/CIO 208-2 digital output 18 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 13 | 301040 | 04 | 12920 | External digital output 14/CIO 208-2 digital output 21 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 14 | 301040 | 04 | 12930 | External digital output 15/CIO 208-2 digital output 24 | BOOL |  |  |  | X | X | X | X
Digital output state | 1039 | 15 | 301040 | 04 | 12940 | External digital output 16/CIO 208-2 digital output 27 | BOOL |  |  |  | X | X | X | X
PM alarm | 1040 | 0 | 301041 | 04 |  | CAN 1 missing ID 1 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 1 | 301041 | 04 |  | CAN 1 missing ID 2 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 8 | 301042 | 04 |  | CAN 1 missing ID 25 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 9 | 301042 | 04 |  | CAN 1 missing ID 26 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 10 | 301042 | 04 |  | CAN 1 missing ID 27 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 11 | 301042 | 04 |  | CAN 1 missing ID 28 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 15 | 301042 | 04 |  | CAN 1 missing ID 32 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 0 | 301043 | 04 |  | CAN 1 missing ID 33 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 1 | 301043 | 04 |  | CAN 1 missing ID 34 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 0 | 301044 | 04 |  | CAN 2 missing ID 1 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 1 | 301044 | 04 |  | CAN 2 missing ID 2 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 8 | 301045 | 04 |  | CAN 2 missing ID 25 | BOOL |  |  |  | X |  | X
PM alarm | 1044 | 9 | 301045 | 04 |  | CAN 2 missing ID 26 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 10 | 301045 | 04 |  | CAN 2 missing ID 27 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 11 | 301045 | 04 |  | CAN 2 missing ID 28 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 15 | 301045 | 04 |  | CAN 2 missing ID 32 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 0 | 301046 | 04 |  | CAN 2 missing ID 33 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 1 | 301046 | 04 |  | CAN 2 missing ID 34 | BOOL |  |  |  | X | X | X
Plant logic state | 1050 | 0 | 301051 | 04 |  | Ready to autostart | BOOL | [5 empty] | X | X
Plant logic state | 1050 | 1 | 301051 | 04 |  | Shore U > 30% of U nominal | BOOL |  |  |  |  | X
Plant logic state | 1050 | 1 | 301051 | 04 |  | GEN U > 30% of U nominal | BOOL | [5 empty] | X
Plant logic state | 1050 | 1 | 301051 | 04 |  | BA U > 30% of U nominal | BOOL |  |  |  | X
Plant logic state | 1050 | 2 | 301051 | 04 |  | BB U > 30% of U nominal | BOOL |  |  |  | X | X | X
Plant logic state | 1050 | 3 | 301051 | 04 |  | Power derate state/active | BOOL | [5 empty] | X
M-Logic state | 1051 |  | 301052 | 04 |  | Virtual events 1-16 | INT16s | AB | 0 |  | X | X | X | X
M-Logic state | 1052 |  | 301053 | 04 |  | Virtual events 17-32 | INT16s | AB | 0 |  | X | X | X | X
Alarm | 1053 | 0 | 301054 | 04 | 6590 | Fan A Failure | BOOL | [5 empty] | X
Alarm | 1053 | 1 | 301054 | 04 | 6600 | Fan B Failure | BOOL | [5 empty] | X
Alarm | 1053 | 2 | 301054 | 04 | 6610 | Fan C Failure | BOOL | [5 empty] | X
Alarm | 1053 | 3 | 301054 | 04 | 6620 | Fan D Failure | BOOL | [5 empty] | X
Alarm | 1053 | 4 | 301054 | 04 | 4610 | Delta analogue 1 - fail 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1053 | 5 | 301054 | 04 | 4620 | Delta analogue 1 - fail 2 | BOOL |  |  |  | X | X | X | X
Alarm | 1053 | 6 | 301054 | 04 | 4630 | Delta analogue 2 - fail 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1053 | 7 | 301054 | 04 | 4640 | Delta analogue 2 - fail 2 | BOOL |  |  |  | X | X | X | X
Alarm | 1053 | 8 | 301054 | 04 | 4650 | Delta analogue 3 - fail 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1053 | 9 | 301054 | 04 | 4660 | Delta analogue 3 - fail 2 | BOOL |  |  |  | X | X | X | X
Alarm | 1053 | 10 | 301054 | 04 | 4680 | Delta analogue 4 - fail 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1053 | 11 | 301054 | 04 | 4690 | Delta analogue 4 - fail 2 | BOOL |  |  |  | X | X | X | X
Alarm | 1053 | 12 | 301054 | 04 | 4700 | Delta analogue 5 - fail 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1053 | 13 | 301054 | 04 | 4710 | Delta analogue 5 - fail 2 | BOOL |  |  |  | X | X | X | X
Alarm | 1053 | 14 | 301054 | 04 | 4720 | Delta analogue 6 - fail 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1053 | 15 | 301054 | 04 | 4730 | Delta analogue 6 - fail 2 | BOOL |  |  |  | X | X | X | X
AC alarm | 1054 | 0 | 301055 | 04 |  | In> inverse | BOOL |  |  |  | X |  | X
AC alarm | 1054 | 1 | 301055 | 04 |  | Ie> inverse | BOOL |  |  |  | X |  | X
Alarm | 1054 | 3 | 301055 | 04 | 6352 | External Engine Stop | BOOL | [5 empty] | X | X
AC alarm | 1054 | 4 | 301055 | 04 | 1710 | Unbalance curr. 2 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 5 | 301055 | 04 | 7480 | Avg U BB > 1 | BOOL | [5 empty] | X
AC alarm | 1054 | 6 | 301055 | 04 | 7490 | Avg U BB > 2 | BOOL | [5 empty] | X
AC alarm | 1054 | 7 | 301055 | 04 | 7440 | 4th CT -P> 1 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 8 | 301055 | 04 | 7450 | 4th CT -P> 2 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 9 | 301055 | 04 | 7460 | 4th CT P> 1 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 10 | 301055 | 04 | 7470 | 4th CT P> 2 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 11 | 301055 | 04 | 1920 | BB f> 4 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 12 | 301055 | 04 | 1930 | BB f< 5 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 13 | 301055 | 04 | 1940 | BB U> 4 | BOOL |  |  |  | X | X | X
AC alarm | 1054 | 14 | 301055 | 04 | 1950 | BB U< 5 | BOOL |  |  |  | X | X | X
DAVR Alarm | 1056 | 0 | 301057 | 04 | 7830 | Digital AVR Communication Error | BOOL | [5 empty] | X
DAVR Alarm | 1056 | 1 | 301057 | 04 | 7761 | Digital AVR Warning | BOOL | [5 empty] | X
DAVR Alarm | 1056 | 2 | 301057 | 04 | 7763 | Digital AVR Trip | BOOL | [5 empty] | X
Alarm | 1056 | 13 | 301057 | 04 | 18000 | SDU status OK error | BOOL | [5 empty] | X
Alarm | 1056 | 14 | 301057 | 04 | 18010 | SDU warning | BOOL | [5 empty] | X
Alarm | 1056 | 15 | 301057 | 04 | 18020 | SDU comm I/F error | BOOL | [5 empty] | X
Alarm | 1057 | 0 | 301058 | 04 |  | Fail class: Block start | BOOL | [6 empty] | X
Alarm | 1057 | 0 | 301058 | 04 |  | Fail class: Block start + breaker on | BOOL |  |  |  | X |  | X
Alarm | 1057 | 1 | 301058 | 04 |  | Fail class: Warning | BOOL |  |  |  | X | X | X | X
Alarm | 1057 | 2 | 301058 | 04 |  | Fail class: Trip GB | BOOL | [5 empty] | X
Alarm | 1057 | 2 | 301058 | 04 |  | Fail class: Trip BTB | BOOL |  |  |  | X
Alarm | 1057 | 3 | 301058 | 04 |  | Fail class: Trip GB + stop with cooling down | BOOL | [5 empty] | X
Alarm | 1057 | 4 | 301058 | 04 |  | Fail class: Shutdown | BOOL | [6 empty] | X
Alarm | 1057 | 4 | 301058 | 04 |  | Fail class: Trip GB + stop without cooling down | BOOL | [5 empty] | X
Alarm | 1057 | 5 | 301058 | 04 |  | Fail class: Trip TB | BOOL | [5 empty] | X
Alarm | 1057 | 5 | 301058 | 04 |  | Fail class: Trip SCB | BOOL |  |  |  |  | X
Alarm | 1057 | 6 | 301058 | 04 |  | Fail class: Safety stop | BOOL | [5 empty] | X
Alarm | 1057 | 7 | 301058 | 04 |  | Fail class: If TB present Trip TB else Trip GB | BOOL | [5 empty] | X
Alarm | 1057 | 8 | 301058 | 04 |  | Fail class: Controlled stop (cooldown) | BOOL | [6 empty] | X
Alarm | 1057 | 8 | 301058 | 04 |  | Fail class: Controlled stop (deload + cooldown) | BOOL | [5 empty] | X
M-Logic state | 1058 |  | 301059 | 04 |  | Virtual events 33-48 | INT16s | AB | 0 |  | X | X | X | X
M-Logic state | 1059 |  | 301060 | 04 |  | Virtual events 49-64 | INT16s | AB | 0 |  | X | X | X | X
M-Logic state | 1060 |  | 301061 | 04 |  | Virtual events 65-80 | INT16s | AB | 0 |  | X | X | X | X
M-Logic state | 1061 |  | 301062 | 04 |  | Virtual events 81-96 | INT16s | AB | 0 |  | X | X | X | X
M-Logic state | 1062 |  | 301063 | 04 |  | Flipflop output 1-16 | INT16s | AB | 0 |  | X | X | X | X
EIC state | 1068 | 0 | 301069 | 04 |  | M-Logic command: Reset trip fuel | BOOL | [5 empty] | X | X
EIC state | 1068 | 1 | 301069 | 04 |  | M-Logic command: MTU Alternate droop setting | BOOL | [5 empty] | X | X
Plant logic state | 1068 | 2 | 301069 | 04 |  | Nominal frequency 50/60Hz | BOOL |  |  |  | X |  | X
Plant logic state | 1068 | 3 | 301069 | 04 |  | Idle run active | BOOL | [5 empty] | X | X
EIC state | 1068 | 5 | 301069 | 04 |  | Engine start | BOOL | [5 empty] | X | X
EIC state | 1068 | 6 | 301069 | 04 |  | Engine stop | BOOL | [5 empty] | X | X
EIC state | 1068 | 7 | 301069 | 04 |  | Disable Engine Cylinder Cutoff2 | BOOL | [5 empty] | X | X
EIC state | 1068 | 8 | 301069 | 04 |  | M-Logic command: Engine overspeed test | BOOL | [5 empty] | X | X
EIC state | 1068 | 9 | 301069 | 04 |  | M-Logic command: Intermittent Oil Priming | BOOL | [5 empty] | X | X
EIC state | 1068 | 10 | 301069 | 04 |  | Engine preheat active | BOOL | [5 empty] | X | X
EIC state | 1068 | 11 | 301069 | 04 |  | CVT transmission enabled | BOOL | [5 empty] | X | X
Alarm | 1074 | 0 | 301075 | 04 | 4750 | Delta analogue 7 - fail 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1074 | 1 | 301075 | 04 | 4760 | Delta analogue 7 - fail 2 | BOOL |  |  |  | X | X | X | X
Alarm | 1074 | 2 | 301075 | 04 | 4770 | Delta analogue 8 - fail 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1074 | 3 | 301075 | 04 | 4780 | Delta analogue 8 - fail 2 | BOOL |  |  |  | X | X | X | X
Alarm | 1074 | 4 | 301075 | 04 | 4790 | Delta analogue 9 - fail 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1074 | 5 | 301075 | 04 | 4800 | Delta analogue 9 - fail 2 | BOOL |  |  |  | X | X | X | X
EIC state | 1076 |  | 301077 | 04 |  | JCB: Dosing Module Status | INT16s | AB | 0 |  |  |  | X | X
EIC state | 1077 |  | 301078 | 04 |  | JCB: Actual Reducing Agent Quantity | INT16s | AB | 0 |  |  |  | X | X
EIC state | 1078 |  | 301079 | 04 |  | JCB: Aftertreatment Lamp | INT16s | AB | 0 |  |  |  | X | X
EIC state | 1079 |  | 301080 | 04 |  | JCB: Refresh Status Byte | INT16s | AB | 0 |  |  |  | X | X
EIC state | 1080 |  | 301081 | 04 |  | JCB: SCR Monitor | INT16s | AB | 0 |  |  |  | X | X
EIC state | 1081 |  | 301082 | 04 |  | JCB: Successful Running Refreshes | INT16s | AB | 0 |  |  |  | X | X
EIC state | 1082 |  | 301083 | 04 |  | JCB: Successful Stationary Refreshes | INT16s | AB | 0 |  |  |  | X | X
EIC state | 1083 |  | 301084 | 04 |  | JCB: Engine Rating | INT16s | AB | 0 |  |  |  | X | X
EIC state | 1085 |  | 301086 | 04 |  | Emergency Shutdown Indication | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1086 |  | 301087 | 04 |  | Humidity Derate Percentage | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1087 |  | 301088 | 04 |  | Volvo Penta: Number of EIO Activations | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1088 |  | 301089 | 04 |  | Volvo Penta: Accumulated EIO time | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1089 |  | 301090 | 04 |  | Volvo Penta: Time left of EIO Operation | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1092 |  | 301093 | 04 |  | HATZ: Remaining Service Hours | INT16s | AB | 0 |  |  |  | X | X
EIC state | 1093 | 0 | 301094 | 04 |  | HATZ: Engine Running | BOOL | [5 empty] | X | X
EIC state | 1093 | 1 | 301094 | 04 |  | HATZ: Service Delay | BOOL | [5 empty] | X | X
EIC state | 1093 | 2 | 301094 | 04 |  | HATZ: Pre-glow Active | BOOL | [5 empty] | X | X
EIC state | 1093 | 3 | 301094 | 04 |  | HATZ: Oil Pressure Missing | BOOL | [5 empty] | X | X
EIC state | 1093 | 4 | 301094 | 04 |  | HATZ: Engine Diagnostic Lamp | BOOL | [5 empty] | X | X
EIC state | 1093 | 5 | 301094 | 04 |  | HATZ: Engine Over temperature | BOOL | [5 empty] | X | X
EIC state | 1093 | 6 | 301094 | 04 |  | HATZ: Air Filter Switch | BOOL | [5 empty] | X | X
EIC state | 1093 | 7 | 301094 | 04 |  | HATZ: DPF Regeneration Not Inhibit Park Brake Not Set | BOOL | [5 empty] | X | X
EIC state | 1093 | 8 | 301094 | 04 |  | HATZ: DPF Regeneration Inhibit Park Brake Not Set | BOOL | [5 empty] | X | X
EIC state | 1093 | 9 | 301094 | 04 |  | HATZ: DPF Regeneration Not Inhibit Out Of Neutral | BOOL | [5 empty] | X | X
EIC state | 1093 | 10 | 301094 | 04 |  | HATZ: DPF Regeneration Inhibit Out Of Neutral | BOOL | [5 empty] | X | X
EIC state | 1093 | 11 | 301094 | 04 |  | HATZ: Parking Brake Switch | BOOL | [5 empty] | X | X
EIC state | 1093 | 12 | 301094 | 04 |  | HATZ: Brake Switch | BOOL | [5 empty] | X | X
EIC state | 1093 | 13 | 301094 | 04 |  | HATZ: Transmission Neutral Switch | BOOL | [5 empty] | X | X
EIC measurement | 1094 |  | 301095 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1095 |  | 301096 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1096 |  | 301097 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1097 |  | 301098 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1098 |  | 301099 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1099 |  | 301100 | 04 |  | Aftertreatment 1 Diesel Oxidation Catalyst Intake Temperature (SPN 4765) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1100 |  | 301101 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1101 |  | 301102 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1102 |  | 301103 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1103 |  | 301104 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1104 |  | 301105 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1105 |  | 301106 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1106 |  | 301107 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1107 |  | 301108 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1108 |  | 301109 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1109 |  | 301110 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1110 |  | 301111 | 04 |  | Isuzu: Escape Mode Enable Flag | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1111 |  | 301112 | 04 |  | Isuzu: Inducement Level | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1112 |  | 301113 | 04 |  | Isuzu: UREA Tank Level | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1113 |  | 301114 | 04 |  | Isuzu: UREA Tank Level Indicator | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1114 |  | 301115 | 04 |  | Isuzu: Level Indicator (Amber) Action | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1115 |  | 301116 | 04 |  | Isuzu: DPF Amber Lamp Mode | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1116 |  | 301117 | 04 |  | Isuzu: Exhaust system lamp | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1117 |  | 301118 | 04 |  | Isuzu: DPF Green Lamp Mode | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1118 |  | 301119 | 04 |  | Isuzu: NO POWER Lamp | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1119 |  | 301120 | 04 |  | Isuzu: Output Limitation | INT16s | AB | 0 |  |  |  | X | X
M-Logic state | 1128 |  | 301129 | 04 |  | Virtual toggle status 1-16 | INT16s | AB | 0 |  | X | X | X | X
M-Logic state | 1129 |  | 301130 | 04 |  | Virtual toggle status 17-32 | INT16s | AB | 0 |  | X | X | X | X
Alarm | 1130 | 0 | 301131 | 04 |  | CIO 308-2 Analogue input 8.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1130 | 1 | 301131 | 04 |  | CIO 308-2 Analogue input 8.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1130 | 2 | 301131 | 04 |  | CIO 308-2 Analogue input 11.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1130 | 3 | 301131 | 04 |  | CIO 308-2 Analogue input 11.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1130 | 4 | 301131 | 04 |  | CIO 308-2 Analogue input 14.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1130 | 5 | 301131 | 04 |  | CIO 308-2 Analogue input 14.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1130 | 6 | 301131 | 04 |  | CIO 308-2 Analogue input 17.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1130 | 7 | 301131 | 04 |  | CIO 308-2 Analogue input 17.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1130 | 8 | 301131 | 04 |  | CIO 308-2 Analogue input 20.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1130 | 9 | 301131 | 04 |  | CIO 308-2 Analogue input 20.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1130 | 10 | 301131 | 04 |  | CIO 308-2 Analogue input 23.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1130 | 11 | 301131 | 04 |  | CIO 308-2 Analogue input 23.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1130 | 12 | 301131 | 04 |  | CIO 308-2 Analogue input 26.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1130 | 13 | 301131 | 04 |  | CIO 308-2 Analogue input 26.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1130 | 14 | 301131 | 04 |  | CIO 308-2 Analogue input 29.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1130 | 15 | 301131 | 04 |  | CIO 308-2 Analogue input 29.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 0 | 301132 | 04 |  | CIO 308-3 Analogue input 8.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 1 | 301132 | 04 |  | CIO 308-3 Analogue input 8.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 2 | 301132 | 04 |  | CIO 308-3 Analogue input 11.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 3 | 301132 | 04 |  | CIO 308-3 Analogue input 11.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 4 | 301132 | 04 |  | CIO 308-3 Analogue input 14.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 5 | 301132 | 04 |  | CIO 308-3 Analogue input 14.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 6 | 301132 | 04 |  | CIO 308-3 Analogue input 17.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 7 | 301132 | 04 |  | CIO 308-3 Analogue input 17.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 8 | 301132 | 04 |  | CIO 308-3 Analogue input 20.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 9 | 301132 | 04 |  | CIO 308-3 Analogue input 20.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 10 | 301132 | 04 |  | CIO 308-3 Analogue input 23.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 11 | 301132 | 04 |  | CIO 308-3 Analogue input 23.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 12 | 301132 | 04 |  | CIO 308-3 Analogue input 26.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 13 | 301132 | 04 |  | CIO 308-3 Analogue input 26.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 14 | 301132 | 04 |  | CIO 308-3 Analogue input 29.1 | BOOL |  |  |  | X | X | X | X
Alarm | 1131 | 15 | 301132 | 04 |  | CIO 308-3 Analogue input 29.2 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 0 | 301133 | 04 |  | CIO 116-2 digital input 10 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 1 | 301133 | 04 |  | CIO 116-2 digital input 11 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 2 | 301133 | 04 |  | CIO 116-2 digital input 12 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 3 | 301133 | 04 |  | CIO 116-2 digital input 13 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 4 | 301133 | 04 |  | CIO 116-2 digital input 14 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 5 | 301133 | 04 |  | CIO 116-2 digital input 15 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 6 | 301133 | 04 |  | CIO 116-2 digital input 16 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 7 | 301133 | 04 |  | CIO 116-2 digital input 17 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 8 | 301133 | 04 |  | CIO 116-2 digital input 18 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 9 | 301133 | 04 |  | CIO 116-2 digital input 20 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 10 | 301133 | 04 |  | CIO 116-2 digital input 21 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 11 | 301133 | 04 |  | CIO 116-2 digital input 22 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 12 | 301133 | 04 |  | CIO 116-2 digital input 23 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 13 | 301133 | 04 |  | CIO 116-2 digital input 24 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 14 | 301133 | 04 |  | CIO 116-2 digital input 25 | BOOL |  |  |  | X | X | X | X
Alarm | 1132 | 15 | 301133 | 04 |  | CIO 116-2 digital input 26 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 0 | 301134 | 04 |  | CIO 116-3 digital input 10 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 1 | 301134 | 04 |  | CIO 116-3 digital input 11 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 2 | 301134 | 04 |  | CIO 116-3 digital input 12 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 3 | 301134 | 04 |  | CIO 116-3 digital input 13 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 4 | 301134 | 04 |  | CIO 116-3 digital input 14 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 5 | 301134 | 04 |  | CIO 116-3 digital input 15 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 6 | 301134 | 04 |  | CIO 116-3 digital input 16 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 7 | 301134 | 04 |  | CIO 116-3 digital input 17 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 8 | 301134 | 04 |  | CIO 116-3 digital input 19 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 9 | 301134 | 04 |  | CIO 116-3 digital input 20 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 10 | 301134 | 04 |  | CIO 116-3 digital input 21 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 11 | 301134 | 04 |  | CIO 116-3 digital input 22 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 12 | 301134 | 04 |  | CIO 116-3 digital input 23 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 13 | 301134 | 04 |  | CIO 116-3 digital input 24 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 14 | 301134 | 04 |  | CIO 116-3 digital input 25 | BOOL |  |  |  | X | X | X | X
Alarm | 1133 | 15 | 301134 | 04 |  | CIO 116-3 digital input 26 | BOOL |  |  |  | X | X | X | X
Digital output state | 1136 | 0 | 301137 | 04 |  | CIO 208-3 digital output 9 | BOOL |  |  |  | X | X | X | X
Digital output state | 1136 | 1 | 301137 | 04 |  | CIO 208-3 digital output 11 | BOOL |  |  |  | X | X | X | X
Digital output state | 1136 | 2 | 301137 | 04 |  | CIO 208-3 digital output 13 | BOOL |  |  |  | X | X | X | X
Digital output state | 1136 | 3 | 301137 | 04 |  | CIO 208-3 digital output 15 | BOOL |  |  |  | X | X | X | X
Digital output state | 1136 | 4 | 301137 | 04 |  | CIO 208-3 digital output 18 | BOOL |  |  |  | X | X | X | X
Digital output state | 1136 | 5 | 301137 | 04 |  | CIO 208-3 digital output 21 | BOOL |  |  |  | X | X | X | X
Digital output state | 1136 | 6 | 301137 | 04 |  | CIO 208-3 digital output 24 | BOOL |  |  |  | X | X | X | X
Digital output state | 1136 | 7 | 301137 | 04 |  | CIO 208-3 digital output 27 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 0 | 301139 | 04 |  | CIO 116 no. 1. Input 10 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 1 | 301139 | 04 |  | CIO 116 no. 1. Input 11 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 2 | 301139 | 04 |  | CIO 116 no. 1. Input 12 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 3 | 301139 | 04 |  | CIO 116 no. 1. Input 13 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 4 | 301139 | 04 |  | CIO 116 no. 1. Input 14 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 5 | 301139 | 04 |  | CIO 116 no. 1. Input 15 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 6 | 301139 | 04 |  | CIO 116 no. 1. Input 16 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 7 | 301139 | 04 |  | CIO 116 no. 1. Input 17 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 8 | 301139 | 04 |  | CIO 116 no. 1. Input 19 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 9 | 301139 | 04 |  | CIO 116 no. 1. Input 20 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 10 | 301139 | 04 |  | CIO 116 no. 1. Input 21 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 11 | 301139 | 04 |  | CIO 116 no. 1. Input 22 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 12 | 301139 | 04 |  | CIO 116 no. 1. Input 23 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 13 | 301139 | 04 |  | CIO 116 no. 1. Input 24 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 14 | 301139 | 04 |  | CIO 116 no. 1. Input 25 | BOOL |  |  |  | X | X | X | X
Digital input state | 1138 | 15 | 301139 | 04 |  | CIO 116 no. 1. Input 26 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 0 | 301140 | 04 |  | CIO 116 no. 2. Input 10 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 1 | 301140 | 04 |  | CIO 116 no. 2. Input 11 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 2 | 301140 | 04 |  | CIO 116 no. 2. Input 12 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 3 | 301140 | 04 |  | CIO 116 no. 2. Input 13 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 4 | 301140 | 04 |  | CIO 116 no. 2. Input 14 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 5 | 301140 | 04 |  | CIO 116 no. 2. Input 15 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 6 | 301140 | 04 |  | CIO 116 no. 2. Input 16 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 7 | 301140 | 04 |  | CIO 116 no. 2. Input 17 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 8 | 301140 | 04 |  | CIO 116 no. 2. Input 19 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 9 | 301140 | 04 |  | CIO 116 no. 2. Input 20 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 10 | 301140 | 04 |  | CIO 116 no. 2. Input 21 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 11 | 301140 | 04 |  | CIO 116 no. 2. Input 22 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 12 | 301140 | 04 |  | CIO 116 no. 2. Input 23 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 13 | 301140 | 04 |  | CIO 116 no. 2. Input 24 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 14 | 301140 | 04 |  | CIO 116 no. 2. Input 25 | BOOL |  |  |  | X | X | X | X
Digital input state | 1139 | 15 | 301140 | 04 |  | CIO 116 no. 2. Input 26 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 0 | 301141 | 04 |  | CIO 116 no. 3. Input 10 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 1 | 301141 | 04 |  | CIO 116 no. 3. Input 11 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 2 | 301141 | 04 |  | CIO 116 no. 3. Input 12 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 3 | 301141 | 04 |  | CIO 116 no. 3. Input 13 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 4 | 301141 | 04 |  | CIO 116 no. 3. Input 14 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 5 | 301141 | 04 |  | CIO 116 no. 3. Input 15 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 6 | 301141 | 04 |  | CIO 116 no. 3. Input 16 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 7 | 301141 | 04 |  | CIO 116 no. 3. Input 17 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 8 | 301141 | 04 |  | CIO 116 no. 3. Input 19 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 9 | 301141 | 04 |  | CIO 116 no. 3. Input 20 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 10 | 301141 | 04 |  | CIO 116 no. 3. Input 21 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 11 | 301141 | 04 |  | CIO 116 no. 3. Input 22 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 12 | 301141 | 04 |  | CIO 116 no. 3. Input 23 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 13 | 301141 | 04 |  | CIO 116 no. 3. Input 24 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 14 | 301141 | 04 |  | CIO 116 no. 3. Input 25 | BOOL |  |  |  | X | X | X | X
Digital input state | 1140 | 15 | 301141 | 04 |  | CIO 116 no. 3. Input 26 | BOOL |  |  |  | X | X | X | X
Digital output state | 1141 | 0 | 301142 | 04 |  | CIO 116 no. 1 conf. status out | BOOL |  |  |  | X | X | X | X
Digital output state | 1141 | 1 | 301142 | 04 |  | CIO 116 no. 2 conf. status out | BOOL |  |  |  | X | X | X | X
Digital output state | 1141 | 2 | 301142 | 04 |  | CIO 116 no. 3 conf. status out | BOOL |  |  |  | X | X | X | X
Digital output state | 1141 | 3 | 301142 | 04 |  | CIO 208 no. 1 conf. status out | BOOL |  |  |  | X | X | X | X
Digital output state | 1141 | 4 | 301142 | 04 |  | CIO 208 no. 2 conf. status out | BOOL |  |  |  | X | X | X | X
Digital output state | 1141 | 5 | 301142 | 04 |  | CIO 208 no. 3 conf. status out | BOOL |  |  |  | X | X | X | X
Digital output state | 1141 | 6 | 301142 | 04 |  | CIO 308 no. 1 conf. status out | BOOL |  |  |  | X | X | X | X
Digital output state | 1141 | 7 | 301142 | 04 |  | CIO 308 no. 2 conf. status out | BOOL |  |  |  | X | X | X | X
Digital output state | 1141 | 8 | 301142 | 04 |  | CIO 308 no. 3 conf. status out | BOOL |  |  |  | X | X | X | X
Digital input state | 1142 | 0 | 301143 | 04 |  | Digital input 39 | BOOL |  |  |  | X | X | X | X
Digital input state | 1142 | 1 | 301143 | 04 |  | Digital input 40 | BOOL |  |  |  | X | X | X | X
Digital input state | 1142 | 2 | 301143 | 04 |  | Digital input 41 | BOOL |  |  |  | X | X | X | X
Digital input state | 1142 | 3 | 301143 | 04 |  | Digital input 42 | BOOL |  |  |  | X | X | X | X
Digital input state | 1142 | 4 | 301143 | 04 |  | Digital input 43 | BOOL |  |  |  | X | X | X | X
Digital input state | 1142 | 5 | 301143 | 04 |  | Digital input 44 | BOOL |  |  |  | X | X | X | X
Digital input state | 1142 | 6 | 301143 | 04 |  | Digital input 45 | BOOL |  |  |  | X | X | X | X
Digital input state | 1142 | 7 | 301143 | 04 |  | Digital input 46 | BOOL |  |  |  | X | X | X | X
Digital input state | 1142 | 9 | 301143 | 04 |  | Emergency stop input 4 | BOOL |  |  |  | X | X | X | X
Digital input state | 1142 | 10 | 301143 | 04 |  | Dplus input 7 | BOOL | [5 empty] | X | X
Digital input state | 1142 | 11 | 301143 | 04 |  | Digital input 47 | BOOL |  |  |  | X | X | X | X
Digital input state | 1142 | 12 | 301143 | 04 |  | Digital input 48 | BOOL |  |  |  | X | X | X | X
Digital input state | 1142 | 13 | 301143 | 04 |  | Digital input 49 | BOOL |  |  |  | X | X | X | X
Digital input state | 1142 | 14 | 301143 | 04 |  | Digital input 50 | BOOL |  |  |  | X | X | X | X
Digital input state | 1145 | 15 | 301146 | 04 |  | CIO 308 no. 2. Input 29 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 0 | 301151 | 04 |  | M-Logic Output evaluation Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 1 | 301151 | 04 |  | M-Logic Output evaluation Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 2 | 301151 | 04 |  | M-Logic Output evaluation Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 3 | 301151 | 04 |  | M-Logic Output evaluation Line 4 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 4 | 301151 | 04 |  | M-Logic Output evaluation Line 5 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 5 | 301151 | 04 |  | M-Logic Output evaluation Line 6 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 6 | 301151 | 04 |  | M-Logic Output evaluation Line 7 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 7 | 301151 | 04 |  | M-Logic Output evaluation Line 8 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 8 | 301151 | 04 |  | M-Logic Output evaluation Line 9 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 9 | 301151 | 04 |  | M-Logic Output evaluation Line 10 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 10 | 301151 | 04 |  | M-Logic Output evaluation Line 11 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 11 | 301151 | 04 |  | M-Logic Output evaluation Line 12 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 12 | 301151 | 04 |  | M-Logic Output evaluation Line 13 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 13 | 301151 | 04 |  | M-Logic Output evaluation Line 14 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 14 | 301151 | 04 |  | M-Logic Output evaluation Line 15 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1150 | 15 | 301151 | 04 |  | M-Logic Output evaluation Line 16 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 0 | 301152 | 04 |  | M-Logic Output evaluation Line 17 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 1 | 301152 | 04 |  | M-Logic Output evaluation Line 18 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 2 | 301152 | 04 |  | M-Logic Output evaluation Line 19 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 3 | 301152 | 04 |  | M-Logic Output evaluation Line 20 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 4 | 301152 | 04 |  | M-Logic Output evaluation Line 21 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 5 | 301152 | 04 |  | M-Logic Output evaluation Line 22 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 6 | 301152 | 04 |  | M-Logic Output evaluation Line 23 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 7 | 301152 | 04 |  | M-Logic Output evaluation Line 24 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 8 | 301152 | 04 |  | M-Logic Output evaluation Line 25 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 9 | 301152 | 04 |  | M-Logic Output evaluation Line 26 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 10 | 301152 | 04 |  | M-Logic Output evaluation Line 27 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 11 | 301152 | 04 |  | M-Logic Output evaluation Line 28 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 12 | 301152 | 04 |  | M-Logic Output evaluation Line 29 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 13 | 301152 | 04 |  | M-Logic Output evaluation Line 30 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 14 | 301152 | 04 |  | M-Logic Output evaluation Line 31 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1151 | 15 | 301152 | 04 |  | M-Logic Output evaluation Line 32 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 0 | 301153 | 04 |  | M-Logic Output evaluation Line 33 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 1 | 301153 | 04 |  | M-Logic Output evaluation Line 34 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 2 | 301153 | 04 |  | M-Logic Output evaluation Line 35 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 3 | 301153 | 04 |  | M-Logic Output evaluation Line 36 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 4 | 301153 | 04 |  | M-Logic Output evaluation Line 37 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 5 | 301153 | 04 |  | M-Logic Output evaluation Line 38 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 6 | 301153 | 04 |  | M-Logic Output evaluation Line 39 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 7 | 301153 | 04 |  | M-Logic Output evaluation Line 40 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 8 | 301153 | 04 |  | M-Logic Output evaluation Line 41 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 9 | 301153 | 04 |  | M-Logic Output evaluation Line 42 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 10 | 301153 | 04 |  | M-Logic Output evaluation Line 43 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 11 | 301153 | 04 |  | M-Logic Output evaluation Line 44 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 12 | 301153 | 04 |  | M-Logic Output evaluation Line 45 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 13 | 301153 | 04 |  | M-Logic Output evaluation Line 46 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 14 | 301153 | 04 |  | M-Logic Output evaluation Line 47 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1152 | 15 | 301153 | 04 |  | M-Logic Output evaluation Line 48 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 0 | 301154 | 04 |  | M-Logic Output evaluation Line 49 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 1 | 301154 | 04 |  | M-Logic Output evaluation Line 50 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 2 | 301154 | 04 |  | M-Logic Output evaluation Line 51 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 3 | 301154 | 04 |  | M-Logic Output evaluation Line 52 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 4 | 301154 | 04 |  | M-Logic Output evaluation Line 53 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 5 | 301154 | 04 |  | M-Logic Output evaluation Line 54 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 6 | 301154 | 04 |  | M-Logic Output evaluation Line 55 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 7 | 301154 | 04 |  | M-Logic Output evaluation Line 56 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 8 | 301154 | 04 |  | M-Logic Output evaluation Line 57 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 9 | 301154 | 04 |  | M-Logic Output evaluation Line 58 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 10 | 301154 | 04 |  | M-Logic Output evaluation Line 59 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 11 | 301154 | 04 |  | M-Logic Output evaluation Line 60 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 12 | 301154 | 04 |  | M-Logic Output evaluation Line 61 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 13 | 301154 | 04 |  | M-Logic Output evaluation Line 62 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 14 | 301154 | 04 |  | M-Logic Output evaluation Line 63 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1153 | 15 | 301154 | 04 |  | M-Logic Output evaluation Line 64 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 0 | 301155 | 04 |  | M-Logic Output evaluation Line 65 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 1 | 301155 | 04 |  | M-Logic Output evaluation Line 66 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 2 | 301155 | 04 |  | M-Logic Output evaluation Line 67 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 3 | 301155 | 04 |  | M-Logic Output evaluation Line 68 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 4 | 301155 | 04 |  | M-Logic Output evaluation Line 69 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 5 | 301155 | 04 |  | M-Logic Output evaluation Line 70 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 6 | 301155 | 04 |  | M-Logic Output evaluation Line 71 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 7 | 301155 | 04 |  | M-Logic Output evaluation Line 72 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 8 | 301155 | 04 |  | M-Logic Output evaluation Line 73 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 9 | 301155 | 04 |  | M-Logic Output evaluation Line 74 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 10 | 301155 | 04 |  | M-Logic Output evaluation Line 75 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 11 | 301155 | 04 |  | M-Logic Output evaluation Line 76 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 12 | 301155 | 04 |  | M-Logic Output evaluation Line 77 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 13 | 301155 | 04 |  | M-Logic Output evaluation Line 78 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 14 | 301155 | 04 |  | M-Logic Output evaluation Line 79 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1154 | 15 | 301155 | 04 |  | M-Logic Output evaluation Line 80 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1155 | 8 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 1 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1155 | 9 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 1 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1155 | 10 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 1 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1155 | 11 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 2 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1155 | 12 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 2 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1155 | 13 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 2 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1155 | 14 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 3 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1155 | 15 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 3 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 0 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 3 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 1 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 4 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 2 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 4 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 3 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 4 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 4 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 5 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 5 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 5 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 6 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 5 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 7 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 6 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 8 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 6 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 9 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 6 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 10 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 7 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 11 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 7 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 12 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 7 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 13 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 8 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 14 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 8 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1156 | 15 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 8 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 0 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 9 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 1 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 9 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 2 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 9 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 3 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 10 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 4 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 10 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 5 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 10 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 6 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 11 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 7 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 11 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 8 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 11 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 9 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 12 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 10 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 12 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 11 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 12 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 12 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 13 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 13 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 13 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 14 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 13 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1157 | 15 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 14 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 0 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 14 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 1 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 14 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 2 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 15 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 3 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 15 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 4 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 15 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 5 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 16 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 6 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 16 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 7 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 16 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 8 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 1 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 9 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 1 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 10 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 1 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 11 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 2 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 12 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 2 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 13 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 2 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 14 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 3 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1158 | 15 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 3 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 0 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 3 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 1 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 4 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 2 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 4 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 3 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 4 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 4 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 5 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 5 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 5 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 6 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 5 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 7 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 6 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 8 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 6 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 9 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 6 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 10 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 7 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 11 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 7 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 12 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 7 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 13 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 8 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 14 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 8 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1159 | 15 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 8 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 0 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 9 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 1 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 9 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 2 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 9 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 3 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 10 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 4 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 10 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 5 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 10 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 6 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 11 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 7 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 11 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 8 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 11 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 9 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 12 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 10 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 12 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 11 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 12 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 12 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 13 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 13 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 13 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 14 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 13 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1160 | 15 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 14 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1161 | 0 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 14 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1161 | 1 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 14 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1161 | 2 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 15 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1161 | 3 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 15 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1161 | 4 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 15 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1161 | 5 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 16 Line 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1161 | 6 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 16 Line 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1161 | 7 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 16 Line 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 0 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 1 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 2 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 3 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 4 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 4 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 5 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 5 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 6 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 6 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 7 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 7 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 8 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 8 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 9 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 10 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 11 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 4 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 12 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 5 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 13 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 6 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 14 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 7 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1171 | 15 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 8 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1173 | 8 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_1 Buzzer 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1173 | 9 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_1 Buzzer 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1173 | 10 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_1 Buzzer 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1173 | 11 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_2 Buzzer 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1173 | 12 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_2 Buzzer 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1173 | 13 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_2 Buzzer 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1174 | 7 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_1 Relay 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1174 | 8 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_1 Relay 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1174 | 9 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_1 Relay 3 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1174 | 10 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_2 Relay 1 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1174 | 11 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_2 Relay 2 | BOOL |  |  |  | X | X | X | X
M-Logic state | 1174 | 12 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_2 Relay 3 | BOOL |  |  |  | X | X | X | X
DAVR measurement | 1214 |  | 301215 | 04 |  | DVC 550 Pt100 #1 | INT16s | AB | 0 |  |  |  | X
DAVR measurement | 1215 |  | 301216 | 04 |  | DVC 550 Pt100 #2 | INT16s | AB | 0 |  |  |  | X
DAVR measurement | 1216 |  | 301217 | 04 |  | DVC 550 Pt100 #3 | INT16s | AB | 0 |  |  |  | X
DAVR measurement | 1217 |  | 301218 | 04 |  | DVC 550 Pt100 #4 | INT16s | AB | 0 |  |  |  | X
DAVR measurement | 1218 |  | 301219 | 04 |  | DVC 550 Pt100 #5 | INT16s | AB | 0 |  |  |  | X
EIC measurement | 1220 | 0 | 301221 | 04 |  | FPT Stage V: Fuel in Oil Detection | BOOL | [5 empty] | X | X
EIC measurement | 1220 | 1 | 301221 | 04 |  | FPT Stage V: Water in Fuel Detection | BOOL | [5 empty] | X | X
EIC measurement | 1220 | 2 | 301221 | 04 |  | FPT Stage V: Engine Protection | BOOL | [5 empty] | X | X
EIC measurement | 1220 | 3 | 301221 | 04 |  | FPT Stage V: Turbo Charger Protection | BOOL | [5 empty] | X | X
EIC measurement | 1220 | 4 | 301221 | 04 |  | FPT Stage V: Scr Injector Overheat Protection | BOOL | [5 empty] | X | X
EIC measurement | 1220 | 5 | 301221 | 04 |  | FPT Stage V: Urea Thawing Mode Active | BOOL | [5 empty] | X | X
EIC measurement | 1220 | 6 | 301221 | 04 |  | FPT Stage V: Engine Over Speed Warning | BOOL | [5 empty] | X | X
EIC measurement | 1220 | 7 | 301221 | 04 |  | FPT Stage V: Exhaust Over Heat Condition | BOOL | [5 empty] | X | X
EIC measurement | 1220 | 8 | 301221 | 04 |  | FPT Stage V: Clogged DPF | BOOL | [5 empty] | X | X
EIC measurement | 1220 | 9 | 301221 | 04 |  | FPT Stage V: Smoke Limitation | BOOL | [5 empty] | X | X
EIC measurement | 1220 | 10 | 301221 | 04 |  | FPT Stage V: Engine Oil Over Temperature | BOOL | [5 empty] | X | X
EIC measurement | 1220 | 11 | 301221 | 04 |  | FPT Stage V: Nh3 Slip Detection | BOOL | [5 empty] | X | X
EIC measurement | 1220 | 12 | 301221 | 04 |  | FPT Stage V: Bad Urea Quality | BOOL | [5 empty] | X | X
EIC measurement | 1220 | 13 | 301221 | 04 |  | FPT Stage V: Low Catalyst Efficiency | BOOL | [5 empty] | X | X
EIC measurement | 1221 |  | 301222 | 04 |  | FPT Stage V: DEF Technical Failure | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1222 |  | 301223 | 04 |  | FPT Stage V: DEF Quality | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1223 |  | 301224 | 04 |  | FPT Stage V: DEF Level | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1224 |  | 301225 | 04 |  | FPT Stage V: Fuel Filter Heater Status | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1225 |  | 301226 | 04 |  | FPT Stage V: Low Idle Increase Desired | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1226 |  | 301227 | 04 |  | Scania: DPF regeneration countdown timer | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1227 |  | 301228 | 04 |  | Scania: Urea level inducement state | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1228 |  | 301229 | 04 |  | Scania: Emission-OBD inducement state | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1229 |  | 301230 | 04 |  | Scania: Emission-OBD inducement failure reason | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1230 |  | 301231 | 04 |  | John Deere STAGE V: Engine Diesel Particulate Filter Regeneration State | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1231 |  | 301232 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Ash Load Percent | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1232 |  | 301233 | 04 |  | Aftertreatment Diesel Particulate Filter Status | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1233 |  | 301234 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Concentration | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1234 |  | 301235 | 04 |  | Engine Requested Fuel Valve 1 Position | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1235 |  | 301236 | 04 |  | Engine Oil Priming State (SPN 3551) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1236 |  | 301237 | 04 |  | Fuel Pump Primer Status (SPN 4083) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1237 |  | 301238 | 04 |  | Sensor supply voltage 1 (SPN 3509) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1238 |  | 301239 | 04 |  | Sensor supply voltage 2 (SPN 3510) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1239 |  | 301240 | 04 |  | Accelerator Pedal Position 2 (SPN 29) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1240 |  | 301241 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Temporary System Lockout (SPN 3714) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1241 |  | 301242 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Permanent System Lockout (SPN 3715) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1242 |  | 301243 | 04 |  | Aftertreatment Ambient Air Temperature (SPN 7441) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1243 |  | 301244 | 04 |  | Aftertreatment Thermal Management Status (SPN 7332) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1244 |  | 301245 | 04 |  | Aftertreatment Engine Speed Increase request (SPN 7502) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1245 |  | 301246 | 04 |  | Aftertreatment Engine Load Request (SPN 7503) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1246 |  | 301247 | 04 |  | Feedback Engine Fueling State (SPN 5794) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1247 |  | 301248 | 04 |  | Engine Fueling Inhibit Allowed (SPN 5795) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1248 |  | 301249 | 04 |  | Engine controlled shutdown request (SPN 3606) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1249 |  | 301250 | 04 |  | Engine oil pre-heated state (SPN 3552) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1250 |  | 301251 | 04 |  | Engine ventilation state (SPN 3554) | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1251 |  | 301252 | 04 |  | Rail pressure (Jichai) | INT16s | AB | 0 |  |  |  | X | X
M-Logic state | 1252 |  | 301253 | 04 |  | Oneshot output 1-16 | INT16s | AB | 0 |  | X | X | X | X
Alarm | 1360 | 0 | 301361 | 04 | 3660 | M-Logic alarm 10 | BOOL |  |  |  | X | X | X | X
Alarm | 1360 | 1 | 301361 | 04 | 3670 | M-Logic alarm 11 | BOOL |  |  |  | X | X | X | X
Alarm | 1360 | 2 | 301361 | 04 | 3680 | M-Logic alarm 12 | BOOL |  |  |  | X | X | X | X
Alarm | 1360 | 3 | 301361 | 04 | 3690 | M-Logic alarm 13 | BOOL |  |  |  | X | X | X | X
Alarm | 1360 | 4 | 301361 | 04 | 3700 | M-Logic alarm 14 | BOOL |  |  |  | X | X | X | X
EIC alarm | 1370 |  | 301371 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #1 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1371 |  | 301372 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #2 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1372 |  | 301373 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #3 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1373 |  | 301374 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #4 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1374 |  | 301375 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #5 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1375 |  | 301376 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #6 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1376 |  | 301377 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #7 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1377 |  | 301378 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #8 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1378 |  | 301379 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #9 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1379 |  | 301380 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #10 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1380 |  | 301381 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #1 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1381 |  | 301382 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #2 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1382 |  | 301383 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #3 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1383 |  | 301384 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #4 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1384 |  | 301385 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #5 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1385 |  | 301386 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #6 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1386 |  | 301387 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #7 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1387 |  | 301388 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #8 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1388 |  | 301389 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #9 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1389 |  | 301390 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #10 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1402 |  | 301403 | 04 |  | Active fail mode identifier (DM1/FMI): #1 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1403 |  | 301404 | 04 |  | Active fail mode identifier (DM1/FMI): #2 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1404 |  | 301405 | 04 |  | Active fail mode identifier (DM1/FMI): #3 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1405 |  | 301406 | 04 |  | Active fail mode identifier (DM1/FMI): #4 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1406 |  | 301407 | 04 |  | Active fail mode identifier (DM1/FMI): #5 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1407 |  | 301408 | 04 |  | Active fail mode identifier (DM1/FMI): #6 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1408 |  | 301409 | 04 |  | Active fail mode identifier (DM1/FMI): #7 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1409 |  | 301410 | 04 |  | Active fail mode identifier (DM1/FMI): #8 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1410 |  | 301411 | 04 |  | Active fail mode identifier (DM1/FMI): #9 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1411 |  | 301412 | 04 |  | Active fail mode identifier (DM1/FMI): #10 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1418 |  | 301419 | 04 |  | Active occurrence counter (DM1/OC): #1 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1419 |  | 301420 | 04 |  | Active occurrence counter (DM1/OC): #2 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1420 |  | 301421 | 04 |  | Active occurrence counter (DM1/OC): #3 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1421 |  | 301422 | 04 |  | Active occurrence counter (DM1/OC): #4 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1422 |  | 301423 | 04 |  | Active occurrence counter (DM1/OC): #5 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1423 |  | 301424 | 04 |  | Active occurrence counter (DM1/OC): #6 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1424 |  | 301425 | 04 |  | Active occurrence counter (DM1/OC): #7 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1425 |  | 301426 | 04 |  | Active occurrence counter (DM1/OC): #8 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1426 |  | 301427 | 04 |  | Active occurrence counter (DM1/OC): #9 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1427 |  | 301428 | 04 |  | Active occurrence counter (DM1/OC): #10 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1434 |  | 301435 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #1 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1435 |  | 301436 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #2 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1436 |  | 301437 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #3 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1437 |  | 301438 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #4 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1438 |  | 301439 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #5 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1439 |  | 301440 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #6 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1440 |  | 301441 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #7 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1441 |  | 301442 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #8 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1442 |  | 301443 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #9 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1443 |  | 301444 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #10 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1444 |  | 301445 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #1 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1445 |  | 301446 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #2 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1446 |  | 301447 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #3 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1447 |  | 301448 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #4 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1448 |  | 301449 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #5 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1449 |  | 301450 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #6 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1450 |  | 301451 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #7 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1451 |  | 301452 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #8 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1452 |  | 301453 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #9 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1453 |  | 301454 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #10 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1466 |  | 301467 | 04 |  | Active fail mode identifier (DM2/FMI): #1 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1467 |  | 301468 | 04 |  | Active fail mode identifier (DM2/FMI): #2 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1468 |  | 301469 | 04 |  | Active fail mode identifier (DM2/FMI): #3 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1469 |  | 301470 | 04 |  | Active fail mode identifier (DM2/FMI): #4 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1470 |  | 301471 | 04 |  | Active fail mode identifier (DM2/FMI): #5 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1471 |  | 301472 | 04 |  | Active fail mode identifier (DM2/FMI): #6 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1472 |  | 301473 | 04 |  | Active fail mode identifier (DM2/FMI): #7 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1473 |  | 301474 | 04 |  | Active fail mode identifier (DM2/FMI): #8 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1474 |  | 301475 | 04 |  | Active fail mode identifier (DM2/FMI): #9 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1475 |  | 301476 | 04 |  | Active fail mode identifier (DM2/FMI): #10 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1482 |  | 301483 | 04 |  | Active occurrence counter (DM2/OC): #1 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1483 |  | 301484 | 04 |  | Active occurrence counter (DM2/OC): #2 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1484 |  | 301485 | 04 |  | Active occurrence counter (DM2/OC): #3 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1485 |  | 301486 | 04 |  | Active occurrence counter (DM2/OC): #4 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1486 |  | 301487 | 04 |  | Active occurrence counter (DM2/OC): #5 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1487 |  | 301488 | 04 |  | Active occurrence counter (DM2/OC): #6 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1488 |  | 301489 | 04 |  | Active occurrence counter (DM2/OC): #7 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1489 |  | 301490 | 04 |  | Active occurrence counter (DM2/OC): #8 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1490 |  | 301491 | 04 |  | Active occurrence counter (DM2/OC): #9 | INT16s | AB | 0 |  |  |  | X | X
EIC alarm | 1491 |  | 301492 | 04 |  | Active occurrence counter (DM2/OC): #10 | INT16s | AB | 0 |  |  |  | X | X
PM AC measurement | 1500 |  | 301501 | 04 |  | Total power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1501 |  | 301502 | 04 |  | Available power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1502 |  | 301503 | 04 |  | Total nominal power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1503 |  | 301504 | 04 |  | Total genset power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1504 |  | 301505 | 04 |  | Total reactive power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1505 |  | 301506 | 04 |  | Number of gensets in application | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1506 |  | 301507 | 04 |  | Plant type | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1507 |  | 301508 | 04 |  | Load-dependent stop, active set-point | INT16s | AB | 0 |  |  |  | X
PM AC measurement | 1508 |  | 301509 | 04 |  | Load-dependent start, active set-point | INT16s | AB | 0 |  |  |  | X
PM AC measurement | 1510 |  | 301511 | 04 |  | Nominal power ID 1 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1511 |  | 301512 | 04 |  | Nominal power ID 2 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1526 |  | 301527 | 04 |  | Active Power ID 1 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1527 |  | 301528 | 04 |  | Active Power ID 2 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1542 |  | 301543 | 04 |  | Reactive Power ID 1 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1543 |  | 301544 | 04 |  | Reactive Power ID 2 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1558 |  | 301559 | 04 |  | Priority of genset | INT16s | AB | 0 |  |  |  | X
PM AC measurement | 1584 |  | 301585 | 04 |  | Active Power ID 32 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1600 |  | 301601 | 04 |  | Reactive Power ID 32 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1601 |  | 301602 | 04 |  | Active Power ID 33 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1602 |  | 301603 | 04 |  | Active Power ID 34 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1609 |  | 301610 | 04 |  | Reactive Power ID 33 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1610 |  | 301611 | 04 |  | Reactive Power ID 34 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1632 |  | 301633 | 04 |  | Plant mode mains 32 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1648 |  | 301649 | 04 |  | Bus power mains 32 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1668 |  | 301669 | 04 |  | Nominal power ID 32 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1696 |  | 301697 | 04 |  | Total PV active power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1697 |  | 301698 | 04 |  | Total PV reactive power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1698 |  | 301699 | 04 |  | Total Battery active power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1699 |  | 301700 | 04 |  | Total Battery reactive power | INT16s | AB | 0 |  | X | X | X
PM Plant logic state | 1700 | 2 | 301701 | 04 |  | Any SCB pos. ON | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 3 | 301701 | 04 |  | All SCB pos. OFF | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 6 | 301701 | 04 |  | Any GB pos. ON | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 7 | 301701 | 04 |  | All GB pos. OFF | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 10 | 301701 | 04 |  | Any BTB pos. ON | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 11 | 301701 | 04 |  | Any BTB pos. OFF | BOOL |  |  |  | X | X | X
Counter | 1842 |  | 301843 | 04 |  | BB Export, active energy counter, total | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1842 |  | 301843 | 04 |  | Bus B Export, active energy counter, total | INT32s | ABCD | 0 | kWh | X
Counter | 1844 |  | 301845 | 04 |  | BB Export, active energy counter, month | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1844 |  | 301845 | 04 |  | Bus B Export, active energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 1846 |  | 301847 | 04 |  | BB Export, active energy counter, week | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1846 |  | 301847 | 04 |  | Bus B Export, active energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 1848 |  | 301849 | 04 |  | BB Export, active energy counter, day | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1848 |  | 301849 | 04 |  | Bus B Export, active energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 1850 |  | 301851 | 04 |  | BB Export, reactive energy counter, total | INT32s | ABCD | 0 | kvarh |  |  | X
Counter | 1850 |  | 301851 | 04 |  | Bus B Export, reactive energy counter, total | INT32s | ABCD | 0 | kvarh | X
Counter | 1852 |  | 301853 | 04 |  | BB Export, reactive energy counter, month | INT32s | ABCD | 0 | kvarh |  |  | X
Counter | 1852 |  | 301853 | 04 |  | Bus B Export, reactive energy counter, month | INT32s | ABCD | 0 | kvarh | X
Counter | 1854 |  | 301855 | 04 |  | BB Export, reactive energy counter, week | INT32s | ABCD | 0 | kvarh |  |  | X
Counter | 1854 |  | 301855 | 04 |  | Bus B Export, reactive energy counter, week | INT32s | ABCD | 0 | kvarh | X
Counter | 1856 |  | 301857 | 04 |  | BB Export, reactive energy counter, day | INT32s | ABCD | 0 | kvarh |  |  | X
Counter | 1856 |  | 301857 | 04 |  | Bus B Export, reactive energy counter, day | INT32s | ABCD | 0 | kvarh | X
Counter | 1858 |  | 301859 | 04 |  | BB Import, active energy counter, total | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1858 |  | 301859 | 04 |  | Bus B Import, active energy counter, total | INT32s | ABCD | 0 | kWh | X
Counter | 1860 |  | 301861 | 04 |  | BB Import, active energy counter, month | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1860 |  | 301861 | 04 |  | Bus B Import, active energy counter, month | INT32s | ABCD | 0 | kWh | X
Counter | 1862 |  | 301863 | 04 |  | BB Import, active energy counter, week | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1862 |  | 301863 | 04 |  | Bus B Import, active energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 1864 |  | 301865 | 04 |  | BB Import, active energy counter, day | INT32s | ABCD | 0 | kWh |  |  | X
Counter | 1864 |  | 301865 | 04 |  | Bus B Import, active energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 1866 |  | 301867 | 04 |  | BB Import, reactive energy counter, total | INT32s | ABCD | 0 | kvarh |  |  | X
Counter | 1866 |  | 301867 | 04 |  | Bus B Import, reactive energy counter, total | INT32s | ABCD | 0 | kvarh | X
Counter | 1868 |  | 301869 | 04 |  | BB Import, reactive energy counter, month | INT32s | ABCD | 0 | kvarh |  |  | X
Counter | 1868 |  | 301869 | 04 |  | Bus B Import, reactive energy counter, month | INT32s | ABCD | 0 | kvarh | X
Counter | 1870 |  | 301871 | 04 |  | BB Import, reactive energy counter, week | INT32s | ABCD | 0 | kvarh |  |  | X
Counter | 1870 |  | 301871 | 04 |  | Bus B Import, reactive energy counter, week | INT32s | ABCD | 0 | kvarh | X
Counter | 1872 |  | 301873 | 04 |  | BB Import, reactive energy counter, day | INT32s | ABCD | 0 | kvarh |  |  | X
Counter | 1872 |  | 301873 | 04 |  | Bus B Import, reactive energy counter, day | INT32s | ABCD | 0 | kvarh | X
DC measurement | 1900 |  | 301901 | 04 |  | General purpose PID 1 prioritized input | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 1901 |  | 301902 | 04 |  | General purpose PID 2 prioritized input | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 1902 |  | 301903 | 04 |  | General purpose PID 3 prioritized input | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 1903 |  | 301904 | 04 |  | General purpose PID 4 prioritized input | INT16s | AB | 0 |  | X | X | X | X
PM AC measurement | 1917 |  | 301918 | 04 |  | Cos phi from PMS ID 1 | INT16s | AB | 0 |  |  |  | X
PM AC measurement | 1918 |  | 301919 | 04 |  | Cos phi from PMS ID 2 | INT16s | AB | 0 |  |  |  | X
PM AC measurement | 1948 |  | 301949 | 04 |  | Cos phi from PMS ID 32 | INT16s | AB | 0 |  |  | X
PM AC measurement | 1957 |  | 301958 | 04 |  | Apparent power ID 1 | INT16s | AB | 0 |  |  |  | X
PM AC measurement | 1958 |  | 301959 | 04 |  | Apparent power ID 2 | INT16s | AB | 0 |  |  |  | X
PM AC measurement | 1988 |  | 301989 | 04 |  | Apparent power ID 32 | INT16s | AB | 0 |  |  | X
EIC measurements value | 26000 |  | 326001 | 04 |  | Engine Speed (SPN 190) | INT16u | AB | 0 | rpm |  |  | X | X
EIC measurements value | 26001 |  | 326002 | 04 |  | Engine Coolant Temperature (SPN 110) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26002 |  | 326003 | 04 |  | Engine Oil Pressure (SPN 100) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26003 |  | 326004 | 04 |  | Active Diagnostic Trouble Code Count (SPN 1218) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26004 |  | 326005 | 04 |  | Engine Oil Temperature 1 (SPN 175) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26005 |  | 326006 | 04 |  | Engine Fuel 1 Temperature 1 (SPN 174) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26006 |  | 326007 | 04 |  | Engine Intake Manifold #1 Pressure (SPN 102) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26007 |  | 326008 | 04 |  | Engine Intake 1 Air Temperature (SPN 172) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26008 |  | 326009 | 04 |  | Engine Coolant Level 1 (SPN 111) | INT16u | AB | 1 | perc |  |  | X | X
EIC measurements value | 26009 |  | 326010 | 04 |  | Engine Fuel Rate (SPN 183) | INT16u | AB | 1 | L/h |  |  | X | X
EIC measurements value | 26010 |  | 326011 | 04 |  | Charge air pressure (MDEC) | INT16u | AB | 0 | bar/psi |  |  | X | X
EIC measurements value | 26011 |  | 326012 | 04 |  | Engine Intake Manifold 1 Temperature (SPN 105) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26012 |  | 326013 | 04 |  | Driver's Demand Engine, Percent Torque (SPN 512) | INT16u | AB | 0 | perc |  |  | X | X
EIC measurements value | 26013 |  | 326014 | 04 |  | Actual Engine, Percent Torque (SPN 513) | INT16u | AB | 0 | perc |  |  | X | X
EIC measurements value | 26014 |  | 326015 | 04 |  | Accelerator Pedal Position 1 (SPN 91) | INT16u | AB | 0 | perc |  |  | X | X
EIC measurements value | 26015 |  | 326016 | 04 |  | Engine Percent Load At Current Speed (SPN 92) | INT16u | AB | 0 | perc |  |  | X | X
EIC measurements value | 26016 |  | 326017 | 04 |  | Engine Intake Air Pressure (SPN 106) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26017 |  | 326018 | 04 |  | Engine Exhaust Temperature (SPN 173) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26018 |  | 326019 | 04 |  | Engine Total Hours of Operation (SPN 247) | INT32u | ABCD | 0 | h |  |  | X | X
EIC measurements value | 26020 |  | 326021 | 04 |  | Engine Oil Filter Differential Pressure (SPN 99) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26021 |  | 326022 | 04 |  | Key Switch Battery Potential (SPN 158) | INT16u | AB | 1 | V |  |  | X | X
EIC measurements value | 26022 |  | 326023 | 04 |  | Engine Fuel Delivery Pressure (SPN 94) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26023 |  | 326024 | 04 |  | Engine Oil Level (SPN 98) | INT16u | AB | 1 | perc |  |  | X | X
EIC measurements value | 26024 |  | 326025 | 04 |  | Engine Crankcase Pressure 1 (SPN 101) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26025 |  | 326026 | 04 |  | Engine Coolant Pressure 1 (SPN 109) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26026 |  | 326027 | 04 |  | Water In Fuel Indicator 1 (SPN 97) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26027 |  | 326028 | 04 |  | Engine Turbocharger 1 Oil Temperature (SPN 176) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26028 |  | 326029 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Intake Pressure (SPN 81) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26029 |  | 326030 | 04 |  | Engine Air Filter 1 Differential Pressure (SPN 107) | INT16u | AB | 3 | bar/psi |  |  | X | X
EIC measurements value | 26030 |  | 326031 | 04 |  | Engine Coolant Filter Differential Pressure (SPN 112) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26031 |  | 326032 | 04 |  | Barometric Pressure (SPN 108) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26032 |  | 326033 | 04 |  | Ambient Air Temperature (SPN 171) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26033 | 0 | 326034 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser Pressure (SPN 6876) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26033 | 1 | 326034 | 04 |  | Isuzu Engine Derate Lamp | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26033 |  | 326034 | 04 |  | Engine Exhaust Manifold Bank 2 Temperature 1 (SPN 2433) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26034 | 6 | 326035 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Intermediate Temperature Preliminary FMI (SPN 3254) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26034 | 7 | 326035 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Outlet Pressure (SPN 3610) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26034 | 8 | 326035 | 04 |  | Aftertreatment 2 SCR Differential Pressure Preliminary FMI (SPN 4412) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26034 | 9 | 326035 | 04 |  | Engine Friction Percent Torque, Point 7 (SPN 5477) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26034 | 10 | 326035 | 04 |  | Engine Friction Percent Torque, Point 6 (SPN 5476) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26034 | 11 | 326035 | 04 |  | Engine Friction Percent Torque, Point 5 (SPN 5475) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26034 | 12 | 326035 | 04 |  | Engine Friction Percent Torque, Point 4 (SPN 5474) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26034 | 13 | 326035 | 04 |  | Engine Friction Percent Torque, Point 3 (SPN 5473) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26034 | 14 | 326035 | 04 |  | Engine Friction Percent Torque, Point 2 (SPN 5472) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26034 | 15 | 326035 | 04 |  | Engine Friction Percent Torque At Idle, Point 1 (SPN 5471) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26034 |  | 326035 | 04 |  | Engine Exhaust Manifold Bank 1 Temperature 1 (SPN 2434) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26035 | 13 | 326036 | 04 |  | Engine Total Fuel Consumption Liquid (SPN 5054) RAW | INT32u | AB |  |  |  |  | X | X
EIC measurements value | 26035 |  | 326036 | 04 |  | Temp. Winding 1 (ADEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26036 |  | 326037 | 04 |  | Temp. Winding 2 (ADEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26037 |  | 326038 | 04 |  | Temp. Winding 3 (ADEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26038 |  | 326039 | 04 |  | Auxiliary_Analog_Info (ADEC) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26039 |  | 326040 | 04 |  | Auxiliary_Analog_Info (ADEC) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26040 |  | 326041 | 04 |  | Engine Turbocharger 1 Compressor Outlet Temperature (ADEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26041 |  | 326042 | 04 |  | Engine Intercooler Temperature (SPN 52) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26042 |  | 326043 | 04 |  | Engine Trip Fuel (SPN 182) | INT32u | ABCD | 0 | L |  |  | X | X
EIC measurements value | 26044 |  | 326045 | 04 |  | Engine Total Fuel Used (SPN 250) | INT32u | ABCD | 0 | kL |  |  | X | X
EIC measurements value | 26046 |  | 326047 | 04 |  | Trip Fuel (Gaseous) (SPN 1039) | INT32u | ABCD | 0 | kg |  |  | X | X
EIC measurements value | 26048 |  | 326049 | 04 |  | Total Fuel Used (Gaseous) (SPN 1040) | INT32u | ABCD | 1 | ton |  |  | X | X
EIC measurements value | 26050 |  | 326051 | 04 |  | Trip Average Fuel Rate (SPN 1029) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26051 |  | 326052 | 04 |  | Engine Rated Power (SPN 166) | INT16u | AB | 0 | kWm |  |  | X | X
EIC measurements value | 26052 |  | 326053 | 04 |  | Engine power (ADEC) | INT16u | AB | 0 | kW |  |  | X | X
EIC measurements value | 26053 |  | 326054 | 04 |  | Engine Intake Manifold #1 Absolute Pressure (SPN 3563) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26054 |  | 326055 | 04 |  | Diesel Particulate Filter Lamp Command (SPN 3697) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26055 |  | 326056 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Inhibit Switch (SPN 3703) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26056 |  | 326057 | 04 |  | Aftertreatment Diesel Particulate Filter Active Regeneration Status (SPN 3700) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26057 |  | 326058 | 04 |  | Aftertreatment Diesel Particulate Filter Status (SPN 3701) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26058 |  | 326059 | 04 |  | Exhaust System High Temperature Lamp Command (SPN 3698) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26059 |  | 326060 | 04 |  | Engine Air Filter 2 Differential Pressure (SPN 2809) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26060 |  | 326061 | 04 |  | Engine Fuel Supply Pump Intake Absolute Pressure (SPN 1381) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26061 |  | 326062 | 04 |  | Engine Fuel Filter (suction side) Differential Pressure (SPN 1382) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26062 |  | 326063 | 04 |  | Engine Fuel Filter Differential Pressure (SPN 95) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26063 |  | 326064 | 04 |  | Speed demand Source (MDEC) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26064 |  | 326065 | 04 |  | P-Lube Oil Limit LO (MDEC) | INT16u | AB | 0 | bar/psi |  |  | X | X
EIC measurements value | 26065 |  | 326066 | 04 |  | P-Lube Oil Limit LOLO (MDEC) | INT16u | AB | 0 | bar/psi |  |  | X | X
EIC measurements value | 26066 |  | 326067 | 04 |  | P-Fuel (MDEC) | INT16u | AB | 0 | bar/psi |  |  | X | X
EIC measurements value | 26067 |  | 326068 | 04 |  | T-Coolant Limit HI (MDEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26068 |  | 326069 | 04 |  | T-Coolant Limit HIHI (MDEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26069 |  | 326070 | 04 |  | T-Coolant Intercooler (MDEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26070 |  | 326071 | 04 |  | Engine ECU Temperature (SPN 1136) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26071 |  | 326072 | 04 |  | Actual Droop (MDEC) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26072 |  | 326073 | 04 |  | Injection Quantity Act.DBR % (MDEC) | INT16u | AB | 0 | perc |  |  | X | X
EIC measurements value | 26073 |  | 326074 | 04 |  | Engine Speed Camshaft (MDEC) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26074 |  | 326075 | 04 |  | T-Lube Oil Limit HI (MDEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26075 |  | 326076 | 04 |  | T-Lube Oil Limit HIHI (MDEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26076 |  | 326077 | 04 |  | Feedback Speed Demand analog (MDEC) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26077 |  | 326078 | 04 |  | Stop signal active (MDEC) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26078 |  | 326079 | 04 |  | Exhaust Port Temperature 01 (SPN 1137) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26079 |  | 326080 | 04 |  | Exhaust Port Temperature 02 (SPN 1138) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26080 |  | 326081 | 04 |  | Exhaust Port Temperature 03 (SPN 1139) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26081 |  | 326082 | 04 |  | Exhaust Port Temperature 04 (SPN 1140) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26082 |  | 326083 | 04 |  | Exhaust Port Temperature 05 (SPN 1141) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26083 |  | 326084 | 04 |  | Exhaust Port Temperature 06 (SPN 1142) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26084 |  | 326085 | 04 |  | Exhaust Port Temperature 07 (SPN 1143) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26085 |  | 326086 | 04 |  | Exhaust Port Temperature 08 (SPN 1144) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26086 |  | 326087 | 04 |  | Exhaust Port Temperature 09 (SPN 1145) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26087 |  | 326088 | 04 |  | Exhaust Port Temperature 10 (SPN 1146) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26088 |  | 326089 | 04 |  | Exhaust Port Temperature 11 (SPN 1147) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26089 |  | 326090 | 04 |  | Exhaust Port Temperature 12 (SPN 1148) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26090 |  | 326091 | 04 |  | Exhaust Port Temperature 13 (SPN 1149) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26091 |  | 326092 | 04 |  | Exhaust Port Temperature 14 (SPN 1150) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26092 |  | 326093 | 04 |  | Exhaust Port Temperature 15 (SPN 1151) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26093 |  | 326094 | 04 |  | Exhaust Port Temperature 16 (SPN 1152) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26094 |  | 326095 | 04 |  | Engine Filtered Fuel Delivery Pressure (SPN 5579) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26095 |  | 326096 | 04 |  | Engine Coolant Temperature 2 (SPN 4076) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26096 |  | 326097 | 04 |  | Engine Coolant Temperature 3 (SPN 6209) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26097 |  | 326098 | 04 |  | Engine Coolant Pump Outlet Temperature (SPN 4193) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26098 |  | 326099 | 04 |  | Engine Auxiliary Coolant Temperature (SPN 1212) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26099 |  | 326100 | 04 |  | Engine Turbocharger 1 Turbine Intake Temperature (SPN 1180) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26100 |  | 326101 | 04 |  | Engine Turbocharger 2 Turbine Intake Temperature (SPN 1181) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26101 |  | 326102 | 04 |  | Engine Auxiliary Coolant Pressure (SPN 1203) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26102 |  | 326103 | 04 |  | Specific Humidity (SPN 4490) | INT16u | AB | 1 | g/kg |  |  | X | X
EIC measurements value | 26103 |  | 326104 | 04 |  | Engine Turbocharger 2 Speed (SPN 1169) | INT16u | AB | 0 | rpm |  |  | X | X
EIC measurements value | 26104 |  | 326105 | 04 |  | Engine Turbocharger 3 Speed (SPN 1170) | INT16u | AB | 0 | rpm |  |  | X | X
EIC measurements value | 26105 |  | 326106 | 04 |  | Trip Engine Running Time (SPN 1036) | INT32u | ABCD | 0 | h |  |  | X | X
EIC measurements value | 26107 |  | 326108 | 04 |  | Trip Idle Time (SPN 1037) | INT32u | ABCD | 0 | h |  |  | X | X
EIC measurements value | 26109 |  | 326110 | 04 |  | Engine Fan 1 Estimated Percent Speed (SPN 975) | INT16u | AB | 1 | perc |  |  | X | X
EIC measurements value | 26110 |  | 326111 | 04 |  | Engine Turbocharger 1 Speed (SPN 103) | INT16u | AB | 0 | rpm |  |  | X | X
EIC measurements value | 26111 |  | 326112 | 04 |  | Nominal Friction - Percent Torque (SPN 514) | INT16u | AB | 0 | perc |  |  | X | X
EIC measurements value | 26112 |  | 326113 | 04 |  | Engine's Desired Operating Speed (SPN 515) | INT16u | AB | 0 | rpm |  |  | X | X
EIC measurements value | 26113 |  | 326114 | 04 |  | Engine Intake Manifold 2 Temperature (SPN 1131) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26114 |  | 326115 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Volume (SPN 1761) | INT16u | AB | 1 | perc |  |  | X | X
EIC measurements value | 26115 |  | 326116 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Temperature 1 (SPN 3031) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26116 |  | 326117 | 04 |  | Aftertreatment 1 SCR Intake NOx 1 (SPN 3216) | INT16u | AB | 0 | ppm |  |  | X | X
EIC measurements value | 26117 |  | 326118 | 04 |  | Aftertreatment 1 Outlet NOx 1 (SPN 3226) | INT16u | AB | 0 | ppm |  |  | X | X
EIC measurements value | 26118 |  | 326119 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Actual Dosing Quantity (SPN 4331) | INT16u | AB | 1 | g/h |  |  | X | X
EIC measurements value | 26119 |  | 326120 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Doser 1 Absolute Pressure (SPN 4334) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26120 |  | 326121 | 04 |  | Aftertreatment 1 SCR Dosing Air Assist Valve (SPN 4336) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26121 |  | 326122 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Dosing Requested Quantity (SPN 4348) | INT16u | AB | 0 | g/h |  |  | X | X
EIC measurements value | 26122 |  | 326123 | 04 |  | Aftertreatment 1 SCR Intake Temperature (SPN 4360) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26123 |  | 326124 | 04 |  | Aftertreatment 1 SCR Outlet Temperature (SPN 4363) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26124 |  | 326125 | 04 |  | Aftertreatment 2 SCR Intake NOx 1 (SPN 3255) | INT16u | AB | 0 | ppm |  |  | X | X
EIC measurements value | 26125 |  | 326126 | 04 |  | Aftertreatment 2 Outlet NOx 1 (SPN 3265) | INT16u | AB | 0 | ppm |  |  | X | X
EIC measurements value | 26126 |  | 326127 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Actual Dosing Quantity (SPN 4384) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26127 |  | 326128 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser 1 Absolute Pressure (SPN 4387) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26128 |  | 326129 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser 1 Temperature (SPN 4390) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26129 |  | 326130 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Dosing Requested Quantity (SPN 4401) | INT16u | AB | 1 | g/h |  |  | X | X
EIC measurements value | 26130 |  | 326131 | 04 |  | Aftertreatment 2 SCR Intake Temperature (SPN 4413) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26131 |  | 326132 | 04 |  | Aftertreatment 2 SCR Outlet Temperature (SPN 4415) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26132 |  | 326133 | 04 |  | Engine Oil Filter Outlet Pressure (SPN 3549) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26133 |  | 326134 | 04 |  | Engine Operating State (SPN 3543) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26134 |  | 326135 | 04 |  | Source Address of Controlling Device for Engine Control (SPN 1483) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26135 |  | 326136 | 04 |  | Engine Rated Speed (SPN 189) | INT16u | AB | 0 | rpm |  |  | X | X
EIC measurements value | 26136 |  | 326137 | 04 |  | Engine Speed At Idle, Point 1 (SPN 188) | INT16u | AB | 0 | rpm |  |  | X | X
EIC measurements value | 26137 |  | 326138 | 04 |  | Fuel Consumption g/KWh (MTU) | INT16u | AB | 0 | g/kWh |  |  | X | X
EIC measurements value | 26138 |  | 326139 | 04 |  | Engine Status of Start procedure (MTU) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26139 |  | 326140 | 04 |  | Exhaust Port Temperature 17 (SPN 1153) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26140 |  | 326141 | 04 |  | Exhaust Port Temperature 18 (SPN 1154) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26141 |  | 326142 | 04 |  | Exhaust Port Temperature 19 (SPN 1155) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26142 |  | 326143 | 04 |  | Exhaust Port Temperature 20 (SPN 1156) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26143 |  | 326144 | 04 |  | UREA Level (Scania and Isuzu) | INT16u | AB | 0 | perc |  |  | X | X
EIC measurements value | 26144 |  | 326145 | 04 |  | Aftertreatment SCR Operator Inducement Severity (SPN 5246) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26145 |  | 326146 | 04 |  | Aftertreatment Diesel Exhaust Fluid Tank Low Level Indicator (SPN 5245) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26146 |  | 326147 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Outlet Temperature (SPN 3246) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26147 |  | 326148 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Time to Next Active Regeneration (SPN 5978) | INT32u | ABCD | 1 | h |  |  | X | X
EIC measurements value | 26149 |  | 326150 | 04 |  | Engine Charge Air Cooler 1 Outlet Temperature (SPN 2630) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26150 |  | 326151 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Soot Load Percent (SPN 3719) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26151 |  | 326152 | 04 |  | Purging Active (Scania) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26152 |  | 326153 | 04 |  | Limit Lamp Status (MTU) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26153 |  | 326154 | 04 |  | Battery Charger 1 Output Voltage (SPN 4992) | INT16u | AB | 0 | V |  |  | X | X
EIC measurements value | 26154 |  | 326155 | 04 |  | Battery Charger 1 Output Current (SPN 4993) | INT16u | AB | 0 | A |  |  | X | X
EIC measurements value | 26155 |  | 326156 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Average Consumption (SPN 3829) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26156 |  | 326157 | 04 |  | Time left to torque reduction (Volvo) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26157 |  | 326158 | 04 |  | Time left to servere torque reduction (Volvo) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26158 |  | 326159 | 04 |  | SCR inducement severity (Volvo) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26159 |  | 326160 | 04 |  | SCR inducement reason (Volvo) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26160 |  | 326161 | 04 |  | Engine Derate Request (SPN 3644) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26161 |  | 326162 | 04 |  | Engine Demand, Percent Torque (SPN 2432) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26162 |  | 326163 | 04 |  | Aftertreatment 1 Intake Percent Oxygen 1 (SPN 3217) | INT16u | AB | 0 | perc |  |  | X | X
EIC measurements value | 26163 |  | 326164 | 04 |  | Aftertreatment 1 Outlet Percent Oxygen 1 (SPN 3227) | INT16u | AB | 0 | perc |  |  | X | X
EIC measurements value | 26164 |  | 326165 | 04 |  | Engine Throttle Actuator 1 Control Command (SPN 3464) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26165 |  | 326166 | 04 |  | Long-term Fuel Trim - Bank 1 (SPN 4237) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26166 |  | 326167 | 04 |  | Short-term Fuel Trim - Bank 1 (SPN 4236) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26167 |  | 326168 | 04 |  | Engine Exhaust Bank 1 O2 Sensor Closed Loop Operation (SPN 4240) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26168 |  | 326169 | 04 |  | Engine Desired Ignition Timing 1 (SPN 1433) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26169 |  | 326170 | 04 |  | Engine Actual Ignition Timing (SPN 1436) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26170 |  | 326171 | 04 |  | EDC4 CAN Status (EMR) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26171 |  | 326172 | 04 |  | Engine Starter Mode (SPN 1675) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26172 |  | 326173 | 04 |  | Actual Maximum Available Engine - Percent Torque (SPN 3357) | INT16u | AB | 0 | perc |  |  | X | X
EIC measurements value | 26173 |  | 326174 | 04 |  | Engine Coolant Pre-heated State (SPN 3553) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26174 |  | 326175 | 04 |  | Engine Safety and Protection Override Status (MTU) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26175 |  | 326176 | 04 |  | Engine Cylinder Cut-off (MTU) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26176 |  | 326177 | 04 |  | Engine Running State (MTU) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26177 |  | 326178 | 04 |  | External Stop State (MTU) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26178 |  | 326179 | 04 |  | Requested Absolute Torque (MTU) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26179 |  | 326180 | 04 |  | Source of Current Speed Demand (MTU) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26180 |  | 326181 | 04 |  | Engine Demanded Operating Speed (MTU) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26181 |  | 326182 | 04 |  | Feedback of Speed Demand CAN (MTU) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26182 |  | 326183 | 04 |  | Feedback of Speed Demand Analogue Input (MTU) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26183 |  | 326184 | 04 |  | Speed Demand Fail Mode (MTU) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26184 |  | 326185 | 04 |  | Engine Shutdown Override Switch (SPN 1237) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26185 |  | 326186 | 04 |  | Engine Requested Speed (SPN 898) | INT16u | AB | 0 | rpm |  |  | X | X
EIC measurements value | 26186 |  | 326187 | 04 |  | Escape Mode Enable Flag (Isuzu) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26187 |  | 326188 | 04 |  | Inducement Timer (Isuzu) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26188 |  | 326189 | 04 |  | Inducement Level (Isuzu) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26189 |  | 326190 | 04 |  | Urea Tank Level (Isuzu) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26190 |  | 326191 | 04 |  | Urea Tank Level Indicator (Isuzu) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26191 |  | 326192 | 04 |  | Level Indicator (Amber) Action (Isuzu) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26192 |  | 326193 | 04 |  | DPF Amber Lamp Mode (Isuzu) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26193 |  | 326194 | 04 |  | EXH.SYSTEM lamp (Isuzu) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26194 |  | 326195 | 04 |  | DPF Green Lamp Mode (Isuzu) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26195 |  | 326196 | 04 |  | NO POWER Lamp (Isuzu) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26196 |  | 326197 | 04 |  | Engine Intake Manifold 3 Temperature (SPN 1132) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26197 |  | 326198 | 04 |  | Engine Intake Manifold 4 Temperature (SPN 1133) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26198 |  | 326199 | 04 |  | Engine Oil Filter Intake Pressure (SPN 1208) | INT16u | AB | 0 | bar/psi |  |  | X | X
EIC measurements value | 26199 |  | 326200 | 04 |  | Engine Turbocharger 2 Boost Pressure (SPN 1128) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26200 |  | 326201 | 04 |  | Engine Fuel 1 Injector Metering Rail 1 Pressure (SPN 157) | INT16u | AB | 0 | bar/psi |  |  | X | X
EIC measurements value | 26201 |  | 326202 | 04 |  | Battery Potential / Power Input 1 (SPN 168) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26202 |  | 326203 | 04 |  | Dosing Module Status (JCB) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26203 |  | 326204 | 04 |  | Actual Reducing Agent Quantity (JCB) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26204 |  | 326205 | 04 |  | Aftertreatment Lamp (JCB) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26205 |  | 326206 | 04 |  | Refresh Status Byte (JCB) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26206 |  | 326207 | 04 |  | SCR Monitor (JCB) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26207 |  | 326208 | 04 |  | Successful Running Refreshes (JCB) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26208 |  | 326209 | 04 |  | Successful Stationary Refreshes (JCB) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26209 |  | 326210 | 04 |  | Engine Rating (JCB) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26210 |  | 326211 | 04 |  | Aftertreatment 1 Exhaust Temperature 1 (SPN 3241) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26211 |  | 326212 | 04 |  | Humidity Derate Percentage (Perkins/CAT) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26212 |  | 326213 | 04 |  | Engine Emergency (Immediate) Shutdown Indication (SPN 3607) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26213 |  | 326214 | 04 |  | Number of EIO Activations (Volvo EMS2.4) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26214 |  | 326215 | 04 |  | Accumulated EIO time (Volvo EMS2.4) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26215 |  | 326216 | 04 |  | Time left of EIO Operation (Volvo EMS2.4) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26216 |  | 326217 | 04 |  | Remaining Service Hours (Hatz) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26217 |  | 326218 | 04 |  | Wheel Based Vehicle Speed (SPN 84) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26218 |  | 326219 | 04 |  | Aftertreatment 1 Exhaust Gas Mass Flow Rate (SPN 3236) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26219 |  | 326220 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Differential Pressure (SPN 3251) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26220 |  | 326221 | 04 |  | Aftertreatment 1 Diesel Oxidation Catalyst Intake Temperature (SPN 4765) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26221 |  | 326222 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Intake Temperature (SPN 3242) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26222 |  | 326223 | 04 |  | Phys. Injection quantity (Hatz) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26223 |  | 326224 | 04 |  | Phys. Torque (Hatz) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26224 |  | 326225 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Out of Neutral (SPN 3708) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26225 |  | 326226 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Parking Brake Not Set (SPN 3710) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26226 |  | 326227 | 04 |  | Operator Inducement Time to Torque Derate Level 1 (SPN 7426) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26227 |  | 326228 | 04 |  | Operator Inducement Time to Torque Derate Level 2 (SPN 7428) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26228 |  | 326229 | 04 |  | Alternator 1 Status (SPN 3353) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26252 |  | 326253 | 04 |  | Engine Throttle Valve 1 Position 1 (SPN 51) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26253 |  | 326254 | 04 |  | Engine Fuel Valve 1 Intake Absolute Pressure (SPN 1390) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26254 |  | 326255 | 04 |  | Engine Turbocharger 1 Boost Pressure (SPN 1127) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26255 |  | 326256 | 04 |  | Engine Cylinder 1 Ignition Timing (SPN 1413) | INT16 | AB | 0 | Deg |  |  | X | X
EIC measurements value | 26256 |  | 326257 | 04 |  | Engine Intake Air Mass Flow Rate (SPN 132) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26257 |  | 326258 | 04 |  | Engine Lambda (Yuchai) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26258 |  | 326259 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Ash Load Percent (SPN 3720) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26259 |  | 326260 | 04 |  | DPF Regeneration State (Scania) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26260 |  | 326261 | 04 |  | DPF Regeneration Countdown Timer (Scania) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26261 |  | 326262 | 04 |  | DEF Level (FPT) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26262 |  | 326263 | 04 |  | DEF Quality (FPT) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26263 |  | 326264 | 04 |  | DEF Technical Failure (FPT) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26264 |  | 326265 | 04 |  | Cold Start Heater Status (FPT) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26265 |  | 326266 | 04 |  | Fuel Filter Heater Status (FPT) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26266 |  | 326267 | 04 |  | Low Idle Increase Desired (FPT) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26267 |  | 326268 | 04 |  | Urea level inducement state (Scania) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26268 |  | 326269 | 04 |  | Emission-OBD inducement state (Scania) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26269 |  | 326270 | 04 |  | Emission-OBD inducement failure reason (Scania) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26270 |  | 326271 | 04 |  | Engine Diesel Particulate Filter Regeneration State (JDEC STAGE V) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26271 |  | 326272 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Concentration (SPN 3516) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26272 |  | 326273 | 04 |  | Engine Requested Fuel Valve 1 Position (SPN 1765) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26273 |  | 326274 | 04 |  | Engine Oil Priming State (SPN 3551) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26274 |  | 326275 | 04 |  | Fuel Pump Primer Status (SPN 4083) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26275 |  | 326276 | 04 |  | Sensor supply voltage 1 (SPN 3509) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26276 |  | 326277 | 04 |  | Sensor supply voltage 2 (SPN 3510) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26277 |  | 326278 | 04 |  | Accelerator Pedal Position 2 (SPN 29) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26278 |  | 326279 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Temporary System Lockout (SPN 3714) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26279 |  | 326280 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Permanent System Lockout (SPN 3715) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26280 |  | 326281 | 04 |  | Aftertreatment Ambient Air Temperature (SPN 7441) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26281 |  | 326282 | 04 |  | Aftertreatment Thermal Management Status (SPN 7332) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26282 |  | 326283 | 04 |  | Aftertreatment Engine Speed Increase request (SPN 7502) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26283 |  | 326284 | 04 |  | Aftertreatment Engine Load Request (SPN 7503) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26284 |  | 326285 | 04 |  | Feedback Engine Fueling State (SPN 5794) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26285 |  | 326286 | 04 |  | Engine Fueling Inhibit Allowed (SPN 5795) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26286 |  | 326287 | 04 |  | Blowby flow (Cummins H6) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26287 |  | 326288 | 04 |  | Fuel rail pressure (Cummins H6) | INT16u | AB | 0 | bar/psi |  |  | X | X
EIC measurements value | 26288 |  | 326289 | 04 |  | Timing rail pressure (Cummins H6) | INT16u | AB | 0 | bar/psi |  |  | X | X
EIC measurements value | 26289 |  | 326290 | 04 |  | Aftercooler water inlet temperature (Cummins H6) | INT16u | AB | 0 | Deg C/F |  |  | X | X
EIC measurements value | 26290 |  | 326291 | 04 |  | Fuel Rank position left (Cummins H6) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26291 |  | 326292 | 04 |  | Fuel Rank position right (Cummins H6) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26292 |  | 326293 | 04 |  | Intake Manifold pressure left (Cummins H6) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26293 |  | 326294 | 04 |  | Intake Manifold pressure right (Cummins H6) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26294 |  | 326295 | 04 |  | Intake Manifold Temperature left (Cummins H6) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26295 |  | 326296 | 04 |  | Intake Manifold Temperature right (Cummins H6) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26296 | 0 | 326297 | 04 |  | DPF Regeneration needed Lowest | BOOL | [5 empty] | X | X
EIC measurements value | 26296 | 1 | 326297 | 04 |  | DPF Regeneration not needed | BOOL | [5 empty] | X | X
EIC measurements value | 26296 | 2 | 326297 | 04 |  | DPF Active Regeneration needed | BOOL | [5 empty] | X | X
EIC measurements value | 26296 | 3 | 326297 | 04 |  | DPF Active Regeneration activated | BOOL | [5 empty] | X | X
EIC measurements value | 26296 | 4 | 326297 | 04 |  | DPF Active Regeneration not activated | BOOL | [5 empty] | X | X
EIC measurements value | 26296 | 5 | 326297 | 04 |  | DPF lamp ON blink | BOOL | [5 empty] | X | X
EIC measurements value | 26296 | 6 | 326297 | 04 |  | DPF lamp ON solid | BOOL | [5 empty] | X | X
EIC measurements value | 26296 | 7 | 326297 | 04 |  | DPF lamp OFF | BOOL | [5 empty] | X | X
EIC measurements validity | 26296 | 8 | 326297 | 04 |  | DPF Regeneration needed Lowest Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26296 | 9 | 326297 | 04 |  | DPF Regeneration not needed Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26296 | 10 | 326297 | 04 |  | DPF Active Regeneration needed Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26296 | 11 | 326297 | 04 |  | DPF Active Regeneration activated Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26296 | 12 | 326297 | 04 |  | DPF Active Regeneration not activated Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26296 | 13 | 326297 | 04 |  | DPF lamp ON blink Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26296 | 14 | 326297 | 04 |  | DPF lamp ON solid Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26296 | 15 | 326297 | 04 |  | DPF lamp OFF Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26297 | 0 | 326298 | 04 |  | MTU limit lamp ON solid | BOOL | [5 empty] | X | X
EIC measurements value | 26297 | 1 | 326298 | 04 |  | MTU limit lamp OFF | BOOL | [5 empty] | X | X
EIC measurements value | 26297 | 2 | 326298 | 04 |  | Exhaust system high temperature ON | BOOL | [5 empty] | X | X
EIC measurements value | 26297 | 3 | 326298 | 04 |  | Exhaust system high temperature OFF | BOOL | [5 empty] | X | X
EIC measurements value | 26297 | 4 | 326298 | 04 |  | DPF Regeneration Inhibit | BOOL | [5 empty] | X | X
EIC measurements value | 26297 | 5 | 326298 | 04 |  | DPF Regeneration Not Inhibit | BOOL | [5 empty] | X | X
EIC measurements value | 26297 | 6 | 326298 | 04 |  | DPF Regeneration needed Highest | BOOL | [5 empty] | X | X
EIC measurements value | 26297 | 7 | 326298 | 04 |  | DPF Regeneration needed Moderate | BOOL | [5 empty] | X | X
EIC measurements validity | 26297 | 8 | 326298 | 04 |  | MTU limit lamp ON solid Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26297 | 9 | 326298 | 04 |  | MTU limit lamp OFF Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26297 | 10 | 326298 | 04 |  | Exhaust system high temperature ON Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26297 | 11 | 326298 | 04 |  | Exhaust system high temperature OFF Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26297 | 12 | 326298 | 04 |  | DPF Regeneration Inhibit Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26297 | 13 | 326298 | 04 |  | DPF Regeneration Not Inhibit Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26297 | 14 | 326298 | 04 |  | DPF Regeneration needed Highest Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26297 | 15 | 326298 | 04 |  | DPF Regeneration needed Moderate Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26298 | 0 | 326299 | 04 |  | EMPTY | BOOL | [5 empty] | X | X
EIC measurements value | 26298 | 1 | 326299 | 04 |  | Volvo Penta Scr Inducement WARNING | BOOL | [5 empty] | X | X
EIC measurements value | 26298 | 2 | 326299 | 04 |  | Volvo Penta Scr Inducement not ACTIVE | BOOL | [5 empty] | X | X
EIC measurements value | 26298 | 3 | 326299 | 04 |  | After run status | BOOL | [5 empty] | X | X
EIC measurements value | 26298 | 4 | 326299 | 04 |  | DEF level low lamp ON blink | BOOL | [5 empty] | X | X
EIC measurements value | 26298 | 5 | 326299 | 04 |  | DEF level low lamp ON solid | BOOL | [5 empty] | X | X
EIC measurements value | 26298 | 6 | 326299 | 04 |  | DEF level low lamp OFF | BOOL | [5 empty] | X | X
EIC measurements value | 26298 | 7 | 326299 | 04 |  | MTU limit lamp ON blink 1Hz | BOOL | [5 empty] | X | X
EIC measurements validity | 26298 | 8 | 326299 | 04 |  | EMPTY validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26298 | 9 | 326299 | 04 |  | Volvo Penta Scr Inducement WARNING Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26298 | 10 | 326299 | 04 |  | Volvo Penta Scr Inducement not ACTIVE Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26298 | 11 | 326299 | 04 |  | After run status Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26298 | 12 | 326299 | 04 |  | DEF level low lamp ON blink Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26298 | 13 | 326299 | 04 |  | DEF level low lamp ON solid Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26298 | 14 | 326299 | 04 |  | DEF level low lamp OFF Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26298 | 15 | 326299 | 04 |  | MTU limit lamp ON blink 1Hz Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26299 | 0 | 326300 | 04 |  | Volvo Penta Absence of Reagent Dosing | BOOL | [5 empty] | X | X
EIC measurements value | 26299 | 1 | 326300 | 04 |  | Volvo Penta Incorrect Reagent Quality | BOOL | [5 empty] | X | X
EIC measurements value | 26299 | 2 | 326300 | 04 |  | Volvo Penta Reagent Tank low | BOOL | [5 empty] | X | X
EIC measurements value | 26299 | 3 | 326300 | 04 |  | Volvo Penta Scr Inducement Reason OK | BOOL | [5 empty] | X | X
EIC measurements value | 26299 | 4 | 326300 | 04 |  | Volvo Penta Temperature Override Derate | BOOL | [5 empty] | X | X
EIC measurements value | 26299 | 5 | 326300 | 04 |  | Volvo Penta Severe Derate | BOOL | [5 empty] | X | X
EIC measurements value | 26299 | 6 | 326300 | 04 |  | Volvo Penta Pre severe Derate WARNING | BOOL | [5 empty] | X | X
EIC measurements value | 26299 | 7 | 326300 | 04 |  | Volvo Penta Scr Derate ACTIVE | BOOL | [5 empty] | X | X
EIC measurements validity | 26299 | 8 | 326300 | 04 |  | Volvo Penta Absence of Reagent Dosing Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26299 | 9 | 326300 | 04 |  | Volvo Penta Incorrect Reagent Quality Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26299 | 10 | 326300 | 04 |  | Volvo Penta Reagent Tank low Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26299 | 11 | 326300 | 04 |  | Volvo Penta Scr Inducement Reason OK Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26299 | 12 | 326300 | 04 |  | Volvo Penta Temperature Override Derate Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26299 | 13 | 326300 | 04 |  | Volvo Penta Severe Derate Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26299 | 14 | 326300 | 04 |  | Volvo Penta Pre severe Derate WARNING Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26299 | 15 | 326300 | 04 |  | Volvo Penta Scr Derate ACTIVE Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26300 | 0 | 326301 | 04 |  | Alarm Red lamp OFF | BOOL | [5 empty] | X | X
EIC measurements value | 26300 | 1 | 326301 | 04 |  | Alarm Yellow lamp ON | BOOL | [5 empty] | X | X
EIC measurements value | 26300 | 2 | 326301 | 04 |  | Alarm Yellow lamp OFF | BOOL | [5 empty] | X | X
EIC measurements value | 26300 | 3 | 326301 | 04 |  | MTU buzzer lamp ON blink 2Hz | BOOL | [5 empty] | X | X
EIC measurements value | 26300 | 4 | 326301 | 04 |  | MTU buzzer lamp ON blink 1Hz | BOOL | [5 empty] | X | X
EIC measurements value | 26300 | 5 | 326301 | 04 |  | MTU buzzer lamp ON solid | BOOL | [5 empty] | X | X
EIC measurements value | 26300 | 6 | 326301 | 04 |  | MTU buzzer lamp OFF | BOOL | [5 empty] | X | X
EIC measurements value | 26300 | 7 | 326301 | 04 |  | MTU TIER4 lamp ON blink 2Hz | BOOL | [5 empty] | X | X
EIC measurements validity | 26300 | 8 | 326301 | 04 |  | Alarm Red lamp OFF Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26300 | 9 | 326301 | 04 |  | Alarm Yellow lamp ON Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26300 | 10 | 326301 | 04 |  | Alarm Yellow lamp OFF Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26300 | 11 | 326301 | 04 |  | MTU buzzer lamp ON blink 2Hz Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26300 | 12 | 326301 | 04 |  | MTU buzzer lamp ON blink 1Hz Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26300 | 13 | 326301 | 04 |  | MTU buzzer lamp ON solid Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26300 | 14 | 326301 | 04 |  | MTU buzzer lamp OFF Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26300 | 15 | 326301 | 04 |  | MTU TIER4 lamp ON blink 2Hz Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26301 | 0 | 326302 | 04 |  | Engine overspeed test | BOOL | [5 empty] | X | X
EIC measurements value | 26301 | 1 | 326302 | 04 |  | Engine ait shutoff command status | BOOL | [5 empty] | X | X
EIC measurements value | 26301 | 2 | 326302 | 04 |  | Engine alarm acknowledge | BOOL | [5 empty] | X | X
EIC measurements value | 26301 | 3 | 326302 | 04 |  | Engine Protect system appro shutdown | BOOL | [5 empty] | X | X
EIC measurements value | 26301 | 4 | 326302 | 04 |  | Engine Protect system shutdown | BOOL | [5 empty] | X | X
EIC measurements value | 26301 | 5 | 326302 | 04 |  | Engine Wait to start | BOOL | [5 empty] | X | X
EIC measurements value | 26301 | 6 | 326302 | 04 |  | Engine fuel leak | BOOL | [5 empty] | X | X
EIC measurements value | 26301 | 7 | 326302 | 04 |  | Alarm Red lamp ON | BOOL | [5 empty] | X | X
EIC measurements validity | 26301 | 8 | 326302 | 04 |  | Engine overspeed test Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26301 | 9 | 326302 | 04 |  | Engine ait shutoff command status Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26301 | 10 | 326302 | 04 |  | Engine alarm acknowledg Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26301 | 11 | 326302 | 04 |  | Engine Protect system appro shutdown Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26301 | 12 | 326302 | 04 |  | Engine Protect system shutdown Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26301 | 13 | 326302 | 04 |  | Engine Wait to start Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26301 | 14 | 326302 | 04 |  | Engine fuel leak Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26301 | 15 | 326302 | 04 |  | Alarm Red lamp ON Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26302 | 0 | 326303 | 04 |  | JCB Red solid | BOOL | [5 empty] | X | X
EIC measurements value | 26302 | 1 | 326303 | 04 |  | JCB Red blink | BOOL | [5 empty] | X | X
EIC measurements value | 26302 | 2 | 326303 | 04 |  | JCB Amber solid | BOOL | [5 empty] | X | X
EIC measurements value | 26302 | 3 | 326303 | 04 |  | JCB Amber blink | BOOL | [5 empty] | X | X
EIC measurements value | 26302 | 4 | 326303 | 04 |  | Force purge | BOOL | [5 empty] | X | X
EIC measurements value | 26302 | 5 | 326303 | 04 |  | Manual purge EIDSS | BOOL | [5 empty] | X | X
EIC measurements value | 26302 | 6 | 326303 | 04 |  | Manual purge ECU | BOOL | [5 empty] | X | X
EIC measurements value | 26302 | 7 | 326303 | 04 |  | Engine shutoff status | BOOL | [5 empty] | X | X
EIC measurements validity | 26302 | 8 | 326303 | 04 |  | JCB Red solid Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26302 | 9 | 326303 | 04 |  | JCB Red blink Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26302 | 10 | 326303 | 04 |  | JCB Amber solid Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26302 | 11 | 326303 | 04 |  | JCB Amber blink Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26302 | 12 | 326303 | 04 |  | Force purge Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26302 | 13 | 326303 | 04 |  | Manual purge EIDSS Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26302 | 14 | 326303 | 04 |  | Manual purge ECU | BOOL | [5 empty] | X | X
EIC measurements validity | 26302 | 15 | 326303 | 04 |  | Engine shutoff status Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26303 | 0 | 326304 | 04 |  | DEF low level - Fast blink | BOOL | [5 empty] | X | X
EIC measurements value | 26303 | 1 | 326304 | 04 |  | DPF lamp - fast blink | BOOL | [5 empty] | X | X
EIC measurements value | 26303 | 2 | 326304 | 04 |  | JCB Particulate filter restricted critical | BOOL | [5 empty] | X | X
EIC measurements value | 26303 | 3 | 326304 | 04 |  | JCB Particulate filter restricted very high | BOOL | [5 empty] | X | X
EIC measurements value | 26303 | 4 | 326304 | 04 |  | JCB Particulate filter restricted high | BOOL | [5 empty] | X | X
EIC measurements value | 26303 | 5 | 326304 | 04 |  | JCB Engine emission system failure high | BOOL | [5 empty] | X | X
EIC measurements value | 26303 | 6 | 326304 | 04 |  | JCB Engine emission system failure low | BOOL | [5 empty] | X | X
EIC measurements value | 26303 | 7 | 326304 | 04 |  | JCB Engine emission system failure warning | BOOL | [5 empty] | X | X
EIC measurements validity | 26303 | 8 | 326304 | 04 |  | DEF low level - Fast blink Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26303 | 9 | 326304 | 04 |  | DPF lamp - fast blink Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26303 | 10 | 326304 | 04 |  | JCB Particulate filter restricted critical Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26303 | 11 | 326304 | 04 |  | JCB Particulate filter restricted very high Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26303 | 12 | 326304 | 04 |  | JCB Particulate filter restricted high Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26303 | 13 | 326304 | 04 |  | JCB Engine emission system failure high Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26303 | 14 | 326304 | 04 |  | JCB Engine emission system failure low Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26303 | 15 | 326304 | 04 |  | JCB Engine emission system failure warning Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26304 | 0 | 326305 | 04 |  | Yellow lamp fast blink | BOOL | [5 empty] | X | X
EIC measurements value | 26304 | 1 | 326305 | 04 |  | Yellow lamp blink | BOOL | [5 empty] | X | X
EIC measurements value | 26304 | 2 | 326305 | 04 |  | Yellow lamp solid | BOOL | [5 empty] | X | X
EIC measurements value | 26304 | 3 | 326305 | 04 |  | Yellow lamp OFF | BOOL | [5 empty] | X | X
EIC measurements value | 26304 | 4 | 326305 | 04 |  | Red lamp fast blink | BOOL | [5 empty] | X | X
EIC measurements value | 26304 | 5 | 326305 | 04 |  | Red lamp blink | BOOL | [5 empty] | X | X
EIC measurements value | 26304 | 6 | 326305 | 04 |  | Red lamp solid | BOOL | [5 empty] | X | X
EIC measurements value | 26304 | 7 | 326305 | 04 |  | Red lamp OFF | BOOL | [5 empty] | X | X
EIC measurements validity | 26304 | 8 | 326305 | 04 |  | Yellow lamp fast blink Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26304 | 9 | 326305 | 04 |  | Yellow lamp blink Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26304 | 10 | 326305 | 04 |  | Yellow lamp solid Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26304 | 11 | 326305 | 04 |  | Yellow lamp OFF Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26304 | 12 | 326305 | 04 |  | Red lamp fast blink Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26304 | 13 | 326305 | 04 |  | Red lamp blink Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26304 | 14 | 326305 | 04 |  | Red lamp solid Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26304 | 15 | 326305 | 04 |  | Red lamp OFF Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26305 | 0 | 326306 | 04 |  | Engine emission system failure lamp fast blink | BOOL | [5 empty] | X | X
EIC measurements value | 26305 | 1 | 326306 | 04 |  | Engine emission system failure lamp blink | BOOL | [5 empty] | X | X
EIC measurements value | 26305 | 2 | 326306 | 04 |  | Engine emission system failure lamp solid | BOOL | [5 empty] | X | X
EIC measurements value | 26305 | 3 | 326306 | 04 |  | Engine emission system failure lamp off | BOOL | [5 empty] | X | X
EIC measurements value | 26305 | 4 | 326306 | 04 |  | MIL lamp fast blink | BOOL | [5 empty] | X | X
EIC measurements value | 26305 | 5 | 326306 | 04 |  | MIL lamp blink | BOOL | [5 empty] | X | X
EIC measurements value | 26305 | 6 | 326306 | 04 |  | MIL lamp solid | BOOL | [5 empty] | X | X
EIC measurements value | 26305 | 7 | 326306 | 04 |  | MIL lamp OFF | BOOL | [5 empty] | X | X
EIC measurements validity | 26305 | 8 | 326306 | 04 |  | Engine emission system failure lamp fast blink Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26305 | 9 | 326306 | 04 |  | Engine emission system failure lamp blink Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26305 | 10 | 326306 | 04 |  | Engine emission system failure lamp solid Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26305 | 11 | 326306 | 04 |  | Engine emission system failure lamp off Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26305 | 12 | 326306 | 04 |  | MIL lamp fast blink Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26305 | 13 | 326306 | 04 |  | MIL lamp blink Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26305 | 14 | 326306 | 04 |  | MIL lamp solid Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26305 | 15 | 326306 | 04 |  | MIL lamp OFF Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26306 | 0 | 326307 | 04 |  | Oil Pressure Missing (Hatz) | BOOL | [5 empty] | X | X
EIC measurements value | 26306 | 1 | 326307 | 04 |  | Pre-glow Active (Hatz) | BOOL | [5 empty] | X | X
EIC measurements value | 26306 | 2 | 326307 | 04 |  | Service Delay (Hatz) | BOOL | [5 empty] | X | X
EIC measurements value | 26306 | 3 | 326307 | 04 |  | Engine Running (Hatz) | BOOL | [5 empty] | X | X
EIC measurements value | 26306 | 4 | 326307 | 04 |  | DPF Regeneration Inhibit Out Of Neutral | BOOL | [5 empty] | X | X
EIC measurements value | 26306 | 5 | 326307 | 04 |  | DPF Regeneration Not Inhibit Out Of Neutral | BOOL | [5 empty] | X | X
EIC measurements value | 26306 | 6 | 326307 | 04 |  | DPF Regeneration Inhibit Park Brake Not Set | BOOL | [5 empty] | X | X
EIC measurements value | 26306 | 7 | 326307 | 04 |  | DPF Regeneration Not Inhibit Park Brake Not Set | BOOL | [5 empty] | X | X
EIC measurements validity | 26306 | 8 | 326307 | 04 |  | Oil Pressure Missing (Hatz) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26306 | 9 | 326307 | 04 |  | Pre-glow Active (Hatz) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26306 | 10 | 326307 | 04 |  | Service Delay (Hatz) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26306 | 11 | 326307 | 04 |  | Engine Running (Hatz) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26306 | 12 | 326307 | 04 |  | DPF Regeneration Inhibit Out Of Neutral Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26306 | 13 | 326307 | 04 |  | DPF Regeneration Not Inhibit Out Of Neutral Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26306 | 14 | 326307 | 04 |  | DPF Regeneration Inhibit Park Brake Not Set Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26306 | 15 | 326307 | 04 |  | DPF Regeneration Not Inhibit Park Brake Not Set Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26307 | 2 | 326308 | 04 |  | Brake Switch (SPN 597) | BOOL | [5 empty] | X | X
EIC measurements value | 26307 | 3 | 326308 | 04 |  | Parking Brake Switch (SPN 70) | BOOL | [5 empty] | X | X
EIC measurements value | 26307 | 4 | 326308 | 04 |  | Transmission Neutral Switch (SPN 604) | BOOL | [5 empty] | X | X
EIC measurements value | 26307 | 5 | 326308 | 04 |  | Air Filter Switch (Hatz) | BOOL | [5 empty] | X | X
EIC measurements value | 26307 | 6 | 326308 | 04 |  | Engine Overtemperature (Hatz) | BOOL | [5 empty] | X | X
EIC measurements value | 26307 | 7 | 326308 | 04 |  | Engine Diagnostic Lamp (Hatz) | BOOL | [5 empty] | X | X
EIC measurements validity | 26307 | 10 | 326308 | 04 |  | Brake Switch (SPN 597) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26307 | 11 | 326308 | 04 |  | Parking Brake Switch (SPN 70) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26307 | 12 | 326308 | 04 |  | Transmission Neutral Switch (SPN 604) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26307 | 13 | 326308 | 04 |  | Air Filter Switch (Hatz) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26307 | 14 | 326308 | 04 |  | Engine Overtemperature (Hatz) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26307 | 15 | 326308 | 04 |  | Engine Diagnostic Lamp (Hatz) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26309 | 0 | 326310 | 04 |  | Water in Fuel Detection (FPT) | BOOL | [5 empty] | X | X
EIC measurements value | 26309 | 1 | 326310 | 04 |  | Engine Protection (FPT) | BOOL | [5 empty] | X | X
EIC measurements value | 26309 | 2 | 326310 | 04 |  | Turbo Charger Protection (FPT) | BOOL | [5 empty] | X | X
EIC measurements value | 26309 | 3 | 326310 | 04 |  | Scr Injector Overheat Protection (FPT) | BOOL | [5 empty] | X | X
EIC measurements value | 26309 | 4 | 326310 | 04 |  | Urea Thawing Mode Active (FPT) | BOOL | [5 empty] | X | X
EIC measurements value | 26309 | 5 | 326310 | 04 |  | Engine Over Speed Warning (FPT) | BOOL | [5 empty] | X | X
EIC measurements value | 26309 | 6 | 326310 | 04 |  | Exhaust Over Heat Condition (FPT) | BOOL | [5 empty] | X | X
EIC measurements validity | 26309 | 8 | 326310 | 04 |  | Water in Fuel Detection (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26309 | 9 | 326310 | 04 |  | Engine Protection (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26309 | 10 | 326310 | 04 |  | Turbo Charger Protection (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26309 | 11 | 326310 | 04 |  | Scr Injector Overheat Protection (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26309 | 12 | 326310 | 04 |  | Urea Thawing Mode Active (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26309 | 13 | 326310 | 04 |  | Engine Over Speed Warning (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26309 | 14 | 326310 | 04 |  | Exhaust Over Heat Condition (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26310 | 0 | 326311 | 04 |  | Oil switch (Kubota) | BOOL | [5 empty] | X | X
EIC measurements value | 26310 | 1 | 326311 | 04 |  | Clogged DPF (FPT) | BOOL | [5 empty] | X | X
EIC measurements value | 26310 | 2 | 326311 | 04 |  | Smoke Limitation (FPT) | BOOL | [5 empty] | X | X
EIC measurements value | 26310 | 3 | 326311 | 04 |  | Engine Oil Over Temperature (FPT) | BOOL | [5 empty] | X | X
EIC measurements value | 26310 | 4 | 326311 | 04 |  | Nh3 Slip Detection (FPT) | BOOL | [5 empty] | X | X
EIC measurements value | 26310 | 5 | 326311 | 04 |  | Bad Urea Quality (FPT) | BOOL | [5 empty] | X | X
EIC measurements value | 26310 | 6 | 326311 | 04 |  | Low Catalyst Efficiency (FPT) | BOOL | [5 empty] | X | X
EIC measurements value | 26310 | 7 | 326311 | 04 |  | Fuel in Oil Detection (FPT) | BOOL | [5 empty] | X | X
EIC measurements validity | 26310 | 8 | 326311 | 04 |  | Oil switch (Kubota) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26310 | 9 | 326311 | 04 |  | Clogged DPF (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26310 | 10 | 326311 | 04 |  | Smoke Limitation (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26310 | 11 | 326311 | 04 |  | Engine Oil Over Temperature (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26310 | 12 | 326311 | 04 |  | Nh3 Slip Detection (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26310 | 13 | 326311 | 04 |  | Bad Urea Quality (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26310 | 14 | 326311 | 04 |  | Low Catalyst Efficiency (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26310 | 15 | 326311 | 04 |  | Fuel in Oil Detection (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26311 |  | 326312 | 04 |  | Trip Average Fuel Rate (SPN 1029) RAW | INT32u | ABCD | 0 |  |  |  | X | X
EIC measurements value | 26313 |  | 326314 | 04 |  | Engine Trip Fuel (SPN 182) RAW | INT32u | ABCD | 0 |  |  |  | X | X
EIC measurements value | 26315 |  | 326316 | 04 |  | Engine Total Fuel Used (SPN 250) RAW | INT32u | ABCD | 0 |  |  |  | X | X
EIC measurements value | 26317 |  | 326318 | 04 |  | Engine Controlled Shutdown Request (SPN 5795) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26318 |  | 326319 | 04 |  | Engine Oil Pre-Heated State (SPN 3552) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26319 |  | 326320 | 04 |  | Engine Ventilation Status (SPN 3554) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26320 |  | 326321 | 04 |  | Rail pressure (Jichai) | INT16u | AB | 2 |  |  |  | X | X
EIC measurements value | 26321 |  | 326322 | 04 |  | Engine Actual Exhaust 1 Oxygen (SPN 1119) | INT16u | AB | 2 |  |  |  | X | X
EIC measurements value | 26322 |  | 326323 | 04 |  | Jichai WYS Fault code 1.1 | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26323 |  | 326324 | 04 |  | Jichai WYS Fault code 1.2 | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26324 |  | 326325 | 04 |  | Jichai WYS Fault code 1.3 | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26325 |  | 326326 | 04 |  | Jichai WYS Fault code 1.4 | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26326 |  | 326327 | 04 |  | Jichai WYS Fault code 2.1 | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26327 |  | 326328 | 04 |  | Jichai WYS Fault code 2.2 | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26328 |  | 326329 | 04 |  | Jichai WYS Fault code 2.3 | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26329 |  | 326330 | 04 |  | Jichai WYS Fault code 2.4 | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26330 |  | 326331 | 04 |  | Jichai Engine torque | INT16u | AB | 0 | Nm |  |  | X | X
EIC measurements value | 26331 |  | 326332 | 04 |  | Jichai Engine reference torque | INT16u | AB | 0 | Nm |  |  | X | X
EIC measurements value | 26332 |  | 326333 | 04 |  | Jichai Oil pressure of boost | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26333 |  | 326334 | 04 |  | Jichai Oil pressure after filtration | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26334 |  | 326335 | 04 |  | Jichai High temperature water inlet temperature | INT16u | AB | 2 | C/F |  |  | X | X
EIC measurements value | 26335 |  | 326336 | 04 |  | Jichai Cooler inlet water temperature | INT16u | AB | 2 | C/F |  |  | X | X
EIC measurements value | 26336 |  | 326337 | 04 |  | Jichai Engine status | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26337 |  | 326338 | 04 |  | Jichai Engine target speed | INT16u | AB | 0 | RPM |  |  | X | X
EIC measurements value | 26338 |  | 326339 | 04 |  | Engine Fuel Valve 1 Position (SPN 1442) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26339 |  | 326340 | 04 |  | Engine Gaseous Fuel Supply Pressure 1 (SPN 159) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26340 |  | 326341 | 04 |  | Fuel Injection Quantity (Kubota) | INT16u | AB | 1 | mm3/st |  |  | X | X
EIC measurements value | 26341 |  | 326342 | 04 |  | Regeneration Status (Kubota) | INT16u | AB | 0 | None |  |  | X | X
EIC measurements value | 26342 |  | 326343 | 04 |  | Ash Accumulation Time (Kubota) | INT32u | ABCD | 1 | h |  |  | X | X
EIC measurements value | 26344 |  | 326345 | 04 |  | Operator Inducement Reason (Kubota) | INT16u | AB | 0 | None |  |  | X | X
EIC measurements value | 26345 |  | 326346 | 04 |  | Operator Inducement Severity (Kubota) | INT16u | AB | 0 | None |  |  | X | X
EIC measurements value | 26346 |  | 326347 | 04 |  | HC Evaporation Status (Scania EMS2 S8) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26347 |  | 326348 | 04 |  | HC Evaporation Required Action (Scania EMS2 S8) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26348 |  | 326349 | 04 |  | HC Evaporation Progress Countdown Timer (Scania EMS2 S8) | INT16u | AB | 0 | min |  |  | X | X
EIC measurements value | 26349 |  | 326350 | 04 |  | HC Evaporation Action Start Countdown Timer (Scania EMS2 S8) | INT16u | AB | 0 | min |  |  | X | X
EIC measurements value | 26350 |  | 326351 | 04 |  | Sulphur Regeneration request (Scania EMS2 S8) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26351 |  | 326352 | 04 |  | deSOx heatup request (Scania EMS2 S8) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26352 |  | 326353 | 04 |  | Insulation resistance (KWG ISO5 isolation monitor) | INT32u | ABCD | 0 | ohm |  |  | X | X
EIC measurements value | 26354 | 0 | 326355 | 04 |  | Turbo heat protection (FPT) | BOOL | [5 empty] | X | X
EIC measurements value | 26354 | 1 | 326355 | 04 |  | Isolation Timeout (KWG ISO5 isolation monitor) | BOOL | [5 empty] | X | X
EIC measurements value | 26354 | 2 | 326355 | 04 |  | Isolation Warning (KWG ISO5 isolation monitor) | BOOL | [5 empty] | X | X
EIC measurements value | 26354 | 3 | 326355 | 04 |  | Isolation Fault (KWG ISO5 isolation monitor) | BOOL | [5 empty] | X | X
EIC measurements value | 26354 | 4 | 326355 | 04 |  | Evaporation Is In Progress (Scania S8) | BOOL | [5 empty] | X | X
EIC measurements value | 26354 | 5 | 326355 | 04 |  | Evaporation Required Urgent (Scania S8) | BOOL | [5 empty] | X | X
EIC measurements value | 26354 | 6 | 326355 | 04 |  | Evaporation Required Less Urgent (Scania S8) | BOOL | [5 empty] | X | X
EIC measurements value | 26354 | 7 | 326355 | 04 |  | Evaporation Not Required (Scania S8) | BOOL | [5 empty] | X | X
EIC measurements validity | 26354 | 8 | 326355 | 04 |  | Turbo heat protection (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26354 | 9 | 326355 | 04 |  | Isolation Timeout (KWG ISO5 isolation monitor) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26354 | 10 | 326355 | 04 |  | Isolation Warning (KWG ISO5 isolation monitor) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26354 | 11 | 326355 | 04 |  | Isolation Fault (KWG ISO5 isolation monitor) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26354 | 12 | 326355 | 04 |  | Evaporation Is In Progress (Scania S8) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26354 | 13 | 326355 | 04 |  | Evaporation Required Urgent (Scania S8) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26354 | 14 | 326355 | 04 |  | Evaporation Required Less Urgent (Scania S8) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26354 | 15 | 326355 | 04 |  | Evaporation Not Required (Scania S8) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26355 | 0 | 326356 | 04 |  | SCR System Cleaning Status (SPN 6916) | BOOL | [5 empty] | X | X
EIC measurements value | 26355 | 1 | 326356 | 04 |  | SCR Thermal Management Active (SPN 5400) | BOOL | [5 empty] | X | X
EIC measurements value | 26355 | 2 | 326356 | 04 |  | DPF Thermal Management Active (SPN 5399) | BOOL | [5 empty] | X | X
EIC measurements value | 26355 | 3 | 326356 | 04 |  | Doosan stage 5 ash lamp status < 121% | BOOL | [5 empty] | X | X
EIC measurements value | 26355 | 4 | 326356 | 04 |  | Doosan stage 5 ash lamp status 111%-120% | BOOL | [5 empty] | X | X
EIC measurements value | 26355 | 5 | 326356 | 04 |  | Doosan stage 5 ash lamp status 106%-110% | BOOL | [5 empty] | X | X
EIC measurements value | 26355 | 6 | 326356 | 04 |  | Doosan stage 5 ash lamp status 100%-105% | BOOL | [5 empty] | X | X
EIC measurements value | 26355 | 7 | 326356 | 04 |  | Doosan stage 5 ash lamp status > 100% | BOOL | [5 empty] | X | X
EIC measurements validity | 26355 | 8 | 326356 | 04 |  | SCR System Cleaning Status (SPN 6916) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26355 | 9 | 326356 | 04 |  | SCR Thermal Management Active (SPN 5400) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26355 | 10 | 326356 | 04 |  | DPF Thermal Management Active (SPN 5399) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26355 | 11 | 326356 | 04 |  | Doosan stage 5 ash lamp status < 121% Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26355 | 12 | 326356 | 04 |  | Doosan stage 5 ash lamp status 111%-120% Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26355 | 13 | 326356 | 04 |  | Doosan stage 5 ash lamp status 106%-110% Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26355 | 14 | 326356 | 04 |  | Doosan stage 5 ash lamp status 100%-105% Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26355 | 15 | 326356 | 04 |  | Doosan stage 5 ash lamp status > 100% Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26356 |  | 326357 | 04 |  | Doosan stage 5 ash lamp status | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26357 | 0 | 326358 | 04 |  | DEF low level -Slow blink | BOOL | [5 empty] | X | X
EIC measurements value | 26357 | 1 | 326358 | 04 |  | Yanmar Stage V DPF regenaration acknowledge lamp | BOOL | [5 empty] | X | X
EIC measurements value | 26357 | 2 | 326358 | 04 |  | Yanmar Stage V Accelerator Interlock Switch feedback | BOOL | [5 empty] | X | X
EIC measurements value | 26357 | 3 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to Engine Not Warmed Up (SPN 6931) | BOOL | [5 empty] | X | X
EIC measurements value | 26357 | 4 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to System Fault Active (SPN 6927) | BOOL | [5 empty] | X | X
EIC measurements value | 26357 | 5 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to Low Exhaust Temperature (SPN 6926) | BOOL | [5 empty] | X | X
EIC measurements value | 26357 | 6 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to Inhibit Switch (SPN 6918) | BOOL | [5 empty] | X | X
EIC measurements value | 26357 | 7 | 326358 | 04 |  | SCR System Cleaning Inhibited Status (SPN 6917) | BOOL | [5 empty] | X | X
EIC measurements validity | 26357 | 8 | 326358 | 04 |  | DEF low level -Slow blink Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26357 | 9 | 326358 | 04 |  | Yanmar Stage V DPF regenaration acknowledge lamp Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26357 | 10 | 326358 | 04 |  | Yanmar Stage V Accelerator Interlock Switch feedback Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26357 | 11 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to Engine Not Warmed Up (SPN 6931) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26357 | 12 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to System Fault Active (SPN 6927) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26357 | 13 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to Low Exhaust Temperature (SPN 6926) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26357 | 14 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to Inhibit Switch (SPN 6918) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26357 | 15 | 326358 | 04 |  | SCR System Cleaning Inhibited Status (SPN 6917) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26358 |  | 326359 | 04 |  | SCR System Cleaning Lamp Command (SPN 6915) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26359 |  | 326360 | 04 |  | SCR System Cleaning Forced Status (SPN 6934) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26360 |  | 326361 | 04 |  | JiChai JC15T JG Fuel Valve Self-Adjust | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26361 |  | 326362 | 04 |  | JiChai JC15T JG Fuel Valve CloseLoop-Adjust | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26362 |  | 326363 | 04 |  | JiChai JC15T JG Air Fuel Ratio | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26363 |  | 326364 | 04 |  | JiChai JC15T JG Natural Gas Temperature | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26364 |  | 326365 | 04 |  | JiChai JC15T JG Natural Gas Pressure | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26365 |  | 326366 | 04 |  | JiChai JC15T JG Gas Supply Amount Per Second | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26366 |  | 326367 | 04 |  | JiChai JC15T JG PHI | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26367 |  | 326368 | 04 |  | Doosan stage 5 Emission OBD Inducement lamp status | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26368 |  | 326369 | 04 |  | Doosan stage 5 Emission OBD lamp failure reason | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26369 |  | 326370 | 04 |  | Engine Fuel Valve 1 Differential Pressure | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26370 |  | 326371 | 04 |  | Engine Fuel Flow Rate 1 | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26371 |  | 326372 | 04 |  | Weichai Engine Oil Pressure | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26372 |  | 326373 | 04 |  | Weichai Engine Oil Pressure | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26373 |  | 326374 | 04 |  | Weichai Pre-throttle Pressure 1 | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26374 |  | 326375 | 04 |  | Weichai Throttle 1 Position | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26375 |  | 326376 | 04 |  | Weichai Throttle 2 Position | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26376 |  | 326377 | 04 |  | Weichai Bypass Valve 1 Position | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26377 |  | 326378 | 04 |  | Weichai Altronic RPM | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26378 |  | 326379 | 04 |  | Weichai Altronic Supply Voltage | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26379 |  | 326380 | 04 |  | Weichai Relative Humidity | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26380 |  | 326381 | 04 |  | Weichai Humidity Sensor Air Temperature | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26381 |  | 326382 | 04 |  | Weichai Air Filter DP | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26382 |  | 326383 | 04 |  | Weichai CH4 Concentration | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26383 |  | 326384 | 04 |  | Weichai H2S Concentration | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26384 |  | 326385 | 04 |  | Weichai Closed Loop Correction | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26385 |  | 326386 | 04 |  | Weichai Engine Exhaust O2 Sensor Fueling Correction | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26386 |  | 326387 | 04 |  | Fan Speed (SPN 1639) | INT16u | AB | 0 | rpm |  |  | X | X
EIC measurements value | 26387 |  | 326388 | 04 |  | DPF Active Regeneration Inhibited Due to System Fault Active (SPN 3712) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26388 |  | 326389 | 04 |  | FPT HC level | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26389 |  | 326390 | 04 |  | FPT EGR / DPF operator inducement | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26390 |  | 326391 | 04 |  | Deutz EMR5 Standstill request reason | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26391 |  | 326392 | 04 |  | Deutz EMR5 SCR warning Lamp / EAT inducement Lamp | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26392 |  | 326393 | 04 |  | Jing Guan Fuel temperature | INT16u | AB | 0 | deg C/F |  |  | X | X
EIC measurements value | 26393 |  | 326394 | 04 |  | Jing Guan Exhaust temperature | INT16u | AB | 1 | deg C/F |  |  | X | X
EIC measurements value | 26394 |  | 326395 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Time since Last Active Regeneration (SPN 3721) | INT32u | ABCD | 1 | h |  |  | X | X
EIC measurements value | 26396 |  | 326397 | 04 |  | Aftertreatment 1 SCR Intake NOx 2 (SPN 7649) | INT16u | AB | 0 | ppm |  |  | X | X
EIC measurements value | 26397 |  | 326398 | 04 |  | Aftertreatment 2 SCR Intake NOx 2 (SPN 7671) | INT16u | AB | 0 | ppm |  |  | X | X
EIC measurements value | 26411 |  | 326412 | 04 |  | Engine Fuel Valve 2 Position (SPN 1443) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26412 |  | 326413 | 04 |  | Engine Fuel Valve 1 Outlet Absolute Pressure (SPN 2980) | INT16u | AB | 0 | bar/psi |  |  | X | X
EIC measurements value | 26413 |  | 326414 | 04 |  | Engine Throttle 2 Position (SPN 3673) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26414 |  | 326415 | 04 |  | Engine Throttle Valve 1 Differential Pressure (SPN 5631) | INT16u | AB | 0 | bar/psi |  |  | X | X
EIC measurements value | 26415 |  | 326416 | 04 |  | Engine Oil Priming Pump Switch (SPN 3550) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26416 |  | 326417 | 04 |  | Engine Gas Mass Flow Rate 1 (SPN 1241) | INT16u | AB | 0 | kg/h |  |  | X | X
EIC measurements value | 26417 |  | 326418 | 04 |  | Instantaneous Estimated Brake Power (SPN 1242) | INT16u | AB | 0 | kW |  |  | X | X
EIC measurements value | 26418 |  | 326419 | 04 |  | Accelerator Pedal 1 Low Idle Switch (SPN 558) | BOOL | AB | 0 |  |  |  | X | X
EIC measurements value | 26419 |  | 326420 | 04 |  | Engine Cylinder 1 Knock Level (SPN 1352, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26420 |  | 326421 | 04 |  | Engine Cylinder 2 Knock Level (SPN 1353, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26421 |  | 326422 | 04 |  | Engine Cylinder 3 Knock Level (SPN 1354, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26422 |  | 326423 | 04 |  | Engine Cylinder 4 Knock Level (SPN 1355, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26423 |  | 326424 | 04 |  | Engine Cylinder 5 Knock Level (SPN 1356, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26424 |  | 326425 | 04 |  | Engine Cylinder 6 Knock Level (SPN 1357, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26425 |  | 326426 | 04 |  | Engine Cylinder 7 Knock Level (SPN 1358, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26426 |  | 326427 | 04 |  | Engine Cylinder 8 Knock Level (SPN 1359, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26427 |  | 326428 | 04 |  | Engine Cylinder 9 Knock Level (SPN 1360, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26428 |  | 326429 | 04 |  | Engine Cylinder 10 Knock Level (SPN 1361, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26429 |  | 326430 | 04 |  | Engine Cylinder 11 Knock Level (SPN 1362, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26430 |  | 326431 | 04 |  | Engine Cylinder 12 Knock Level (SPN 1363, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26431 |  | 326432 | 04 |  | Engine Cylinder 13 Knock Level (SPN 1364, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26432 |  | 326433 | 04 |  | Engine Cylinder 14 Knock Level (SPN 1365, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26433 |  | 326434 | 04 |  | Engine Cylinder 15 Knock Level (SPN 1366, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26434 |  | 326435 | 04 |  | Engine Cylinder 16 Knock Level (SPN 1367, Cummins) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26435 |  | 326436 | 04 |  | Cylinder 1 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26436 |  | 326437 | 04 |  | Cylinder 2 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26437 |  | 326438 | 04 |  | Cylinder 3 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26438 |  | 326439 | 04 |  | Cylinder 4 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26439 |  | 326440 | 04 |  | Cylinder 5 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26440 |  | 326441 | 04 |  | Cylinder 6 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26441 |  | 326442 | 04 |  | Cylinder 7 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26442 |  | 326443 | 04 |  | Cylinder 8 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26443 |  | 326444 | 04 |  | Cylinder 9 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26444 |  | 326445 | 04 |  | Cylinder 10 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26445 |  | 326446 | 04 |  | Cylinder 11 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26446 |  | 326447 | 04 |  | Cylinder 12 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26447 |  | 326448 | 04 |  | Cylinder 13 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26448 |  | 326449 | 04 |  | Cylinder 14 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26449 |  | 326450 | 04 |  | Cylinder 15 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26450 |  | 326451 | 04 |  | Cylinder 16 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26451 |  | 326452 | 04 |  | Engine Cylinder 2 Ignition Timing (SPN 1414, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X
EIC measurements value | 26452 |  | 326453 | 04 |  | Engine Cylinder 3 Ignition Timing (SPN 1415, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X
EIC measurements value | 26453 |  | 326454 | 04 |  | Engine Cylinder 4 Ignition Timing (SPN 1416, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X
EIC measurements value | 26454 |  | 326455 | 04 |  | Engine Cylinder 5 Ignition Timing (SPN 1417, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X
EIC measurements value | 26455 |  | 326456 | 04 |  | Engine Cylinder 6 Ignition Timing (SPN 1418, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X
EIC measurements value | 26456 |  | 326457 | 04 |  | Engine Cylinder 7 Ignition Timing (SPN 1419, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X
EIC measurements value | 26457 |  | 326458 | 04 |  | Engine Cylinder 8 Ignition Timing (SPN 1420, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X
EIC measurements value | 26458 |  | 326459 | 04 |  | Engine Cylinder 9 Ignition Timing (SPN 1421, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X
EIC measurements value | 26459 |  | 326460 | 04 |  | Engine Cylinder 10 Ignition Timing (SPN 1422, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X
EIC measurements value | 26460 |  | 326461 | 04 |  | Engine Cylinder 11 Ignition Timing (SPN 1423, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X
EIC measurements value | 26461 |  | 326462 | 04 |  | Engine Cylinder 12 Ignition Timing (SPN 1424, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X
EIC measurements value | 26462 |  | 326463 | 04 |  | Engine Cylinder 13 Ignition Timing (SPN 1425, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X
EIC measurements value | 26463 |  | 326464 | 04 |  | Engine Cylinder 14 Ignition Timing (SPN 1426, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X
EIC measurements value | 26464 |  | 326465 | 04 |  | Engine Cylinder 15 Ignition Timing (SPN 1427, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X
EIC measurements value | 26465 |  | 326466 | 04 |  | Engine Cylinder 16 Ignition Timing (SPN 1428, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X
EIC measurements value | 26466 |  | 326467 | 04 |  | Engine Spark Plug 1 (SPN 1294, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26467 |  | 326468 | 04 |  | Engine Spark Plug 2 (SPN 1295, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26468 |  | 326469 | 04 |  | Engine Spark Plug 3 (SPN 1296, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26469 |  | 326470 | 04 |  | Engine Spark Plug 4 (SPN 1297, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26470 |  | 326471 | 04 |  | Engine Spark Plug 5 (SPN 1298, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26471 |  | 326472 | 04 |  | Engine Spark Plug 6 (SPN 1299, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26472 |  | 326473 | 04 |  | Engine Spark Plug 7 (SPN 1300, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26473 |  | 326474 | 04 |  | Engine Spark Plug 8 (SPN 1301, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26474 |  | 326475 | 04 |  | Engine Spark Plug 9 (SPN 1302, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26475 |  | 326476 | 04 |  | Engine Spark Plug 10 (SPN 1303, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26476 |  | 326477 | 04 |  | Engine Spark Plug 11 (SPN 1304, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26477 |  | 326478 | 04 |  | Engine Spark Plug 12 (SPN 1305, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26478 |  | 326479 | 04 |  | Engine Spark Plug 13 (SPN 1306, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26479 |  | 326480 | 04 |  | Engine Spark Plug 14 (SPN 1307, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26480 |  | 326481 | 04 |  | Engine Spark Plug 15 (SPN 1308, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26481 |  | 326482 | 04 |  | Engine Spark Plug 16 (SPN 1309, Cummins) | INT16u | AB | 2 | kV |  |  | X | X
EIC measurements value | 26482 |  | 326483 | 04 |  | Engine extended range oil filter diff press (SPN 6321) | INT16u | AB | 2/1 | bar/psi |  |  | X | X
EIC measurements value | 26483 |  | 326484 | 04 |  | Sea Water Pump Outlet Pressure (SPN 2435) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26484 |  | 326485 | 04 |  | Water In Fuel Indicator 2 (SPN 6301) | BOOL | AB | 0 |  |  |  | X | X
EIC measurements value | 26485 |  | 326486 | 04 |  | Aftertreatment 1 SCR System Hydrocarbon (SPN 7934) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26486 |  | 326487 | 04 |  | Aftertreatment System Enable Status (SPN 7851) | BOOL | AB | 0 |  |  |  | X | X
EIC measurements value | 26487 |  | 326488 | 04 |  | Aftertreatment DEF Dosing Mode Status (SPN 9176) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26488 |  | 326489 | 04 |  | Aftertreatment 1 SCR System State (SPN 4332) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26489 |  | 326490 | 04 |  | Aftertreatment 1 SCR Intake Pressure (SPN 6586) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26490 |  | 326491 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Doser Pressure (SPN 6875) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26491 |  | 326492 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Quick Thaw Temperature (SPN 4368) | INT16u | AB | 0 | C/F |  |  | X | X
EIC measurements value | 26492 |  | 326493 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Quick Thaw Tank Volume (SPN 4367) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26493 |  | 326494 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Fill Valve Command (SPN 5434) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26494 |  | 326495 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Pump Drive Percentage (SPN 4375) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26495 |  | 326496 | 04 |  | Aftertreatment 1 Total Diesel Exhaust Fluid Used (SPN 5963) | INT32u | AB | 0 | L |  |  | X | X
EIC measurements value | 26497 |  | 326498 | 04 |  | Total Aftertreatment Operating Hours (SPN 8629) | INT16u | AB | 0 | h |  |  | X | X
EIC measurements value | 26499 |  | 326500 | 04 |  | Engine Fuel Rate (High Resolution) (SPN 1600) | INT16u | AB | 2 | L/h |  |  | X | X
EIC measurements value | 26501 |  | 326502 | 04 |  | Engine Fuel Leakage 1 (SPN 1239) | BOOL | AB | 0 |  |  |  | X | X
EIC measurements value | 26502 |  | 326503 | 04 |  | Restriction level according to DEF tank level | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26503 |  | 326504 | 04 |  | DEF tank level – Thresholds | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26504 |  | 326505 | 04 |  | Restriction caused by standstill request | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26505 |  | 326506 | 04 |  | Restriction level according to NOx reduction | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26506 |  | 326507 | 04 |  | Restriction level according to anti-tampering | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26507 |  | 326508 | 04 |  | SCR operator inducement reason | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26508 |  | 326509 | 04 |  | Pedal Input Delay (Kohler KDI3404) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26509 |  | 326510 | 04 |  | Driver Warning System Indicator Status (SPN 5825) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26510 |  | 326511 | 04 |  | Emission Control System Operator Inducement Severity (SPN 5826) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26511 |  | 326512 | 04 |  | EIC Time remaining to inducement act (Kohler KDI3404) | INT16u | AB | 0 | min |  |  | X | X
EIC measurements value | 26512 |  | 326513 | 04 |  | EIC Fuel Main Fltr Out Press L (Mitsubishi MGS3100) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26513 |  | 326514 | 04 |  | EIC Fuel Pre Fltr Dif Press (Mitsubishi MGS3100) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26514 |  | 326515 | 04 |  | EIC Engine Fuel Supply Pump Intake Pressure #2 (YC-ECU-A) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26515 |  | 326516 | 04 |  | EIC Engine Fuel Filter (suction side) Differential Pressure #2 (YC-ECU-A) | INT16u | AB | 2 | bar |  |  | X | X
EIC measurements value | 26516 |  | 326517 | 04 |  | EIC Engine Torque Mode (SPN 899) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26517 |  | 326518 | 04 |  | EIC Actual Engine - Percent Torque (Fractional) (SPN 4154) | INT16u | AB | 3 | % |  |  | X | X
EIC measurements value | 26518 |  | 326519 | 04 |  | EIC Engine Desired Speed Asymmetrical Adjustment (SPN 519) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26519 |  | 326520 | 04 |  | EIC Estimated Engine Parasitic Losses (SPN 2978) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26520 |  | 326521 | 04 |  | EIC Aftertreatment 1 Intake Dew Point (SPN 3237) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26521 |  | 326522 | 04 |  | EIC Aftertreatment 1 Exhaust Dew Point (SPN 3238) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26522 |  | 326523 | 04 |  | EIC Aftertreatment 2 Intake Dew Point (SPN 3239) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26523 |  | 326524 | 04 |  | EIC Aftertreatment 2 Exhaust Dew Point (SPN 3240) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26524 |  | 326525 | 04 |  | EIC Charge Air Cooler Thermostat Opening (SPN 1134) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26525 |  | 326526 | 04 |  | EIC Engine Extended Crankcase Blowby Pressure (SPN 22) | INT16u | AB | 2 | bar/psi |  |  | X | X
EIC measurements value | 26526 |  | 326527 | 04 |  | EIC Accelerator Pedal Kickdown Switch (SPN 559) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26527 |  | 326528 | 04 |  | EIC Road Speed Limit Status (SPN 1437) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26528 |  | 326529 | 04 |  | EIC Accelerator Pedal 2 Low Idle Switch (SPN 2970) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26529 |  | 326530 | 04 |  | EIC Remote Accelerator Pedal Position (SPN 974) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26530 |  | 326531 | 04 |  | EIC Vehicle Acceleration Rate Limit Status (SPN 2979) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26531 |  | 326532 | 04 |  | EIC Momentary Engine Maximum Power Enable Feedback (SPN 5021) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26532 |  | 326533 | 04 |  | EIC Estimated Pumping Percentage Torque (SPN 5398) | INT16u | AB | 0 | % |  |  | X | X
EIC measurements value | 26533 |  | 326534 | 04 |  | EIC Engine Total Revolutions (SPN 249) | INT32u | ABCD | 0 | h |  |  | X | X
EIC measurements value | 26535 |  | 326536 | 04 |  | EIC Cab Interior Temperature (SPN 170) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26536 |  | 326537 | 04 |  | EIC Road Surface Temperature (SPN 79) | INT16u | AB | 1 | Deg C/F |  |  | X | X
EIC measurements value | 26537 |  | 326538 | 04 |  | EIC Transmission Oil Temperature 1 (SPN 177, CVT transmission) | INT16u | AB | 1 | bar |  |  | X | X
EIC measurements value | 26538 |  | 326539 | 04 |  | EIC Transmission Actual Gear Ratio (SPN 526, CVT transmission) | INT16u | AB | 3 | none |  |  | X | X
EIC measurements value | 26539 |  | 326540 | 04 |  | EIC Transmission Engine Crank Enable (SPN 2900, CVT transmission) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26540 |  | 326541 | 04 |  | EIC Transmission Shift Inhibit Indicator (SPN 1851, CVT transmission) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26542 |  | 326543 | 04 |  | Isuzu Engine Derate Lamp | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26543 |  | 326544 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser Pressure (SPN 6876) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26544 |  | 326545 | 04 |  | Engine Friction Percent Torque At Idle, Point 1 (SPN 5471) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26545 |  | 326546 | 04 |  | Engine Friction Percent Torque, Point 2 (SPN 5472) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26546 |  | 326547 | 04 |  | Engine Friction Percent Torque, Point 3 (SPN 5473) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26547 |  | 326548 | 04 |  | Engine Friction Percent Torque, Point 4 (SPN 5474) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26548 |  | 326549 | 04 |  | Engine Friction Percent Torque, Point 5 (SPN 5475) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26549 |  | 326550 | 04 |  | Engine Friction Percent Torque, Point 6 (SPN 5476) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26550 |  | 326551 | 04 |  | Engine Friction Percent Torque, Point 7 (SPN 5477) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26551 |  | 326552 | 04 |  | Aftertreatment 2 SCR Differential Pressure Preliminary FMI (SPN 4412) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26552 |  | 326553 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Outlet Pressure (SPN 3610) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26553 |  | 326554 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Intermediate Temperature Preliminary FMI (SPN 3254) | INT16u | AB | 0 | none |  |  | X | X
EIC measurements value | 26554 |  | 326555 | 04 |  | Operator Inducement Time to Torque Derate Level 3/FINAL (SPN 7719) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26555 |  | 326556 | 04 |  | OBD Malfunction Indicator Lamp Command (SPN 5080) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26556 |  | 326557 | 04 |  | Engine Throttle position 2 (Kingbang) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26557 |  | 326558 | 04 |  | Aftertreatment 2 Intake %O2 (SPN 3256) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26558 | 0 | 326559 | 04 |  | Engine Oil Change (FPT Stage V) | BOOL | [5 empty] | X | X
EIC measurements value | 26558 | 1 | 326559 | 04 |  | High coolant temperature (VecV E694) | BOOL | [5 empty] | X | X
EIC measurements value | 26558 | 2 | 326559 | 04 |  | Low oil pressure (VecV E694) | BOOL | [5 empty] | X | X
EIC measurements value | 26558 | 3 | 326559 | 04 |  | Engine Oil Low Pressure (FPT Stage V) | BOOL | [5 empty] | X | X
EIC measurements value | 26558 | 4 | 326559 | 04 |  | Engine High Oil Temperature (FPT Stage V) | BOOL | [5 empty] | X | X
EIC measurements value | 26558 | 5 | 326559 | 04 |  | Engine Overspeed (FPT Stage V) | BOOL | [5 empty] | X | X
EIC measurements value | 26558 | 6 | 326559 | 04 |  | Engine Over Temperature - Coolant Warning (FPT Stage V) | BOOL | [5 empty] | X | X
EIC measurements value | 26558 | 7 | 326559 | 04 |  | Engine Over Temperature - Coolant Pre-Warning (FPT Stage V) | BOOL | [5 empty] | X | X
EIC measurements value | 26558 | 8 | 326559 | 04 |  | Engine Oil Change (FPT Stage V) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26558 | 9 | 326559 | 04 |  | High coolant temperature (VecV E694) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26558 | 10 | 326559 | 04 |  | Low oil pressure (VecV E694) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26558 | 11 | 326559 | 04 |  | Engine Oil Low Pressure (FPT Stage V) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26558 | 12 | 326559 | 04 |  | Engine High Oil Temperature (FPT Stage V) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26558 | 13 | 326559 | 04 |  | Engine Overspeed (FPT Stage V) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26558 | 14 | 326559 | 04 |  | Engine Over Temperature - Coolant Warning (FPT Stage V) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26558 | 15 | 326559 | 04 |  | Engine Over Temperature - Coolant Pre-Warning (FPT Stage V) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 0 | 326560 | 04 |  | DEF Shutdown lamp (FPT Stage V) | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 1 | 326560 | 04 |  | DEF Warning lamp (FPT Stage V) | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 2 | 326560 | 04 |  | Air Filter Clogging lamp (FPT Stage V) | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 3 | 326560 | 04 |  | Fuel Filter Clogging lamp (FPT Stage V) | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 4 | 326560 | 04 |  | HC burn off lamp (FPT Stage V) | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 5 | 326560 | 04 |  | DEF Level Severe Inducement lamp (FPT Stage V) | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 6 | 326560 | 04 |  | DEF Level Mid Level Inducement lamp (FPT Stage V) | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 7 | 326560 | 04 |  | DEF Level Fill Operator Warning lamp (FPT Stage V) | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 8 | 326560 | 04 |  | DEF Shutdown lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 9 | 326560 | 04 |  | DEF Warning lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 10 | 326560 | 04 |  | Air Filter Clogging lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 11 | 326560 | 04 |  | Fuel Filter Clogging lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 12 | 326560 | 04 |  | HC burn off lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 13 | 326560 | 04 |  | DEF Level Severe Inducement lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 14 | 326560 | 04 |  | DEF Level Mid Level Inducement lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26559 | 15 | 326560 | 04 |  | DEF Level Fill Operator Warning lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26560 | 7 | 326561 | 04 |  | AdBlue lamp (VecV E694) | BOOL | [5 empty] | X | X
EIC measurements value | 26560 | 15 | 326561 | 04 |  | AdBlue lamp (VecV E694) Validity | BOOL | [5 empty] | X | X
EIC measurements value | 26561 |  | 326562 | 04 |  | Diesel Particulate Filter Active Regeneration Forced Status (SPN 4175) | INT16u | AB | 0 |  |  |  | X | X
EIC measurements value | 26562 |  | 326563 | 04 |  | Engine Total Fuel Consumption Liquid (SPN 5054) RAW | INT32u | AB | 0 |  |  |  | X | X
EIC measurements validity | 26900 | 0 | 326901 | 04 |  | Engine Percent Load At Current Speed (SPN 92) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26900 | 1 | 326901 | 04 |  | Accelerator Pedal Position 1 (SPN 91) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26900 | 2 | 326901 | 04 |  | Actual Engine, Percent Torque (SPN 513) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26900 | 3 | 326901 | 04 |  | Driver's Demand Engine, Percent Torque (SPN 512) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26900 | 4 | 326901 | 04 |  | Engine Intake Manifold 1 Temperature (SPN 105) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26900 | 5 | 326901 | 04 |  | Charge air pressure (MDEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26900 | 6 | 326901 | 04 |  | Engine Fuel Rate (SPN 183) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26900 | 7 | 326901 | 04 |  | Engine Coolant Level 1 (SPN 111) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26900 | 8 | 326901 | 04 |  | Engine Intake 1 Air Temperature (SPN 172) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26900 | 9 | 326901 | 04 |  | Engine Intake Manifold #1 Pressure (SPN 102) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26900 | 10 | 326901 | 04 |  | Engine Fuel 1 Temperature 1 (SPN 174) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26900 | 11 | 326901 | 04 |  | Engine Oil Temperature 1 (SPN 175) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26900 | 12 | 326901 | 04 |  | Active Diagnostic Trouble Code Count (SPN 1218) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26900 | 13 | 326901 | 04 |  | Engine Oil Pressure (SPN 100) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26900 | 14 | 326901 | 04 |  | Engine Coolant Temperature (SPN 110) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26900 | 15 | 326901 | 04 |  | Engine Speed (SPN 190) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26901 | 0 | 326902 | 04 |  | Barometric Pressure (SPN 108) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26901 | 1 | 326902 | 04 |  | Engine Coolant Filter Differential Pressure (SPN 112) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26901 | 2 | 326902 | 04 |  | Engine Air Filter 1 Differential Pressure (SPN 107) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26901 | 3 | 326902 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Intake Pressure (SPN 81) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26901 | 4 | 326902 | 04 |  | Engine Turbocharger 1 Oil Temperature (SPN 176) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26901 | 5 | 326902 | 04 |  | Water In Fuel Indicator 1 (SPN 97) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26901 | 6 | 326902 | 04 |  | Engine Coolant Pressure 1 (SPN 109) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26901 | 7 | 326902 | 04 |  | Engine Crankcase Pressure 1 (SPN 101) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26901 | 8 | 326902 | 04 |  | Engine Oil Level (SPN 98) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26901 | 9 | 326902 | 04 |  | Engine Fuel Delivery Pressure (SPN 94) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26901 | 10 | 326902 | 04 |  | Key Switch Battery Potential (SPN 158) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26901 | 11 | 326902 | 04 |  | Engine Oil Filter Differential Pressure (SPN 99) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26901 | 13 | 326902 | 04 |  | Engine Total Hours of Operation (SPN 247) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26901 | 14 | 326902 | 04 |  | Engine Exhaust Temperature (SPN 173) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26901 | 15 | 326902 | 04 |  | Engine Intake Air Pressure (SPN 106) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26902 | 1 | 326903 | 04 |  | Trip Fuel (Gaseous) (SPN 1039) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26902 | 3 | 326903 | 04 |  | Engine Total Fuel Used (SPN 250) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26902 | 5 | 326903 | 04 |  | Engine Trip Fuel (SPN 182) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26902 | 6 | 326903 | 04 |  | Engine Intercooler Temperature (SPN 52) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26902 | 7 | 326903 | 04 |  | Engine Turbocharger 1 Compressor Outlet Temperature (ADEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26902 | 8 | 326903 | 04 |  | Auxiliary_Analog_Info Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26902 | 9 | 326903 | 04 |  | Auxiliary_Analog_Info (ADEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26902 | 10 | 326903 | 04 |  | Temp. Winding 3 (ADEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26902 | 11 | 326903 | 04 |  | Temp. Winding 2 (ADEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26902 | 12 | 326903 | 04 |  | Temp. Winding 1 (ADEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26902 | 13 | 326903 | 04 |  | Engine Exhaust Manifold Bank 1 Temperature 1 (SPN 2434) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26902 | 14 | 326903 | 04 |  | Engine Exhaust Manifold Bank 2 Temperature 1 (SPN 2433) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26902 | 15 | 326903 | 04 |  | Ambient Air Temperature (SPN 171) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26903 | 0 | 326904 | 04 |  | Speed demand Source (MDEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26903 | 1 | 326904 | 04 |  | Engine Fuel Filter Differential Pressure (SPN 95) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26903 | 2 | 326904 | 04 |  | Engine Fuel Filter (suction side) Differential Pressure (SPN 1382) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26903 | 3 | 326904 | 04 |  | Engine Fuel Supply Pump Intake Absolute Pressure (SPN 1381) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26903 | 4 | 326904 | 04 |  | Engine Air Filter 2 Differential Pressure (SPN 2809) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26903 | 5 | 326904 | 04 |  | Exhaust System High Temperature Lamp Command (SPN 3698) | BOOL | [5 empty] | X | X
EIC measurements validity | 26903 | 6 | 326904 | 04 |  | Aftertreatment Diesel Particulate Filter Status (SPN 3701) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26903 | 7 | 326904 | 04 |  | Aftertreatment Diesel Particulate Filter Active Regeneration Status (SPN 3700) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26903 | 8 | 326904 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Inhibit Switch (SPN 3703) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26903 | 9 | 326904 | 04 |  | Diesel Particulate Filter Lamp Command (SPN 3697) | BOOL | [5 empty] | X | X
EIC measurements validity | 26903 | 10 | 326904 | 04 |  | Engine Intake Manifold #1 Absolute Pressure (SPN 3563) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26903 | 11 | 326904 | 04 |  | Engine power (ADEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26903 | 12 | 326904 | 04 |  | Engine Rated Power (SPN 166) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26903 | 13 | 326904 | 04 |  | Trip Average Fuel Rate (SPN 1029) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26903 | 15 | 326904 | 04 |  | Total Fuel Used (Gaseous) (SPN 1040) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 0 | 326905 | 04 |  | Exhaust Port Temperature 02 (SPN 1138) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 1 | 326905 | 04 |  | Exhaust Port Temperature 01 (SPN 1137) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 2 | 326905 | 04 |  | Stop signal active (MDEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 3 | 326905 | 04 |  | Feedback Speed Demand analog (MDEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 4 | 326905 | 04 |  | T-Lube Oil Limit HIHI (MDEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 5 | 326905 | 04 |  | T-Lube Oil Limit HI (MDEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 6 | 326905 | 04 |  | Engine Speed Camshaft (MDEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 7 | 326905 | 04 |  | Injection Quantity Act.DBR % (MDEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 8 | 326905 | 04 |  | Actual Droop (MDEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 9 | 326905 | 04 |  | Engine ECU Temperature (SPN 1136) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 10 | 326905 | 04 |  | T-Coolant Intercooler (MDEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 11 | 326905 | 04 |  | T-Coolant Limit HIHI (MDEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 12 | 326905 | 04 |  | T-Coolant Limit HI (MDEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 13 | 326905 | 04 |  | P-Fuel (MDEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 14 | 326905 | 04 |  | P-Lube Oil Limit LOLO (MDEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26904 | 15 | 326905 | 04 |  | P-Lube Oil Limit LO (MDEC) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 0 | 326906 | 04 |  | Engine Coolant Temperature 2 (SPN 4076) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 1 | 326906 | 04 |  | Engine Filtered Fuel Delivery Pressure (SPN 5579) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 2 | 326906 | 04 |  | Exhaust Port Temperature 16 (SPN 1152) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 3 | 326906 | 04 |  | Exhaust Port Temperature 15 (SPN 1151) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 4 | 326906 | 04 |  | Exhaust Port Temperature 14 (SPN 1150) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 5 | 326906 | 04 |  | Exhaust Port Temperature 13 (SPN 1149) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 6 | 326906 | 04 |  | Exhaust Port Temperature 12 (SPN 1148) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 7 | 326906 | 04 |  | Exhaust Port Temperature 11 (SPN 1147) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 8 | 326906 | 04 |  | Exhaust Port Temperature 10 (SPN 1146) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 9 | 326906 | 04 |  | Exhaust Port Temperature 09 (SPN 1145) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 10 | 326906 | 04 |  | Exhaust Port Temperature 08 (SPN 1144) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 11 | 326906 | 04 |  | Exhaust Port Temperature 07 (SPN 1143) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 12 | 326906 | 04 |  | Exhaust Port Temperature 06 (SPN 1142) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 13 | 326906 | 04 |  | Exhaust Port Temperature 05 (SPN 1141) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 14 | 326906 | 04 |  | Exhaust Port Temperature 04 (SPN 1140) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26905 | 15 | 326906 | 04 |  | Exhaust Port Temperature 03 (SPN 1139) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26906 | 0 | 326907 | 04 |  | Nominal Friction - Percent Torque (SPN 514) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26906 | 1 | 326907 | 04 |  | Engine Turbocharger 1 Speed (SPN 103) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26906 | 2 | 326907 | 04 |  | Engine Fan 1 Estimated Percent Speed (SPN 975) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26906 | 4 | 326907 | 04 |  | Trip Idle Time (SPN 1037) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26906 | 6 | 326907 | 04 |  | Trip Engine Running Time (SPN 1036) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26906 | 7 | 326907 | 04 |  | Engine Turbocharger 3 Speed (SPN 1170) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26906 | 8 | 326907 | 04 |  | Engine Turbocharger 2 Speed (SPN 1169) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26906 | 9 | 326907 | 04 |  | Specific Humidity (SPN 4490) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26906 | 10 | 326907 | 04 |  | Engine Auxiliary Coolant Pressure (SPN 1203) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26906 | 11 | 326907 | 04 |  | Engine Turbocharger 2 Turbine Intake Temperature (SPN 1181) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26906 | 12 | 326907 | 04 |  | Engine Turbocharger 1 Turbine Intake Temperature (SPN 1180) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26906 | 13 | 326907 | 04 |  | Engine Auxiliary Coolant Temperature (SPN 1212) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26906 | 14 | 326907 | 04 |  | Engine Coolant Pump Outlet Temperature (SPN 4193) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26906 | 15 | 326907 | 04 |  | Engine Coolant Temperature 3 (SPN 6209) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 0 | 326908 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser 1 Absolute Pressure (SPN 4387) | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 1 | 326908 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Actual Dosing Quantity (SPN 4384) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 2 | 326908 | 04 |  | Aftertreatment 2 Outlet NOx 1 (SPN 3265) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 3 | 326908 | 04 |  | Aftertreatment 2 SCR Intake NOx 1 (SPN 3255) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 4 | 326908 | 04 |  | Aftertreatment 1 SCR Outlet Temperature (SPN 4363) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 5 | 326908 | 04 |  | Aftertreatment 1 SCR Intake Temperature (SPN 4360) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 6 | 326908 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Dosing Requested Quantity (SPN 4348) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 7 | 326908 | 04 |  | Aftertreatment 1 SCR Dosing Air Assist Valve (SPN 4336) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 8 | 326908 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Doser 1 Absolute Pressure (SPN 4334) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 9 | 326908 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Actual Dosing Quantity (SPN 4331) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 10 | 326908 | 04 |  | Aftertreatment 1 Outlet NOx 1 (SPN 3226) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 11 | 326908 | 04 |  | Aftertreatment 1 SCR Intake NOx 1 (SPN 3216) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 12 | 326908 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Temperature 1 (SPN 3031) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 13 | 326908 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Volume (SPN 1761) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 14 | 326908 | 04 |  | Engine Intake Manifold 2 Temperature (SPN 1131) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26907 | 15 | 326908 | 04 |  | Engine's Desired Operating Speed (SPN 515) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 0 | 326909 | 04 |  | UREA Level (Scania) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 1 | 326909 | 04 |  | Exhaust Port Temperature 20 (SPN 1156) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 2 | 326909 | 04 |  | Exhaust Port Temperature 19 (SPN 1155) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 3 | 326909 | 04 |  | Exhaust Port Temperature 18 (SPN 1154) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 4 | 326909 | 04 |  | Exhaust Port Temperature 17 (SPN 1153) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 5 | 326909 | 04 |  | Engine Status of Start procedure (MTU) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 6 | 326909 | 04 |  | Fuel Consumption g/KWh (MTU) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 7 | 326909 | 04 |  | Engine Speed At Idle, Point 1 (SPN 188) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 8 | 326909 | 04 |  | Engine Rated Speed (SPN 189) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 9 | 326909 | 04 |  | Source Address of Controlling Device for Engine Control (SPN 1483) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 10 | 326909 | 04 |  | Engine Operating State (SPN 3543) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 11 | 326909 | 04 |  | Engine Oil Filter Outlet Pressure (SPN 3549) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 12 | 326909 | 04 |  | Aftertreatment 2 SCR Outlet Temperature (SPN 4415) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 13 | 326909 | 04 |  | Aftertreatment 2 SCR Intake Temperature (SPN 4413) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 14 | 326909 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Dosing Requested Quantity (SPN 4401) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26908 | 15 | 326909 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser 1 Temperature (SPN 4390) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26909 | 0 | 326910 | 04 |  | SCR inducement reason (Volvo) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26909 | 1 | 326910 | 04 |  | SCR inducement severity (Volvo) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26909 | 2 | 326910 | 04 |  | Time left to servere torque reduction (Volvo) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26909 | 3 | 326910 | 04 |  | Time left to torque reduction (Volvo) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26909 | 4 | 326910 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Average Consumption (SPN 3829) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26909 | 5 | 326910 | 04 |  | Battery Charger 1 Output Current (SPN 4993) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26909 | 6 | 326910 | 04 |  | Battery Charger 1 Output Voltage (SPN 4992) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26909 | 7 | 326910 | 04 |  | Limit Lamp Status (MTU) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26909 | 8 | 326910 | 04 |  | Purging Active (Scania) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26909 | 9 | 326910 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Soot Load Percent (SPN 3719) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26909 | 10 | 326910 | 04 |  | Engine Charge Air Cooler 1 Outlet Temperature (SPN 2630) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26909 | 12 | 326910 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Time to Next Active Regeneration (SPN 5978) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26909 | 13 | 326910 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Outlet Temperature (SPN 3246) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26909 | 14 | 326910 | 04 |  | Aftertreatment Diesel Exhaust Fluid Tank Low Level Indicator (SPN 5245) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26909 | 15 | 326910 | 04 |  | Aftertreatment SCR Operator Inducement Severity (SPN 5246) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 0 | 326911 | 04 |  | Engine Cylinder Cut-off (MTU) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 1 | 326911 | 04 |  | Engine Safety and Protection Override Status (MTU) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 2 | 326911 | 04 |  | Engine Coolant Pre-heated State (SPN 3553) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 3 | 326911 | 04 |  | Actual Maximum Available Engine - Percent Torque (SPN 3357) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 4 | 326911 | 04 |  | Engine Starter Mode (SPN 1675) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 5 | 326911 | 04 |  | EDC4 CAN Status (EMR) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 6 | 326911 | 04 |  | Engine Actual Ignition Timing (SPN 1436) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 7 | 326911 | 04 |  | Engine Desired Ignition Timing 1 (SPN 1433) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 8 | 326911 | 04 |  | Engine Exhaust Bank 1 O2 Sensor Closed Loop Operation (SPN 4240) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 9 | 326911 | 04 |  | Short-term Fuel Trim - Bank 1 (SPN 4236) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 10 | 326911 | 04 |  | Long-term Fuel Trim - Bank 1 (SPN 4237) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 11 | 326911 | 04 |  | Engine Throttle Actuator 1 Control Command (SPN 3464) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 12 | 326911 | 04 |  | Aftertreatment 1 Outlet Percent Oxygen 1 (SPN 3227) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 13 | 326911 | 04 |  | Aftertreatment 1 Intake Percent Oxygen 1 (SPN 3217) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 14 | 326911 | 04 |  | Engine Demand, Percent Torque (SPN 2432) | BOOL | [5 empty] | X | X
EIC measurements validity | 26910 | 15 | 326911 | 04 |  | Engine Derate Request (SPN 3644) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 0 | 326912 | 04 |  | Level Indicator (Amber) Action (Isuzu) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 1 | 326912 | 04 |  | Urea Tank Level Indicator (Isuzu) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 2 | 326912 | 04 |  | Urea Tank Level (Isuzu) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 3 | 326912 | 04 |  | Inducement Level (Isuzu) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 4 | 326912 | 04 |  | Inducement Timer (Isuzu) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 5 | 326912 | 04 |  | Escape Mode Enable Flag (Isuzu) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 6 | 326912 | 04 |  | Engine Requested Speed (SPN 898) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 7 | 326912 | 04 |  | Engine Shutdown Override Switch (SPN 1237) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 8 | 326912 | 04 |  | Speed Demand Fail Mode (MTU) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 9 | 326912 | 04 |  | Feedback of Speed Demand Analogue Input (MTU) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 10 | 326912 | 04 |  | Feedback of Speed Demand CAN (MTU) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 11 | 326912 | 04 |  | Engine Demanded Operating Speed (MTU) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 12 | 326912 | 04 |  | Source of Current Speed Demand (MTU) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 13 | 326912 | 04 |  | Requested Absolute Torque (MTU) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 14 | 326912 | 04 |  | External Stop State (MTU) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26911 | 15 | 326912 | 04 |  | Engine Running State (MTU) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 0 | 326913 | 04 |  | Successful Running Refreshes (JCB) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 1 | 326913 | 04 |  | SCR Monitor (JCB) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 2 | 326913 | 04 |  | Refresh Status Byte (JCB) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 3 | 326913 | 04 |  | Aftertreatment Lamp (JCB) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 4 | 326913 | 04 |  | Actual Reducing Agent Quantity (JCB) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 5 | 326913 | 04 |  | Dosing Module Status (JCB) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 6 | 326913 | 04 |  | Battery Potential / Power Input 1 (SPN 168) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 7 | 326913 | 04 |  | Engine Fuel 1 Injector Metering Rail 1 Pressure (SPN 157) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 8 | 326913 | 04 |  | Engine Turbocharger 2 Boost Pressure (SPN 1128) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 9 | 326913 | 04 |  | Engine Oil Filter Intake Pressure (SPN 1208) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 10 | 326913 | 04 |  | Engine Intake Manifold 4 Temperature (SPN 1133) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 11 | 326913 | 04 |  | Engine Intake Manifold 3 Temperature (SPN 1132) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 12 | 326913 | 04 |  | NO POWER Lamp (Isuzu) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 13 | 326913 | 04 |  | DPF Green Lamp Mode (Isuzu) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 14 | 326913 | 04 |  | EXH.SYSTEM lamp (Isuzu) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26912 | 15 | 326913 | 04 |  | DPF Amber Lamp Mode (Isuzu) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 0 | 326914 | 04 |  | Phys. Torque (Hatz) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 1 | 326914 | 04 |  | Phys. Injection quantity (Hatz) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 2 | 326914 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Intake Temperature (SPN 3242) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 3 | 326914 | 04 |  | Aftertreatment 1 Diesel Oxidation Catalyst Intake Temperature (SPN 4765) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 4 | 326914 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Differential Pressure (SPN 3251) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 5 | 326914 | 04 |  | Aftertreatment 1 Exhaust Gas Mass Flow Rate (SPN 3236) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 6 | 326914 | 04 |  | Wheel Based Vehicle Speed (SPN 84) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 7 | 326914 | 04 |  | Remaining Service Hours (Hatz) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 8 | 326914 | 04 |  | Time left of EIO Operation (Volvo EMS2.4) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 9 | 326914 | 04 |  | Accumulated EIO time (Volvo EMS2.4) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 10 | 326914 | 04 |  | Number of EIO Activations (Volvo EMS2.4) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 11 | 326914 | 04 |  | Engine Emergency (Immediate) Shutdown Indication (SPN 3607 Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 12 | 326914 | 04 |  | Humidity Derate Percentage (Perkins/CAT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 13 | 326914 | 04 |  | Aftertreatment 1 Exhaust Temperature 1 (SPN 3241) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 14 | 326914 | 04 |  | Engine Rating (JCB) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26913 | 15 | 326914 | 04 |  | Successful Stationary Refreshes (JCB) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26914 | 11 | 326915 | 04 |  | Alternator 1 Status (SPN 3353) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26914 | 12 | 326915 | 04 |  | Operator Inducement Time to Torque Derate Level 2 (SPN 7428) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26914 | 13 | 326915 | 04 |  | Engine Coolant Level 1 (SPN 111) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26914 | 14 | 326915 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Parking Brake Not Set (SPN 3710) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26914 | 15 | 326915 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Out of Neutral (SPN 3708) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26915 | 0 | 326916 | 04 |  | Engine Cylinder 1 Ignition Timing (SPN 1413) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26915 | 1 | 326916 | 04 |  | Engine Turbocharger 1 Boost Pressure (SPN 1127) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26915 | 2 | 326916 | 04 |  | Engine Fuel Valve 1 Intake Absolute Pressure (SPN 1390) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26915 | 3 | 326916 | 04 |  | Engine Throttle Valve 1 Position 1 (SPN 51) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 0 | 326917 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Concentration (SPN 3516) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 1 | 326917 | 04 |  | Engine Diesel Particulate Filter Regeneration State (JDEC STAGE V) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 2 | 326917 | 04 |  | Emission-OBD inducement failure reason (Scania) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 3 | 326917 | 04 |  | Emission-OBD inducement state (Scania) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 4 | 326917 | 04 |  | Urea level inducement state (Scania) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 5 | 326917 | 04 |  | Low Idle Increase Desired (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 6 | 326917 | 04 |  | Fuel Filter Heater Status (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 7 | 326917 | 04 |  | Cold Start Heater Status (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 8 | 326917 | 04 |  | DEF Technical Failure (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 9 | 326917 | 04 |  | DEF Quality (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 10 | 326917 | 04 |  | DEF Level (FPT) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 11 | 326917 | 04 |  | DPF Regeneration Countdown Timer (Scania) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 12 | 326917 | 04 |  | DPF Regeneration State (Scania) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 13 | 326917 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Ash Load Percent (SPN 3720) | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 14 | 326917 | 04 |  | Engine Lambda (Yuchai) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26916 | 15 | 326917 | 04 |  | Engine Intake Air Mass Flow Rate (SPN 132) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 0 | 326918 | 04 |  | Fuel rail pressure (Cummins H6) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 1 | 326918 | 04 |  | Blowby flow (Cummins H6) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 2 | 326918 | 04 |  | Engine Fueling Inhibit Allowed (SPN 5795) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 3 | 326918 | 04 |  | Feedback Engine Fueling State (SPN 5794) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 4 | 326918 | 04 |  | Aftertreatment Engine Load Request (SPN 7503) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 5 | 326918 | 04 |  | Aftertreatment Engine Speed Increase request (SPN 7502) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 6 | 326918 | 04 |  | Aftertreatment Thermal Management Status (SPN 7332) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 7 | 326918 | 04 |  | Aftertreatment Ambient Air Temperature (SPN 7441) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 8 | 326918 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Permanent System Lockout (SPN 3715) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 9 | 326918 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Temporary System Lockout (SPN 3714) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 10 | 326918 | 04 |  | Accelerator Pedal Position 2 (SPN 29) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 11 | 326918 | 04 |  | Sensor supply voltage 2 (SPN 3510) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 12 | 326918 | 04 |  | Sensor supply voltage 1 (SPN 3509) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 13 | 326918 | 04 |  | Fuel Pump Primer Status (SPN 4083) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 14 | 326918 | 04 |  | Engine Oil Priming State (SPN 3551) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26917 | 15 | 326918 | 04 |  | Engine Requested Fuel Valve 1 Position (SPN 1765) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 0 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 1 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 2 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 3 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 4 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 5 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 6 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 7 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 8 | 326919 | 04 |  | Intake Manifold Temperature right (Cummins H6) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 9 | 326919 | 04 |  | Intake Manifold Temperature left (Cummins H6) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 10 | 326919 | 04 |  | Intake Manifold pressure right (Cummins H6) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 11 | 326919 | 04 |  | Intake Manifold pressure left (Cummins H6) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 12 | 326919 | 04 |  | Fuel Rank position right (Cummins H6) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 13 | 326919 | 04 |  | Fuel Rank position left (Cummins H6) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 14 | 326919 | 04 |  | Aftercooler water inlet temperature (Cummins H6) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26918 | 15 | 326919 | 04 |  | Timing rail pressure (Cummins H6) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26919 | 0 | 326920 | 04 |  | Engine Ventilation Status (SPN 3554) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26919 | 1 | 326920 | 04 |  | Engine Oil Pre-Heated State (SPN 3552) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26919 | 2 | 326920 | 04 |  | Engine Controlled Shutdown Request (SPN 5795) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26919 | 4 | 326920 | 04 |  | Engine Total Fuel Used (SPN 250) RAW Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26919 | 6 | 326920 | 04 |  | Engine Trip Fuel (SPN 182) RAW Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26919 | 8 | 326920 | 04 |  | Trip Average Fuel Rate (SPN 1029) RAW Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26919 | 9 | 326920 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26919 | 10 | 326920 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26919 | 11 | 326920 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26919 | 12 | 326920 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26919 | 13 | 326920 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26919 | 14 | 326920 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26919 | 15 | 326920 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26920 | 0 | 326921 | 04 |  | Jichai Cooler inlet water temperature Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26920 | 1 | 326921 | 04 |  | Jichai High temperature water inlet temperature Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26920 | 2 | 326921 | 04 |  | Jichai Oil pressure after filtration Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26920 | 3 | 326921 | 04 |  | Jichai Oil pressure of boost Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26920 | 4 | 326921 | 04 |  | Jichai Engine reference torque Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26920 | 5 | 326921 | 04 |  | Jichai Engine torque Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26920 | 6 | 326921 | 04 |  | Jichai WYS Fault code 2.4 Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26920 | 7 | 326921 | 04 |  | Jichai WYS Fault code 2.3 Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26920 | 8 | 326921 | 04 |  | Jichai WYS Fault code 2.2 Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26920 | 9 | 326921 | 04 |  | Jichai WYS Fault code 2.1 Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26920 | 10 | 326921 | 04 |  | Jichai WYS Fault code 1.4 Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26920 | 11 | 326921 | 04 |  | Jichai WYS Fault code 1.3 Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26920 | 12 | 326921 | 04 |  | Jichai WYS Fault code 1.2 Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26920 | 13 | 326921 | 04 |  | Jichai WYS Fault code 1.1 Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26920 | 14 | 326921 | 04 |  | Engine Actual Exhaust 1 Oxygen (SPN 1119) Validity | INT16u | AB |  |  |  |  | X | X
EIC measurements validity | 26920 | 15 | 326921 | 04 |  | Rail pressure (Jichai) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26921 | 0 | 326922 | 04 |  | deSOx heatup request (Scania EMS2 S8) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26921 | 1 | 326922 | 04 |  | Sulphur Regeneration request (Scania EMS2 S8) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26921 | 2 | 326922 | 04 |  | HC Evaporation Action Start Countdown Timer (Scania EMS2 S8) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26921 | 3 | 326922 | 04 |  | HC Evaporation Progress Countdown Timer (Scania EMS2 S8) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26921 | 4 | 326922 | 04 |  | HC Evaporation Required Action (Scania EMS2 S8) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26921 | 5 | 326922 | 04 |  | HC Evaporation Status (Scania EMS2 S8) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26921 | 6 | 326922 | 04 |  | Operator Inducement Severity (Kubota) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26921 | 7 | 326922 | 04 |  | Operator Inducement Reason (Kubota) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26921 | 9 | 326922 | 04 |  | Ash Accumulation Time (Kubota) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26921 | 10 | 326922 | 04 |  | Regeneration Status (Kubota) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26921 | 11 | 326922 | 04 |  | Fuel Injection Quantity (Kubota) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26921 | 12 | 326922 | 04 |  | Engine Gaseous Fuel Supply Pressure 1 (SPN 159) | BOOL | [5 empty] | X | X
EIC measurements validity | 26921 | 13 | 326922 | 04 |  | Engine Fuel Valve 1 Position (SPN 1442) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26921 | 14 | 326922 | 04 |  | Jichai Engine target speed Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26921 | 15 | 326922 | 04 |  | Jichai Engine status Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 0 | 326923 | 04 |  | Doosan stage 5 Emission OBD Inducement lamp status Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 1 | 326923 | 04 |  | JiChai JC15T JG Gas Supply Amount Per Second Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 2 | 326923 | 04 |  | JiChai JC15T JG Natural Gas Pressure Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 3 | 326923 | 04 |  | JiChai JC15T JG PHI Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 4 | 326923 | 04 |  | JiChai JC15T JG Natural Gas Temperature Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 5 | 326923 | 04 |  | JiChai JC15T JG Air Fuel Ratio Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 6 | 326923 | 04 |  | JiChai JC15T JG Fuel Valve CloseLoop-Adjust Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 7 | 326923 | 04 |  | JiChai JC15T JG Fuel Valve Self-Adjust Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 8 | 326923 | 04 |  | SCR System Cleaning Forced Status (SPN 6934) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 9 | 326923 | 04 |  | SCR System Cleaning Lamp Command (SPN 6915) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 10 | 326923 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 11 | 326923 | 04 |  | Doosan stage 5 ash lamp status Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 12 | 326923 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 12 | 326923 | 04 |  | Weichai Engine Oil Pressure Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 13 | 326923 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 13 | 326923 | 04 |  | Engine Fuel Flow Rate 1 Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 14 | 326923 | 04 |  | Engine Fuel Valve 1 Differential Pressure Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26922 | 15 | 326923 | 04 |  | Insulation resistance (KWG ISO5 isolation monitor) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26923 | 0 | 326924 | 04 |  | Weichai H2S Concentration Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26923 | 1 | 326924 | 04 |  | Weichai CH4 Concentration Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26923 | 2 | 326924 | 04 |  | Weichai Air Filter DP Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26923 | 3 | 326924 | 04 |  | Weichai Humidity Sensor Air Temperature Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26923 | 4 | 326924 | 04 |  | Weichai Relative Humidity Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26923 | 5 | 326924 | 04 |  | Weichai Altronic Supply Voltage Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26923 | 6 | 326924 | 04 |  | Weichai Altronic RPM Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26923 | 7 | 326924 | 04 |  | Weichai Bypass Valve 1 Position Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26923 | 8 | 326924 | 04 |  | Weichai Throttle 2 Position Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26923 | 9 | 326924 | 04 |  | Weichai Throttle 1 Position Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26923 | 10 | 326924 | 04 |  | Weichai Pre-throttle Pressure 1 Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26923 | 11 | 326924 | 04 |  | Weichai Engine Oil Pressure Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26923 | 15 | 326924 | 04 |  | Doosan stage 5 Emission OBD lamp failure reason Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26924 | 2 | 326925 | 04 |  | Aftertreatment 2 SCR Intake NOx 2 (SPN 7671) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26924 | 3 | 326925 | 04 |  | Aftertreatment 1 SCR Intake NOx 2 (SPN 7649) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26924 | 5 | 326925 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Time since Last Active Regeneration (SPN 3721) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26924 | 6 | 326925 | 04 |  | Jing Guan Exhaust temperature Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26924 | 7 | 326925 | 04 |  | Jing Guan Fuel temperature Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26924 | 8 | 326925 | 04 |  | Deutz EMR5 SCR warning Lamp / EAT inducement Lamp Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26924 | 9 | 326925 | 04 |  | Deutz EMR5 Standstill request reason Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26924 | 10 | 326925 | 04 |  | FPT EGR / DPF operator inducement Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26924 | 11 | 326925 | 04 |  | FPT HC level Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26924 | 12 | 326925 | 04 |  | DPF Active Regeneration Inhibited Due to System Fault Active (SPN 3712) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26924 | 13 | 326925 | 04 |  | Fan Speed (SPN 1639) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26924 | 14 | 326925 | 04 |  | Weichai Engine Exhaust O2 Sensor Fueling Correction Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26924 | 15 | 326925 | 04 |  | Weichai Closed Loop Correction Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26925 | 0 | 326926 | 04 |  | Engine Oil Priming Pump Switch (SPN 3550) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26925 | 1 | 326926 | 04 |  | Engine Throttle Valve 1 Differential Pressure (SPN 5631) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26925 | 2 | 326926 | 04 |  | Engine Throttle 2 Position (SPN 3673) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26925 | 3 | 326926 | 04 |  | Engine Fuel Valve 1 Outlet Absolute Pressure (SPN 2980) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26925 | 4 | 326926 | 04 |  | Engine Fuel Valve 2 Position (SPN 1443) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 0 | 326927 | 04 |  | Engine Cylinder 13 Knock Level (SPN 1364, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 1 | 326927 | 04 |  | Engine Cylinder 12 Knock Level (SPN 1363, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 2 | 326927 | 04 |  | Engine Cylinder 11 Knock Level (SPN 1362, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 3 | 326927 | 04 |  | Engine Cylinder 10 Knock Level (SPN 1361, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 4 | 326927 | 04 |  | Engine Cylinder 9 Knock Level (SPN 1360, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 5 | 326927 | 04 |  | Engine Cylinder 8 Knock Level (SPN 1359, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 6 | 326927 | 04 |  | Engine Cylinder 7 Knock Level (SPN 1358, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 7 | 326927 | 04 |  | Engine Cylinder 6 Knock Level (SPN 1357, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 8 | 326927 | 04 |  | Engine Cylinder 5 Knock Level (SPN 1356, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 9 | 326927 | 04 |  | Engine Cylinder 4 Knock Level (SPN 1355, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 10 | 326927 | 04 |  | Engine Cylinder 3 Knock Level (SPN 1354, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 11 | 326927 | 04 |  | Engine Cylinder 2 Knock Level (SPN 1353, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 12 | 326927 | 04 |  | Engine Cylinder 1 Knock Level (SPN 1352, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 13 | 326927 | 04 |  | Accelerator Pedal 1 Low Idle Switch (SPN 558) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 14 | 326927 | 04 |  | Instantaneous Estimated Brake Power (SPN 1242) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26926 | 15 | 326927 | 04 |  | Engine Gas Mass Flow Rate 1 (SPN 1241) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 0 | 326928 | 04 |  | Cylinder 13 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 1 | 326928 | 04 |  | Cylinder 12 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 2 | 326928 | 04 |  | Cylinder 11 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 3 | 326928 | 04 |  | Cylinder 10 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 4 | 326928 | 04 |  | Cylinder 9 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 5 | 326928 | 04 |  | Cylinder 8 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 6 | 326928 | 04 |  | Cylinder 7 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 7 | 326928 | 04 |  | Cylinder 6 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 8 | 326928 | 04 |  | Cylinder 5 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 9 | 326928 | 04 |  | Cylinder 4 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 10 | 326928 | 04 |  | Cylinder 3 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 11 | 326928 | 04 |  | Cylinder 2 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 12 | 326928 | 04 |  | Cylinder 1 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 13 | 326928 | 04 |  | Engine Cylinder 16 Knock Level (SPN 1367, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 14 | 326928 | 04 |  | Engine Cylinder 15 Knock Level (SPN 1366, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26927 | 15 | 326928 | 04 |  | Engine Cylinder 14 Knock Level (SPN 1365, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 0 | 326929 | 04 |  | Engine Cylinder 14 Ignition Timing (SPN 1426, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 1 | 326929 | 04 |  | Engine Cylinder 13 Ignition Timing (SPN 1425, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 2 | 326929 | 04 |  | Engine Cylinder 12 Ignition Timing (SPN 1424, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 3 | 326929 | 04 |  | Engine Cylinder 11 Ignition Timing (SPN 1423, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 4 | 326929 | 04 |  | Engine Cylinder 10 Ignition Timing (SPN 1422, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 5 | 326929 | 04 |  | Engine Cylinder 9 Ignition Timing (SPN 1421, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 6 | 326929 | 04 |  | Engine Cylinder 8 Ignition Timing (SPN 1420, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 7 | 326929 | 04 |  | Engine Cylinder 7 Ignition Timing (SPN 1419, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 8 | 326929 | 04 |  | Engine Cylinder 6 Ignition Timing (SPN 1418, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 9 | 326929 | 04 |  | Engine Cylinder 5 Ignition Timing (SPN 1417, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 10 | 326929 | 04 |  | Engine Cylinder 4 Ignition Timing (SPN 1416, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 11 | 326929 | 04 |  | Engine Cylinder 3 Ignition Timing (SPN 1415, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 12 | 326929 | 04 |  | Engine Cylinder 2 Ignition Timing (SPN 1414, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 13 | 326929 | 04 |  | Cylinder 16 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 14 | 326929 | 04 |  | Cylinder 15 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26928 | 15 | 326929 | 04 |  | Cylinder 14 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 0 | 326930 | 04 |  | Engine Spark Plug 14 (SPN 1307, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 1 | 326930 | 04 |  | Engine Spark Plug 13 (SPN 1306, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 2 | 326930 | 04 |  | Engine Spark Plug 12 (SPN 1305, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 3 | 326930 | 04 |  | Engine Spark Plug 11 (SPN 1304, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 4 | 326930 | 04 |  | Engine Spark Plug 10 (SPN 1303, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 5 | 326930 | 04 |  | Engine Spark Plug 9 (SPN 1302, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 6 | 326930 | 04 |  | Engine Spark Plug 8 (SPN 1301, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 7 | 326930 | 04 |  | Engine Spark Plug 7 (SPN 1300, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 8 | 326930 | 04 |  | Engine Spark Plug 6 (SPN 1299, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 9 | 326930 | 04 |  | Engine Spark Plug 5 (SPN 1298, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 10 | 326930 | 04 |  | Engine Spark Plug 4 (SPN 1297, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 11 | 326930 | 04 |  | Engine Spark Plug 3 (SPN 1296, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 12 | 326930 | 04 |  | Engine Spark Plug 2 (SPN 1295, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 13 | 326930 | 04 |  | Engine Spark Plug 1 (SPN 1294, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 14 | 326930 | 04 |  | Engine Cylinder 16 Ignition Timing (SPN 1428, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26929 | 15 | 326930 | 04 |  | Engine Cylinder 15 Ignition Timing (SPN 1427, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 0 | 326931 | 04 |  | Aftertreatment 1 Total Diesel Exhaust Fluid Used (SPN 5963) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 1 | 326931 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Pump Drive Percentage (SPN 4375) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 2 | 326931 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Fill Valve Command (SPN 5434) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 3 | 326931 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Quick Thaw Tank Volume (SPN 4367) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 4 | 326931 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Quick Thaw Temperature (SPN 4368) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 5 | 326931 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Doser Pressure (SPN 6875) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 6 | 326931 | 04 |  | Aftertreatment 1 SCR Intake Pressure (SPN 6586) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 7 | 326931 | 04 |  | Aftertreatment 1 SCR System State (SPN 4332) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 8 | 326931 | 04 |  | Aftertreatment DEF Dosing Mode Status (SPN 9176) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 9 | 326931 | 04 |  | Aftertreatment System Enable Status (SPN 7851) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 10 | 326931 | 04 |  | Aftertreatment 1 SCR System Hydrocarbon (SPN 7934) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 11 | 326931 | 04 |  | Water In Fuel Indicator 2 (SPN 6301) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 12 | 326931 | 04 |  | Sea Water Pump Outlet Pressure (SPN 2435) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 13 | 326931 | 04 |  | Engine extended range oil filter diff press (SPN 6321) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 14 | 326931 | 04 |  | Engine Spark Plug 16 (SPN 1309, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26930 | 15 | 326931 | 04 |  | Engine Spark Plug 15 (SPN 1308, Cummins) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26931 | 0 | 326932 | 04 |  | EIC Time remaining to inducement act (Kohler KDI3404) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26931 | 1 | 326932 | 04 |  | Emission Control System Operator Inducement Severity (SPN 5826) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26931 | 2 | 326932 | 04 |  | Driver Warning System Indicator Status (SPN 5825) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26931 | 3 | 326932 | 04 |  | Pedal Input Delay (Kohler KDI3404) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26931 | 4 | 326932 | 04 |  | SCR operator inducement reason Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26931 | 5 | 326932 | 04 |  | Restriction level according to anti-tampering Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26931 | 6 | 326932 | 04 |  | Restriction level according to NOx reduction Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26931 | 7 | 326932 | 04 |  | Restriction caused by standstill request Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26931 | 8 | 326932 | 04 |  | DEF tank level – Thresholds Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26931 | 9 | 326932 | 04 |  | Restriction level according to DEF tank level Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26931 | 10 | 326932 | 04 |  | Engine Fuel Leakage 1 (SPN 1239) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26931 | 12 | 326932 | 04 |  | Engine Fuel Rate (High Resolution) (SPN 1600) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26931 | 14 | 326932 | 04 |  | Total Aftertreatment Operating Hours (SPN 8629) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 0 | 326933 | 04 |  | EIC Road Speed Limit Status (SPN 1437) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 1 | 326933 | 04 |  | EIC Accelerator Pedal Kickdown Switch (SPN 559) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 2 | 326933 | 04 |  | EIC Engine Extended Crankcase Blowby Pressure (SPN 22) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 3 | 326933 | 04 |  | EIC Charge Air Cooler Thermostat Opening (SPN 1134) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 4 | 326933 | 04 |  | EIC Aftertreatment 2 Exhaust Dew Point (SPN 3240) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 5 | 326933 | 04 |  | EIC Aftertreatment 2 Intake Dew Point (SPN 3239) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 6 | 326933 | 04 |  | EIC Aftertreatment 1 Exhaust Dew Point (SPN 3238) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 7 | 326933 | 04 |  | EIC Aftertreatment 1 Intake Dew Point (SPN 3237) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 8 | 326933 | 04 |  | EIC Estimated Engine Parasitic Losses (SPN 2978) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 9 | 326933 | 04 |  | EIC Engine Desired Speed Asymmetrical Adjustment (SPN 519) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 10 | 326933 | 04 |  | EIC Actual Engine - Percent Torque (Fractional) (SPN 4154) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 11 | 326933 | 04 |  | EIC Engine Torque Mode (SPN 899) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 12 | 326933 | 04 |  | EIC Engine Fuel Filter (suction side) Differential Pressure #2 (YC-ECU-A) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 13 | 326933 | 04 |  | EIC Engine Fuel Supply Pump Intake Pressure #2 (YC-ECU-A) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 14 | 326933 | 04 |  | EIC Fuel Pre Fltr Dif Press (Mitsubishi MGS3100) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26932 | 15 | 326933 | 04 |  | EIC Fuel Main Fltr Out Press L (Mitsubishi MGS3100) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26933 | 3 | 326934 | 04 |  | EIC Transmission Shift Inhibit Indicator (SPN 1851, CVT transmission) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26933 | 4 | 326934 | 04 |  | EIC Transmission Engine Crank Enable (SPN 2900, CVT transmission) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26933 | 5 | 326934 | 04 |  | EIC Transmission Actual Gear Ratio (SPN 526, CVT transmission) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26933 | 6 | 326934 | 04 |  | EIC Transmission Oil Temperature 1 (SPN 177, CVT transmission) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26933 | 7 | 326934 | 04 |  | EIC Road Surface Temperature (SPN 79) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26933 | 8 | 326934 | 04 |  | EIC Cab Interior Temperature (SPN 170) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26933 | 10 | 326934 | 04 |  | EIC Engine Total Revolutions (SPN 249) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26933 | 11 | 326934 | 04 |  | EIC Estimated Pumping Percentage Torque (SPN 5398) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26933 | 12 | 326934 | 04 |  | EIC Momentary Engine Maximum Power Enable Feedback (SPN 5021) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26933 | 13 | 326934 | 04 |  | EIC Vehicle Acceleration Rate Limit Status (SPN 2979) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26933 | 14 | 326934 | 04 |  | EIC Remote Accelerator Pedal Position (SPN 974) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26933 | 15 | 326934 | 04 |  | EIC Accelerator Pedal 2 Low Idle Switch (SPN 2970) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26934 | 0 | 326935 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26934 | 1 | 326935 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
EIC measurements validity | 26934 | 2 | 326935 | 04 |  | Aftertreatment 2 Intake %O2 (SPN 3256) | BOOL | AB |  |  |  |  | X | X
EIC measurements validity | 26934 | 3 | 326935 | 04 |  | Engine Throttle position 2 (Kingbang) | BOOL | AB |  |  |  |  | X | X
EIC measurements validity | 26934 | 4 | 326935 | 04 |  | OBD Malfunction Indicator Lamp Command (SPN 5080) | BOOL | AB |  |  |  |  | X | X
EIC measurements validity | 26934 | 5 | 326935 | 04 |  | Operator Inducement Time to Torque Derate Level 3/FINAL (SPN 7719) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26935 | 14 | 326936 | 04 |  | Diesel Particulate Filter Active Regeneration Forced Status (SPN 4175) Validity | BOOL | [5 empty] | X | X
EIC measurements validity | 26935 | 15 | 326936 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X
Plant config | 36000 |  | 336001 | 04 |  | Plant option - Plant type | INT16s | AB | 0 |  | X | X | X | X
Plant config | 36001 |  | 336002 | 04 |  | Plant option - PMS CAN | INT16s | AB | 0 |  | X | X | X | X
Plant config | 36002 |  | 336003 | 04 |  | Plant source ID 1 | INT16s | AB | 0 |  | X | X | X | X
Plant config | 36003 |  | 336004 | 04 |  | Plant source ID 2 | INT16s | AB | 0 |  | X | X | X | X
Plant config | 36026 |  | 336027 | 04 |  | Plant source ID 25 | INT16s | AB | 0 |  | X | X | X | X
Plant config | 36027 |  | 336028 | 04 |  | Plant source ID 26 | INT16s | AB | 0 |  | X | X | X | X
Plant config | 36028 |  | 336029 | 04 |  | Plant source ID 27 | INT16s | AB | 0 |  | X | X | X | X
Plant config | 36029 |  | 336030 | 04 |  | Plant source ID 28 | INT16s | AB | 0 |  | X | X | X | X
Plant config | 36033 |  | 336034 | 04 |  | Plant source ID 32 | INT16s | AB | 0 |  | X | X | X | X
Plant config | 36034 |  | 336035 | 04 |  | Plant source ID 33 | INT16s | AB | 0 |  | X | X | X | X
Plant config | 36035 |  | 336036 | 04 |  | Plant source ID 34 | INT16s | AB | 0 |  | X | X | X | X