## Descriptions
ASC-4 Battery and ASC 150 Storage Modbus client
Software version
The information contained in these tables (Revision G) is applicable to:
ASC-4 software version 4.29.0
ASC 150 software version 1.20.0
See the ASC-4 Modbus client User manual and the ASC 150 Modbus client User manual for more information.
Row | Hyperlink index
15 | Modbus function codes
21 | Output holding register
26 | Input register
Back to index | Modbus function codes
| Function code | Description
| 04 | Read a single or multiple input registers.
| 06 | Write a value to a single output holding register.
| 16 | Write a value to multiple consecutive output holding registers.
Back to index | Output holding register (function code 06 or 16: Write)
| Function group | Description
| Configuration | Writes one bit to activate the configuration. 0 (false) when the configuration is not activated. 1 (true) when the configuration is activated.
| Control command | Activate a command.
Back to index | Input register (function code 04: Read)
| Function group | Description
| AC measurement | Read the operating value of the AC measurement.
| Alarm | Read one bit to see whether the alarm is activated. 0 (false) when the alarm is not activated. 1 (true) when the alarm is activated.
| Configuration | Read the configured value.
| DC measurement | Read the operating value of the DC measurement.
| Measurement | Read the operating value of the measurement.
| Status | Read the status.

## BCU PCS DEIF Generic
BCU/PCS data scheme
DEIF Generic is selected in ESS Protocol (parameter 7561).
* For 32-bit integers, only the first Modbus address is listed. The DEIF generic offset (parameter 7960) is 30000 (default).
** This register is only relevant for ASC 150 Storage in a greenfield installation, with ground relay activated.
Note: To prevent problems with future expansions of the protocol, allow writing of all registers from 0 to 99, and reading of all registers from 30000 to 30099.
Function group | Modbus address (offset 30000)* | Modbus address (offset 1000) | Bit | Function code | BCU/PCS function name | Data type | Data format | Scaling (10⁻ˣ) | Range | Unit | ASC Modbus server address (function code 03) | ASC parameter
Control command | 0 | 0 |  | 06; 16 | ESS start/stop 0 = Stop 1 = Start | INT16s | AB | 0
Control command | 1 | 1 |  | 06; 16 | ESS mode 0 = P/Q mode (grid-tie) 1 = V/f mode (island/off grid/grid forming) 2 = Droop mode (V/f) | INT16s | AB | 0
Control command | 2 | 2 |  | 06; 16 | P set point (% of nominal power or kW) | INT16s | AB | 1 / 0 | -100.0% to 100.0% / -100% to 100% / -3000.0kW to 3000.0kW / -30000kW to 30000kW | % / kW
Control command | 3 | 3 |  | 06; 16 | Q set point (% of nominal reactive power or kvar) | INT16s | AB | 1 / 0 | -100.0% to 100.0% / -100% to 100% / -3000.0kvar to 3000.0kvar / -30000kvar to 30000kvar | % / kvar
Control command | 4 | 4 |  | 06; 16 | Frequency set point (used for nominal f and synchronising) | INT32s | ABCD | 3 | 45 to 65 | Hz
Control command | 6 | 6 |  | 06; 16 | Voltage set point | INT32s | ABCD | 1 | 350 to 550 | V
Control command | 8 | 8 |  | 06; 16 | Droop delta frequency set point for V/f operation (island and droop) | INT16s | AB | 3 | -5 to 5 | Hz
Control command | 9 | 9 |  | 06; 16 | Droop delta voltage set point for V/f operation (island and droop) | INT16s | AB | 1 | -100 to 100 | V
Control command | 10 | 10 |  | 06; 16 | Heart beat (toggle 0x55AA/0xAA55 for each cycle) | INT16s | AB | 0
Configuration | 11 | 11 | 0 | 06; 16 | Phase rotation 0 = L1L2L3 1 = L1L3L2 | BOOL
Configuration | 11 | 11 | 1-2 | 06; 16 | Reserved | BOOL
Configuration | 11 | 11 | 3 | 06; 16 | Activated by ASC M-Logic "Custom input to ESS" | BOOL
Configuration | 11 | 11 | 4 | 06; 16 | Activated by ASC M-Logic "Ack. alarms on ESS" | BOOL
Configuration | 11 | 11 | 5 | 06; 16 | Activated by ASC M-Logic "Ack. Alarms on BMS" | BOOL
Configuration | 11 | 11 | 6 - 15 | 06; 16 | Reserved
Control command | 12 | 12 |  | 06; 16 | Ground relay 0 = Open ground relay 1 = Close ground relay** | BOOL
AC measurement | 30000 | 1000 |  | 4 | Frequency slope | INT32s | ABCD | 1 |  | % P/Hz | 40315
AC measurement | 30002 | 1002 |  | 4 | Voltage slope | INT32s | ABCD | 1 |  | % Q/V | 40316
AC measurement | 30004 | 1004 |  | 4 | Actual active power production (P) | INT32s | ABCD | 1 |  | kW | 40102
AC measurement | 30006 | 1006 |  | 4 | Actual reactive power production (Q) | INT32s | ABCD | 1 |  | kvar | 40122
AC measurement | 30008 | 1008 |  | 4 | Actual apparent power production (S) | INT32s | ABCD | 1 |  | kVA | 40124
AC measurement | 30010 | 1010 |  | 4 | Actual voltage L1-L2 | INT32s | ABCD | 1 | 350 to 550 | V | 40336
AC measurement | 30012 | 1012 |  | 4 | Actual voltage L2-L3 | INT32s | ABCD | 1 | 350 to 550 | V | 40337
AC measurement | 30014 | 1014 |  | 4 | Actual voltage L3-L1 | INT32s | ABCD | 1 | 350 to 550 | V | 40338
AC measurement | 30016 | 1016 |  | 4 | Actual frequency | INT32s | ABCD | 3 | 0 to 70 | Hz | 40342
Alarm | 30018 | 1018 | 0 | 4 | BCU/PCS warning. 0 = No alarm, 1 = Alarm activated | BOOL |  |  |  |  | 40343 | 7580
Alarm | 30018 | 1018 | 1 | 4 | BCU/PCS shutdown. 0 = No alarm, 1 = Alarm activated | BOOL |  |  |  |  | 40343 | 7590
Status | 30019 | 1019 |  | 4 | ESS status 0 = Stopped / Fault 1 = Standby 2 = P/Q 3 = V/f 4 = Droop 5 = Wait | INT16s | ABCD | 1 |  | A | 40324
Configuration | 30020 | 1020 | 0 | 4 | Reserved | [5 empty] | 40369
Configuration | 30020 | 1020 | 1 | 4 | P/Q set point format 0 = % (default) 1 = kW/kvar | BOOL |  |  |  |  | 40369
Configuration | 30020 | 1020 | 2 | 4 | P/Q set point scaling 0 = 1 decimal (default) 1 = 0 decimals | BOOL |  |  |  |  | 40369
Configuration | 30020 | 1020 | 3 | 4 | Activate ASC M-Logic "Custom output 1 from EMS" | BOOL |  |  |  |  | 40369
Configuration | 30020 | 1020 | 4 | 4 | Activate ASC M-Logic "Custom output 2 from EMS" | BOOL |  |  |  |  | 40369
Configuration | 30020 | 1020 | 5 | 4 | Activate ASC M-Logic "Custom output 3 from EMS" | BOOL |  |  |  |  | 40369
Configuration | 30020 | 1020 | 6 - 15 | 4 | Reserved | [5 empty] | 40369
Note on A8: More information about each function group is available in the description sheet.
Note on D8: Bit location of the function in the associated Modbus address.
Note on E8: 04 - Read single or multiple 06 or 16 - Write
Note on F8: The controller function name shows the name of the parameter in the Utility Software. Some functions might contain additional information.
Note on H8: AB - Most significant byte first ABCD - Most significant byte first and most significant word first
Note on I8: Example: Scaling = 1 Read Data = 266 Actual value = 26,6
Note on K8: Unit of the associated function

## BCU BMS DEIF Generic
BCU/BMS data scheme
DEIF Generic is selected in BMS Protocol (parameter 7681).
* For 32-bit integers, only the first Modbus address is listed. The DEIF generic offset (parameter 7960) is 30000 (default).
Note: To prevent problems with future expansions of the protocol, allow reading of all registers from 30100 to 30199.
Function group | Modbus address (offset 30000)* | Modbus address (offset 1000)* | Bit | Function code | BCU/BMS function name | Data type | Data format | Scaling (10⁻ˣ) | Range | Unit | ASC Modbus slave address (function code 03) | ASC parameter
AC measurement | 30100 | 1100 |  | 4 | Maximum charge | INT32s | ABCD | 1 |  | kW | 40311
AC measurement | 30102 | 1102 |  | 4 | Maximum discharge | INT32s | ABCD | 1 |  | kW | 40309
Measurement | 30104 | 1104 |  | 4 | State of charge (% of nominal capacity) | INT16s | AB | 2 | 0 to 100 | % | 40300
Measurement | 30105 | 1105 |  | 4 | State of health (% of nominal capacity) | INT16s | AB | 2 | 0 to 100 | % | 40317
DC measurement | 30106 | 1106 |  | 4 | DC battery voltage | INT16s | AB | 0 |  | V | 40318
DC measurement | 30107 | 1107 |  | 4 | DC battery current | INT32s | ABCD | 1 |  | A | 40326
Alarm | 30109 | 1109 | 0 | 4 | Warning. 0 = No alarm, 1= Alarm activated | BOOL |  |  |  |  | 40360 | 7610
Alarm | 30109 | 1109 | 1 | 4 | Shutdown. 0 = No alarm, 1= Alarm activated | BOOL |  |  |  |  | 40360 | 7620
Configuration | 30110 | 1110 | 0 | 4 | Activate ASC M-Logic "Custom output from BMS" | [5 empty] | 40370
Configuration | 30110 | 1110 | 1-15 | 4 | Reserved | [5 empty] | 40370
Note on A7: More information about each function group is available in the description sheet.
Note on D7: Bit location of the function in the associated Modbus address.
Note on E7: 04 - Read single or multiple
Note on F7: The controller function name shows the name of the parameter in the Utility Software. Some functions might contain additional information.
Note on H7: AB - Most significant byte first ABCD - Most significant byte first and most significant word first
Note on I7: Example: Scaling = 1 Read Data = 266 Actual value = 26,6
Note on K7: Unit of the associated function