Alarm status: Delay timer remaining time | 24621 |  | 324622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24621 |  | 324622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24622 |  | 324623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24622 |  | 324623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24622 |  | 324623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24623 |  | 324624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24623 |  | 324624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24623 |  | 324624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24624 |  | 324625 | Parameters - Generator - Current protections - Over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24624 |  | 324625 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24624 |  | 324625 | Parameters - Mains - Current protections - Over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24625 |  | 324626 | Parameters - Generator - Current protections - Over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24625 |  | 324626 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24625 |  | 324626 | Parameters - Mains - Current protections - Over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24626 |  | 324627 | Parameters - Generator - Current protections - Over-current 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24626 |  | 324627 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24626 |  | 324627 | Parameters - Mains - Current protections - Over-current 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24627 |  | 324628 | Parameters - Generator - Current protections - Over-current 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24627 |  | 324628 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24627 |  | 324628 | Parameters - Mains - Current protections - Over-current 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24628 |  | 324629 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24628 |  | 324629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24628 |  | 324629 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24629 |  | 324630 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24629 |  | 324630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24629 |  | 324630 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24630 |  | 324631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24630 |  | 324631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24630 |  | 324631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24631 |  | 324632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24631 |  | 324632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24631 |  | 324632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24632 |  | 324633 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24632 |  | 324633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24632 |  | 324633 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24633 |  | 324634 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24633 |  | 324634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24633 |  | 324634 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24634 |  | 324635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24635 |  | 324636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24636 |  | 324637 | Parameters - Generator - Current protections - Negative sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24636 |  | 324637 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24636 |  | 324637 | Parameters - Mains - Current protections - Negative sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24637 |  | 324638 | Parameters - Generator - Current protections - Zero sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24637 |  | 324638 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24637 |  | 324638 | Parameters - Mains - Current protections - Zero sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24638 |  | 324639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24638 |  | 324639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24638 |  | 324639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24639 |  | 324640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24639 |  | 324640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24639 |  | 324640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24640 |  | 324641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24640 |  | 324641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24640 |  | 324641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24641 |  | 324642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24641 |  | 324642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24641 |  | 324642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24642 |  | 324643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24642 |  | 324643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24642 |  | 324643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24643 |  | 324644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24643 |  | 324644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24643 |  | 324644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24644 |  | 324645 | Parameters - Generator - Power protections - Overload 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24644 |  | 324645 | Parameters - Busbar A - Power protections - Power export 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24644 |  | 324645 | Parameters - Mains - Power protections - Overload 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24645 |  | 324646 | Parameters - Generator - Power protections - Overload 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24645 |  | 324646 | Parameters - Busbar A - Power protections - Power export 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24645 |  | 324646 | Parameters - Mains - Power protections - Overload 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24646 |  | 324647 | Parameters - Generator - Power protections - Overload 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24646 |  | 324647 | Parameters - Busbar A - Power protections - Power export 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24646 |  | 324647 | Parameters - Mains - Power protections - Overload 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24647 |  | 324648 | Parameters - Generator - Power protections - Overload 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24647 |  | 324648 | Parameters - Busbar A - Power protections - Power export 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24647 |  | 324648 | Parameters - Mains - Power protections - Overload 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24648 |  | 324649 | Parameters - Generator - Power protections - Overload 5 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24648 |  | 324649 | Parameters - Busbar A - Power protections - Power export 5 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24648 |  | 324649 | Parameters - Mains - Power protections - Overload 5 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24649 |  | 324650 | Parameters - Generator - Power protections - Reverse power 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24649 |  | 324650 | Parameters - Busbar A - Power protections - Power import 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24649 |  | 324650 | Parameters - Mains - Power protections - Reverse power 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24650 |  | 324651 | Parameters - Generator - Power protections - Reverse power 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24650 |  | 324651 | Parameters - Busbar A - Power protections - Power import 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24650 |  | 324651 | Parameters - Mains - Power protections - Reverse power 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24651 |  | 324652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24651 |  | 324652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24651 |  | 324652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24652 |  | 324653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24652 |  | 324653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24652 |  | 324653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24653 |  | 324654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24653 |  | 324654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24653 |  | 324654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24654 |  | 324655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24654 |  | 324655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24654 |  | 324655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24655 |  | 324656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24655 |  | 324656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24655 |  | 324656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24656 |  | 324657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24656 |  | 324657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24656 |  | 324657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24657 |  | 324658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24657 |  | 324658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24657 |  | 324658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24658 |  | 324659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24658 |  | 324659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24658 |  | 324659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24659 |  | 324660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24659 |  | 324660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24659 |  | 324660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24660 |  | 324661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24660 |  | 324661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24660 |  | 324661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24661 |  | 324662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24661 |  | 324662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24661 |  | 324662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24662 |  | 324663 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24662 |  | 324663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24662 |  | 324663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24663 |  | 324664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24663 |  | 324664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24663 |  | 324664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24664 |  | 324665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24664 |  | 324665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24664 |  | 324665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24665 |  | 324666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24665 |  | 324666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24665 |  | 324666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24666 |  | 324667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24666 |  | 324667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24666 |  | 324667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24667 |  | 324668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24667 |  | 324668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24667 |  | 324668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24668 |  | 324669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24668 |  | 324669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24668 |  | 324669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24669 |  | 324670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24669 |  | 324670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24669 |  | 324670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24670 |  | 324671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24670 |  | 324671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24670 |  | 324671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24671 |  | 324672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24671 |  | 324672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24671 |  | 324672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24672 |  | 324673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X
Alarm status: Delay timer remaining time | 24672 |  | 324673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X |  | X | X
Alarm status: Delay timer remaining time | 24672 |  | 324673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24854 |  | 324855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X
Alarm status: Delay timer remaining time | 24854 |  | 324855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24854 |  | 324855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
Alarm status: Delay timer remaining time | 24855 |  | 324856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X
Alarm status: Delay timer remaining time | 24855 |  | 324856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
Alarm status: Delay timer remaining time | 24857 |  | 324858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24858 |  | 324859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24859 |  | 324860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24860 |  | 324861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24861 |  | 324862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24862 |  | 324863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24863 |  | 324864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24864 |  | 324865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24865 |  | 324866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24866 |  | 324867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24867 |  | 324868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24868 |  | 324869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24869 |  | 324870 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24870 |  | 324871 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24871 |  | 324872 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24872 |  | 324873 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24873 |  | 324874 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24874 |  | 324875 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24875 |  | 324876 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24876 |  | 324877 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24878 |  | 324879 | Parameters - System - Monitoring - Data loss from a controller - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24879 |  | 324880 | Parameters - System - Monitoring - Data loss on DEIF network - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24880 |  | 324881 | Parameters - System - Monitoring - High traffic on DEIF network - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24881 |  | 324882 | Card configuration failed - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24883 |  | 324884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24884 |  | 324885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24885 |  | 324886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X
Alarm status: Delay timer remaining time | 24886 |  | 324887 | Licence error - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25500 |  | 325501 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25501 |  | 325502 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25502 |  | 325503 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25503 |  | 325504 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25504 |  | 325505 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25505 |  | 325506 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25506 |  | 325507 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25507 |  | 325508 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25508 |  | 325509 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25509 |  | 325510 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25510 |  | 325511 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25511 |  | 325512 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25512 |  | 325513 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25513 |  | 325514 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25514 |  | 325515 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25515 |  | 325516 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25516 |  | 325517 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25517 |  | 325518 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25518 |  | 325519 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25519 |  | 325520 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25520 |  | 325521 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25521 |  | 325522 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25522 |  | 325523 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25523 |  | 325524 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25524 |  | 325525 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25525 |  | 325526 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25526 |  | 325527 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25527 |  | 325528 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25528 |  | 325529 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25529 |  | 325530 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25530 |  | 325531 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25531 |  | 325532 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25532 |  | 325533 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25533 |  | 325534 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25534 |  | 325535 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25535 |  | 325536 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25536 |  | 325537 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25537 |  | 325538 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25538 |  | 325539 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25539 |  | 325540 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25540 |  | 325541 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25541 |  | 325542 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25542 |  | 325543 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25543 |  | 325544 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25544 |  | 325545 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25545 |  | 325546 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25546 |  | 325547 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25547 |  | 325548 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25548 |  | 325549 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25549 |  | 325550 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25600 |  | 325601 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25601 |  | 325602 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25602 |  | 325603 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25603 |  | 325604 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25604 |  | 325605 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25605 |  | 325606 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25606 |  | 325607 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25607 |  | 325608 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25608 |  | 325609 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25609 |  | 325610 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25610 |  | 325611 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25611 |  | 325612 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25612 |  | 325613 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25613 |  | 325614 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25614 |  | 325615 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25615 |  | 325616 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25616 |  | 325617 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25617 |  | 325618 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25618 |  | 325619 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25619 |  | 325620 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25620 |  | 325621 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25621 |  | 325622 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25622 |  | 325623 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25623 |  | 325624 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25624 |  | 325625 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25625 |  | 325626 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25626 |  | 325627 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25627 |  | 325628 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25628 |  | 325629 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25629 |  | 325630 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25630 |  | 325631 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25631 |  | 325632 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25632 |  | 325633 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25633 |  | 325634 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25634 |  | 325635 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25635 |  | 325636 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25636 |  | 325637 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25637 |  | 325638 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25638 |  | 325639 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25639 |  | 325640 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25640 |  | 325641 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25641 |  | 325642 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25642 |  | 325643 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25643 |  | 325644 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25644 |  | 325645 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25645 |  | 325646 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25646 |  | 325647 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25647 |  | 325648 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25648 |  | 325649 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25649 |  | 325650 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25650 |  | 325651 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25651 |  | 325652 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25652 |  | 325653 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25653 |  | 325654 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25654 |  | 325655 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25655 |  | 325656 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25656 |  | 325657 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25657 |  | 325658 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25658 |  | 325659 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25659 |  | 325660 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25660 |  | 325661 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25661 |  | 325662 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25662 |  | 325663 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25663 |  | 325664 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25664 |  | 325665 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25665 |  | 325666 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25666 |  | 325667 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25667 |  | 325668 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25668 |  | 325669 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25669 |  | 325670 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25670 |  | 325671 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25671 |  | 325672 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25672 |  | 325673 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25673 |  | 325674 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25674 |  | 325675 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25675 |  | 325676 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25676 |  | 325677 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25677 |  | 325678 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25678 |  | 325679 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25679 |  | 325680 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25680 |  | 325681 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25681 |  | 325682 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25682 |  | 325683 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25683 |  | 325684 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25684 |  | 325685 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25685 |  | 325686 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25686 |  | 325687 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25687 |  | 325688 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25688 |  | 325689 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25689 |  | 325690 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25690 |  | 325691 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25691 |  | 325692 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25692 |  | 325693 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25693 |  | 325694 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25694 |  | 325695 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25695 |  | 325696 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25696 |  | 325697 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25697 |  | 325698 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25698 |  | 325699 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25699 |  | 325700 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25700 |  | 325701 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25701 |  | 325702 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25702 |  | 325703 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25703 |  | 325704 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25704 |  | 325705 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25705 |  | 325706 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25706 |  | 325707 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25707 |  | 325708 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25708 |  | 325709 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25709 |  | 325710 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25710 |  | 325711 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25711 |  | 325712 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25712 |  | 325713 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25713 |  | 325714 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25714 |  | 325715 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25715 |  | 325716 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25716 |  | 325717 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25717 |  | 325718 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25718 |  | 325719 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25719 |  | 325720 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25720 |  | 325721 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25721 |  | 325722 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25722 |  | 325723 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25723 |  | 325724 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25724 |  | 325725 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25725 |  | 325726 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25726 |  | 325727 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25727 |  | 325728 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25728 |  | 325729 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25729 |  | 325730 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25730 |  | 325731 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25731 |  | 325732 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25732 |  | 325733 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25733 |  | 325734 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25734 |  | 325735 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25735 |  | 325736 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25736 |  | 325737 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25737 |  | 325738 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25738 |  | 325739 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25739 |  | 325740 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25740 |  | 325741 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25741 |  | 325742 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25742 |  | 325743 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25743 |  | 325744 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25744 |  | 325745 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25745 |  | 325746 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25746 |  | 325747 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25747 |  | 325748 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25748 |  | 325749 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25749 |  | 325750 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25750 |  | 325751 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25751 |  | 325752 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25752 |  | 325753 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25753 |  | 325754 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25754 |  | 325755 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25755 |  | 325756 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25756 |  | 325757 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25757 |  | 325758 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25758 |  | 325759 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25759 |  | 325760 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25760 |  | 325761 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25761 |  | 325762 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25762 |  | 325763 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25763 |  | 325764 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25764 |  | 325765 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25765 |  | 325766 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25766 |  | 325767 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25767 |  | 325768 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25768 |  | 325769 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25769 |  | 325770 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25770 |  | 325771 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25771 |  | 325772 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25772 |  | 325773 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25773 |  | 325774 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25774 |  | 325775 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25775 |  | 325776 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25776 |  | 325777 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25777 |  | 325778 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25778 |  | 325779 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25779 |  | 325780 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25780 |  | 325781 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25781 |  | 325782 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25782 |  | 325783 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25783 |  | 325784 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25784 |  | 325785 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25785 |  | 325786 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25786 |  | 325787 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25787 |  | 325788 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25788 |  | 325789 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25789 |  | 325790 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25790 |  | 325791 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25791 |  | 325792 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25792 |  | 325793 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25793 |  | 325794 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25794 |  | 325795 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25795 |  | 325796 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25796 |  | 325797 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25797 |  | 325798 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25798 |  | 325799 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25799 |  | 325800 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
Alarm status: Alarm state | 26000 |  | 326001 | Application initialisation error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26001 |  | 326002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26002 |  | 326003 | Preliminary software | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26003 |  | 326004 | Parameters - Engine - Stop sequence - Stop failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26004 |  | 326005 | Parameters - Engine - Start sequence - Start failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26005 |  | 326006 | Parameters - Engine - Start sequence - Crank failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26006 |  | 326007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26007 |  | 326008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26008 |  | 326009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26009 |  | 326010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26010 |  | 326011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Magnetic pickup wire break alarm | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26011 |  | 326012 | Parameters - Engine - Stop sequence - Externally stopped - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26012 |  | 326013 | Parameters - Engine - Start sequence - Externally started - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26013 |  | 326014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26014 |  | 326015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26015 |  | 326016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26016 |  | 326017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26017 |  | 326018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26018 |  | 326019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26019 |  | 326020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26020 |  | 326021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26021 |  | 326022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26022 |  | 326023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26023 |  | 326024 | Number of configured stand-alone alarms is too high | INT16 | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm state | 26024 |  | 326025 | EIM3.1 hardware revision does not support stand-alone | INT16 | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm state | 26025 |  | 326026 | EIM3.1 safety shutdown still has control | INT16 | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm state | 26026 |  | 326027 | EIM3.1 safety shutdown configuration is not correct | INT16 | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm state | 26027 |  | 326028 | Parameters - Engine - Running detection - Primary running feedback failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26028 |  | 326029 | Parameters - Engine - Maintenance - Running hours total - Information - Total running hours notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26029 |  | 326030 | Parameters - Engine - Maintenance - Running hours trip 1 - Information - Trip running hours 1 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26030 |  | 326031 | Parameters - Engine - Maintenance - Running hours trip 2 - Information - Trip running hours 2 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26031 |  | 326032 | Parameters - Engine - Maintenance - Running hours trip 3 - Information - Trip running hours 3 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26032 |  | 326033 | Parameters - Engine - Maintenance - Running hours trip 4 - Information - Trip running hours 4 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26033 |  | 326034 | Parameters - Engine - Maintenance - Running hours trip 5 - Information - Trip running hours 5 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26034 |  | 326035 | Parameters - Engine - Maintenance - Running hours trip 6 - Information - Trip running hours 6 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26035 |  | 326036 | Parameters - Engine - Maintenance - Running hours trip 7 - Information - Trip running hours 7 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26036 |  | 326037 | Parameters - Engine - Maintenance - Running hours trip 8 - Information - Trip running hours 8 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26037 |  | 326038 | Parameters - Engine - Maintenance - Running hours trip 9 - Information - Trip running hours 9 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26038 |  | 326039 | Parameters - Engine - Maintenance - Running hours trip 10 - Information - Trip running hours 10 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26040 |  | 326041 | Parameters - Engine - Start sequence - Start enable removed during start - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26041 |  | 326042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - GB closing failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26041 |  | 326042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - BTB closing failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26041 |  | 326042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - MB closing failure | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26042 |  | 326043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - GB opening failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26042 |  | 326043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - BTB opening failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26042 |  | 326043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - MB opening failure | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26043 |  | 326044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - GB position failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26043 |  | 326044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - BTB position failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26043 |  | 326044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - MB position failure | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26044 |  | 326045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - GB configuration failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26044 |  | 326045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - BTB configuration failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26044 |  | 326045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - MB configuration failure | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26045 |  | 326046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - GB synchronisation failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26045 |  | 326046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - BTB synchronisation failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26045 |  | 326046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - MB synchronisation failure | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26046 |  | 326047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - GB de-load failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26046 |  | 326047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - BTB de-load failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26046 |  | 326047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - MB de-load failure | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26047 |  | 326048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - GB tripped (external) | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26047 |  | 326048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - BTB tripped (external) | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26047 |  | 326048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - MB tripped (external) | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26048 |  | 326049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - GB short circuit | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26048 |  | 326049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - BTB short circuit | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26048 |  | 326049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - MB short circuit | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26049 |  | 326050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - MB closing failure | INT16 | X * 1 | X * 1 |  | X
Alarm status: Alarm state | 26049 |  | 326050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - TB closing failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26050 |  | 326051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - MB opening failure | INT16 | X * 1 | X * 1 |  | X
Alarm status: Alarm state | 26050 |  | 326051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - TB opening failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26051 |  | 326052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - MB position failure | INT16 | X * 1 | X * 1 |  | X
Alarm status: Alarm state | 26051 |  | 326052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - TB position failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26052 |  | 326053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - MB configuration failure | INT16 | X * 1 | X * 1 |  | X
Alarm status: Alarm state | 26052 |  | 326053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - TB configuration failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26053 |  | 326054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - MB synchronisation failure | INT16 | X * 1 | X * 1 |  | X
Alarm status: Alarm state | 26053 |  | 326054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - TB synchronisation failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26054 |  | 326055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - MB de-load failure | INT16 | X * 1 | X * 1 |  | X
Alarm status: Alarm state | 26054 |  | 326055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - TB de-load failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26055 |  | 326056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - MB tripped (external) | INT16 | X * 1 | X * 1 |  | X
Alarm status: Alarm state | 26055 |  | 326056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - TB tripped (external) | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26056 |  | 326057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - MB short circuit | INT16 | X * 1 | X * 1 |  | X
Alarm status: Alarm state | 26056 |  | 326057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - TB short circuit | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26060 |  | 326061 | Parameters - Mains - AC setup - Phase sequence error - Information - Mains phase sequence error | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26060 |  | 326061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Busbar phase sequence error | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26060 |  | 326061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Busbar B phase sequence error | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26061 |  | 326062 | Parameters - Generator - AC setup - Phase sequence error - Information - Generator phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26061 |  | 326062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Busbar A phase sequence error | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26061 |  | 326062 | Parameters - Mains - AC setup - Phase sequence error - Information - Mains phase sequence error | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26062 |  | 326063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26103 |  | 326104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26103 |  | 326104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26103 |  | 326104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26104 |  | 326105 | Parameters - Mains - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26104 |  | 326105 | Parameters - Busbar - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26104 |  | 326105 | Parameters - Busbar B - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26105 |  | 326106 | Parameters - Generator - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26105 |  | 326106 | Parameters - Busbar A - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26105 |  | 326106 | Parameters - Mains - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26106 |  | 326107 | Parameters - Local - 4th current input - Earth inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26107 |  | 326108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26108 |  | 326109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26108 |  | 326109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26108 |  | 326109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26109 |  | 326110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26109 |  | 326110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26109 |  | 326110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26110 |  | 326111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26110 |  | 326111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26110 |  | 326111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26111 |  | 326112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26111 |  | 326112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26111 |  | 326112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26115 |  | 326116 | Protection set point out of range | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26116 |  | 326117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Stabilised differential | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26117 |  | 326118 | Parameters - Generator - Current protections - High set differential current - Information - High set differential | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26118 |  | 326119 | Protection set point out of range (differential current) | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26119 |  | 326120 | Parameters - Local - Mode - Not under remote control - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26120 |  | 326121 | Trip AVR output not configured | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26121 |  | 326122 | Parameters - Local - Monitoring - System not OK - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26122 |  | 326123 | Configuration update delayed | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26123 |  | 326124 | Critical process error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26124 |  | 326125 | Restore error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26125 |  | 326126 | SD-card format error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26126 |  | 326127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26127 |  | 326128 | Fieldbus configuration exceeded maximum I/O configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26128 |  | 326129 | Parameters - Custom alarm - Custom alarm 0 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26129 |  | 326130 | Parameters - Custom alarm - Custom alarm 1 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26130 |  | 326131 | Parameters - Custom alarm - Custom alarm 2 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26131 |  | 326132 | Parameters - Custom alarm - Custom alarm 3 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26132 |  | 326133 | Parameters - Custom alarm - Custom alarm 4 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26133 |  | 326134 | Parameters - Custom alarm - Custom alarm 5 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26134 |  | 326135 | Parameters - Custom alarm - Custom alarm 6 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26135 |  | 326136 | Parameters - Custom alarm - Custom alarm 7 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26136 |  | 326137 | Parameters - Custom alarm - Custom alarm 8 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26137 |  | 326138 | Parameters - Custom alarm - Custom alarm 9 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26138 |  | 326139 | Parameters - Custom alarm - Custom alarm 10 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26139 |  | 326140 | Parameters - Custom alarm - Custom alarm 11 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26140 |  | 326141 | Parameters - Custom alarm - Custom alarm 12 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26141 |  | 326142 | Parameters - Custom alarm - Custom alarm 13 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26142 |  | 326143 | Parameters - Custom alarm - Custom alarm 14 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26143 |  | 326144 | Parameters - Custom alarm - Custom alarm 15 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26144 |  | 326145 | Parameters - Custom alarm - Custom alarm 16 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26145 |  | 326146 | Parameters - Custom alarm - Custom alarm 17 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26146 |  | 326147 | Parameters - Custom alarm - Custom alarm 18 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26147 |  | 326148 | Parameters - Custom alarm - Custom alarm 19 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26148 |  | 326149 | Parameters - Custom alarm - Custom alarm 20 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26149 |  | 326150 | Parameters - Custom alarm - Custom alarm 21 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26150 |  | 326151 | Parameters - Custom alarm - Custom alarm 22 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26151 |  | 326152 | Parameters - Custom alarm - Custom alarm 23 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26152 |  | 326153 | Parameters - Custom alarm - Custom alarm 24 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26153 |  | 326154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - GOV regulation error | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26154 |  | 326155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - AVR regulation error | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26155 |  | 326156 | Parameters - Regulators - GOV - Monitoring - P load sharing failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26156 |  | 326157 | Parameters - Regulators - AVR - Monitoring - Q load sharing failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26157 |  | 326158 | AVR relay setup incomplete | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26158 |  | 326159 | GOV relay setup incomplete | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26159 |  | 326160 | Parameters - Regulators - GOV - Monitoring - Regulation mode not selected - Information - GOV regulator mode not selected | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26160 |  | 326161 | Parameters - Regulators - AVR - Monitoring - Regulation mode not selected - Information - AVR regulator mode not selected | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26161 |  | 326162 | Parameters - Regulators - GOV - General configuration - Stand-alone configuration error - Information - GOV stand-alone configuration error | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26162 |  | 326163 | Parameters - Regulators - AVR - General configuration - Stand-alone configuration error - Information - AVR stand-alone configuration error | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26163 |  | 326164 | Required hardware card(s) not found | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26164 |  | 326165 | Software mismatch on hardware module(s) | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26165 |  | 326166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Mains L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26165 |  | 326166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Busbar L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm state | 26165 |  | 326166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Busbar B L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26166 |  | 326167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Generator L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm state | 26166 |  | 326167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Busbar A L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26166 |  | 326167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Mains L1-L2-L3 wire break | INT16 | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm state | 26167 |  | 326168 | Parameters - Mains - AC setup - L1 wire break - Information - Mains L1 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26167 |  | 326168 | Parameters - Busbar - AC setup - L1 wire break - Information - Busbar L1 wire break | INT16 | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm state | 26167 |  | 326168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Busbar B L1 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26168 |  | 326169 | Parameters - Mains - AC setup - L2 wire break - Information - Mains L2 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26168 |  | 326169 | Parameters - Busbar - AC setup - L2 wire break - Information - Busbar L2 wire break | INT16 | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm state | 26168 |  | 326169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Busbar B L2 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26169 |  | 326170 | Parameters - Mains - AC setup - L3 wire break - Information - Mains L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26169 |  | 326170 | Parameters - Busbar - AC setup - L3 wire break - Information - Busbar L3 wire break | INT16 | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm state | 26169 |  | 326170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Busbar B L3 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26170 |  | 326171 | Parameters - Generator - AC setup - L1 wire break - Information - Generator L1 wire break | INT16 | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm state | 26170 |  | 326171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Busbar A L1 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26170 |  | 326171 | Parameters - Mains - AC setup - L1 wire break - Information - Mains L1 wire break | INT16 | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm state | 26171 |  | 326172 | Parameters - Generator - AC setup - L2 wire break - Information - Generator L2 wire break | INT16 | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm state | 26171 |  | 326172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Busbar A L2 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26171 |  | 326172 | Parameters - Mains - AC setup - L2 wire break - Information - Mains L2 wire break | INT16 | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm state | 26172 |  | 326173 | Parameters - Generator - AC setup - L3 wire break - Information - Generator L3 wire break | INT16 | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm state | 26172 |  | 326173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Busbar A L3 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26172 |  | 326173 | Parameters - Mains - AC setup - L3 wire break - Information - Mains L3 wire break | INT16 | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm state | 26173 |  | 326174 | Parameters - Hardware - GAM3.2 1 - Status not OK alarm - Information - GAM3.2 1 status not OK | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26174 |  | 326175 | Parameters - Hardware - GAM3.2 2 - Status not OK alarm - Information - GAM3.2 2 status not OK | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26175 |  | 326176 | Parameters - Hardware - GAM3.2 3 - Status not OK alarm - Information - GAM3.2 3 status not OK | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26176 |  | 326177 | Parameters - Breakers - Generator breaker monitoring - No synchronisation signal - Information - No synchronisation signal for asynchronous generator | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26177 |  | 326178 | Parameters - Generator - Voltage protections - Asynchronous over-voltage - Information - Asynchronous generator over-voltage | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26178 |  | 326179 | Parameters - Mains - AC setup - Supervision alarm - Information - Mains supervision alarm | INT16 | X * 1 | X * 1 |  | X | X |  |  | X | X
Alarm status: Alarm state | 26179 |  | 326180 | Parameters - Engine - Emergency stop - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26180 |  | 326181 | Clock battery failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26181 |  | 326182 | Controller temperature too high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26182 |  | 326183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - PSM3.1 1 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26183 |  | 326184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - PSM3.1 1 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26184 |  | 326185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - PSM3.2 1 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26185 |  | 326186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - PSM3.2 1 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26186 |  | 326187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - PSM3.2 2 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26187 |  | 326188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - PSM3.2 2 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26188 |  | 326189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - PSM3.2 3 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26189 |  | 326190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - PSM3.2 3 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26190 |  | 326191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - EIM3.1 1 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26191 |  | 326192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - EIM3.1 1 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26192 |  | 326193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - EIM3.1 2 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26193 |  | 326194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - EIM3.1 2 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26194 |  | 326195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - EIM3.1 3 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26195 |  | 326196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - EIM3.1 3 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26196 |  | 326197 | EIM3.1 4 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26197 |  | 326198 | EIM3.1 4 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26198 |  | 326199 | EIM3.1 5 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26199 |  | 326200 | EIM3.1 5 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26200 |  | 326201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - EIM3.1 1 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26201 |  | 326202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - EIM3.1 2 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26202 |  | 326203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - EIM3.1 3 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26203 |  | 326204 | EIM3.1 4 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26204 |  | 326205 | EIM3.1 5 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26205 |  | 326206 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26206 |  | 326207 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26207 |  | 326208 | AC protections not running (differential current) | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26208 |  | 326209 | AC data is missing (differential current) | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26209 |  | 326210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - GAM3.2 1 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26210 |  | 326211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - GAM3.2 1 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26211 |  | 326212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - GAM3.2 2 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26212 |  | 326213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - GAM3.2 2 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26213 |  | 326214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - GAM3.2 3 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26214 |  | 326215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - GAM3.2 3 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26215 |  | 326216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - PSM3.2 4 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26216 |  | 326217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - PSM3.2 4 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26217 |  | 326218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - PSM3.2 5 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26218 |  | 326219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - PSM3.2 5 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26219 |  | 326220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - PSM3.2 6 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26220 |  | 326221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - PSM3.2 6 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26221 |  | 326222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - PSM3.2 7 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26222 |  | 326223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - PSM3.2 7 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26223 |  | 326224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - PSM3.2 8 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26224 |  | 326225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - PSM3.2 8 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26225 |  | 326226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - PSM3.2 9 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26226 |  | 326227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - PSM3.2 9 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26227 |  | 326228 | Parameters - System - Monitoring - Any bus tie breaker position failure - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26228 |  | 326229 | Parameters - System - Monitoring - Duplicate controller ID - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26229 |  | 326230 | Parameters - System - Monitoring - Missing all controllers - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26230 |  | 326231 | Parameters - System - Monitoring - Missing any controller - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26231 |  | 326232 | Controller ID not configured | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26232 |  | 326233 | Parameters - System - Monitoring - Any mains breaker position failure - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26233 |  | 326234 | Parameters - System - Monitoring - Data loss from a controller - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26234 |  | 326235 | Parameters - System - Monitoring - Data loss on DEIF network - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26235 |  | 326236 | Parameters - System - Monitoring - High traffic on DEIF network - Information - High traffic to DEIF network | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26236 |  | 326237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26237 |  | 326238 | Parameters - System - Monitoring - Blackout detection mismatch - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26239 |  | 326240 | Parameters - System - Monitoring - Group alarm - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26240 |  | 326241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - NTP server 1 could not connect | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26241 |  | 326242 | Parameters - Communication - NTP - NTP server 1 no response - Information - NTP server 1 is not responding | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26242 |  | 326243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - NTP server 2 could not connect | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26243 |  | 326244 | Parameters - Communication - NTP - NTP server 2 no response - Information - NTP server 2 is not responding | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26244 |  | 326245 | Parameters - Communication - NTP - No NTP server time synchronisation - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26245 |  | 326246 | Parameters - Communication - NTP - No NTP server(s) connected - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26246 |  | 326247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26247 |  | 326248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26248 |  | 326249 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26249 |  | 326250 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26250 |  | 326251 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26251 |  | 326252 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26252 |  | 326253 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26253 |  | 326254 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26254 |  | 326255 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26255 |  | 326256 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26256 |  | 326257 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26257 |  | 326258 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26258 |  | 326259 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26259 |  | 326260 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26260 |  | 326261 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26261 |  | 326262 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26262 |  | 326263 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26263 |  | 326264 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26264 |  | 326265 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26265 |  | 326266 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26266 |  | 326267 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26267 |  | 326268 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26268 |  | 326269 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26269 |  | 326270 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26270 |  | 326271 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26271 |  | 326272 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26272 |  | 326273 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26273 |  | 326274 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26274 |  | 326275 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26275 |  | 326276 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26276 |  | 326277 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26277 |  | 326278 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26278 |  | 326279 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26279 |  | 326280 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26280 |  | 326281 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26281 |  | 326282 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26282 |  | 326283 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26283 |  | 326284 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26284 |  | 326285 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26285 |  | 326286 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26286 |  | 326287 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26287 |  | 326288 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26288 |  | 326289 | Parameters - Breakers - Breaker 1 feedback monitoring - Position failure - Information - Breaker 1 position failure | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm state | 26289 |  | 326290 | Parameters - Breakers - Breaker 1 feedback monitoring - Feedback mismatch - Information - Breaker 1 feedback mismatch | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm state | 26290 |  | 326291 | Parameters - Breakers - Breaker 2 feedback monitoring - Position failure - Information - Breaker 2 position failure | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm state | 26290 |  | 326291 | Parameters - Breakers - BTB 1 feedback monitoring - Position failure - Information - BTB 1 position failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26291 |  | 326292 | Parameters - Breakers - Breaker 2 feedback monitoring - Feedback mismatch - Information - Breaker 2 feedback mismatch | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm state | 26291 |  | 326292 | Parameters - Breakers - BTB 1 feedback monitoring - Feedback mismatch - Information - BTB 1 feedback mismatch | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26292 |  | 326293 | Parameters - Breakers - Breaker 3 feedback monitoring - Position failure - Information - Breaker 3 position failure | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm state | 26292 |  | 326293 | Parameters - Breakers - BTB 2 feedback monitoring - Position failure - Information - BTB 2 position failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26293 |  | 326294 | Parameters - Breakers - Breaker 3 feedback monitoring - Feedback mismatch - Information - Breaker 3 feedback mismatch | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm state | 26293 |  | 326294 | Parameters - Breakers - BTB 2 feedback monitoring - Feedback mismatch - Information - BTB 2 feedback mismatch | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26294 |  | 326295 | Parameters - Breakers - Breaker 4 feedback monitoring - Position failure - Information - Breaker 4 position failure | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm state | 26294 |  | 326295 | Parameters - Breakers - BTB 3 feedback monitoring - Position failure - Information - BTB 3 position failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26295 |  | 326296 | Parameters - Breakers - Breaker 4 feedback monitoring - Feedback mismatch - Information - Breaker 4 feedback mismatch | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm state | 26295 |  | 326296 | Parameters - Breakers - BTB 3 feedback monitoring - Feedback mismatch - Information - BTB 3 feedback mismatch | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26296 |  | 326297 | Controller not part of system | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26297 |  | 326298 | Different single-line configurations | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26298 |  | 326299 | Single-line missing/none active | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26299 |  | 326300 | Parameters - Communication - Modbus - Modbus communication timeout - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26300 |  | 326301 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - CODESYS configuration conflict | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26301 |  | 326302 | Parameters - CODESYS - Monitoring - Application not OK - Information - CODESYS application not OK | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26302 |  | 326303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26303 |  | 326304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26304 |  | 326305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26305 |  | 326306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26306 |  | 326307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26307 |  | 326308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26308 |  | 326309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26309 |  | 326310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26310 |  | 326311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26311 |  | 326312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26312 |  | 326313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26313 |  | 326314 | Emulation disabled (live power) | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26315 |  | 326316 | Parameters - Local - CustomLogic - Configuration invalid - Information - CustomLogic configuration invalid | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26316 |  | 326317 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Digital AVR communication error | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26317 |  | 326318 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26318 |  | 326319 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26319 |  | 326320 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26320 |  | 326321 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26321 |  | 326322 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26322 |  | 326323 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26323 |  | 326324 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26324 |  | 326325 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26325 |  | 326326 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26326 |  | 326327 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26327 |  | 326328 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26328 |  | 326329 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26329 |  | 326330 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26330 |  | 326331 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26331 |  | 326332 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26332 |  | 326333 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26333 |  | 326334 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26334 |  | 326335 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26335 |  | 326336 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26336 |  | 326337 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26337 |  | 326338 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26338 |  | 326339 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26339 |  | 326340 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26340 |  | 326341 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26341 |  | 326342 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26342 |  | 326343 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26343 |  | 326344 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26344 |  | 326345 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26345 |  | 326346 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26346 |  | 326347 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26347 |  | 326348 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26348 |  | 326349 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26349 |  | 326350 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26350 |  | 326351 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26351 |  | 326352 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26352 |  | 326353 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26353 |  | 326354 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26354 |  | 326355 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26355 |  | 326356 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26356 |  | 326357 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26357 |  | 326358 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26358 |  | 326359 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26359 |  | 326360 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26360 |  | 326361 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26361 |  | 326362 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26362 |  | 326363 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26363 |  | 326364 | DAVR unsupported AC configuration | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26364 |  | 326365 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Illegal DAVR configuration | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26365 |  | 326366 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Generator under-voltage 1 | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26365 |  | 326366 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Busbar A under-voltage 1 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26365 |  | 326366 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Mains under-voltage 1 | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26366 |  | 326367 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Generator under-voltage 2 | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26366 |  | 326367 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Busbar A under-voltage 2 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26366 |  | 326367 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Mains under-voltage 2 | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26367 |  | 326368 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Generator under-voltage 3 | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26367 |  | 326368 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Busbar A under-voltage 3 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26367 |  | 326368 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Mains under-voltage 3 | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26368 |  | 326369 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Generator over-voltage 1 | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26368 |  | 326369 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Busbar A over-voltage 1 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26368 |  | 326369 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Mains over-voltage 1 | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26369 |  | 326370 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Generator over-voltage 2 | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26369 |  | 326370 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Busbar A over-voltage 2 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26369 |  | 326370 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Mains over-voltage 2 | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26370 |  | 326371 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Generator voltage unbalance | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26370 |  | 326371 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Busbar A voltage unbalance | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26370 |  | 326371 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Mains voltage unbalance | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26371 |  | 326372 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Generator negative sequence voltage | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26371 |  | 326372 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Busbar A negative sequence voltage | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26371 |  | 326372 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Mains negative sequence voltage | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26372 |  | 326373 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Generator zero sequence voltage | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26372 |  | 326373 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Busbar A zero sequence voltage | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26372 |  | 326373 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Mains zero sequence voltage | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26373 |  | 326374 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Generator positive sequence under-voltage | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26373 |  | 326374 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Busbar A positive sequence under-voltage | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26373 |  | 326374 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Mains positive sequence under-voltage | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26374 |  | 326375 | Parameters - Generator - Current protections - Over-current 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26374 |  | 326375 | Parameters - Busbar A - Current protections - Over-current 1 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26374 |  | 326375 | Parameters - Mains - Current protections - Over-current 1 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26375 |  | 326376 | Parameters - Generator - Current protections - Over-current 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26375 |  | 326376 | Parameters - Busbar A - Current protections - Over-current 2 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26375 |  | 326376 | Parameters - Mains - Current protections - Over-current 2 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26376 |  | 326377 | Parameters - Generator - Current protections - Over-current 3 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26376 |  | 326377 | Parameters - Busbar A - Current protections - Over-current 3 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26376 |  | 326377 | Parameters - Mains - Current protections - Over-current 3 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26377 |  | 326378 | Parameters - Generator - Current protections - Over-current 4 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26377 |  | 326378 | Parameters - Busbar A - Current protections - Over-current 4 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26377 |  | 326378 | Parameters - Mains - Current protections - Over-current 4 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26378 |  | 326379 | Parameters - Generator - Current protections - Fast over-current 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26378 |  | 326379 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26378 |  | 326379 | Parameters - Mains - Current protections - Fast over-current 1 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26379 |  | 326380 | Parameters - Generator - Current protections - Fast over-current 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26379 |  | 326380 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26379 |  | 326380 | Parameters - Mains - Current protections - Fast over-current 2 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26380 |  | 326381 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26380 |  | 326381 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26380 |  | 326381 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26381 |  | 326382 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26381 |  | 326382 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26381 |  | 326382 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26382 |  | 326383 | Parameters - Generator - Current protections - Directional over-current 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26382 |  | 326383 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26382 |  | 326383 | Parameters - Mains - Current protections - Directional over-current 1 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26383 |  | 326384 | Parameters - Generator - Current protections - Directional over-current 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26383 |  | 326384 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26383 |  | 326384 | Parameters - Mains - Current protections - Directional over-current 2 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26384 |  | 326385 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26385 |  | 326386 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26386 |  | 326387 | Parameters - Generator - Current protections - Negative sequence current - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26386 |  | 326387 | Parameters - Busbar A - Current protections - Negative sequence current - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26386 |  | 326387 | Parameters - Mains - Current protections - Negative sequence current - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26387 |  | 326388 | Parameters - Generator - Current protections - Zero sequence current - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26387 |  | 326388 | Parameters - Busbar A - Current protections - Zero sequence current - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26387 |  | 326388 | Parameters - Mains - Current protections - Zero sequence current - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26388 |  | 326389 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Generator over-frequency 1 | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26388 |  | 326389 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Busbar A over-frequency 1 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26388 |  | 326389 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Mains over-frequency 1 | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26389 |  | 326390 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Generator over-frequency 2 | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26389 |  | 326390 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Busbar A over-frequency 2 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26389 |  | 326390 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Mains over-frequency 2 | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26390 |  | 326391 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Generator over-frequency 3 | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26390 |  | 326391 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Busbar A over-frequency 3 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26390 |  | 326391 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Mains over-frequency 3 | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26391 |  | 326392 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Generator under-frequency 1 | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26391 |  | 326392 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Busbar A under-frequency 1 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26391 |  | 326392 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Mains under-frequency 1 | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26392 |  | 326393 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Generator under-frequency 2 | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26392 |  | 326393 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Busbar A under-frequency 2 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26392 |  | 326393 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Mains under-frequency 2 | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26393 |  | 326394 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Generator under-frequency 3 | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26393 |  | 326394 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Busbar A under-frequency 3 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26393 |  | 326394 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Mains under-frequency 3 | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26394 |  | 326395 | Parameters - Generator - Power protections - Overload 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26394 |  | 326395 | Parameters - Busbar A - Power protections - Power export 1 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26394 |  | 326395 | Parameters - Mains - Power protections - Overload 1 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26395 |  | 326396 | Parameters - Generator - Power protections - Overload 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26395 |  | 326396 | Parameters - Busbar A - Power protections - Power export 2 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26395 |  | 326396 | Parameters - Mains - Power protections - Overload 2 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26396 |  | 326397 | Parameters - Generator - Power protections - Overload 3 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26396 |  | 326397 | Parameters - Busbar A - Power protections - Power export 3 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26396 |  | 326397 | Parameters - Mains - Power protections - Overload 3 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26397 |  | 326398 | Parameters - Generator - Power protections - Overload 4 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26397 |  | 326398 | Parameters - Busbar A - Power protections - Power export 4 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26397 |  | 326398 | Parameters - Mains - Power protections - Overload 4 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26398 |  | 326399 | Parameters - Generator - Power protections - Overload 5 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26398 |  | 326399 | Parameters - Busbar A - Power protections - Power export 5 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26398 |  | 326399 | Parameters - Mains - Power protections - Overload 5 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26399 |  | 326400 | Parameters - Generator - Power protections - Reverse power 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26399 |  | 326400 | Parameters - Busbar A - Power protections - Power import 1 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26399 |  | 326400 | Parameters - Mains - Power protections - Reverse power 1 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26400 |  | 326401 | Parameters - Generator - Power protections - Reverse power 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26400 |  | 326401 | Parameters - Busbar A - Power protections - Power import 2 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26400 |  | 326401 | Parameters - Mains - Power protections - Reverse power 2 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26401 |  | 326402 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26401 |  | 326402 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26401 |  | 326402 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26402 |  | 326403 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26402 |  | 326403 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26402 |  | 326403 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26403 |  | 326404 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26403 |  | 326404 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26403 |  | 326404 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26404 |  | 326405 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26404 |  | 326405 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26404 |  | 326405 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26405 |  | 326406 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Mains over-voltage 1 | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26405 |  | 326406 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Busbar over-voltage 1 | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26405 |  | 326406 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Busbar B over-voltage 1 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26406 |  | 326407 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Mains over-voltage 2 | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26406 |  | 326407 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Busbar over-voltage 2 | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26406 |  | 326407 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Busbar B over-voltage 2 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26407 |  | 326408 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Mains over-voltage 3 | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26407 |  | 326408 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Busbar over-voltage 3 | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26407 |  | 326408 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Busbar B over-voltage 3 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26408 |  | 326409 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Mains under-voltage 1 | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26408 |  | 326409 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Busbar under-voltage 1 | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26408 |  | 326409 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Busbar B under-voltage 1 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26409 |  | 326410 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Mains under-voltage 2 | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26409 |  | 326410 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Busbar under-voltage 2 | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26409 |  | 326410 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Busbar B under-voltage 2 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26410 |  | 326411 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Mains under-voltage 3 | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26410 |  | 326411 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Busbar under-voltage 3 | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26410 |  | 326411 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Busbar B under-voltage 3 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26411 |  | 326412 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Mains under-voltage 4 | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26411 |  | 326412 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Busbar under-voltage 4 | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26411 |  | 326412 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Busbar B under-voltage 4 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26412 |  | 326413 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Mains voltage unbalance | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26412 |  | 326413 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Busbar voltage unbalance | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26412 |  | 326413 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Busbar B voltage unbalance | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26413 |  | 326414 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Mains over-frequency 1 | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26413 |  | 326414 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Busbar over-frequency 1 | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26413 |  | 326414 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Busbar B over-frequency 1 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26414 |  | 326415 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Mains over-frequency 2 | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26414 |  | 326415 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Busbar over-frequency 2 | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26414 |  | 326415 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Busbar B over-frequency 2 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26415 |  | 326416 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Mains over-frequency 3 | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26415 |  | 326416 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Busbar over-frequency 3 | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26415 |  | 326416 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Busbar B over-frequency 3 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26416 |  | 326417 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Mains under-frequency 1 | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26416 |  | 326417 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Busbar under-frequency 1 | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26416 |  | 326417 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Busbar B under-frequency 1 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26417 |  | 326418 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Mains under-frequency 2 | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26417 |  | 326418 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Busbar under-frequency 2 | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26417 |  | 326418 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Busbar B under-frequency 2 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26418 |  | 326419 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Mains under-frequency 3 | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26418 |  | 326419 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Busbar under-frequency 3 | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26418 |  | 326419 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Busbar B under-frequency 3 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26419 |  | 326420 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Mains under-frequency 4 | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26419 |  | 326420 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Busbar under-frequency 4 | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26419 |  | 326420 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Busbar B under-frequency 4 | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26420 |  | 326421 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Busbar negative sequence voltage | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26420 |  | 326421 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Busbar negative sequence voltage | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26420 |  | 326421 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Busbar B negative sequence voltage | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26421 |  | 326422 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Busbar zero sequence voltage | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26421 |  | 326422 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Busbar zero sequence voltage | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26421 |  | 326422 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Busbar B zero sequence voltage | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26422 |  | 326423 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Busbar positive sequence under-voltage | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Alarm state | 26422 |  | 326423 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Busbar positive sequence under-voltage | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm state | 26422 |  | 326423 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Busbar B positive sequence under-voltage | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26423 |  | 326424 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26424 |  | 326425 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26425 |  | 326426 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26426 |  | 326427 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26427 |  | 326428 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26428 |  | 326429 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26429 |  | 326430 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26430 |  | 326431 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26431 |  | 326432 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26432 |  | 326433 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26433 |  | 326434 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26434 |  | 326435 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26435 |  | 326436 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26436 |  | 326437 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26437 |  | 326438 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26438 |  | 326439 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26439 |  | 326440 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26440 |  | 326441 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26441 |  | 326442 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26442 |  | 326443 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26443 |  | 326444 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26444 |  | 326445 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26445 |  | 326446 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26446 |  | 326447 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26447 |  | 326448 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26448 |  | 326449 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26449 |  | 326450 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26450 |  | 326451 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26451 |  | 326452 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26452 |  | 326453 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26453 |  | 326454 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26454 |  | 326455 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26455 |  | 326456 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26456 |  | 326457 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26457 |  | 326458 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26458 |  | 326459 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26459 |  | 326460 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26460 |  | 326461 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26461 |  | 326462 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26462 |  | 326463 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26463 |  | 326464 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26464 |  | 326465 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26465 |  | 326466 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26466 |  | 326467 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm state | 26600 |  | 326601 | Parameters - Communication - DEIF network - DEIF network fork detected - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26602 |  | 326603 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26604 |  | 326605 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26604 |  | 326605 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26604 |  | 326605 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm state | 26605 |  | 326606 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 |  | X
Alarm status: Alarm state | 26605 |  | 326606 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26607 |  | 326608 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26608 |  | 326609 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26609 |  | 326610 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26610 |  | 326611 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26611 |  | 326612 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26612 |  | 326613 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26613 |  | 326614 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26614 |  | 326615 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26615 |  | 326616 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26616 |  | 326617 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26617 |  | 326618 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26618 |  | 326619 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26619 |  | 326620 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26620 |  | 326621 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26621 |  | 326622 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26622 |  | 326623 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26623 |  | 326624 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26624 |  | 326625 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26625 |  | 326626 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26626 |  | 326627 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26628 |  | 326629 | Internal issue detected. A restart is required soon! | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26630 |  | 326631 | Card issue detected | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26631 |  | 326632 | Card configuration failed | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26632 |  | 326633 | Unknown traffic on DEIF network | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26633 |  | 326634 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26634 |  | 326635 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26635 |  | 326636 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm state | 26636 |  | 326637 | Local IO service error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26637 |  | 326638 | App logging failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26638 |  | 326639 | Event logging failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26639 |  | 326640 | Licence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 26640 |  | 326641 | Brightness is dimmed according to temperature | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27500 |  | 327501 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27501 |  | 327502 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27502 |  | 327503 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27503 |  | 327504 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27504 |  | 327505 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27505 |  | 327506 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27506 |  | 327507 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27507 |  | 327508 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27508 |  | 327509 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27509 |  | 327510 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27510 |  | 327511 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27511 |  | 327512 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27512 |  | 327513 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27513 |  | 327514 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27514 |  | 327515 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27515 |  | 327516 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27516 |  | 327517 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27517 |  | 327518 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27518 |  | 327519 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27519 |  | 327520 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27520 |  | 327521 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27521 |  | 327522 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27522 |  | 327523 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27523 |  | 327524 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27524 |  | 327525 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27525 |  | 327526 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27526 |  | 327527 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27527 |  | 327528 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27528 |  | 327529 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27529 |  | 327530 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27530 |  | 327531 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27531 |  | 327532 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27532 |  | 327533 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27533 |  | 327534 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27534 |  | 327535 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27535 |  | 327536 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27536 |  | 327537 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27537 |  | 327538 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27538 |  | 327539 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27539 |  | 327540 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27540 |  | 327541 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27541 |  | 327542 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27542 |  | 327543 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27543 |  | 327544 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27544 |  | 327545 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27545 |  | 327546 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27546 |  | 327547 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27547 |  | 327548 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27548 |  | 327549 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27549 |  | 327550 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27600 |  | 327601 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27601 |  | 327602 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27602 |  | 327603 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27603 |  | 327604 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27604 |  | 327605 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27605 |  | 327606 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27606 |  | 327607 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27607 |  | 327608 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27608 |  | 327609 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27609 |  | 327610 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27610 |  | 327611 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27611 |  | 327612 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27612 |  | 327613 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27613 |  | 327614 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27614 |  | 327615 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27615 |  | 327616 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27616 |  | 327617 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27617 |  | 327618 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27618 |  | 327619 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27619 |  | 327620 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27620 |  | 327621 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27621 |  | 327622 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27622 |  | 327623 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27623 |  | 327624 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27624 |  | 327625 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27625 |  | 327626 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27626 |  | 327627 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27627 |  | 327628 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27628 |  | 327629 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27629 |  | 327630 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27630 |  | 327631 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27631 |  | 327632 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27632 |  | 327633 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27633 |  | 327634 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27634 |  | 327635 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27635 |  | 327636 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27636 |  | 327637 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27637 |  | 327638 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27638 |  | 327639 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27639 |  | 327640 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27640 |  | 327641 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27641 |  | 327642 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27642 |  | 327643 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27643 |  | 327644 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27644 |  | 327645 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27645 |  | 327646 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27646 |  | 327647 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27647 |  | 327648 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27648 |  | 327649 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27649 |  | 327650 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27650 |  | 327651 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27651 |  | 327652 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27652 |  | 327653 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27653 |  | 327654 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27654 |  | 327655 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27655 |  | 327656 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27656 |  | 327657 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27657 |  | 327658 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27658 |  | 327659 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27659 |  | 327660 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27660 |  | 327661 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27661 |  | 327662 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27662 |  | 327663 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27663 |  | 327664 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27664 |  | 327665 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27665 |  | 327666 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27666 |  | 327667 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27667 |  | 327668 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27668 |  | 327669 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27669 |  | 327670 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27670 |  | 327671 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27671 |  | 327672 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27672 |  | 327673 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27673 |  | 327674 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27674 |  | 327675 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27675 |  | 327676 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27676 |  | 327677 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27677 |  | 327678 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27678 |  | 327679 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27679 |  | 327680 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27680 |  | 327681 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27681 |  | 327682 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27682 |  | 327683 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27683 |  | 327684 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27684 |  | 327685 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27685 |  | 327686 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27686 |  | 327687 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27687 |  | 327688 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27688 |  | 327689 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27689 |  | 327690 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27690 |  | 327691 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27691 |  | 327692 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27692 |  | 327693 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27693 |  | 327694 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27694 |  | 327695 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27695 |  | 327696 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27696 |  | 327697 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27697 |  | 327698 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27698 |  | 327699 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27699 |  | 327700 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27700 |  | 327701 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27701 |  | 327702 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27702 |  | 327703 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27703 |  | 327704 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27704 |  | 327705 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27705 |  | 327706 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27706 |  | 327707 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27707 |  | 327708 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27708 |  | 327709 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27709 |  | 327710 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27710 |  | 327711 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27711 |  | 327712 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27712 |  | 327713 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27713 |  | 327714 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27714 |  | 327715 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27715 |  | 327716 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27716 |  | 327717 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27717 |  | 327718 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27718 |  | 327719 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27719 |  | 327720 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27720 |  | 327721 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27721 |  | 327722 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27722 |  | 327723 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27723 |  | 327724 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27724 |  | 327725 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27725 |  | 327726 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27726 |  | 327727 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27727 |  | 327728 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27728 |  | 327729 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27729 |  | 327730 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27730 |  | 327731 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27731 |  | 327732 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27732 |  | 327733 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27733 |  | 327734 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27734 |  | 327735 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27735 |  | 327736 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27736 |  | 327737 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27737 |  | 327738 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27738 |  | 327739 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27739 |  | 327740 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27740 |  | 327741 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27741 |  | 327742 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27742 |  | 327743 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27743 |  | 327744 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27744 |  | 327745 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27745 |  | 327746 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27746 |  | 327747 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27747 |  | 327748 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27748 |  | 327749 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27749 |  | 327750 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27750 |  | 327751 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27751 |  | 327752 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27752 |  | 327753 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27753 |  | 327754 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27754 |  | 327755 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27755 |  | 327756 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27756 |  | 327757 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27757 |  | 327758 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27758 |  | 327759 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27759 |  | 327760 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27760 |  | 327761 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27761 |  | 327762 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27762 |  | 327763 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27763 |  | 327764 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27764 |  | 327765 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27765 |  | 327766 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27766 |  | 327767 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27767 |  | 327768 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27768 |  | 327769 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27769 |  | 327770 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27770 |  | 327771 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27771 |  | 327772 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27772 |  | 327773 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27773 |  | 327774 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27774 |  | 327775 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27775 |  | 327776 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27776 |  | 327777 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27777 |  | 327778 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27778 |  | 327779 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27779 |  | 327780 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27780 |  | 327781 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27781 |  | 327782 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27782 |  | 327783 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27783 |  | 327784 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27784 |  | 327785 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27785 |  | 327786 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27786 |  | 327787 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27787 |  | 327788 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27788 |  | 327789 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27789 |  | 327790 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27790 |  | 327791 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27791 |  | 327792 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27792 |  | 327793 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27793 |  | 327794 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27794 |  | 327795 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27795 |  | 327796 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27796 |  | 327797 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27797 |  | 327798 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27798 |  | 327799 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm state | 27799 |  | 327800 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28000 | 0 | 328001 | Application initialisation error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28000 | 1 | 328001 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28000 | 2 | 328001 | Preliminary software | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28000 | 3 | 328001 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28000 | 4 | 328001 | Parameters - Engine - Start sequence - Start failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28000 | 5 | 328001 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28000 | 6 | 328001 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28000 | 7 | 328001 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28000 | 8 | 328001 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28000 | 9 | 328001 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28000 | 10 | 328001 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28000 | 11 | 328001 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28000 | 12 | 328001 | Parameters - Engine - Start sequence - Externally started - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28000 | 13 | 328001 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28000 | 14 | 328001 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28000 | 15 | 328001 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28001 | 0 | 328002 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28001 | 1 | 328002 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28001 | 2 | 328002 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28001 | 3 | 328002 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28001 | 4 | 328002 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28001 | 5 | 328002 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28001 | 6 | 328002 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28001 | 7 | 328002 | Number of configured stand-alone alarms is too high | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm active | 28001 | 8 | 328002 | EIM3.1 hardware revision does not support stand-alone | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm active | 28001 | 9 | 328002 | EIM3.1 safety shutdown still has control | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm active | 28001 | 10 | 328002 | EIM3.1 safety shutdown configuration is not correct | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm active | 28001 | 11 | 328002 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28001 | 12 | 328002 | Parameters - Engine - Maintenance - Running hours total - Information - Flags - Total running hours notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28001 | 13 | 328002 | Parameters - Engine - Maintenance - Running hours trip 1 - Information - Flags - Trip running hours 1 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28001 | 14 | 328002 | Parameters - Engine - Maintenance - Running hours trip 2 - Information - Flags - Trip running hours 2 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28001 | 15 | 328002 | Parameters - Engine - Maintenance - Running hours trip 3 - Information - Flags - Trip running hours 3 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 0 | 328003 | Parameters - Engine - Maintenance - Running hours trip 4 - Information - Flags - Trip running hours 4 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 1 | 328003 | Parameters - Engine - Maintenance - Running hours trip 5 - Information - Flags - Trip running hours 5 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 2 | 328003 | Parameters - Engine - Maintenance - Running hours trip 6 - Information - Flags - Trip running hours 6 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 3 | 328003 | Parameters - Engine - Maintenance - Running hours trip 7 - Information - Flags - Trip running hours 7 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 4 | 328003 | Parameters - Engine - Maintenance - Running hours trip 8 - Information - Flags - Trip running hours 8 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 5 | 328003 | Parameters - Engine - Maintenance - Running hours trip 9 - Information - Flags - Trip running hours 9 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 6 | 328003 | Parameters - Engine - Maintenance - Running hours trip 10 - Information - Flags - Trip running hours 10 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 8 | 328003 | Parameters - Engine - Start sequence - Start enable removed during start - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 9 | 328003 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 9 | 328003 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28002 | 9 | 328003 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28002 | 10 | 328003 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 10 | 328003 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28002 | 10 | 328003 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28002 | 11 | 328003 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 11 | 328003 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28002 | 11 | 328003 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28002 | 12 | 328003 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 12 | 328003 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28002 | 12 | 328003 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28002 | 13 | 328003 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 13 | 328003 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28002 | 13 | 328003 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28002 | 14 | 328003 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 14 | 328003 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28002 | 14 | 328003 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28002 | 15 | 328003 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28002 | 15 | 328003 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28002 | 15 | 328003 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28003 | 0 | 328004 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28003 | 0 | 328004 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28003 | 0 | 328004 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28003 | 1 | 328004 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm active | 28003 | 1 | 328004 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28003 | 2 | 328004 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm active | 28003 | 2 | 328004 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28003 | 3 | 328004 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm active | 28003 | 3 | 328004 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28003 | 4 | 328004 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm active | 28003 | 4 | 328004 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28003 | 5 | 328004 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm active | 28003 | 5 | 328004 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28003 | 6 | 328004 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm active | 28003 | 6 | 328004 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28003 | 7 | 328004 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm active | 28003 | 7 | 328004 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28003 | 8 | 328004 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm active | 28003 | 8 | 328004 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28003 | 12 | 328004 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28003 | 12 | 328004 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28003 | 12 | 328004 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28003 | 13 | 328004 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28003 | 13 | 328004 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28003 | 13 | 328004 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28003 | 14 | 328004 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28006 | 7 | 328007 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28006 | 7 | 328007 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28006 | 7 | 328007 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28006 | 8 | 328007 | Parameters - Mains - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28006 | 8 | 328007 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28006 | 8 | 328007 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28006 | 9 | 328007 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28006 | 9 | 328007 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28006 | 9 | 328007 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28006 | 10 | 328007 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28006 | 11 | 328007 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28006 | 12 | 328007 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28006 | 12 | 328007 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28006 | 12 | 328007 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28006 | 13 | 328007 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28006 | 13 | 328007 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28006 | 13 | 328007 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28006 | 14 | 328007 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28006 | 14 | 328007 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28006 | 14 | 328007 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28006 | 15 | 328007 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28006 | 15 | 328007 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28006 | 15 | 328007 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28007 | 3 | 328008 | Protection set point out of range | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 4 | 328008 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28007 | 5 | 328008 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28007 | 6 | 328008 | Protection set point out of range (differential current) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28007 | 7 | 328008 | Parameters - Local - Mode - Not under remote control - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 8 | 328008 | Trip AVR output not configured | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28007 | 9 | 328008 | Parameters - Local - Monitoring - System not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 10 | 328008 | Configuration update delayed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 11 | 328008 | Critical process error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 12 | 328008 | Restore error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 13 | 328008 | SD-card format error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 14 | 328008 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 15 | 328008 | Fieldbus configuration exceeded maximum I/O configuration | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 0 | 328009 | Parameters - Custom alarm - Custom alarm 0 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 1 | 328009 | Parameters - Custom alarm - Custom alarm 1 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 2 | 328009 | Parameters - Custom alarm - Custom alarm 2 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 3 | 328009 | Parameters - Custom alarm - Custom alarm 3 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 4 | 328009 | Parameters - Custom alarm - Custom alarm 4 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 5 | 328009 | Parameters - Custom alarm - Custom alarm 5 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 6 | 328009 | Parameters - Custom alarm - Custom alarm 6 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 7 | 328009 | Parameters - Custom alarm - Custom alarm 7 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 8 | 328009 | Parameters - Custom alarm - Custom alarm 8 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 9 | 328009 | Parameters - Custom alarm - Custom alarm 9 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 10 | 328009 | Parameters - Custom alarm - Custom alarm 10 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 11 | 328009 | Parameters - Custom alarm - Custom alarm 11 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 12 | 328009 | Parameters - Custom alarm - Custom alarm 12 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 13 | 328009 | Parameters - Custom alarm - Custom alarm 13 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 14 | 328009 | Parameters - Custom alarm - Custom alarm 14 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 15 | 328009 | Parameters - Custom alarm - Custom alarm 15 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 0 | 328010 | Parameters - Custom alarm - Custom alarm 16 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 1 | 328010 | Parameters - Custom alarm - Custom alarm 17 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 2 | 328010 | Parameters - Custom alarm - Custom alarm 18 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 3 | 328010 | Parameters - Custom alarm - Custom alarm 19 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 4 | 328010 | Parameters - Custom alarm - Custom alarm 20 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 5 | 328010 | Parameters - Custom alarm - Custom alarm 21 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 6 | 328010 | Parameters - Custom alarm - Custom alarm 22 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 7 | 328010 | Parameters - Custom alarm - Custom alarm 23 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 8 | 328010 | Parameters - Custom alarm - Custom alarm 24 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 9 | 328010 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28009 | 10 | 328010 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28009 | 11 | 328010 | Parameters - Regulators - GOV - Monitoring - P load sharing failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28009 | 12 | 328010 | Parameters - Regulators - AVR - Monitoring - Q load sharing failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28009 | 13 | 328010 | AVR relay setup incomplete | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28009 | 14 | 328010 | GOV relay setup incomplete | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28009 | 15 | 328010 | Parameters - Regulators - GOV - Monitoring - Regulation mode not selected - Information - Flags - GOV regulator mode not selected | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28010 | 0 | 328011 | Parameters - Regulators - AVR - Monitoring - Regulation mode not selected - Information - Flags - AVR regulator mode not selected | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28010 | 1 | 328011 | Parameters - Regulators - GOV - General configuration - Stand-alone configuration error - Information - Flags - GOV stand-alone configuration error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28010 | 2 | 328011 | Parameters - Regulators - AVR - General configuration - Stand-alone configuration error - Information - Flags - AVR stand-alone configuration error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28010 | 3 | 328011 | Required hardware card(s) not found | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28010 | 4 | 328011 | Software mismatch on hardware module(s) | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28010 | 5 | 328011 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28010 | 5 | 328011 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm active | 28010 | 5 | 328011 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28010 | 6 | 328011 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm active | 28010 | 6 | 328011 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28010 | 6 | 328011 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm active | 28010 | 7 | 328011 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28010 | 7 | 328011 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm active | 28010 | 7 | 328011 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28010 | 8 | 328011 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28010 | 8 | 328011 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm active | 28010 | 8 | 328011 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28010 | 9 | 328011 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28010 | 9 | 328011 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm active | 28010 | 9 | 328011 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28010 | 10 | 328011 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm active | 28010 | 10 | 328011 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28010 | 10 | 328011 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm active | 28010 | 11 | 328011 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm active | 28010 | 11 | 328011 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28010 | 11 | 328011 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm active | 28010 | 12 | 328011 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm active | 28010 | 12 | 328011 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28010 | 12 | 328011 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm active | 28010 | 13 | 328011 | Parameters - Hardware - GAM3.2 1 - Status not OK alarm - Information - Flags - GAM3.2 1 status not OK | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28010 | 14 | 328011 | Parameters - Hardware - GAM3.2 2 - Status not OK alarm - Information - Flags - GAM3.2 2 status not OK | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28010 | 15 | 328011 | Parameters - Hardware - GAM3.2 3 - Status not OK alarm - Information - Flags - GAM3.2 3 status not OK | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28011 | 0 | 328012 | Parameters - Breakers - Generator breaker monitoring - No synchronisation signal - Information - Flags - No synchronisation signal for asynchronous generator | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28011 | 1 | 328012 | Parameters - Generator - Voltage protections - Asynchronous over-voltage - Information - Flags - Asynchronous generator over-voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28011 | 2 | 328012 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm | BOOL | X * 1 | X * 1 |  | X | X |  |  | X | X
Alarm status: Alarm active | 28011 | 3 | 328012 | Parameters - Engine - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28011 | 4 | 328012 | Clock battery failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 5 | 328012 | Controller temperature too high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 6 | 328012 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 7 | 328012 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 8 | 328012 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 9 | 328012 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 10 | 328012 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 11 | 328012 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 12 | 328012 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 13 | 328012 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 14 | 328012 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 15 | 328012 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 0 | 328013 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 1 | 328013 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 2 | 328013 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 3 | 328013 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 4 | 328013 | EIM3.1 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 5 | 328013 | EIM3.1 4 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 6 | 328013 | EIM3.1 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 7 | 328013 | EIM3.1 5 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 8 | 328013 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 9 | 328013 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 10 | 328013 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 11 | 328013 | EIM3.1 4 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 12 | 328013 | EIM3.1 5 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 13 | 328013 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 14 | 328013 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 15 | 328013 | AC protections not running (differential current) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28013 | 0 | 328014 | AC data is missing (differential current) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28013 | 1 | 328014 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 2 | 328014 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 3 | 328014 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 4 | 328014 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 5 | 328014 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 6 | 328014 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 7 | 328014 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 8 | 328014 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 9 | 328014 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 10 | 328014 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 11 | 328014 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 12 | 328014 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 13 | 328014 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 14 | 328014 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 15 | 328014 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 0 | 328015 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 1 | 328015 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 2 | 328015 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 3 | 328015 | Parameters - System - Monitoring - Any bus tie breaker position failure - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28014 | 4 | 328015 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 5 | 328015 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28014 | 6 | 328015 | Parameters - System - Monitoring - Missing any controller - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28014 | 7 | 328015 | Controller ID not configured | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 8 | 328015 | Parameters - System - Monitoring - Any mains breaker position failure - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28014 | 9 | 328015 | Parameters - System - Monitoring - Data loss from a controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 10 | 328015 | Parameters - System - Monitoring - Data loss on DEIF network - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 11 | 328015 | Parameters - System - Monitoring - High traffic on DEIF network - Information - Flags - High traffic to DEIF network | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 12 | 328015 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 13 | 328015 | Parameters - System - Monitoring - Blackout detection mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28014 | 15 | 328015 | Parameters - System - Monitoring - Group alarm - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28015 | 0 | 328016 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28015 | 1 | 328016 | Parameters - Communication - NTP - NTP server 1 no response - Information - Flags - NTP server 1 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28015 | 2 | 328016 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28015 | 3 | 328016 | Parameters - Communication - NTP - NTP server 2 no response - Information - Flags - NTP server 2 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28015 | 4 | 328016 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28015 | 5 | 328016 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28015 | 6 | 328016 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28015 | 7 | 328016 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28015 | 8 | 328016 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28015 | 9 | 328016 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28015 | 10 | 328016 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28015 | 11 | 328016 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28015 | 12 | 328016 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28015 | 13 | 328016 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28015 | 14 | 328016 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28015 | 15 | 328016 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 0 | 328017 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 1 | 328017 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 2 | 328017 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 3 | 328017 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 4 | 328017 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 5 | 328017 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 6 | 328017 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 7 | 328017 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 8 | 328017 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 9 | 328017 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 10 | 328017 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 11 | 328017 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 12 | 328017 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 13 | 328017 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 14 | 328017 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28016 | 15 | 328017 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 0 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 1 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 2 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 3 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 4 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 5 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 6 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 7 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 8 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 9 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 10 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 11 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 12 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 13 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 14 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28017 | 15 | 328018 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28018 | 0 | 328019 | Parameters - Breakers - Breaker 1 feedback monitoring - Position failure - Information - Flags - Breaker 1 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm active | 28018 | 1 | 328019 | Parameters - Breakers - Breaker 1 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 1 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm active | 28018 | 2 | 328019 | Parameters - Breakers - Breaker 2 feedback monitoring - Position failure - Information - Flags - Breaker 2 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm active | 28018 | 2 | 328019 | Parameters - Breakers - BTB 1 feedback monitoring - Position failure - Information - Flags - BTB 1 position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28018 | 3 | 328019 | Parameters - Breakers - Breaker 2 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 2 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm active | 28018 | 3 | 328019 | Parameters - Breakers - BTB 1 feedback monitoring - Feedback mismatch - Information - Flags - BTB 1 feedback mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28018 | 4 | 328019 | Parameters - Breakers - Breaker 3 feedback monitoring - Position failure - Information - Flags - Breaker 3 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm active | 28018 | 4 | 328019 | Parameters - Breakers - BTB 2 feedback monitoring - Position failure - Information - Flags - BTB 2 position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28018 | 5 | 328019 | Parameters - Breakers - Breaker 3 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 3 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm active | 28018 | 5 | 328019 | Parameters - Breakers - BTB 2 feedback monitoring - Feedback mismatch - Information - Flags - BTB 2 feedback mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28018 | 6 | 328019 | Parameters - Breakers - Breaker 4 feedback monitoring - Position failure - Information - Flags - Breaker 4 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm active | 28018 | 6 | 328019 | Parameters - Breakers - BTB 3 feedback monitoring - Position failure - Information - Flags - BTB 3 position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28018 | 7 | 328019 | Parameters - Breakers - Breaker 4 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 4 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm active | 28018 | 7 | 328019 | Parameters - Breakers - BTB 3 feedback monitoring - Feedback mismatch - Information - Flags - BTB 3 feedback mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28018 | 8 | 328019 | Controller not part of system | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28018 | 9 | 328019 | Different single-line configurations | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28018 | 10 | 328019 | Single-line missing/none active | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28018 | 11 | 328019 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28018 | 12 | 328019 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28018 | 13 | 328019 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28018 | 14 | 328019 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28018 | 15 | 328019 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28019 | 0 | 328020 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28019 | 1 | 328020 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28019 | 2 | 328020 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28019 | 3 | 328020 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28019 | 4 | 328020 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28019 | 5 | 328020 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28019 | 6 | 328020 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28019 | 7 | 328020 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28019 | 8 | 328020 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28019 | 9 | 328020 | Emulation disabled (live power) | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28019 | 11 | 328020 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28019 | 12 | 328020 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28019 | 13 | 328020 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28019 | 14 | 328020 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28019 | 15 | 328020 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 0 | 328021 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 1 | 328021 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 2 | 328021 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 3 | 328021 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 4 | 328021 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 5 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 6 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 7 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 8 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 9 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 10 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 11 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 12 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 13 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 14 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28020 | 15 | 328021 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 0 | 328022 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 1 | 328022 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 2 | 328022 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 3 | 328022 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 4 | 328022 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 5 | 328022 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 6 | 328022 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 7 | 328022 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 8 | 328022 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 9 | 328022 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 10 | 328022 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 11 | 328022 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 12 | 328022 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 13 | 328022 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 14 | 328022 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28021 | 15 | 328022 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 0 | 328023 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 1 | 328023 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 2 | 328023 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 3 | 328023 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 4 | 328023 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 5 | 328023 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 6 | 328023 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 7 | 328023 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 8 | 328023 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 9 | 328023 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 10 | 328023 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 11 | 328023 | DAVR unsupported AC configuration | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 12 | 328023 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 13 | 328023 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 13 | 328023 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28022 | 13 | 328023 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28022 | 14 | 328023 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 14 | 328023 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28022 | 14 | 328023 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28022 | 15 | 328023 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28022 | 15 | 328023 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28022 | 15 | 328023 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 0 | 328024 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 0 | 328024 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 0 | 328024 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 1 | 328024 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 1 | 328024 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 1 | 328024 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 2 | 328024 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 2 | 328024 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 2 | 328024 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 3 | 328024 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 3 | 328024 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 3 | 328024 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 4 | 328024 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 4 | 328024 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 4 | 328024 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 5 | 328024 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 5 | 328024 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 5 | 328024 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 6 | 328024 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 6 | 328024 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 6 | 328024 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 7 | 328024 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 7 | 328024 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 7 | 328024 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 8 | 328024 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 8 | 328024 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 8 | 328024 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 9 | 328024 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 9 | 328024 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 9 | 328024 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 10 | 328024 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 10 | 328024 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 10 | 328024 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 11 | 328024 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 11 | 328024 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 11 | 328024 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 12 | 328024 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 12 | 328024 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 12 | 328024 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 13 | 328024 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 13 | 328024 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 13 | 328024 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 14 | 328024 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 14 | 328024 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 14 | 328024 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28023 | 15 | 328024 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28023 | 15 | 328024 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28023 | 15 | 328024 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28024 | 0 | 328025 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 1 | 328025 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 2 | 328025 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28024 | 2 | 328025 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 2 | 328025 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28024 | 3 | 328025 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28024 | 3 | 328025 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 3 | 328025 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28024 | 4 | 328025 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28024 | 4 | 328025 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 4 | 328025 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28024 | 5 | 328025 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28024 | 5 | 328025 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 5 | 328025 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28024 | 6 | 328025 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28024 | 6 | 328025 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 6 | 328025 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28024 | 7 | 328025 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28024 | 7 | 328025 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 7 | 328025 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28024 | 8 | 328025 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28024 | 8 | 328025 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 8 | 328025 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28024 | 9 | 328025 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28024 | 9 | 328025 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 9 | 328025 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28024 | 10 | 328025 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28024 | 10 | 328025 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 10 | 328025 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28024 | 11 | 328025 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28024 | 11 | 328025 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 11 | 328025 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28024 | 12 | 328025 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28024 | 12 | 328025 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 12 | 328025 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28024 | 13 | 328025 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28024 | 13 | 328025 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 13 | 328025 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28024 | 14 | 328025 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28024 | 14 | 328025 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 14 | 328025 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28024 | 15 | 328025 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28024 | 15 | 328025 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28024 | 15 | 328025 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28025 | 0 | 328026 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28025 | 0 | 328026 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28025 | 0 | 328026 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28025 | 1 | 328026 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28025 | 1 | 328026 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28025 | 1 | 328026 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28025 | 2 | 328026 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28025 | 2 | 328026 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28025 | 2 | 328026 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28025 | 3 | 328026 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28025 | 3 | 328026 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28025 | 3 | 328026 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28025 | 4 | 328026 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28025 | 4 | 328026 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28025 | 4 | 328026 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28025 | 5 | 328026 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28025 | 5 | 328026 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28025 | 5 | 328026 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28025 | 6 | 328026 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28025 | 6 | 328026 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28025 | 6 | 328026 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28025 | 7 | 328026 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28025 | 7 | 328026 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28025 | 7 | 328026 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28025 | 8 | 328026 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28025 | 8 | 328026 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28025 | 8 | 328026 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28025 | 9 | 328026 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28025 | 9 | 328026 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28025 | 9 | 328026 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28025 | 10 | 328026 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28025 | 10 | 328026 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28025 | 10 | 328026 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28025 | 11 | 328026 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28025 | 11 | 328026 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28025 | 11 | 328026 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28025 | 12 | 328026 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28025 | 12 | 328026 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28025 | 12 | 328026 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28025 | 13 | 328026 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28025 | 13 | 328026 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28025 | 13 | 328026 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28025 | 14 | 328026 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28025 | 14 | 328026 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28025 | 14 | 328026 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28025 | 15 | 328026 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28025 | 15 | 328026 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28025 | 15 | 328026 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28026 | 0 | 328027 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28026 | 0 | 328027 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28026 | 0 | 328027 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28026 | 1 | 328027 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28026 | 1 | 328027 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28026 | 1 | 328027 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28026 | 2 | 328027 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28026 | 2 | 328027 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28026 | 2 | 328027 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28026 | 3 | 328027 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28026 | 3 | 328027 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28026 | 3 | 328027 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28026 | 4 | 328027 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28026 | 4 | 328027 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28026 | 4 | 328027 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28026 | 5 | 328027 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28026 | 5 | 328027 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28026 | 5 | 328027 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28026 | 6 | 328027 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm active | 28026 | 6 | 328027 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm active | 28026 | 6 | 328027 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28026 | 7 | 328027 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28026 | 8 | 328027 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28026 | 9 | 328027 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28026 | 10 | 328027 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28026 | 11 | 328027 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28026 | 12 | 328027 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28026 | 13 | 328027 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28026 | 14 | 328027 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28026 | 15 | 328027 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 0 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 1 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 2 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 3 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 4 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 5 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 6 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 7 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 8 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 9 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 10 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 11 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 12 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 13 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 14 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28027 | 15 | 328028 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 0 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 1 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 2 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 3 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 4 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 5 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 6 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 7 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 8 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 9 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 10 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 11 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 12 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 13 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 14 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28028 | 15 | 328029 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28029 | 0 | 328030 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28029 | 1 | 328030 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28029 | 2 | 328030 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm active | 28037 | 8 | 328038 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28037 | 10 | 328038 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28037 | 12 | 328038 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28037 | 12 | 328038 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28037 | 12 | 328038 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm active | 28037 | 13 | 328038 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm active | 28037 | 13 | 328038 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28037 | 15 | 328038 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 0 | 328039 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 1 | 328039 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 2 | 328039 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 3 | 328039 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 4 | 328039 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 5 | 328039 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 6 | 328039 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 7 | 328039 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 8 | 328039 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 9 | 328039 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 10 | 328039 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 11 | 328039 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 12 | 328039 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 13 | 328039 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 14 | 328039 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 15 | 328039 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 0 | 328040 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 1 | 328040 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 2 | 328040 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 4 | 328040 | Internal issue detected. A restart is required soon! | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 6 | 328040 | Card issue detected | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 7 | 328040 | Card configuration failed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 8 | 328040 | Unknown traffic on DEIF network | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 9 | 328040 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28039 | 10 | 328040 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28039 | 11 | 328040 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm active | 28039 | 12 | 328040 | Local IO service error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 13 | 328040 | App logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 14 | 328040 | Event logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 15 | 328040 | Licence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28040 | 0 | 328041 | Brightness is dimmed according to temperature | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28093 | 12 | 328094 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28093 | 13 | 328094 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28093 | 14 | 328094 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28093 | 15 | 328094 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 0 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 1 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 2 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 3 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 4 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 5 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 6 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 7 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 8 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 9 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 10 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 11 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 12 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 13 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 14 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 15 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 0 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 1 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 2 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 3 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 4 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 5 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 6 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 7 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 8 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 9 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 10 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 11 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 12 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 13 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 14 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 15 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 0 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 1 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 2 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 3 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 4 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 5 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 6 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 7 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 8 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 9 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 10 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 11 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 12 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 13 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 0 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 1 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 2 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 3 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 4 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 5 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 6 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 7 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 8 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 9 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 10 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 11 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 12 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 13 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 14 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 15 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 0 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 1 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 2 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 3 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 4 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 5 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 6 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 7 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 8 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 9 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 10 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 11 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 12 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 13 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 14 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 15 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 0 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 1 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 2 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 3 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 4 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 5 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 6 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 7 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 8 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 9 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 10 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 11 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 12 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 13 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 14 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 15 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 0 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 1 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 2 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 3 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 4 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 5 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 6 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 7 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 8 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 9 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 10 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 11 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 12 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 13 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 14 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 15 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 0 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 1 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 2 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 3 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 4 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 5 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 6 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 7 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 8 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 9 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 10 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 11 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 12 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 13 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 14 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 15 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 0 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 1 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 2 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 3 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 4 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 5 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 6 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 7 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 8 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 9 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 10 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 11 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 12 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 13 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 14 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 15 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 0 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 1 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 2 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 3 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 4 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 5 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 6 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 7 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 8 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 9 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 10 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 11 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 12 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 13 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 14 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 15 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 0 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 1 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 2 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 3 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 4 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 5 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 6 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 7 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 8 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 9 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 10 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 11 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 12 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 13 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 14 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 15 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 0 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 1 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 2 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 3 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 4 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 5 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 6 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 7 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 8 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 9 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 10 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 11 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 12 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 13 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 14 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 15 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 0 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 1 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 2 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 3 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 4 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 5 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 6 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 7 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 8 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 9 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 10 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 11 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 12 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 13 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 14 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 15 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 0 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 1 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 2 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 3 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 4 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 5 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 6 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 7 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 8 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 9 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 10 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 11 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 12 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 13 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 14 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 15 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 0 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 1 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 2 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 3 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 4 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 5 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 6 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 7 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 8 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 9 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 10 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 11 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 12 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 13 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 14 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 15 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 0 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 1 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 2 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 3 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 4 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 5 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 6 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 7 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28125 | 0 | 328126 | Application initialisation error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28125 | 1 | 328126 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28125 | 2 | 328126 | Preliminary software | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28125 | 3 | 328126 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 4 | 328126 | Parameters - Engine - Start sequence - Start failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 5 | 328126 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 6 | 328126 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 7 | 328126 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 8 | 328126 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 9 | 328126 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 10 | 328126 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 11 | 328126 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 12 | 328126 | Parameters - Engine - Start sequence - Externally started - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 13 | 328126 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 14 | 328126 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 15 | 328126 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 0 | 328127 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 1 | 328127 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 2 | 328127 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 3 | 328127 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 4 | 328127 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 5 | 328127 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 6 | 328127 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 7 | 328127 | Number of configured stand-alone alarms is too high | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm acknowledged | 28126 | 8 | 328127 | EIM3.1 hardware revision does not support stand-alone | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm acknowledged | 28126 | 9 | 328127 | EIM3.1 safety shutdown still has control | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm acknowledged | 28126 | 10 | 328127 | EIM3.1 safety shutdown configuration is not correct | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm acknowledged | 28126 | 11 | 328127 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 12 | 328127 | Parameters - Engine - Maintenance - Running hours total - Information - Flags - Total running hours notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 13 | 328127 | Parameters - Engine - Maintenance - Running hours trip 1 - Information - Flags - Trip running hours 1 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 14 | 328127 | Parameters - Engine - Maintenance - Running hours trip 2 - Information - Flags - Trip running hours 2 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 15 | 328127 | Parameters - Engine - Maintenance - Running hours trip 3 - Information - Flags - Trip running hours 3 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 0 | 328128 | Parameters - Engine - Maintenance - Running hours trip 4 - Information - Flags - Trip running hours 4 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 1 | 328128 | Parameters - Engine - Maintenance - Running hours trip 5 - Information - Flags - Trip running hours 5 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 2 | 328128 | Parameters - Engine - Maintenance - Running hours trip 6 - Information - Flags - Trip running hours 6 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 3 | 328128 | Parameters - Engine - Maintenance - Running hours trip 7 - Information - Flags - Trip running hours 7 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 4 | 328128 | Parameters - Engine - Maintenance - Running hours trip 8 - Information - Flags - Trip running hours 8 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 5 | 328128 | Parameters - Engine - Maintenance - Running hours trip 9 - Information - Flags - Trip running hours 9 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 6 | 328128 | Parameters - Engine - Maintenance - Running hours trip 10 - Information - Flags - Trip running hours 10 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 8 | 328128 | Parameters - Engine - Start sequence - Start enable removed during start - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 9 | 328128 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 9 | 328128 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28127 | 9 | 328128 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28127 | 10 | 328128 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 10 | 328128 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28127 | 10 | 328128 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28127 | 11 | 328128 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 11 | 328128 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28127 | 11 | 328128 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28127 | 12 | 328128 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 12 | 328128 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28127 | 12 | 328128 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28127 | 13 | 328128 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 13 | 328128 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28127 | 13 | 328128 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28127 | 14 | 328128 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 14 | 328128 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28127 | 14 | 328128 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28127 | 15 | 328128 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 15 | 328128 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28127 | 15 | 328128 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28128 | 0 | 328129 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28128 | 0 | 328129 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28128 | 0 | 328129 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28128 | 1 | 328129 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm acknowledged | 28128 | 1 | 328129 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28128 | 2 | 328129 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm acknowledged | 28128 | 2 | 328129 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28128 | 3 | 328129 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm acknowledged | 28128 | 3 | 328129 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28128 | 4 | 328129 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm acknowledged | 28128 | 4 | 328129 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28128 | 5 | 328129 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm acknowledged | 28128 | 5 | 328129 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28128 | 6 | 328129 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm acknowledged | 28128 | 6 | 328129 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28128 | 7 | 328129 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm acknowledged | 28128 | 7 | 328129 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28128 | 8 | 328129 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm acknowledged | 28128 | 8 | 328129 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28128 | 12 | 328129 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28128 | 12 | 328129 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28128 | 12 | 328129 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28128 | 13 | 328129 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28128 | 13 | 328129 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28128 | 13 | 328129 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28128 | 14 | 328129 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28131 | 7 | 328132 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28131 | 7 | 328132 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28131 | 7 | 328132 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28131 | 8 | 328132 | Parameters - Mains - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28131 | 8 | 328132 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28131 | 8 | 328132 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28131 | 9 | 328132 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28131 | 9 | 328132 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28131 | 9 | 328132 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28131 | 10 | 328132 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28131 | 11 | 328132 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28131 | 12 | 328132 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28131 | 12 | 328132 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28131 | 12 | 328132 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28131 | 13 | 328132 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28131 | 13 | 328132 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28131 | 13 | 328132 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28131 | 14 | 328132 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28131 | 14 | 328132 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28131 | 14 | 328132 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28131 | 15 | 328132 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28131 | 15 | 328132 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28131 | 15 | 328132 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28132 | 3 | 328133 | Protection set point out of range | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 4 | 328133 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28132 | 5 | 328133 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28132 | 6 | 328133 | Protection set point out of range (differential current) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28132 | 7 | 328133 | Parameters - Local - Mode - Not under remote control - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 8 | 328133 | Trip AVR output not configured | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28132 | 9 | 328133 | Parameters - Local - Monitoring - System not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 10 | 328133 | Configuration update delayed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 11 | 328133 | Critical process error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 12 | 328133 | Restore error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 13 | 328133 | SD-card format error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 14 | 328133 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 15 | 328133 | Fieldbus configuration exceeded maximum I/O configuration | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 0 | 328134 | Parameters - Custom alarm - Custom alarm 0 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 1 | 328134 | Parameters - Custom alarm - Custom alarm 1 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 2 | 328134 | Parameters - Custom alarm - Custom alarm 2 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 3 | 328134 | Parameters - Custom alarm - Custom alarm 3 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 4 | 328134 | Parameters - Custom alarm - Custom alarm 4 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 5 | 328134 | Parameters - Custom alarm - Custom alarm 5 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 6 | 328134 | Parameters - Custom alarm - Custom alarm 6 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 7 | 328134 | Parameters - Custom alarm - Custom alarm 7 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 8 | 328134 | Parameters - Custom alarm - Custom alarm 8 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 9 | 328134 | Parameters - Custom alarm - Custom alarm 9 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 10 | 328134 | Parameters - Custom alarm - Custom alarm 10 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 11 | 328134 | Parameters - Custom alarm - Custom alarm 11 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 12 | 328134 | Parameters - Custom alarm - Custom alarm 12 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 13 | 328134 | Parameters - Custom alarm - Custom alarm 13 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 14 | 328134 | Parameters - Custom alarm - Custom alarm 14 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 15 | 328134 | Parameters - Custom alarm - Custom alarm 15 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 0 | 328135 | Parameters - Custom alarm - Custom alarm 16 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 1 | 328135 | Parameters - Custom alarm - Custom alarm 17 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 2 | 328135 | Parameters - Custom alarm - Custom alarm 18 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 3 | 328135 | Parameters - Custom alarm - Custom alarm 19 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 4 | 328135 | Parameters - Custom alarm - Custom alarm 20 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 5 | 328135 | Parameters - Custom alarm - Custom alarm 21 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 6 | 328135 | Parameters - Custom alarm - Custom alarm 22 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 7 | 328135 | Parameters - Custom alarm - Custom alarm 23 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 8 | 328135 | Parameters - Custom alarm - Custom alarm 24 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 9 | 328135 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28134 | 10 | 328135 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28134 | 11 | 328135 | Parameters - Regulators - GOV - Monitoring - P load sharing failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28134 | 12 | 328135 | Parameters - Regulators - AVR - Monitoring - Q load sharing failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28134 | 13 | 328135 | AVR relay setup incomplete | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28134 | 14 | 328135 | GOV relay setup incomplete | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28134 | 15 | 328135 | Parameters - Regulators - GOV - Monitoring - Regulation mode not selected - Information - Flags - GOV regulator mode not selected | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28135 | 0 | 328136 | Parameters - Regulators - AVR - Monitoring - Regulation mode not selected - Information - Flags - AVR regulator mode not selected | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28135 | 1 | 328136 | Parameters - Regulators - GOV - General configuration - Stand-alone configuration error - Information - Flags - GOV stand-alone configuration error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28135 | 2 | 328136 | Parameters - Regulators - AVR - General configuration - Stand-alone configuration error - Information - Flags - AVR stand-alone configuration error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28135 | 3 | 328136 | Required hardware card(s) not found | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28135 | 4 | 328136 | Software mismatch on hardware module(s) | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28135 | 5 | 328136 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28135 | 5 | 328136 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm acknowledged | 28135 | 5 | 328136 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28135 | 6 | 328136 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm acknowledged | 28135 | 6 | 328136 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28135 | 6 | 328136 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm acknowledged | 28135 | 7 | 328136 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28135 | 7 | 328136 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm acknowledged | 28135 | 7 | 328136 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28135 | 8 | 328136 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28135 | 8 | 328136 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm acknowledged | 28135 | 8 | 328136 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28135 | 9 | 328136 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28135 | 9 | 328136 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm acknowledged | 28135 | 9 | 328136 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28135 | 10 | 328136 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm acknowledged | 28135 | 10 | 328136 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28135 | 10 | 328136 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm acknowledged | 28135 | 11 | 328136 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm acknowledged | 28135 | 11 | 328136 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28135 | 11 | 328136 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm acknowledged | 28135 | 12 | 328136 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm acknowledged | 28135 | 12 | 328136 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28135 | 12 | 328136 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm acknowledged | 28135 | 13 | 328136 | Parameters - Hardware - GAM3.2 1 - Status not OK alarm - Information - Flags - GAM3.2 1 status not OK | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28135 | 14 | 328136 | Parameters - Hardware - GAM3.2 2 - Status not OK alarm - Information - Flags - GAM3.2 2 status not OK | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28135 | 15 | 328136 | Parameters - Hardware - GAM3.2 3 - Status not OK alarm - Information - Flags - GAM3.2 3 status not OK | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28136 | 0 | 328137 | Parameters - Breakers - Generator breaker monitoring - No synchronisation signal - Information - Flags - No synchronisation signal for asynchronous generator | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28136 | 1 | 328137 | Parameters - Generator - Voltage protections - Asynchronous over-voltage - Information - Flags - Asynchronous generator over-voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28136 | 2 | 328137 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm | BOOL | X * 1 | X * 1 |  | X | X |  |  | X | X
Alarm status: Alarm acknowledged | 28136 | 3 | 328137 | Parameters - Engine - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28136 | 4 | 328137 | Clock battery failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 5 | 328137 | Controller temperature too high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 6 | 328137 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 7 | 328137 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 8 | 328137 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 9 | 328137 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 10 | 328137 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 11 | 328137 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 12 | 328137 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 13 | 328137 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 14 | 328137 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 15 | 328137 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 0 | 328138 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 1 | 328138 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 2 | 328138 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 3 | 328138 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 4 | 328138 | EIM3.1 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 5 | 328138 | EIM3.1 4 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 6 | 328138 | EIM3.1 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 7 | 328138 | EIM3.1 5 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 8 | 328138 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 9 | 328138 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 10 | 328138 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 11 | 328138 | EIM3.1 4 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 12 | 328138 | EIM3.1 5 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 13 | 328138 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 14 | 328138 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 15 | 328138 | AC protections not running (differential current) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28138 | 0 | 328139 | AC data is missing (differential current) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28138 | 1 | 328139 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 2 | 328139 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 3 | 328139 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 4 | 328139 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 5 | 328139 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 6 | 328139 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 7 | 328139 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 8 | 328139 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 9 | 328139 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 10 | 328139 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 11 | 328139 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 12 | 328139 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 13 | 328139 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 14 | 328139 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 15 | 328139 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 0 | 328140 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 1 | 328140 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 2 | 328140 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 3 | 328140 | Parameters - System - Monitoring - Any bus tie breaker position failure - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 4 | 328140 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 5 | 328140 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 6 | 328140 | Parameters - System - Monitoring - Missing any controller - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 7 | 328140 | Controller ID not configured | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 8 | 328140 | Parameters - System - Monitoring - Any mains breaker position failure - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 9 | 328140 | Parameters - System - Monitoring - Data loss from a controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 10 | 328140 | Parameters - System - Monitoring - Data loss on DEIF network - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 11 | 328140 | Parameters - System - Monitoring - High traffic on DEIF network - Information - Flags - High traffic to DEIF network | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 12 | 328140 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 13 | 328140 | Parameters - System - Monitoring - Blackout detection mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 15 | 328140 | Parameters - System - Monitoring - Group alarm - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 0 | 328141 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 1 | 328141 | Parameters - Communication - NTP - NTP server 1 no response - Information - Flags - NTP server 1 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 2 | 328141 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 3 | 328141 | Parameters - Communication - NTP - NTP server 2 no response - Information - Flags - NTP server 2 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 4 | 328141 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 5 | 328141 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 6 | 328141 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 7 | 328141 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 8 | 328141 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 9 | 328141 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 10 | 328141 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 11 | 328141 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 12 | 328141 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 13 | 328141 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 14 | 328141 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 15 | 328141 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 0 | 328142 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 1 | 328142 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 2 | 328142 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 3 | 328142 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 4 | 328142 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 5 | 328142 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 6 | 328142 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 7 | 328142 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 8 | 328142 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 9 | 328142 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 10 | 328142 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 11 | 328142 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 12 | 328142 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 13 | 328142 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 14 | 328142 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28141 | 15 | 328142 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 0 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 1 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 2 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 3 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 4 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 5 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 6 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 7 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 8 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 9 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 10 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 11 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 12 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 13 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 14 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28142 | 15 | 328143 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28143 | 0 | 328144 | Parameters - Breakers - Breaker 1 feedback monitoring - Position failure - Information - Flags - Breaker 1 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28143 | 1 | 328144 | Parameters - Breakers - Breaker 1 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 1 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28143 | 2 | 328144 | Parameters - Breakers - Breaker 2 feedback monitoring - Position failure - Information - Flags - Breaker 2 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28143 | 2 | 328144 | Parameters - Breakers - BTB 1 feedback monitoring - Position failure - Information - Flags - BTB 1 position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28143 | 3 | 328144 | Parameters - Breakers - Breaker 2 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 2 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28143 | 3 | 328144 | Parameters - Breakers - BTB 1 feedback monitoring - Feedback mismatch - Information - Flags - BTB 1 feedback mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28143 | 4 | 328144 | Parameters - Breakers - Breaker 3 feedback monitoring - Position failure - Information - Flags - Breaker 3 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28143 | 4 | 328144 | Parameters - Breakers - BTB 2 feedback monitoring - Position failure - Information - Flags - BTB 2 position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28143 | 5 | 328144 | Parameters - Breakers - Breaker 3 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 3 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28143 | 5 | 328144 | Parameters - Breakers - BTB 2 feedback monitoring - Feedback mismatch - Information - Flags - BTB 2 feedback mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28143 | 6 | 328144 | Parameters - Breakers - Breaker 4 feedback monitoring - Position failure - Information - Flags - Breaker 4 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28143 | 6 | 328144 | Parameters - Breakers - BTB 3 feedback monitoring - Position failure - Information - Flags - BTB 3 position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28143 | 7 | 328144 | Parameters - Breakers - Breaker 4 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 4 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28143 | 7 | 328144 | Parameters - Breakers - BTB 3 feedback monitoring - Feedback mismatch - Information - Flags - BTB 3 feedback mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28143 | 8 | 328144 | Controller not part of system | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28143 | 9 | 328144 | Different single-line configurations | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28143 | 10 | 328144 | Single-line missing/none active | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28143 | 11 | 328144 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28143 | 12 | 328144 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28143 | 13 | 328144 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28143 | 14 | 328144 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28143 | 15 | 328144 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 0 | 328145 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 1 | 328145 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 2 | 328145 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 3 | 328145 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 4 | 328145 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 5 | 328145 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 6 | 328145 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 7 | 328145 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28144 | 8 | 328145 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28144 | 9 | 328145 | Emulation disabled (live power) | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28144 | 11 | 328145 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28144 | 12 | 328145 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 13 | 328145 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 14 | 328145 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 15 | 328145 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 0 | 328146 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 1 | 328146 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 2 | 328146 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 3 | 328146 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 4 | 328146 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 5 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 6 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 7 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 8 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 9 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 10 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 11 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 12 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 13 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 14 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 15 | 328146 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 0 | 328147 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 1 | 328147 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 2 | 328147 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 3 | 328147 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 4 | 328147 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 5 | 328147 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 6 | 328147 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 7 | 328147 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 8 | 328147 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 9 | 328147 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 10 | 328147 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 11 | 328147 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 12 | 328147 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 13 | 328147 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 14 | 328147 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 15 | 328147 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 0 | 328148 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 1 | 328148 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 2 | 328148 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 3 | 328148 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 4 | 328148 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 5 | 328148 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 6 | 328148 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 7 | 328148 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 8 | 328148 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 9 | 328148 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 10 | 328148 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 11 | 328148 | DAVR unsupported AC configuration | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 12 | 328148 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 13 | 328148 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 13 | 328148 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28147 | 13 | 328148 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28147 | 14 | 328148 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 14 | 328148 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28147 | 14 | 328148 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28147 | 15 | 328148 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 15 | 328148 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28147 | 15 | 328148 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 0 | 328149 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 0 | 328149 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 0 | 328149 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 1 | 328149 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 1 | 328149 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 1 | 328149 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 2 | 328149 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 2 | 328149 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 2 | 328149 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 3 | 328149 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 3 | 328149 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 3 | 328149 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 4 | 328149 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 4 | 328149 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 4 | 328149 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 5 | 328149 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 5 | 328149 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 5 | 328149 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 6 | 328149 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 6 | 328149 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 6 | 328149 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 7 | 328149 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 7 | 328149 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 7 | 328149 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 8 | 328149 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 8 | 328149 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 8 | 328149 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 9 | 328149 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 9 | 328149 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 9 | 328149 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 10 | 328149 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 10 | 328149 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 10 | 328149 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 11 | 328149 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 11 | 328149 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 11 | 328149 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 12 | 328149 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 12 | 328149 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 12 | 328149 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 13 | 328149 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 13 | 328149 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 13 | 328149 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 14 | 328149 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 14 | 328149 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 14 | 328149 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 15 | 328149 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 15 | 328149 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28148 | 15 | 328149 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 0 | 328150 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 1 | 328150 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 2 | 328150 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 2 | 328150 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 2 | 328150 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 3 | 328150 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 3 | 328150 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 3 | 328150 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 4 | 328150 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 4 | 328150 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 4 | 328150 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 5 | 328150 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 5 | 328150 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 5 | 328150 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 6 | 328150 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 6 | 328150 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 6 | 328150 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 7 | 328150 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 7 | 328150 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 7 | 328150 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 8 | 328150 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 8 | 328150 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 8 | 328150 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 9 | 328150 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 9 | 328150 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 9 | 328150 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 10 | 328150 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 10 | 328150 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 10 | 328150 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 11 | 328150 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 11 | 328150 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 11 | 328150 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 12 | 328150 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 12 | 328150 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 12 | 328150 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 13 | 328150 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 13 | 328150 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 13 | 328150 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 14 | 328150 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 14 | 328150 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 14 | 328150 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 15 | 328150 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 15 | 328150 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28149 | 15 | 328150 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28150 | 0 | 328151 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 0 | 328151 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28150 | 0 | 328151 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28150 | 1 | 328151 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 1 | 328151 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28150 | 1 | 328151 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28150 | 2 | 328151 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 2 | 328151 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28150 | 2 | 328151 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28150 | 3 | 328151 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 3 | 328151 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28150 | 3 | 328151 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28150 | 4 | 328151 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 4 | 328151 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28150 | 4 | 328151 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28150 | 5 | 328151 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28150 | 5 | 328151 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28150 | 5 | 328151 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28150 | 6 | 328151 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28150 | 6 | 328151 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28150 | 6 | 328151 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28150 | 7 | 328151 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28150 | 7 | 328151 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28150 | 7 | 328151 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28150 | 8 | 328151 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28150 | 8 | 328151 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28150 | 8 | 328151 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28150 | 9 | 328151 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28150 | 9 | 328151 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28150 | 9 | 328151 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28150 | 10 | 328151 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28150 | 10 | 328151 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28150 | 10 | 328151 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28150 | 11 | 328151 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28150 | 11 | 328151 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28150 | 11 | 328151 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28150 | 12 | 328151 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28150 | 12 | 328151 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28150 | 12 | 328151 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28150 | 13 | 328151 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28150 | 13 | 328151 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28150 | 13 | 328151 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28150 | 14 | 328151 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28150 | 14 | 328151 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28150 | 14 | 328151 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28150 | 15 | 328151 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28150 | 15 | 328151 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28150 | 15 | 328151 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28151 | 0 | 328152 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28151 | 0 | 328152 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28151 | 0 | 328152 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28151 | 1 | 328152 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28151 | 1 | 328152 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28151 | 1 | 328152 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28151 | 2 | 328152 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28151 | 2 | 328152 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28151 | 2 | 328152 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28151 | 3 | 328152 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28151 | 3 | 328152 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28151 | 3 | 328152 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28151 | 4 | 328152 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28151 | 4 | 328152 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28151 | 4 | 328152 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28151 | 5 | 328152 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28151 | 5 | 328152 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28151 | 5 | 328152 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28151 | 6 | 328152 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm acknowledged | 28151 | 6 | 328152 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm acknowledged | 28151 | 6 | 328152 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28151 | 7 | 328152 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28151 | 8 | 328152 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28151 | 9 | 328152 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28151 | 10 | 328152 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28151 | 11 | 328152 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28151 | 12 | 328152 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28151 | 13 | 328152 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28151 | 14 | 328152 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28151 | 15 | 328152 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 0 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 1 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 2 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 3 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 4 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 5 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 6 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 7 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 8 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 9 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 10 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 11 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 12 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 13 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 14 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28152 | 15 | 328153 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 0 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 1 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 2 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 3 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 4 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 5 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 6 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 7 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 8 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 9 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 10 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 11 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 12 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 13 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 14 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28153 | 15 | 328154 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28154 | 0 | 328155 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28154 | 1 | 328155 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28154 | 2 | 328155 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm acknowledged | 28162 | 8 | 328163 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28162 | 10 | 328163 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28162 | 12 | 328163 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28162 | 12 | 328163 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28162 | 12 | 328163 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm acknowledged | 28162 | 13 | 328163 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm acknowledged | 28162 | 13 | 328163 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28162 | 15 | 328163 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 0 | 328164 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 1 | 328164 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 2 | 328164 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 3 | 328164 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 4 | 328164 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 5 | 328164 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 6 | 328164 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 7 | 328164 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 8 | 328164 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 9 | 328164 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 10 | 328164 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 11 | 328164 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 12 | 328164 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 13 | 328164 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 14 | 328164 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 15 | 328164 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 0 | 328165 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 1 | 328165 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 2 | 328165 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 4 | 328165 | Internal issue detected. A restart is required soon! | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 6 | 328165 | Card issue detected | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 7 | 328165 | Card configuration failed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 8 | 328165 | Unknown traffic on DEIF network | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 9 | 328165 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28164 | 10 | 328165 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28164 | 11 | 328165 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm acknowledged | 28164 | 12 | 328165 | Local IO service error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 13 | 328165 | App logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 14 | 328165 | Event logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 15 | 328165 | Licence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28165 | 0 | 328166 | Brightness is dimmed according to temperature | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28218 | 12 | 328219 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28218 | 13 | 328219 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28218 | 14 | 328219 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28218 | 15 | 328219 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 0 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 1 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 2 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 3 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 4 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 5 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 6 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 7 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 8 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 9 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 10 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 11 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 12 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 13 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 14 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 15 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 0 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 1 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 2 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 3 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 4 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 5 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 6 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 7 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 8 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 9 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 10 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 11 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 12 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 13 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 14 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 15 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 0 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 1 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 2 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 3 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 4 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 5 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 6 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 7 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 8 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 9 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 10 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 11 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 12 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 13 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 0 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 1 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 2 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 3 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 4 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 5 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 6 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 7 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 8 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 9 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 10 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 11 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 12 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 13 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 14 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 15 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 0 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 1 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 2 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 3 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 4 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 5 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 6 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 7 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 8 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 9 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 10 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 11 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 12 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 13 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 14 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 15 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 0 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 1 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 2 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 3 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 4 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 5 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 6 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 7 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 8 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 9 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 10 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 11 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 12 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 13 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 14 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 15 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 0 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 1 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 2 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 3 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 4 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 5 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 6 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 7 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 8 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 9 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 10 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 11 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 12 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 13 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 14 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 15 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 0 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 1 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 2 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 3 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 4 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 5 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 6 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 7 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 8 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 9 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 10 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 11 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 12 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 13 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 14 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 15 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 0 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 1 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 2 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 3 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 4 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 5 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 6 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 7 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 8 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 9 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 10 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 11 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 12 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 13 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 14 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 15 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 0 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 1 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 2 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 3 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 4 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 5 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 6 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 7 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 8 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 9 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 10 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 11 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 12 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 13 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 14 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 15 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 0 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 1 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 2 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 3 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 4 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 5 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 6 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 7 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 8 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 9 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 10 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 11 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 12 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 13 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 14 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 15 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 0 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 1 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 2 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 3 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 4 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 5 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 6 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 7 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 8 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 9 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 10 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 11 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 12 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 13 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 14 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 15 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 0 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 1 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 2 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 3 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 4 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 5 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 6 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 7 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 8 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 9 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 10 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 11 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 12 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 13 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 14 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 15 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 0 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 1 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 2 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 3 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 4 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 5 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 6 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 7 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 8 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 9 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 10 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 11 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 12 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 13 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 14 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 15 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 0 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 1 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 2 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 3 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 4 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 5 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 6 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 7 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 8 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 9 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 10 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 11 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 12 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 13 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 14 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 15 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 0 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 1 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 2 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 3 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 4 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 5 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 6 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 7 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28250 | 0 | 328251 | Application initialisation error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28250 | 1 | 328251 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28250 | 2 | 328251 | Preliminary software | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28250 | 3 | 328251 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28250 | 4 | 328251 | Parameters - Engine - Start sequence - Start failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28250 | 5 | 328251 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28250 | 6 | 328251 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28250 | 7 | 328251 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28250 | 8 | 328251 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28250 | 9 | 328251 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28250 | 10 | 328251 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28250 | 11 | 328251 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28250 | 12 | 328251 | Parameters - Engine - Start sequence - Externally started - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28250 | 13 | 328251 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28250 | 14 | 328251 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28250 | 15 | 328251 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28251 | 0 | 328252 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28251 | 1 | 328252 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28251 | 2 | 328252 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28251 | 3 | 328252 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28251 | 4 | 328252 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28251 | 5 | 328252 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28251 | 6 | 328252 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28251 | 7 | 328252 | Number of configured stand-alone alarms is too high | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm latched | 28251 | 8 | 328252 | EIM3.1 hardware revision does not support stand-alone | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm latched | 28251 | 9 | 328252 | EIM3.1 safety shutdown still has control | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm latched | 28251 | 10 | 328252 | EIM3.1 safety shutdown configuration is not correct | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Alarm latched | 28251 | 11 | 328252 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28251 | 12 | 328252 | Parameters - Engine - Maintenance - Running hours total - Information - Flags - Total running hours notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28251 | 13 | 328252 | Parameters - Engine - Maintenance - Running hours trip 1 - Information - Flags - Trip running hours 1 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28251 | 14 | 328252 | Parameters - Engine - Maintenance - Running hours trip 2 - Information - Flags - Trip running hours 2 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28251 | 15 | 328252 | Parameters - Engine - Maintenance - Running hours trip 3 - Information - Flags - Trip running hours 3 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 0 | 328253 | Parameters - Engine - Maintenance - Running hours trip 4 - Information - Flags - Trip running hours 4 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 1 | 328253 | Parameters - Engine - Maintenance - Running hours trip 5 - Information - Flags - Trip running hours 5 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 2 | 328253 | Parameters - Engine - Maintenance - Running hours trip 6 - Information - Flags - Trip running hours 6 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 3 | 328253 | Parameters - Engine - Maintenance - Running hours trip 7 - Information - Flags - Trip running hours 7 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 4 | 328253 | Parameters - Engine - Maintenance - Running hours trip 8 - Information - Flags - Trip running hours 8 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 5 | 328253 | Parameters - Engine - Maintenance - Running hours trip 9 - Information - Flags - Trip running hours 9 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 6 | 328253 | Parameters - Engine - Maintenance - Running hours trip 10 - Information - Flags - Trip running hours 10 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 8 | 328253 | Parameters - Engine - Start sequence - Start enable removed during start - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 9 | 328253 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 9 | 328253 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28252 | 9 | 328253 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28252 | 10 | 328253 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 10 | 328253 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28252 | 10 | 328253 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28252 | 11 | 328253 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 11 | 328253 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28252 | 11 | 328253 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28252 | 12 | 328253 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 12 | 328253 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28252 | 12 | 328253 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28252 | 13 | 328253 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 13 | 328253 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28252 | 13 | 328253 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28252 | 14 | 328253 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 14 | 328253 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28252 | 14 | 328253 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28252 | 15 | 328253 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28252 | 15 | 328253 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28252 | 15 | 328253 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28253 | 0 | 328254 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28253 | 0 | 328254 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28253 | 0 | 328254 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28253 | 1 | 328254 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm latched | 28253 | 1 | 328254 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28253 | 2 | 328254 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm latched | 28253 | 2 | 328254 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28253 | 3 | 328254 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm latched | 28253 | 3 | 328254 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28253 | 4 | 328254 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm latched | 28253 | 4 | 328254 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28253 | 5 | 328254 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm latched | 28253 | 5 | 328254 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28253 | 6 | 328254 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm latched | 28253 | 6 | 328254 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28253 | 7 | 328254 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm latched | 28253 | 7 | 328254 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28253 | 8 | 328254 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm latched | 28253 | 8 | 328254 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28253 | 12 | 328254 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28253 | 12 | 328254 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28253 | 12 | 328254 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28253 | 13 | 328254 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28253 | 13 | 328254 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28253 | 13 | 328254 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28253 | 14 | 328254 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28256 | 7 | 328257 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28256 | 7 | 328257 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28256 | 7 | 328257 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28256 | 8 | 328257 | Parameters - Mains - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28256 | 8 | 328257 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28256 | 8 | 328257 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28256 | 9 | 328257 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28256 | 9 | 328257 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28256 | 9 | 328257 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28256 | 10 | 328257 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28256 | 11 | 328257 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28256 | 12 | 328257 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28256 | 12 | 328257 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28256 | 12 | 328257 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28256 | 13 | 328257 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28256 | 13 | 328257 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28256 | 13 | 328257 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28256 | 14 | 328257 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28256 | 14 | 328257 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28256 | 14 | 328257 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28256 | 15 | 328257 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28256 | 15 | 328257 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28256 | 15 | 328257 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28257 | 3 | 328258 | Protection set point out of range | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 4 | 328258 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28257 | 5 | 328258 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28257 | 6 | 328258 | Protection set point out of range (differential current) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28257 | 7 | 328258 | Parameters - Local - Mode - Not under remote control - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 8 | 328258 | Trip AVR output not configured | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28257 | 9 | 328258 | Parameters - Local - Monitoring - System not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 10 | 328258 | Configuration update delayed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 11 | 328258 | Critical process error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 12 | 328258 | Restore error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 13 | 328258 | SD-card format error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 14 | 328258 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 15 | 328258 | Fieldbus configuration exceeded maximum I/O configuration | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 0 | 328259 | Parameters - Custom alarm - Custom alarm 0 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 1 | 328259 | Parameters - Custom alarm - Custom alarm 1 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 2 | 328259 | Parameters - Custom alarm - Custom alarm 2 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 3 | 328259 | Parameters - Custom alarm - Custom alarm 3 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 4 | 328259 | Parameters - Custom alarm - Custom alarm 4 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 5 | 328259 | Parameters - Custom alarm - Custom alarm 5 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 6 | 328259 | Parameters - Custom alarm - Custom alarm 6 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 7 | 328259 | Parameters - Custom alarm - Custom alarm 7 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 8 | 328259 | Parameters - Custom alarm - Custom alarm 8 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 9 | 328259 | Parameters - Custom alarm - Custom alarm 9 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 10 | 328259 | Parameters - Custom alarm - Custom alarm 10 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 11 | 328259 | Parameters - Custom alarm - Custom alarm 11 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 12 | 328259 | Parameters - Custom alarm - Custom alarm 12 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 13 | 328259 | Parameters - Custom alarm - Custom alarm 13 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 14 | 328259 | Parameters - Custom alarm - Custom alarm 14 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 15 | 328259 | Parameters - Custom alarm - Custom alarm 15 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 0 | 328260 | Parameters - Custom alarm - Custom alarm 16 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 1 | 328260 | Parameters - Custom alarm - Custom alarm 17 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 2 | 328260 | Parameters - Custom alarm - Custom alarm 18 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 3 | 328260 | Parameters - Custom alarm - Custom alarm 19 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 4 | 328260 | Parameters - Custom alarm - Custom alarm 20 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 5 | 328260 | Parameters - Custom alarm - Custom alarm 21 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 6 | 328260 | Parameters - Custom alarm - Custom alarm 22 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 7 | 328260 | Parameters - Custom alarm - Custom alarm 23 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 8 | 328260 | Parameters - Custom alarm - Custom alarm 24 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 9 | 328260 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28259 | 10 | 328260 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28259 | 11 | 328260 | Parameters - Regulators - GOV - Monitoring - P load sharing failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28259 | 12 | 328260 | Parameters - Regulators - AVR - Monitoring - Q load sharing failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28259 | 13 | 328260 | AVR relay setup incomplete | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28259 | 14 | 328260 | GOV relay setup incomplete | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28259 | 15 | 328260 | Parameters - Regulators - GOV - Monitoring - Regulation mode not selected - Information - Flags - GOV regulator mode not selected | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28260 | 0 | 328261 | Parameters - Regulators - AVR - Monitoring - Regulation mode not selected - Information - Flags - AVR regulator mode not selected | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28260 | 1 | 328261 | Parameters - Regulators - GOV - General configuration - Stand-alone configuration error - Information - Flags - GOV stand-alone configuration error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28260 | 2 | 328261 | Parameters - Regulators - AVR - General configuration - Stand-alone configuration error - Information - Flags - AVR stand-alone configuration error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28260 | 3 | 328261 | Required hardware card(s) not found | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28260 | 4 | 328261 | Software mismatch on hardware module(s) | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28260 | 5 | 328261 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28260 | 5 | 328261 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm latched | 28260 | 5 | 328261 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28260 | 6 | 328261 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm latched | 28260 | 6 | 328261 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28260 | 6 | 328261 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm latched | 28260 | 7 | 328261 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28260 | 7 | 328261 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm latched | 28260 | 7 | 328261 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28260 | 8 | 328261 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28260 | 8 | 328261 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm latched | 28260 | 8 | 328261 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28260 | 9 | 328261 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28260 | 9 | 328261 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Alarm latched | 28260 | 9 | 328261 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28260 | 10 | 328261 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm latched | 28260 | 10 | 328261 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28260 | 10 | 328261 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm latched | 28260 | 11 | 328261 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm latched | 28260 | 11 | 328261 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28260 | 11 | 328261 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm latched | 28260 | 12 | 328261 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Alarm latched | 28260 | 12 | 328261 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28260 | 12 | 328261 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Alarm latched | 28260 | 13 | 328261 | Parameters - Hardware - GAM3.2 1 - Status not OK alarm - Information - Flags - GAM3.2 1 status not OK | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28260 | 14 | 328261 | Parameters - Hardware - GAM3.2 2 - Status not OK alarm - Information - Flags - GAM3.2 2 status not OK | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28260 | 15 | 328261 | Parameters - Hardware - GAM3.2 3 - Status not OK alarm - Information - Flags - GAM3.2 3 status not OK | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28261 | 0 | 328262 | Parameters - Breakers - Generator breaker monitoring - No synchronisation signal - Information - Flags - No synchronisation signal for asynchronous generator | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28261 | 1 | 328262 | Parameters - Generator - Voltage protections - Asynchronous over-voltage - Information - Flags - Asynchronous generator over-voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28261 | 2 | 328262 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm | BOOL | X * 1 | X * 1 |  | X | X |  |  | X | X
Alarm status: Alarm latched | 28261 | 3 | 328262 | Parameters - Engine - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28261 | 4 | 328262 | Clock battery failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 5 | 328262 | Controller temperature too high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 6 | 328262 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 7 | 328262 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 8 | 328262 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 9 | 328262 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 10 | 328262 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 11 | 328262 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 12 | 328262 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 13 | 328262 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 14 | 328262 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 15 | 328262 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 0 | 328263 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 1 | 328263 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 2 | 328263 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 3 | 328263 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 4 | 328263 | EIM3.1 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 5 | 328263 | EIM3.1 4 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 6 | 328263 | EIM3.1 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 7 | 328263 | EIM3.1 5 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 8 | 328263 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 9 | 328263 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 10 | 328263 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 11 | 328263 | EIM3.1 4 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 12 | 328263 | EIM3.1 5 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 13 | 328263 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 14 | 328263 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 15 | 328263 | AC protections not running (differential current) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28263 | 0 | 328264 | AC data is missing (differential current) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28263 | 1 | 328264 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 2 | 328264 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 3 | 328264 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 4 | 328264 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 5 | 328264 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 6 | 328264 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 7 | 328264 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 8 | 328264 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 9 | 328264 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 10 | 328264 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 11 | 328264 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 12 | 328264 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 13 | 328264 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 14 | 328264 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 15 | 328264 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 0 | 328265 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 1 | 328265 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 2 | 328265 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 3 | 328265 | Parameters - System - Monitoring - Any bus tie breaker position failure - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28264 | 4 | 328265 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 5 | 328265 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28264 | 6 | 328265 | Parameters - System - Monitoring - Missing any controller - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28264 | 7 | 328265 | Controller ID not configured | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 8 | 328265 | Parameters - System - Monitoring - Any mains breaker position failure - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28264 | 9 | 328265 | Parameters - System - Monitoring - Data loss from a controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 10 | 328265 | Parameters - System - Monitoring - Data loss on DEIF network - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 11 | 328265 | Parameters - System - Monitoring - High traffic on DEIF network - Information - Flags - High traffic to DEIF network | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 12 | 328265 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 13 | 328265 | Parameters - System - Monitoring - Blackout detection mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28264 | 15 | 328265 | Parameters - System - Monitoring - Group alarm - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28265 | 0 | 328266 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28265 | 1 | 328266 | Parameters - Communication - NTP - NTP server 1 no response - Information - Flags - NTP server 1 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28265 | 2 | 328266 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28265 | 3 | 328266 | Parameters - Communication - NTP - NTP server 2 no response - Information - Flags - NTP server 2 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28265 | 4 | 328266 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28265 | 5 | 328266 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28265 | 6 | 328266 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28265 | 7 | 328266 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28265 | 8 | 328266 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28265 | 9 | 328266 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28265 | 10 | 328266 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28265 | 11 | 328266 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28265 | 12 | 328266 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28265 | 13 | 328266 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28265 | 14 | 328266 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28265 | 15 | 328266 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 0 | 328267 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 1 | 328267 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 2 | 328267 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 3 | 328267 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 4 | 328267 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 5 | 328267 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 6 | 328267 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 7 | 328267 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 8 | 328267 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 9 | 328267 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 10 | 328267 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 11 | 328267 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 12 | 328267 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 13 | 328267 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 14 | 328267 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28266 | 15 | 328267 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 0 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 1 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 2 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 3 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 4 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 5 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 6 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 7 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 8 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 9 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 10 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 11 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 12 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 13 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 14 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28267 | 15 | 328268 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28268 | 0 | 328269 | Parameters - Breakers - Breaker 1 feedback monitoring - Position failure - Information - Flags - Breaker 1 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm latched | 28268 | 1 | 328269 | Parameters - Breakers - Breaker 1 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 1 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm latched | 28268 | 2 | 328269 | Parameters - Breakers - Breaker 2 feedback monitoring - Position failure - Information - Flags - Breaker 2 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm latched | 28268 | 2 | 328269 | Parameters - Breakers - BTB 1 feedback monitoring - Position failure - Information - Flags - BTB 1 position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28268 | 3 | 328269 | Parameters - Breakers - Breaker 2 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 2 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm latched | 28268 | 3 | 328269 | Parameters - Breakers - BTB 1 feedback monitoring - Feedback mismatch - Information - Flags - BTB 1 feedback mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28268 | 4 | 328269 | Parameters - Breakers - Breaker 3 feedback monitoring - Position failure - Information - Flags - Breaker 3 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm latched | 28268 | 4 | 328269 | Parameters - Breakers - BTB 2 feedback monitoring - Position failure - Information - Flags - BTB 2 position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28268 | 5 | 328269 | Parameters - Breakers - Breaker 3 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 3 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm latched | 28268 | 5 | 328269 | Parameters - Breakers - BTB 2 feedback monitoring - Feedback mismatch - Information - Flags - BTB 2 feedback mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28268 | 6 | 328269 | Parameters - Breakers - Breaker 4 feedback monitoring - Position failure - Information - Flags - Breaker 4 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm latched | 28268 | 6 | 328269 | Parameters - Breakers - BTB 3 feedback monitoring - Position failure - Information - Flags - BTB 3 position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28268 | 7 | 328269 | Parameters - Breakers - Breaker 4 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 4 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Alarm latched | 28268 | 7 | 328269 | Parameters - Breakers - BTB 3 feedback monitoring - Feedback mismatch - Information - Flags - BTB 3 feedback mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28268 | 8 | 328269 | Controller not part of system | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28268 | 9 | 328269 | Different single-line configurations | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28268 | 10 | 328269 | Single-line missing/none active | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28268 | 11 | 328269 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28268 | 12 | 328269 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28268 | 13 | 328269 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28268 | 14 | 328269 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28268 | 15 | 328269 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28269 | 0 | 328270 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28269 | 1 | 328270 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28269 | 2 | 328270 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28269 | 3 | 328270 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28269 | 4 | 328270 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28269 | 5 | 328270 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28269 | 6 | 328270 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28269 | 7 | 328270 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28269 | 8 | 328270 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28269 | 9 | 328270 | Emulation disabled (live power) | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28269 | 11 | 328270 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28269 | 12 | 328270 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28269 | 13 | 328270 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28269 | 14 | 328270 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28269 | 15 | 328270 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 0 | 328271 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 1 | 328271 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 2 | 328271 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 3 | 328271 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 4 | 328271 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 5 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 6 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 7 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 8 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 9 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 10 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 11 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 12 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 13 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 14 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28270 | 15 | 328271 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 0 | 328272 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 1 | 328272 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 2 | 328272 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 3 | 328272 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 4 | 328272 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 5 | 328272 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 6 | 328272 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 7 | 328272 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 8 | 328272 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 9 | 328272 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 10 | 328272 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 11 | 328272 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 12 | 328272 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 13 | 328272 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 14 | 328272 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28271 | 15 | 328272 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 0 | 328273 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 1 | 328273 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 2 | 328273 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 3 | 328273 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 4 | 328273 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 5 | 328273 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 6 | 328273 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 7 | 328273 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 8 | 328273 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 9 | 328273 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 10 | 328273 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 11 | 328273 | DAVR unsupported AC configuration | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 12 | 328273 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 13 | 328273 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 13 | 328273 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28272 | 13 | 328273 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28272 | 14 | 328273 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 14 | 328273 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28272 | 14 | 328273 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28272 | 15 | 328273 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28272 | 15 | 328273 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28272 | 15 | 328273 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 0 | 328274 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 0 | 328274 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 0 | 328274 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 1 | 328274 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 1 | 328274 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 1 | 328274 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 2 | 328274 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 2 | 328274 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 2 | 328274 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 3 | 328274 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 3 | 328274 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 3 | 328274 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 4 | 328274 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 4 | 328274 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 4 | 328274 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 5 | 328274 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 5 | 328274 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 5 | 328274 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 6 | 328274 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 6 | 328274 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 6 | 328274 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 7 | 328274 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 7 | 328274 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 7 | 328274 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 8 | 328274 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 8 | 328274 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 8 | 328274 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 9 | 328274 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 9 | 328274 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 9 | 328274 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 10 | 328274 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 10 | 328274 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 10 | 328274 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 11 | 328274 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 11 | 328274 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 11 | 328274 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 12 | 328274 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 12 | 328274 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 12 | 328274 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 13 | 328274 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 13 | 328274 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 13 | 328274 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 14 | 328274 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 14 | 328274 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 14 | 328274 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28273 | 15 | 328274 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28273 | 15 | 328274 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28273 | 15 | 328274 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28274 | 0 | 328275 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 1 | 328275 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 2 | 328275 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28274 | 2 | 328275 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 2 | 328275 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28274 | 3 | 328275 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28274 | 3 | 328275 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 3 | 328275 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28274 | 4 | 328275 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28274 | 4 | 328275 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 4 | 328275 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28274 | 5 | 328275 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28274 | 5 | 328275 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 5 | 328275 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28274 | 6 | 328275 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28274 | 6 | 328275 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 6 | 328275 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28274 | 7 | 328275 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28274 | 7 | 328275 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 7 | 328275 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28274 | 8 | 328275 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28274 | 8 | 328275 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 8 | 328275 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28274 | 9 | 328275 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28274 | 9 | 328275 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 9 | 328275 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28274 | 10 | 328275 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28274 | 10 | 328275 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 10 | 328275 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28274 | 11 | 328275 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28274 | 11 | 328275 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 11 | 328275 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28274 | 12 | 328275 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28274 | 12 | 328275 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 12 | 328275 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28274 | 13 | 328275 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28274 | 13 | 328275 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 13 | 328275 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28274 | 14 | 328275 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28274 | 14 | 328275 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 14 | 328275 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28274 | 15 | 328275 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28274 | 15 | 328275 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28274 | 15 | 328275 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28275 | 0 | 328276 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28275 | 0 | 328276 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28275 | 0 | 328276 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28275 | 1 | 328276 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28275 | 1 | 328276 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28275 | 1 | 328276 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28275 | 2 | 328276 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28275 | 2 | 328276 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28275 | 2 | 328276 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28275 | 3 | 328276 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28275 | 3 | 328276 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28275 | 3 | 328276 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28275 | 4 | 328276 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28275 | 4 | 328276 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28275 | 4 | 328276 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28275 | 5 | 328276 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28275 | 5 | 328276 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28275 | 5 | 328276 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28275 | 6 | 328276 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28275 | 6 | 328276 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28275 | 6 | 328276 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28275 | 7 | 328276 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28275 | 7 | 328276 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28275 | 7 | 328276 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28275 | 8 | 328276 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28275 | 8 | 328276 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28275 | 8 | 328276 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28275 | 9 | 328276 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28275 | 9 | 328276 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28275 | 9 | 328276 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28275 | 10 | 328276 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28275 | 10 | 328276 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28275 | 10 | 328276 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28275 | 11 | 328276 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28275 | 11 | 328276 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28275 | 11 | 328276 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28275 | 12 | 328276 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28275 | 12 | 328276 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28275 | 12 | 328276 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28275 | 13 | 328276 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28275 | 13 | 328276 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28275 | 13 | 328276 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28275 | 14 | 328276 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28275 | 14 | 328276 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28275 | 14 | 328276 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28275 | 15 | 328276 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28275 | 15 | 328276 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28275 | 15 | 328276 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28276 | 0 | 328277 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28276 | 0 | 328277 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28276 | 0 | 328277 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28276 | 1 | 328277 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28276 | 1 | 328277 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28276 | 1 | 328277 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28276 | 2 | 328277 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28276 | 2 | 328277 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28276 | 2 | 328277 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28276 | 3 | 328277 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28276 | 3 | 328277 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28276 | 3 | 328277 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28276 | 4 | 328277 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28276 | 4 | 328277 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28276 | 4 | 328277 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28276 | 5 | 328277 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28276 | 5 | 328277 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28276 | 5 | 328277 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28276 | 6 | 328277 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Alarm latched | 28276 | 6 | 328277 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Alarm latched | 28276 | 6 | 328277 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28276 | 7 | 328277 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28276 | 8 | 328277 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28276 | 9 | 328277 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28276 | 10 | 328277 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28276 | 11 | 328277 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28276 | 12 | 328277 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28276 | 13 | 328277 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28276 | 14 | 328277 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28276 | 15 | 328277 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 0 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 1 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 2 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 3 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 4 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 5 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 6 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 7 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 8 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 9 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 10 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 11 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 12 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 13 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 14 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28277 | 15 | 328278 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 0 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 1 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 2 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 3 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 4 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 5 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 6 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 7 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 8 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 9 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 10 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 11 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 12 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 13 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 14 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28278 | 15 | 328279 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28279 | 0 | 328280 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28279 | 1 | 328280 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28279 | 2 | 328280 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Alarm latched | 28287 | 8 | 328288 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28287 | 10 | 328288 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28287 | 12 | 328288 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28287 | 12 | 328288 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28287 | 12 | 328288 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Alarm latched | 28287 | 13 | 328288 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  | X
Alarm status: Alarm latched | 28287 | 13 | 328288 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28287 | 15 | 328288 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 0 | 328289 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 1 | 328289 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 2 | 328289 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 3 | 328289 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 4 | 328289 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 5 | 328289 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 6 | 328289 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 7 | 328289 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 8 | 328289 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 9 | 328289 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 10 | 328289 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 11 | 328289 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 12 | 328289 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 13 | 328289 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 14 | 328289 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 15 | 328289 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 0 | 328290 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 1 | 328290 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 2 | 328290 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 4 | 328290 | Internal issue detected. A restart is required soon! | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 6 | 328290 | Card issue detected | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 7 | 328290 | Card configuration failed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 8 | 328290 | Unknown traffic on DEIF network | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 9 | 328290 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28289 | 10 | 328290 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28289 | 11 | 328290 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Alarm latched | 28289 | 12 | 328290 | Local IO service error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 13 | 328290 | App logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 14 | 328290 | Event logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 15 | 328290 | Licence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28290 | 0 | 328291 | Brightness is dimmed according to temperature | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28343 | 12 | 328344 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28343 | 13 | 328344 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28343 | 14 | 328344 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28343 | 15 | 328344 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 0 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 1 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 2 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 3 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 4 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 5 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 6 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 7 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 8 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 9 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 10 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 11 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 12 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 13 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 14 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 15 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 0 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 1 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 2 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 3 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 4 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 5 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 6 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 7 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 8 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 9 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 10 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 11 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 12 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 13 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 14 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 15 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 0 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 1 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 2 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 3 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 4 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 5 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 6 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 7 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 8 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 9 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 10 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 11 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 12 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 13 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 0 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 1 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 2 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 3 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 4 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 5 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 6 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 7 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 8 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 9 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 10 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 11 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 12 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 13 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 14 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 15 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 0 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 1 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 2 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 3 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 4 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 5 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 6 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 7 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 8 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 9 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 10 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 11 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 12 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 13 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 14 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 15 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 0 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 1 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 2 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 3 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 4 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 5 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 6 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 7 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 8 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 9 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 10 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 11 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 12 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 13 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 14 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 15 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 0 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 1 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 2 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 3 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 4 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 5 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 6 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 7 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 8 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 9 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 10 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 11 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 12 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 13 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 14 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 15 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 0 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 1 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 2 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 3 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 4 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 5 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 6 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 7 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 8 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 9 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 10 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 11 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 12 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 13 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 14 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 15 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 0 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 1 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 2 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 3 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 4 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 5 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 6 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 7 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 8 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 9 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 10 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 11 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 12 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 13 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 14 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 15 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 0 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 1 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 2 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 3 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 4 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 5 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 6 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 7 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 8 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 9 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 10 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 11 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 12 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 13 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 14 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 15 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 0 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 1 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 2 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 3 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 4 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 5 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 6 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 7 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 8 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 9 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 10 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 11 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 12 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 13 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 14 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 15 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 0 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 1 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 2 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 3 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 4 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 5 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 6 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 7 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 8 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 9 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 10 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 11 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 12 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 13 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 14 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 15 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 0 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 1 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 2 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 3 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 4 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 5 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 6 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 7 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 8 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 9 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 10 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 11 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 12 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 13 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 14 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 15 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 0 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 1 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 2 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 3 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 4 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 5 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 6 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 7 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 8 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 9 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 10 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 11 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 12 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 13 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 14 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 15 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 0 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 1 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 2 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 3 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 4 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 5 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 6 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 7 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 8 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 9 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 10 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 11 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 12 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 13 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 14 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 15 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 0 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 1 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 2 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 3 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 4 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 5 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 6 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 7 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28375 | 0 | 328376 | Application initialisation error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28375 | 1 | 328376 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28375 | 2 | 328376 | Preliminary software | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28375 | 3 | 328376 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28375 | 4 | 328376 | Parameters - Engine - Start sequence - Start failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28375 | 5 | 328376 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28375 | 6 | 328376 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28375 | 7 | 328376 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28375 | 8 | 328376 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28375 | 9 | 328376 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28375 | 10 | 328376 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28375 | 11 | 328376 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28375 | 12 | 328376 | Parameters - Engine - Start sequence - Externally started - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28375 | 13 | 328376 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28375 | 14 | 328376 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28375 | 15 | 328376 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28376 | 0 | 328377 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28376 | 1 | 328377 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28376 | 2 | 328377 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28376 | 3 | 328377 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28376 | 4 | 328377 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28376 | 5 | 328377 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28376 | 6 | 328377 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28376 | 7 | 328377 | Number of configured stand-alone alarms is too high | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Inhibited | 28376 | 8 | 328377 | EIM3.1 hardware revision does not support stand-alone | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Inhibited | 28376 | 9 | 328377 | EIM3.1 safety shutdown still has control | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Inhibited | 28376 | 10 | 328377 | EIM3.1 safety shutdown configuration is not correct | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Inhibited | 28376 | 11 | 328377 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28376 | 12 | 328377 | Parameters - Engine - Maintenance - Running hours total - Information - Flags - Total running hours notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28376 | 13 | 328377 | Parameters - Engine - Maintenance - Running hours trip 1 - Information - Flags - Trip running hours 1 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28376 | 14 | 328377 | Parameters - Engine - Maintenance - Running hours trip 2 - Information - Flags - Trip running hours 2 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28376 | 15 | 328377 | Parameters - Engine - Maintenance - Running hours trip 3 - Information - Flags - Trip running hours 3 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 0 | 328378 | Parameters - Engine - Maintenance - Running hours trip 4 - Information - Flags - Trip running hours 4 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 1 | 328378 | Parameters - Engine - Maintenance - Running hours trip 5 - Information - Flags - Trip running hours 5 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 2 | 328378 | Parameters - Engine - Maintenance - Running hours trip 6 - Information - Flags - Trip running hours 6 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 3 | 328378 | Parameters - Engine - Maintenance - Running hours trip 7 - Information - Flags - Trip running hours 7 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 4 | 328378 | Parameters - Engine - Maintenance - Running hours trip 8 - Information - Flags - Trip running hours 8 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 5 | 328378 | Parameters - Engine - Maintenance - Running hours trip 9 - Information - Flags - Trip running hours 9 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 6 | 328378 | Parameters - Engine - Maintenance - Running hours trip 10 - Information - Flags - Trip running hours 10 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 8 | 328378 | Parameters - Engine - Start sequence - Start enable removed during start - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 9 | 328378 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 9 | 328378 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28377 | 9 | 328378 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28377 | 10 | 328378 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 10 | 328378 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28377 | 10 | 328378 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28377 | 11 | 328378 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 11 | 328378 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28377 | 11 | 328378 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28377 | 12 | 328378 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 12 | 328378 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28377 | 12 | 328378 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28377 | 13 | 328378 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 13 | 328378 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28377 | 13 | 328378 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28377 | 14 | 328378 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 14 | 328378 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28377 | 14 | 328378 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28377 | 15 | 328378 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28377 | 15 | 328378 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28377 | 15 | 328378 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28378 | 0 | 328379 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28378 | 0 | 328379 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28378 | 0 | 328379 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28378 | 1 | 328379 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Inhibited | 28378 | 1 | 328379 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28378 | 2 | 328379 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Inhibited | 28378 | 2 | 328379 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28378 | 3 | 328379 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Inhibited | 28378 | 3 | 328379 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28378 | 4 | 328379 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Inhibited | 28378 | 4 | 328379 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28378 | 5 | 328379 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Inhibited | 28378 | 5 | 328379 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28378 | 6 | 328379 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Inhibited | 28378 | 6 | 328379 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28378 | 7 | 328379 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 |  | X
Alarm status: Inhibited | 28378 | 7 | 328379 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28378 | 8 | 328379 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 |  | X
Alarm status: Inhibited | 28378 | 8 | 328379 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28378 | 12 | 328379 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28378 | 12 | 328379 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28378 | 12 | 328379 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28378 | 13 | 328379 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28378 | 13 | 328379 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28378 | 13 | 328379 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28378 | 14 | 328379 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28381 | 7 | 328382 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28381 | 7 | 328382 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28381 | 7 | 328382 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28381 | 8 | 328382 | Parameters - Mains - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28381 | 8 | 328382 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28381 | 8 | 328382 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28381 | 9 | 328382 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28381 | 9 | 328382 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28381 | 9 | 328382 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28381 | 10 | 328382 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28381 | 11 | 328382 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28381 | 12 | 328382 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28381 | 12 | 328382 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28381 | 12 | 328382 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28381 | 13 | 328382 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28381 | 13 | 328382 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28381 | 13 | 328382 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28381 | 14 | 328382 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28381 | 14 | 328382 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28381 | 14 | 328382 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28381 | 15 | 328382 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28381 | 15 | 328382 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28381 | 15 | 328382 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28382 | 3 | 328383 | Protection set point out of range | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 4 | 328383 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28382 | 5 | 328383 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28382 | 6 | 328383 | Protection set point out of range (differential current) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28382 | 7 | 328383 | Parameters - Local - Mode - Not under remote control - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 8 | 328383 | Trip AVR output not configured | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28382 | 9 | 328383 | Parameters - Local - Monitoring - System not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 10 | 328383 | Configuration update delayed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 11 | 328383 | Critical process error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 12 | 328383 | Restore error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 13 | 328383 | SD-card format error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 14 | 328383 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 15 | 328383 | Fieldbus configuration exceeded maximum I/O configuration | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 0 | 328384 | Parameters - Custom alarm - Custom alarm 0 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 1 | 328384 | Parameters - Custom alarm - Custom alarm 1 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 2 | 328384 | Parameters - Custom alarm - Custom alarm 2 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 3 | 328384 | Parameters - Custom alarm - Custom alarm 3 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 4 | 328384 | Parameters - Custom alarm - Custom alarm 4 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 5 | 328384 | Parameters - Custom alarm - Custom alarm 5 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 6 | 328384 | Parameters - Custom alarm - Custom alarm 6 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 7 | 328384 | Parameters - Custom alarm - Custom alarm 7 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 8 | 328384 | Parameters - Custom alarm - Custom alarm 8 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 9 | 328384 | Parameters - Custom alarm - Custom alarm 9 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 10 | 328384 | Parameters - Custom alarm - Custom alarm 10 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 11 | 328384 | Parameters - Custom alarm - Custom alarm 11 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 12 | 328384 | Parameters - Custom alarm - Custom alarm 12 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 13 | 328384 | Parameters - Custom alarm - Custom alarm 13 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 14 | 328384 | Parameters - Custom alarm - Custom alarm 14 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 15 | 328384 | Parameters - Custom alarm - Custom alarm 15 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 0 | 328385 | Parameters - Custom alarm - Custom alarm 16 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 1 | 328385 | Parameters - Custom alarm - Custom alarm 17 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 2 | 328385 | Parameters - Custom alarm - Custom alarm 18 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 3 | 328385 | Parameters - Custom alarm - Custom alarm 19 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 4 | 328385 | Parameters - Custom alarm - Custom alarm 20 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 5 | 328385 | Parameters - Custom alarm - Custom alarm 21 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 6 | 328385 | Parameters - Custom alarm - Custom alarm 22 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 7 | 328385 | Parameters - Custom alarm - Custom alarm 23 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 8 | 328385 | Parameters - Custom alarm - Custom alarm 24 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 9 | 328385 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28384 | 10 | 328385 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28384 | 11 | 328385 | Parameters - Regulators - GOV - Monitoring - P load sharing failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28384 | 12 | 328385 | Parameters - Regulators - AVR - Monitoring - Q load sharing failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28384 | 13 | 328385 | AVR relay setup incomplete | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28384 | 14 | 328385 | GOV relay setup incomplete | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28384 | 15 | 328385 | Parameters - Regulators - GOV - Monitoring - Regulation mode not selected - Information - Flags - GOV regulator mode not selected | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28385 | 0 | 328386 | Parameters - Regulators - AVR - Monitoring - Regulation mode not selected - Information - Flags - AVR regulator mode not selected | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28385 | 1 | 328386 | Parameters - Regulators - GOV - General configuration - Stand-alone configuration error - Information - Flags - GOV stand-alone configuration error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28385 | 2 | 328386 | Parameters - Regulators - AVR - General configuration - Stand-alone configuration error - Information - Flags - AVR stand-alone configuration error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28385 | 3 | 328386 | Required hardware card(s) not found | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28385 | 4 | 328386 | Software mismatch on hardware module(s) | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28385 | 5 | 328386 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28385 | 5 | 328386 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Inhibited | 28385 | 5 | 328386 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28385 | 6 | 328386 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Inhibited | 28385 | 6 | 328386 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28385 | 6 | 328386 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Inhibited | 28385 | 7 | 328386 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28385 | 7 | 328386 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Inhibited | 28385 | 7 | 328386 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28385 | 8 | 328386 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28385 | 8 | 328386 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Inhibited | 28385 | 8 | 328386 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28385 | 9 | 328386 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28385 | 9 | 328386 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Inhibited | 28385 | 9 | 328386 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28385 | 10 | 328386 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Inhibited | 28385 | 10 | 328386 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28385 | 10 | 328386 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Inhibited | 28385 | 11 | 328386 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Inhibited | 28385 | 11 | 328386 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28385 | 11 | 328386 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Inhibited | 28385 | 12 | 328386 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Inhibited | 28385 | 12 | 328386 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28385 | 12 | 328386 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Inhibited | 28385 | 13 | 328386 | Parameters - Hardware - GAM3.2 1 - Status not OK alarm - Information - Flags - GAM3.2 1 status not OK | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28385 | 14 | 328386 | Parameters - Hardware - GAM3.2 2 - Status not OK alarm - Information - Flags - GAM3.2 2 status not OK | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28385 | 15 | 328386 | Parameters - Hardware - GAM3.2 3 - Status not OK alarm - Information - Flags - GAM3.2 3 status not OK | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28386 | 0 | 328387 | Parameters - Breakers - Generator breaker monitoring - No synchronisation signal - Information - Flags - No synchronisation signal for asynchronous generator | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28386 | 1 | 328387 | Parameters - Generator - Voltage protections - Asynchronous over-voltage - Information - Flags - Asynchronous generator over-voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28386 | 2 | 328387 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm | BOOL | X * 1 | X * 1 |  | X | X |  |  | X | X
Alarm status: Inhibited | 28386 | 3 | 328387 | Parameters - Engine - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28386 | 4 | 328387 | Clock battery failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 5 | 328387 | Controller temperature too high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 6 | 328387 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 7 | 328387 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 8 | 328387 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 9 | 328387 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 10 | 328387 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 11 | 328387 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 12 | 328387 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 13 | 328387 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 14 | 328387 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 15 | 328387 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 0 | 328388 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 1 | 328388 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 2 | 328388 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 3 | 328388 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 4 | 328388 | EIM3.1 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 5 | 328388 | EIM3.1 4 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 6 | 328388 | EIM3.1 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 7 | 328388 | EIM3.1 5 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 8 | 328388 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 9 | 328388 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 10 | 328388 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 11 | 328388 | EIM3.1 4 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 12 | 328388 | EIM3.1 5 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 13 | 328388 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 14 | 328388 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 15 | 328388 | AC protections not running (differential current) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28388 | 0 | 328389 | AC data is missing (differential current) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28388 | 1 | 328389 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 2 | 328389 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 3 | 328389 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 4 | 328389 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 5 | 328389 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 6 | 328389 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 7 | 328389 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 8 | 328389 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 9 | 328389 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 10 | 328389 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 11 | 328389 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 12 | 328389 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 13 | 328389 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 14 | 328389 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 15 | 328389 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 0 | 328390 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 1 | 328390 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 2 | 328390 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 3 | 328390 | Parameters - System - Monitoring - Any bus tie breaker position failure - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28389 | 4 | 328390 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 5 | 328390 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28389 | 6 | 328390 | Parameters - System - Monitoring - Missing any controller - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28389 | 7 | 328390 | Controller ID not configured | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 8 | 328390 | Parameters - System - Monitoring - Any mains breaker position failure - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28389 | 9 | 328390 | Parameters - System - Monitoring - Data loss from a controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 10 | 328390 | Parameters - System - Monitoring - Data loss on DEIF network - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 11 | 328390 | Parameters - System - Monitoring - High traffic on DEIF network - Information - Flags - High traffic to DEIF network | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 12 | 328390 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 13 | 328390 | Parameters - System - Monitoring - Blackout detection mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28389 | 15 | 328390 | Parameters - System - Monitoring - Group alarm - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28390 | 0 | 328391 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 1 | 328391 | Parameters - Communication - NTP - NTP server 1 no response - Information - Flags - NTP server 1 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 2 | 328391 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 3 | 328391 | Parameters - Communication - NTP - NTP server 2 no response - Information - Flags - NTP server 2 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 4 | 328391 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 5 | 328391 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 6 | 328391 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 7 | 328391 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 8 | 328391 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28390 | 9 | 328391 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28390 | 10 | 328391 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28390 | 11 | 328391 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28390 | 12 | 328391 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28390 | 13 | 328391 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28390 | 14 | 328391 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28390 | 15 | 328391 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 0 | 328392 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 1 | 328392 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 2 | 328392 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 3 | 328392 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 4 | 328392 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 5 | 328392 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 6 | 328392 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 7 | 328392 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 8 | 328392 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 9 | 328392 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 10 | 328392 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 11 | 328392 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 12 | 328392 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 13 | 328392 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 14 | 328392 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28391 | 15 | 328392 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 0 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 1 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 2 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 3 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 4 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 5 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 6 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 7 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 8 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 9 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 10 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 11 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 12 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 13 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 14 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28392 | 15 | 328393 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28393 | 0 | 328394 | Parameters - Breakers - Breaker 1 feedback monitoring - Position failure - Information - Flags - Breaker 1 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Inhibited | 28393 | 1 | 328394 | Parameters - Breakers - Breaker 1 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 1 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Inhibited | 28393 | 2 | 328394 | Parameters - Breakers - Breaker 2 feedback monitoring - Position failure - Information - Flags - Breaker 2 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Inhibited | 28393 | 2 | 328394 | Parameters - Breakers - BTB 1 feedback monitoring - Position failure - Information - Flags - BTB 1 position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28393 | 3 | 328394 | Parameters - Breakers - Breaker 2 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 2 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Inhibited | 28393 | 3 | 328394 | Parameters - Breakers - BTB 1 feedback monitoring - Feedback mismatch - Information - Flags - BTB 1 feedback mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28393 | 4 | 328394 | Parameters - Breakers - Breaker 3 feedback monitoring - Position failure - Information - Flags - Breaker 3 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Inhibited | 28393 | 4 | 328394 | Parameters - Breakers - BTB 2 feedback monitoring - Position failure - Information - Flags - BTB 2 position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28393 | 5 | 328394 | Parameters - Breakers - Breaker 3 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 3 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Inhibited | 28393 | 5 | 328394 | Parameters - Breakers - BTB 2 feedback monitoring - Feedback mismatch - Information - Flags - BTB 2 feedback mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28393 | 6 | 328394 | Parameters - Breakers - Breaker 4 feedback monitoring - Position failure - Information - Flags - Breaker 4 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Inhibited | 28393 | 6 | 328394 | Parameters - Breakers - BTB 3 feedback monitoring - Position failure - Information - Flags - BTB 3 position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28393 | 7 | 328394 | Parameters - Breakers - Breaker 4 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 4 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Inhibited | 28393 | 7 | 328394 | Parameters - Breakers - BTB 3 feedback monitoring - Feedback mismatch - Information - Flags - BTB 3 feedback mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28393 | 8 | 328394 | Controller not part of system | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28393 | 9 | 328394 | Different single-line configurations | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28393 | 10 | 328394 | Single-line missing/none active | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28393 | 11 | 328394 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28393 | 12 | 328394 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28393 | 13 | 328394 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28393 | 14 | 328394 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28393 | 15 | 328394 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28394 | 0 | 328395 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28394 | 1 | 328395 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28394 | 2 | 328395 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28394 | 3 | 328395 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28394 | 4 | 328395 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28394 | 5 | 328395 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28394 | 6 | 328395 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28394 | 7 | 328395 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28394 | 8 | 328395 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28394 | 9 | 328395 | Emulation disabled (live power) | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28394 | 11 | 328395 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28394 | 12 | 328395 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28394 | 13 | 328395 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28394 | 14 | 328395 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28394 | 15 | 328395 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 0 | 328396 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 1 | 328396 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 2 | 328396 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 3 | 328396 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 4 | 328396 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 5 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 6 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 7 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 8 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 9 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 10 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 11 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 12 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 13 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 14 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28395 | 15 | 328396 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 0 | 328397 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 1 | 328397 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 2 | 328397 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 3 | 328397 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 4 | 328397 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 5 | 328397 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 6 | 328397 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 7 | 328397 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 8 | 328397 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 9 | 328397 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 10 | 328397 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 11 | 328397 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 12 | 328397 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 13 | 328397 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 14 | 328397 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28396 | 15 | 328397 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 0 | 328398 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 1 | 328398 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 2 | 328398 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 3 | 328398 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 4 | 328398 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 5 | 328398 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 6 | 328398 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 7 | 328398 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 8 | 328398 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 9 | 328398 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 10 | 328398 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 11 | 328398 | DAVR unsupported AC configuration | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 12 | 328398 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 13 | 328398 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 13 | 328398 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28397 | 13 | 328398 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28397 | 14 | 328398 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 14 | 328398 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28397 | 14 | 328398 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28397 | 15 | 328398 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28397 | 15 | 328398 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28397 | 15 | 328398 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 0 | 328399 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 0 | 328399 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 0 | 328399 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 1 | 328399 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 1 | 328399 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 1 | 328399 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 2 | 328399 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 2 | 328399 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 2 | 328399 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 3 | 328399 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 3 | 328399 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 3 | 328399 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 4 | 328399 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 4 | 328399 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 4 | 328399 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 5 | 328399 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 5 | 328399 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 5 | 328399 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 6 | 328399 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 6 | 328399 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 6 | 328399 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 7 | 328399 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 7 | 328399 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 7 | 328399 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 8 | 328399 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 8 | 328399 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 8 | 328399 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 9 | 328399 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 9 | 328399 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 9 | 328399 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 10 | 328399 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 10 | 328399 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 10 | 328399 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 11 | 328399 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 11 | 328399 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 11 | 328399 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 12 | 328399 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 12 | 328399 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 12 | 328399 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 13 | 328399 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 13 | 328399 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 13 | 328399 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 14 | 328399 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 14 | 328399 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 14 | 328399 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28398 | 15 | 328399 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28398 | 15 | 328399 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28398 | 15 | 328399 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28399 | 0 | 328400 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 1 | 328400 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 2 | 328400 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28399 | 2 | 328400 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 2 | 328400 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28399 | 3 | 328400 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28399 | 3 | 328400 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 3 | 328400 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28399 | 4 | 328400 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28399 | 4 | 328400 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 4 | 328400 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28399 | 5 | 328400 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28399 | 5 | 328400 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 5 | 328400 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28399 | 6 | 328400 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28399 | 6 | 328400 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 6 | 328400 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28399 | 7 | 328400 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28399 | 7 | 328400 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 7 | 328400 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28399 | 8 | 328400 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28399 | 8 | 328400 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 8 | 328400 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28399 | 9 | 328400 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28399 | 9 | 328400 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 9 | 328400 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28399 | 10 | 328400 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28399 | 10 | 328400 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 10 | 328400 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28399 | 11 | 328400 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28399 | 11 | 328400 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 11 | 328400 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28399 | 12 | 328400 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28399 | 12 | 328400 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 12 | 328400 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28399 | 13 | 328400 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28399 | 13 | 328400 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 13 | 328400 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28399 | 14 | 328400 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28399 | 14 | 328400 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 14 | 328400 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28399 | 15 | 328400 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28399 | 15 | 328400 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28399 | 15 | 328400 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28400 | 0 | 328401 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28400 | 0 | 328401 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28400 | 0 | 328401 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28400 | 1 | 328401 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28400 | 1 | 328401 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28400 | 1 | 328401 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28400 | 2 | 328401 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28400 | 2 | 328401 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28400 | 2 | 328401 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28400 | 3 | 328401 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28400 | 3 | 328401 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28400 | 3 | 328401 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28400 | 4 | 328401 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28400 | 4 | 328401 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28400 | 4 | 328401 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28400 | 5 | 328401 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28400 | 5 | 328401 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28400 | 5 | 328401 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28400 | 6 | 328401 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28400 | 6 | 328401 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28400 | 6 | 328401 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28400 | 7 | 328401 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28400 | 7 | 328401 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28400 | 7 | 328401 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28400 | 8 | 328401 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28400 | 8 | 328401 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28400 | 8 | 328401 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28400 | 9 | 328401 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28400 | 9 | 328401 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28400 | 9 | 328401 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28400 | 10 | 328401 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28400 | 10 | 328401 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28400 | 10 | 328401 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28400 | 11 | 328401 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28400 | 11 | 328401 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28400 | 11 | 328401 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28400 | 12 | 328401 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28400 | 12 | 328401 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28400 | 12 | 328401 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28400 | 13 | 328401 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28400 | 13 | 328401 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28400 | 13 | 328401 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28400 | 14 | 328401 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28400 | 14 | 328401 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28400 | 14 | 328401 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28400 | 15 | 328401 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28400 | 15 | 328401 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28400 | 15 | 328401 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28401 | 0 | 328402 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28401 | 0 | 328402 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28401 | 0 | 328402 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28401 | 1 | 328402 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28401 | 1 | 328402 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28401 | 1 | 328402 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28401 | 2 | 328402 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28401 | 2 | 328402 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28401 | 2 | 328402 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28401 | 3 | 328402 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28401 | 3 | 328402 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28401 | 3 | 328402 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28401 | 4 | 328402 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28401 | 4 | 328402 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28401 | 4 | 328402 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28401 | 5 | 328402 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28401 | 5 | 328402 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28401 | 5 | 328402 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28401 | 6 | 328402 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Inhibited | 28401 | 6 | 328402 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Inhibited | 28401 | 6 | 328402 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28401 | 7 | 328402 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28401 | 8 | 328402 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28401 | 9 | 328402 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28401 | 10 | 328402 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28401 | 11 | 328402 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28401 | 12 | 328402 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28401 | 13 | 328402 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28401 | 14 | 328402 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28401 | 15 | 328402 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 0 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 1 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 2 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 3 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 4 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 5 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 6 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 7 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 8 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 9 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 10 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 11 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 12 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 13 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 14 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28402 | 15 | 328403 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 0 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 1 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 2 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 3 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 4 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 5 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 6 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 7 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 8 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 9 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 10 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 11 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 12 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 13 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 14 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28403 | 15 | 328404 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28404 | 0 | 328405 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28404 | 1 | 328405 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28404 | 2 | 328405 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Inhibited | 28412 | 8 | 328413 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28412 | 10 | 328413 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28412 | 12 | 328413 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28412 | 12 | 328413 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28412 | 12 | 328413 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Inhibited | 28412 | 13 | 328413 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  | X
Alarm status: Inhibited | 28412 | 13 | 328413 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28412 | 15 | 328413 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 0 | 328414 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 1 | 328414 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 2 | 328414 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 3 | 328414 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 4 | 328414 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 5 | 328414 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 6 | 328414 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 7 | 328414 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 8 | 328414 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 9 | 328414 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 10 | 328414 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 11 | 328414 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 12 | 328414 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 13 | 328414 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 14 | 328414 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 15 | 328414 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 0 | 328415 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 1 | 328415 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 2 | 328415 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 4 | 328415 | Internal issue detected. A restart is required soon! | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 6 | 328415 | Card issue detected | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 7 | 328415 | Card configuration failed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 8 | 328415 | Unknown traffic on DEIF network | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 9 | 328415 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28414 | 10 | 328415 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28414 | 11 | 328415 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Inhibited | 28414 | 12 | 328415 | Local IO service error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 13 | 328415 | App logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 14 | 328415 | Event logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 15 | 328415 | Licence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28415 | 0 | 328416 | Brightness is dimmed according to temperature | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28468 | 12 | 328469 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28468 | 13 | 328469 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28468 | 14 | 328469 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28468 | 15 | 328469 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 0 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 1 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 2 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 3 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 4 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 5 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 6 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 7 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 8 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 9 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 10 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 11 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 12 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 13 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 14 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 15 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 0 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 1 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 2 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 3 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 4 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 5 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 6 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 7 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 8 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 9 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 10 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 11 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 12 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 13 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 14 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 15 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 0 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 1 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 2 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 3 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 4 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 5 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 6 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 7 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 8 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 9 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 10 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 11 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 12 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 13 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 0 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 1 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 2 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 3 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 4 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 5 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 6 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 7 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 8 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 9 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 10 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 11 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 12 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 13 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 14 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 15 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 0 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 1 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 2 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 3 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 4 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 5 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 6 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 7 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 8 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 9 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 10 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 11 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 12 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 13 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 14 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 15 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 0 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 1 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 2 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 3 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 4 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 5 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 6 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 7 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 8 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 9 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 10 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 11 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 12 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 13 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 14 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 15 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 0 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 1 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 2 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 3 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 4 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 5 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 6 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 7 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 8 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 9 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 10 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 11 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 12 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 13 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 14 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 15 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 0 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 1 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 2 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 3 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 4 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 5 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 6 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 7 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 8 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 9 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 10 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 11 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 12 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 13 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 14 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 15 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 0 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 1 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 2 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 3 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 4 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 5 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 6 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 7 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 8 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 9 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 10 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 11 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 12 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 13 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 14 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 15 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 0 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 1 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 2 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 3 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 4 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 5 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 6 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 7 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 8 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 9 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 10 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 11 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 12 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 13 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 14 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 15 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 0 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 1 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 2 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 3 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 4 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 5 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 6 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 7 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 8 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 9 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 10 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 11 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 12 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 13 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 14 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 15 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 0 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 1 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 2 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 3 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 4 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 5 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 6 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 7 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 8 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 9 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 10 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 11 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 12 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 13 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 14 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 15 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 0 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 1 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 2 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 3 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 4 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 5 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 6 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 7 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 8 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 9 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 10 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 11 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 12 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 13 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 14 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 15 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 0 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 1 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 2 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 3 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 4 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 5 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 6 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 7 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 8 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 9 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 10 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 11 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 12 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 13 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 14 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 15 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 0 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 1 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 2 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 3 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 4 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 5 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 6 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 7 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 8 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 9 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 10 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 11 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 12 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 13 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 14 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 15 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 0 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 1 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 2 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 3 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 4 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 5 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 6 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 7 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28500 | 0 | 328501 | Application initialisation error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28500 | 1 | 328501 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28500 | 2 | 328501 | Preliminary software | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28500 | 3 | 328501 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28500 | 4 | 328501 | Parameters - Engine - Start sequence - Start failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28500 | 5 | 328501 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28500 | 6 | 328501 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28500 | 7 | 328501 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28500 | 8 | 328501 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28500 | 9 | 328501 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28500 | 10 | 328501 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28500 | 11 | 328501 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28500 | 12 | 328501 | Parameters - Engine - Start sequence - Externally started - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28500 | 13 | 328501 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28500 | 14 | 328501 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28500 | 15 | 328501 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28501 | 0 | 328502 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28501 | 1 | 328502 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28501 | 2 | 328502 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28501 | 3 | 328502 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28501 | 4 | 328502 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28501 | 5 | 328502 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28501 | 6 | 328502 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28501 | 7 | 328502 | Number of configured stand-alone alarms is too high | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Out of service | 28501 | 8 | 328502 | EIM3.1 hardware revision does not support stand-alone | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Out of service | 28501 | 9 | 328502 | EIM3.1 safety shutdown still has control | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Out of service | 28501 | 10 | 328502 | EIM3.1 safety shutdown configuration is not correct | BOOL | X * 1 | X * 1 |  | X |  | X
Alarm status: Out of service | 28501 | 11 | 328502 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28501 | 12 | 328502 | Parameters - Engine - Maintenance - Running hours total - Information - Flags - Total running hours notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28501 | 13 | 328502 | Parameters - Engine - Maintenance - Running hours trip 1 - Information - Flags - Trip running hours 1 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28501 | 14 | 328502 | Parameters - Engine - Maintenance - Running hours trip 2 - Information - Flags - Trip running hours 2 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28501 | 15 | 328502 | Parameters - Engine - Maintenance - Running hours trip 3 - Information - Flags - Trip running hours 3 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 0 | 328503 | Parameters - Engine - Maintenance - Running hours trip 4 - Information - Flags - Trip running hours 4 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 1 | 328503 | Parameters - Engine - Maintenance - Running hours trip 5 - Information - Flags - Trip running hours 5 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 2 | 328503 | Parameters - Engine - Maintenance - Running hours trip 6 - Information - Flags - Trip running hours 6 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 3 | 328503 | Parameters - Engine - Maintenance - Running hours trip 7 - Information - Flags - Trip running hours 7 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 4 | 328503 | Parameters - Engine - Maintenance - Running hours trip 8 - Information - Flags - Trip running hours 8 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 5 | 328503 | Parameters - Engine - Maintenance - Running hours trip 9 - Information - Flags - Trip running hours 9 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 6 | 328503 | Parameters - Engine - Maintenance - Running hours trip 10 - Information - Flags - Trip running hours 10 notification | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 8 | 328503 | Parameters - Engine - Start sequence - Start enable removed during start - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 9 | 328503 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 9 | 328503 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28502 | 9 | 328503 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28502 | 10 | 328503 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 10 | 328503 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28502 | 10 | 328503 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28502 | 11 | 328503 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 11 | 328503 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28502 | 11 | 328503 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28502 | 12 | 328503 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 12 | 328503 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28502 | 12 | 328503 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28502 | 13 | 328503 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 13 | 328503 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28502 | 13 | 328503 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28502 | 14 | 328503 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 14 | 328503 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28502 | 14 | 328503 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28502 | 15 | 328503 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28502 | 15 | 328503 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28502 | 15 | 328503 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28503 | 0 | 328504 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28503 | 0 | 328504 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28503 | 0 | 328504 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28503 | 1 | 328504 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Out of service | 28503 | 1 | 328504 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28503 | 2 | 328504 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Out of service | 28503 | 2 | 328504 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28503 | 3 | 328504 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Out of service | 28503 | 3 | 328504 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28503 | 4 | 328504 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Out of service | 28503 | 4 | 328504 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28503 | 5 | 328504 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Out of service | 28503 | 5 | 328504 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28503 | 6 | 328504 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 |  | X
Alarm status: Out of service | 28503 | 6 | 328504 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28503 | 7 | 328504 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 |  | X
Alarm status: Out of service | 28503 | 7 | 328504 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28503 | 8 | 328504 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 |  | X
Alarm status: Out of service | 28503 | 8 | 328504 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28503 | 12 | 328504 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28503 | 12 | 328504 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28503 | 12 | 328504 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28503 | 13 | 328504 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28503 | 13 | 328504 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28503 | 13 | 328504 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28503 | 14 | 328504 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28506 | 7 | 328507 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28506 | 7 | 328507 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28506 | 7 | 328507 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28506 | 8 | 328507 | Parameters - Mains - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28506 | 8 | 328507 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28506 | 8 | 328507 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28506 | 9 | 328507 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28506 | 9 | 328507 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28506 | 9 | 328507 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28506 | 10 | 328507 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28506 | 11 | 328507 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28506 | 12 | 328507 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28506 | 12 | 328507 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28506 | 12 | 328507 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28506 | 13 | 328507 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28506 | 13 | 328507 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28506 | 13 | 328507 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28506 | 14 | 328507 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28506 | 14 | 328507 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28506 | 14 | 328507 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28506 | 15 | 328507 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28506 | 15 | 328507 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28506 | 15 | 328507 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28507 | 3 | 328508 | Protection set point out of range | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 4 | 328508 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28507 | 5 | 328508 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28507 | 6 | 328508 | Protection set point out of range (differential current) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28507 | 7 | 328508 | Parameters - Local - Mode - Not under remote control - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 8 | 328508 | Trip AVR output not configured | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28507 | 9 | 328508 | Parameters - Local - Monitoring - System not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 10 | 328508 | Configuration update delayed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 11 | 328508 | Critical process error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 12 | 328508 | Restore error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 13 | 328508 | SD-card format error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 14 | 328508 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 15 | 328508 | Fieldbus configuration exceeded maximum I/O configuration | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 0 | 328509 | Parameters - Custom alarm - Custom alarm 0 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 1 | 328509 | Parameters - Custom alarm - Custom alarm 1 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 2 | 328509 | Parameters - Custom alarm - Custom alarm 2 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 3 | 328509 | Parameters - Custom alarm - Custom alarm 3 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 4 | 328509 | Parameters - Custom alarm - Custom alarm 4 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 5 | 328509 | Parameters - Custom alarm - Custom alarm 5 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 6 | 328509 | Parameters - Custom alarm - Custom alarm 6 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 7 | 328509 | Parameters - Custom alarm - Custom alarm 7 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 8 | 328509 | Parameters - Custom alarm - Custom alarm 8 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 9 | 328509 | Parameters - Custom alarm - Custom alarm 9 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 10 | 328509 | Parameters - Custom alarm - Custom alarm 10 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 11 | 328509 | Parameters - Custom alarm - Custom alarm 11 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 12 | 328509 | Parameters - Custom alarm - Custom alarm 12 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 13 | 328509 | Parameters - Custom alarm - Custom alarm 13 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 14 | 328509 | Parameters - Custom alarm - Custom alarm 14 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 15 | 328509 | Parameters - Custom alarm - Custom alarm 15 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 0 | 328510 | Parameters - Custom alarm - Custom alarm 16 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 1 | 328510 | Parameters - Custom alarm - Custom alarm 17 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 2 | 328510 | Parameters - Custom alarm - Custom alarm 18 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 3 | 328510 | Parameters - Custom alarm - Custom alarm 19 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 4 | 328510 | Parameters - Custom alarm - Custom alarm 20 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 5 | 328510 | Parameters - Custom alarm - Custom alarm 21 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 6 | 328510 | Parameters - Custom alarm - Custom alarm 22 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 7 | 328510 | Parameters - Custom alarm - Custom alarm 23 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 8 | 328510 | Parameters - Custom alarm - Custom alarm 24 - Information - Flags - | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 9 | 328510 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28509 | 10 | 328510 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28509 | 11 | 328510 | Parameters - Regulators - GOV - Monitoring - P load sharing failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28509 | 12 | 328510 | Parameters - Regulators - AVR - Monitoring - Q load sharing failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28509 | 13 | 328510 | AVR relay setup incomplete | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28509 | 14 | 328510 | GOV relay setup incomplete | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28509 | 15 | 328510 | Parameters - Regulators - GOV - Monitoring - Regulation mode not selected - Information - Flags - GOV regulator mode not selected | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28510 | 0 | 328511 | Parameters - Regulators - AVR - Monitoring - Regulation mode not selected - Information - Flags - AVR regulator mode not selected | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28510 | 1 | 328511 | Parameters - Regulators - GOV - General configuration - Stand-alone configuration error - Information - Flags - GOV stand-alone configuration error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28510 | 2 | 328511 | Parameters - Regulators - AVR - General configuration - Stand-alone configuration error - Information - Flags - AVR stand-alone configuration error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28510 | 3 | 328511 | Required hardware card(s) not found | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28510 | 4 | 328511 | Software mismatch on hardware module(s) | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28510 | 5 | 328511 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28510 | 5 | 328511 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Out of service | 28510 | 5 | 328511 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28510 | 6 | 328511 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Out of service | 28510 | 6 | 328511 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28510 | 6 | 328511 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Out of service | 28510 | 7 | 328511 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28510 | 7 | 328511 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Out of service | 28510 | 7 | 328511 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28510 | 8 | 328511 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28510 | 8 | 328511 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Out of service | 28510 | 8 | 328511 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28510 | 9 | 328511 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28510 | 9 | 328511 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Out of service | 28510 | 9 | 328511 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28510 | 10 | 328511 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Out of service | 28510 | 10 | 328511 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28510 | 10 | 328511 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Out of service | 28510 | 11 | 328511 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Out of service | 28510 | 11 | 328511 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28510 | 11 | 328511 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Out of service | 28510 | 12 | 328511 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | BOOL | X * 1 | X * 1 |  |  | X | X
Alarm status: Out of service | 28510 | 12 | 328511 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28510 | 12 | 328511 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 | [5 empty] | X
Alarm status: Out of service | 28510 | 13 | 328511 | Parameters - Hardware - GAM3.2 1 - Status not OK alarm - Information - Flags - GAM3.2 1 status not OK | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28510 | 14 | 328511 | Parameters - Hardware - GAM3.2 2 - Status not OK alarm - Information - Flags - GAM3.2 2 status not OK | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28510 | 15 | 328511 | Parameters - Hardware - GAM3.2 3 - Status not OK alarm - Information - Flags - GAM3.2 3 status not OK | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28511 | 0 | 328512 | Parameters - Breakers - Generator breaker monitoring - No synchronisation signal - Information - Flags - No synchronisation signal for asynchronous generator | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28511 | 1 | 328512 | Parameters - Generator - Voltage protections - Asynchronous over-voltage - Information - Flags - Asynchronous generator over-voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28511 | 2 | 328512 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm | BOOL | X * 1 | X * 1 |  | X | X |  |  | X | X
Alarm status: Out of service | 28511 | 3 | 328512 | Parameters - Engine - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28511 | 4 | 328512 | Clock battery failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 5 | 328512 | Controller temperature too high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 6 | 328512 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 7 | 328512 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 8 | 328512 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 9 | 328512 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 10 | 328512 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 11 | 328512 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 12 | 328512 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 13 | 328512 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 14 | 328512 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 15 | 328512 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 0 | 328513 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 1 | 328513 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 2 | 328513 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 3 | 328513 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 4 | 328513 | EIM3.1 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 5 | 328513 | EIM3.1 4 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 6 | 328513 | EIM3.1 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 7 | 328513 | EIM3.1 5 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 8 | 328513 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 9 | 328513 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 10 | 328513 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 11 | 328513 | EIM3.1 4 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 12 | 328513 | EIM3.1 5 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 13 | 328513 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 14 | 328513 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 15 | 328513 | AC protections not running (differential current) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28513 | 0 | 328514 | AC data is missing (differential current) | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28513 | 1 | 328514 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 2 | 328514 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 3 | 328514 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 4 | 328514 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 5 | 328514 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 6 | 328514 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 7 | 328514 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 8 | 328514 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 9 | 328514 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 10 | 328514 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 11 | 328514 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 12 | 328514 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 13 | 328514 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 14 | 328514 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 15 | 328514 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 0 | 328515 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 1 | 328515 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 2 | 328515 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 3 | 328515 | Parameters - System - Monitoring - Any bus tie breaker position failure - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28514 | 4 | 328515 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 5 | 328515 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28514 | 6 | 328515 | Parameters - System - Monitoring - Missing any controller - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28514 | 7 | 328515 | Controller ID not configured | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 8 | 328515 | Parameters - System - Monitoring - Any mains breaker position failure - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28514 | 9 | 328515 | Parameters - System - Monitoring - Data loss from a controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 10 | 328515 | Parameters - System - Monitoring - Data loss on DEIF network - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 11 | 328515 | Parameters - System - Monitoring - High traffic on DEIF network - Information - Flags - High traffic to DEIF network | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 12 | 328515 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 13 | 328515 | Parameters - System - Monitoring - Blackout detection mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28514 | 15 | 328515 | Parameters - System - Monitoring - Group alarm - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28515 | 0 | 328516 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28515 | 1 | 328516 | Parameters - Communication - NTP - NTP server 1 no response - Information - Flags - NTP server 1 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28515 | 2 | 328516 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28515 | 3 | 328516 | Parameters - Communication - NTP - NTP server 2 no response - Information - Flags - NTP server 2 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28515 | 4 | 328516 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28515 | 5 | 328516 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28515 | 6 | 328516 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28515 | 7 | 328516 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28515 | 8 | 328516 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28515 | 9 | 328516 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28515 | 10 | 328516 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28515 | 11 | 328516 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28515 | 12 | 328516 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28515 | 13 | 328516 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28515 | 14 | 328516 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28515 | 15 | 328516 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 0 | 328517 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 1 | 328517 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 2 | 328517 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 3 | 328517 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 4 | 328517 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 5 | 328517 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 6 | 328517 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 7 | 328517 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 8 | 328517 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 9 | 328517 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 10 | 328517 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 11 | 328517 | Missing controller(s) in group | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 12 | 328517 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 13 | 328517 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 14 | 328517 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28516 | 15 | 328517 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 0 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 1 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 2 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 3 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 4 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 5 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 6 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 7 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 8 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 9 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 10 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 11 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 12 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 13 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 14 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28517 | 15 | 328518 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28518 | 0 | 328519 | Parameters - Breakers - Breaker 1 feedback monitoring - Position failure - Information - Flags - Breaker 1 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Out of service | 28518 | 1 | 328519 | Parameters - Breakers - Breaker 1 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 1 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Out of service | 28518 | 2 | 328519 | Parameters - Breakers - Breaker 2 feedback monitoring - Position failure - Information - Flags - Breaker 2 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Out of service | 28518 | 2 | 328519 | Parameters - Breakers - BTB 1 feedback monitoring - Position failure - Information - Flags - BTB 1 position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28518 | 3 | 328519 | Parameters - Breakers - Breaker 2 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 2 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Out of service | 28518 | 3 | 328519 | Parameters - Breakers - BTB 1 feedback monitoring - Feedback mismatch - Information - Flags - BTB 1 feedback mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28518 | 4 | 328519 | Parameters - Breakers - Breaker 3 feedback monitoring - Position failure - Information - Flags - Breaker 3 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Out of service | 28518 | 4 | 328519 | Parameters - Breakers - BTB 2 feedback monitoring - Position failure - Information - Flags - BTB 2 position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28518 | 5 | 328519 | Parameters - Breakers - Breaker 3 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 3 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Out of service | 28518 | 5 | 328519 | Parameters - Breakers - BTB 2 feedback monitoring - Feedback mismatch - Information - Flags - BTB 2 feedback mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28518 | 6 | 328519 | Parameters - Breakers - Breaker 4 feedback monitoring - Position failure - Information - Flags - Breaker 4 position failure | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Out of service | 28518 | 6 | 328519 | Parameters - Breakers - BTB 3 feedback monitoring - Position failure - Information - Flags - BTB 3 position failure | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28518 | 7 | 328519 | Parameters - Breakers - Breaker 4 feedback monitoring - Feedback mismatch - Information - Flags - Breaker 4 feedback mismatch | BOOL | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Out of service | 28518 | 7 | 328519 | Parameters - Breakers - BTB 3 feedback monitoring - Feedback mismatch - Information - Flags - BTB 3 feedback mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28518 | 8 | 328519 | Controller not part of system | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28518 | 9 | 328519 | Different single-line configurations | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28518 | 10 | 328519 | Single-line missing/none active | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28518 | 11 | 328519 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28518 | 12 | 328519 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28518 | 13 | 328519 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28518 | 14 | 328519 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28518 | 15 | 328519 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28519 | 0 | 328520 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28519 | 1 | 328520 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28519 | 2 | 328520 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28519 | 3 | 328520 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28519 | 4 | 328520 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28519 | 5 | 328520 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28519 | 6 | 328520 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28519 | 7 | 328520 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28519 | 8 | 328520 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28519 | 9 | 328520 | Emulation disabled (live power) | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28519 | 11 | 328520 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28519 | 12 | 328520 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28519 | 13 | 328520 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28519 | 14 | 328520 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28519 | 15 | 328520 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 0 | 328521 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 1 | 328521 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 2 | 328521 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 3 | 328521 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 4 | 328521 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 5 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 6 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 7 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 8 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 9 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 10 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 11 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 12 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 13 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 14 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28520 | 15 | 328521 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 0 | 328522 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 1 | 328522 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 2 | 328522 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 3 | 328522 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 4 | 328522 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 5 | 328522 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 6 | 328522 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 7 | 328522 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 8 | 328522 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 9 | 328522 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 10 | 328522 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 11 | 328522 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 12 | 328522 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 13 | 328522 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 14 | 328522 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28521 | 15 | 328522 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 0 | 328523 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 1 | 328523 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 2 | 328523 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 3 | 328523 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 4 | 328523 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 5 | 328523 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 6 | 328523 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 7 | 328523 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 8 | 328523 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 9 | 328523 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 10 | 328523 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 11 | 328523 | DAVR unsupported AC configuration | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 12 | 328523 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 13 | 328523 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 13 | 328523 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28522 | 13 | 328523 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28522 | 14 | 328523 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 14 | 328523 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28522 | 14 | 328523 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28522 | 15 | 328523 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28522 | 15 | 328523 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28522 | 15 | 328523 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 0 | 328524 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 0 | 328524 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 0 | 328524 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 1 | 328524 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 1 | 328524 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 1 | 328524 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 2 | 328524 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 2 | 328524 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 2 | 328524 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 3 | 328524 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 3 | 328524 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 3 | 328524 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 4 | 328524 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 4 | 328524 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 4 | 328524 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 5 | 328524 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 5 | 328524 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 5 | 328524 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 6 | 328524 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 6 | 328524 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 6 | 328524 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 7 | 328524 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 7 | 328524 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 7 | 328524 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 8 | 328524 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 8 | 328524 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 8 | 328524 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 9 | 328524 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 9 | 328524 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 9 | 328524 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 10 | 328524 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 10 | 328524 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 10 | 328524 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 11 | 328524 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 11 | 328524 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 11 | 328524 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 12 | 328524 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 12 | 328524 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 12 | 328524 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 13 | 328524 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 13 | 328524 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 13 | 328524 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 14 | 328524 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 14 | 328524 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 14 | 328524 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28523 | 15 | 328524 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28523 | 15 | 328524 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28523 | 15 | 328524 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28524 | 0 | 328525 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 1 | 328525 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 2 | 328525 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28524 | 2 | 328525 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 2 | 328525 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28524 | 3 | 328525 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28524 | 3 | 328525 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 3 | 328525 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28524 | 4 | 328525 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28524 | 4 | 328525 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 4 | 328525 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28524 | 5 | 328525 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28524 | 5 | 328525 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 5 | 328525 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28524 | 6 | 328525 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28524 | 6 | 328525 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 6 | 328525 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28524 | 7 | 328525 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28524 | 7 | 328525 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 7 | 328525 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28524 | 8 | 328525 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28524 | 8 | 328525 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 8 | 328525 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28524 | 9 | 328525 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28524 | 9 | 328525 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 9 | 328525 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28524 | 10 | 328525 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28524 | 10 | 328525 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 10 | 328525 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28524 | 11 | 328525 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28524 | 11 | 328525 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 11 | 328525 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28524 | 12 | 328525 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28524 | 12 | 328525 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 12 | 328525 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28524 | 13 | 328525 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28524 | 13 | 328525 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 13 | 328525 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28524 | 14 | 328525 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28524 | 14 | 328525 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 14 | 328525 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28524 | 15 | 328525 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28524 | 15 | 328525 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28524 | 15 | 328525 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28525 | 0 | 328526 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28525 | 0 | 328526 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28525 | 0 | 328526 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28525 | 1 | 328526 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28525 | 1 | 328526 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28525 | 1 | 328526 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28525 | 2 | 328526 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28525 | 2 | 328526 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28525 | 2 | 328526 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28525 | 3 | 328526 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28525 | 3 | 328526 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28525 | 3 | 328526 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28525 | 4 | 328526 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28525 | 4 | 328526 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28525 | 4 | 328526 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28525 | 5 | 328526 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28525 | 5 | 328526 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28525 | 5 | 328526 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28525 | 6 | 328526 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28525 | 6 | 328526 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28525 | 6 | 328526 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28525 | 7 | 328526 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28525 | 7 | 328526 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28525 | 7 | 328526 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28525 | 8 | 328526 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28525 | 8 | 328526 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28525 | 8 | 328526 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28525 | 9 | 328526 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28525 | 9 | 328526 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28525 | 9 | 328526 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28525 | 10 | 328526 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28525 | 10 | 328526 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28525 | 10 | 328526 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28525 | 11 | 328526 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28525 | 11 | 328526 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28525 | 11 | 328526 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28525 | 12 | 328526 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28525 | 12 | 328526 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28525 | 12 | 328526 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28525 | 13 | 328526 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28525 | 13 | 328526 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28525 | 13 | 328526 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28525 | 14 | 328526 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28525 | 14 | 328526 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28525 | 14 | 328526 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28525 | 15 | 328526 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28525 | 15 | 328526 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28525 | 15 | 328526 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28526 | 0 | 328527 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28526 | 0 | 328527 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28526 | 0 | 328527 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28526 | 1 | 328527 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28526 | 1 | 328527 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28526 | 1 | 328527 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28526 | 2 | 328527 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28526 | 2 | 328527 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28526 | 2 | 328527 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28526 | 3 | 328527 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28526 | 3 | 328527 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28526 | 3 | 328527 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28526 | 4 | 328527 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28526 | 4 | 328527 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28526 | 4 | 328527 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28526 | 5 | 328527 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28526 | 5 | 328527 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28526 | 5 | 328527 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28526 | 6 | 328527 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X | X
Alarm status: Out of service | 28526 | 6 | 328527 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Out of service | 28526 | 6 | 328527 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28526 | 7 | 328527 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28526 | 8 | 328527 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28526 | 9 | 328527 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28526 | 10 | 328527 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28526 | 11 | 328527 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28526 | 12 | 328527 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28526 | 13 | 328527 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28526 | 14 | 328527 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28526 | 15 | 328527 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 0 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 1 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 2 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 3 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 4 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 5 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 6 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 7 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 8 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 9 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 10 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 11 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 12 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 13 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 14 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28527 | 15 | 328528 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 0 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 1 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 2 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 3 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 4 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 5 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 6 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 7 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 8 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 9 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 10 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 11 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 12 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 13 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 14 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28528 | 15 | 328529 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28529 | 0 | 328530 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28529 | 1 | 328530 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28529 | 2 | 328530 | Missing controller | BOOL | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Out of service | 28537 | 8 | 328538 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28537 | 10 | 328538 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28537 | 12 | 328538 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28537 | 12 | 328538 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28537 | 12 | 328538 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Out of service | 28537 | 13 | 328538 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  | X
Alarm status: Out of service | 28537 | 13 | 328538 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28537 | 15 | 328538 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 0 | 328539 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 1 | 328539 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 2 | 328539 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 3 | 328539 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 4 | 328539 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 5 | 328539 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 6 | 328539 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 7 | 328539 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 8 | 328539 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 9 | 328539 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 10 | 328539 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 11 | 328539 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 12 | 328539 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 13 | 328539 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 14 | 328539 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 15 | 328539 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 0 | 328540 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 1 | 328540 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 2 | 328540 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 4 | 328540 | Internal issue detected. A restart is required soon! | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 6 | 328540 | Card issue detected | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 7 | 328540 | Card configuration failed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 8 | 328540 | Unknown traffic on DEIF network | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 9 | 328540 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28539 | 10 | 328540 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28539 | 11 | 328540 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X | X | X
Alarm status: Out of service | 28539 | 12 | 328540 | Local IO service error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 13 | 328540 | App logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 14 | 328540 | Event logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 15 | 328540 | Licence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28540 | 0 | 328541 | Brightness is dimmed according to temperature | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28593 | 12 | 328594 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28593 | 13 | 328594 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28593 | 14 | 328594 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28593 | 15 | 328594 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 0 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 1 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 2 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 3 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 4 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 5 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 6 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 7 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 8 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 9 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 10 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 11 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 12 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 13 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 14 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 15 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 0 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 1 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 2 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 3 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 4 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 5 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 6 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 7 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 8 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 9 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 10 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 11 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 12 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 13 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 14 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 15 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 0 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 1 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 2 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 3 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 4 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 5 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 6 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 7 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 8 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 9 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 10 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 11 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 12 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 13 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 0 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 1 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 2 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 3 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 4 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 5 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 6 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 7 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 8 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 9 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 10 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 11 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 12 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 13 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 14 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 15 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 0 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 1 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 2 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 3 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 4 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 5 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 6 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 7 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 8 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 9 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 10 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 11 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 12 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 13 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 14 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 15 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 0 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 1 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 2 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 3 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 4 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 5 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 6 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 7 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 8 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 9 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 10 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 11 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 12 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 13 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 14 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 15 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 0 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 1 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 2 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 3 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 4 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 5 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 6 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 7 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 8 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 9 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 10 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 11 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 12 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 13 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 14 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 15 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 0 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 1 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 2 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 3 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 4 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 5 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 6 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 7 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 8 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 9 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 10 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 11 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 12 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 13 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 14 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 15 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 0 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 1 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 2 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 3 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 4 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 5 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 6 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 7 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 8 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 9 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 10 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 11 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 12 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 13 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 14 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 15 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 0 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 1 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 2 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 3 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 4 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 5 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 6 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 7 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 8 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 9 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 10 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 11 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 12 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 13 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 14 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 15 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 0 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 1 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 2 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 3 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 4 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 5 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 6 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 7 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 8 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 9 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 10 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 11 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 12 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 13 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 14 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 15 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 0 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 1 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 2 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 3 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 4 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 5 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 6 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 7 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 8 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 9 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 10 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 11 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 12 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 13 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 14 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 15 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 0 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 1 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 2 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 3 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 4 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 5 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 6 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 7 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 8 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 9 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 10 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 11 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 12 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 13 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 14 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 15 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 0 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 1 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 2 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 3 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 4 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 5 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 6 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 7 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 8 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 9 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 10 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 11 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 12 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 13 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 14 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 15 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 0 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 1 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 2 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 3 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 4 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 5 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 6 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 7 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 8 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 9 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 10 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 11 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 12 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 13 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 14 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 15 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 0 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 1 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 2 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 3 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 4 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 5 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 6 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 7 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30000 |  | 330001 | Application initialisation error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30001 |  | 330002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30002 |  | 330003 | Preliminary software | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30003 |  | 330004 | Parameters - Engine - Stop sequence - Stop failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30004 |  | 330005 | Parameters - Engine - Start sequence - Start failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30005 |  | 330006 | Parameters - Engine - Start sequence - Crank failure - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30006 |  | 330007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30007 |  | 330008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30008 |  | 330009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30009 |  | 330010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30010 |  | 330011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Magnetic pickup wire break alarm | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30011 |  | 330012 | Parameters - Engine - Stop sequence - Externally stopped - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30012 |  | 330013 | Parameters - Engine - Start sequence - Externally started - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30013 |  | 330014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30014 |  | 330015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30015 |  | 330016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30016 |  | 330017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30017 |  | 330018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30018 |  | 330019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30019 |  | 330020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30020 |  | 330021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30021 |  | 330022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30022 |  | 330023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30023 |  | 330024 | Number of configured stand-alone alarms is too high | INT16 | X * 1 | X * 1 |  | X |  | X
Alarm status: Triggered value | 30024 |  | 330025 | EIM3.1 hardware revision does not support stand-alone | INT16 | X * 1 | X * 1 |  | X |  | X
Alarm status: Triggered value | 30025 |  | 330026 | EIM3.1 safety shutdown still has control | INT16 | X * 1 | X * 1 |  | X |  | X
Alarm status: Triggered value | 30026 |  | 330027 | EIM3.1 safety shutdown configuration is not correct | INT16 | X * 1 | X * 1 |  | X |  | X
Alarm status: Triggered value | 30027 |  | 330028 | Parameters - Engine - Running detection - Primary running feedback failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30028 |  | 330029 | Parameters - Engine - Maintenance - Running hours total - Information - Total running hours notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30029 |  | 330030 | Parameters - Engine - Maintenance - Running hours trip 1 - Information - Trip running hours 1 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30030 |  | 330031 | Parameters - Engine - Maintenance - Running hours trip 2 - Information - Trip running hours 2 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30031 |  | 330032 | Parameters - Engine - Maintenance - Running hours trip 3 - Information - Trip running hours 3 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30032 |  | 330033 | Parameters - Engine - Maintenance - Running hours trip 4 - Information - Trip running hours 4 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30033 |  | 330034 | Parameters - Engine - Maintenance - Running hours trip 5 - Information - Trip running hours 5 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30034 |  | 330035 | Parameters - Engine - Maintenance - Running hours trip 6 - Information - Trip running hours 6 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30035 |  | 330036 | Parameters - Engine - Maintenance - Running hours trip 7 - Information - Trip running hours 7 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30036 |  | 330037 | Parameters - Engine - Maintenance - Running hours trip 8 - Information - Trip running hours 8 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30037 |  | 330038 | Parameters - Engine - Maintenance - Running hours trip 9 - Information - Trip running hours 9 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30038 |  | 330039 | Parameters - Engine - Maintenance - Running hours trip 10 - Information - Trip running hours 10 notification | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30040 |  | 330041 | Parameters - Engine - Start sequence - Start enable removed during start - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30041 |  | 330042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - GB closing failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30041 |  | 330042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - BTB closing failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30041 |  | 330042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - MB closing failure | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Triggered value | 30042 |  | 330043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - GB opening failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30042 |  | 330043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - BTB opening failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30042 |  | 330043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - MB opening failure | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Triggered value | 30043 |  | 330044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - GB position failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30043 |  | 330044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - BTB position failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30043 |  | 330044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - MB position failure | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Triggered value | 30044 |  | 330045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - GB configuration failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30044 |  | 330045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - BTB configuration failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30044 |  | 330045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - MB configuration failure | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Triggered value | 30045 |  | 330046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - GB synchronisation failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30045 |  | 330046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - BTB synchronisation failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30045 |  | 330046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - MB synchronisation failure | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Triggered value | 30046 |  | 330047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - GB de-load failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30046 |  | 330047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - BTB de-load failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30046 |  | 330047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - MB de-load failure | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Triggered value | 30047 |  | 330048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - GB tripped (external) | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30047 |  | 330048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - BTB tripped (external) | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30047 |  | 330048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - MB tripped (external) | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Triggered value | 30048 |  | 330049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - GB short circuit | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30048 |  | 330049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - BTB short circuit | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30048 |  | 330049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - MB short circuit | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Triggered value | 30049 |  | 330050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - MB closing failure | INT16 | X * 1 | X * 1 |  | X
Alarm status: Triggered value | 30049 |  | 330050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - TB closing failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30050 |  | 330051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - MB opening failure | INT16 | X * 1 | X * 1 |  | X
Alarm status: Triggered value | 30050 |  | 330051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - TB opening failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30051 |  | 330052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - MB position failure | INT16 | X * 1 | X * 1 |  | X
Alarm status: Triggered value | 30051 |  | 330052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - TB position failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30052 |  | 330053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - MB configuration failure | INT16 | X * 1 | X * 1 |  | X
Alarm status: Triggered value | 30052 |  | 330053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - TB configuration failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30053 |  | 330054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - MB synchronisation failure | INT16 | X * 1 | X * 1 |  | X
Alarm status: Triggered value | 30053 |  | 330054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - TB synchronisation failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30054 |  | 330055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - MB de-load failure | INT16 | X * 1 | X * 1 |  | X
Alarm status: Triggered value | 30054 |  | 330055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - TB de-load failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30055 |  | 330056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - MB tripped (external) | INT16 | X * 1 | X * 1 |  | X
Alarm status: Triggered value | 30055 |  | 330056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - TB tripped (external) | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30056 |  | 330057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - MB short circuit | INT16 | X * 1 | X * 1 |  | X
Alarm status: Triggered value | 30056 |  | 330057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - TB short circuit | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30060 |  | 330061 | Parameters - Mains - AC setup - Phase sequence error - Information - Mains phase sequence error | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Triggered value | 30060 |  | 330061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Busbar phase sequence error | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30060 |  | 330061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Busbar B phase sequence error | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30061 |  | 330062 | Parameters - Generator - AC setup - Phase sequence error - Information - Generator phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30061 |  | 330062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Busbar A phase sequence error | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30061 |  | 330062 | Parameters - Mains - AC setup - Phase sequence error - Information - Mains phase sequence error | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Triggered value | 30062 |  | 330063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30103 |  | 330104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Triggered value | 30103 |  | 330104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30103 |  | 330104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30104 |  | 330105 | Parameters - Mains - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 |  | X | X
Alarm status: Triggered value | 30104 |  | 330105 | Parameters - Busbar - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30104 |  | 330105 | Parameters - Busbar B - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30105 |  | 330106 | Parameters - Generator - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30105 |  | 330106 | Parameters - Busbar A - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30105 |  | 330106 | Parameters - Mains - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Triggered value | 30106 |  | 330107 | Parameters - Local - 4th current input - Earth inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30107 |  | 330108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30108 |  | 330109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30108 |  | 330109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30108 |  | 330109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30109 |  | 330110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30109 |  | 330110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30109 |  | 330110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30110 |  | 330111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30110 |  | 330111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30110 |  | 330111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30111 |  | 330112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30111 |  | 330112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30111 |  | 330112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30115 |  | 330116 | Protection set point out of range | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30116 |  | 330117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Stabilised differential | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30117 |  | 330118 | Parameters - Generator - Current protections - High set differential current - Information - High set differential | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30118 |  | 330119 | Protection set point out of range (differential current) | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30119 |  | 330120 | Parameters - Local - Mode - Not under remote control - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30120 |  | 330121 | Trip AVR output not configured | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30121 |  | 330122 | Parameters - Local - Monitoring - System not OK - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30122 |  | 330123 | Configuration update delayed | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30123 |  | 330124 | Critical process error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30124 |  | 330125 | Restore error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30125 |  | 330126 | SD-card format error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30126 |  | 330127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30127 |  | 330128 | Fieldbus configuration exceeded maximum I/O configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30128 |  | 330129 | Parameters - Custom alarm - Custom alarm 0 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30129 |  | 330130 | Parameters - Custom alarm - Custom alarm 1 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30130 |  | 330131 | Parameters - Custom alarm - Custom alarm 2 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30131 |  | 330132 | Parameters - Custom alarm - Custom alarm 3 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30132 |  | 330133 | Parameters - Custom alarm - Custom alarm 4 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30133 |  | 330134 | Parameters - Custom alarm - Custom alarm 5 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30134 |  | 330135 | Parameters - Custom alarm - Custom alarm 6 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30135 |  | 330136 | Parameters - Custom alarm - Custom alarm 7 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30136 |  | 330137 | Parameters - Custom alarm - Custom alarm 8 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30137 |  | 330138 | Parameters - Custom alarm - Custom alarm 9 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30138 |  | 330139 | Parameters - Custom alarm - Custom alarm 10 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30139 |  | 330140 | Parameters - Custom alarm - Custom alarm 11 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30140 |  | 330141 | Parameters - Custom alarm - Custom alarm 12 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30141 |  | 330142 | Parameters - Custom alarm - Custom alarm 13 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30142 |  | 330143 | Parameters - Custom alarm - Custom alarm 14 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30143 |  | 330144 | Parameters - Custom alarm - Custom alarm 15 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30144 |  | 330145 | Parameters - Custom alarm - Custom alarm 16 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30145 |  | 330146 | Parameters - Custom alarm - Custom alarm 17 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30146 |  | 330147 | Parameters - Custom alarm - Custom alarm 18 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30147 |  | 330148 | Parameters - Custom alarm - Custom alarm 19 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30148 |  | 330149 | Parameters - Custom alarm - Custom alarm 20 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30149 |  | 330150 | Parameters - Custom alarm - Custom alarm 21 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30150 |  | 330151 | Parameters - Custom alarm - Custom alarm 22 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30151 |  | 330152 | Parameters - Custom alarm - Custom alarm 23 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30152 |  | 330153 | Parameters - Custom alarm - Custom alarm 24 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30153 |  | 330154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - GOV regulation error | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30154 |  | 330155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - AVR regulation error | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30155 |  | 330156 | Parameters - Regulators - GOV - Monitoring - P load sharing failure - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30156 |  | 330157 | Parameters - Regulators - AVR - Monitoring - Q load sharing failure - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30157 |  | 330158 | AVR relay setup incomplete | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30158 |  | 330159 | GOV relay setup incomplete | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30159 |  | 330160 | Parameters - Regulators - GOV - Monitoring - Regulation mode not selected - Information - GOV regulator mode not selected | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30160 |  | 330161 | Parameters - Regulators - AVR - Monitoring - Regulation mode not selected - Information - AVR regulator mode not selected | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30161 |  | 330162 | Parameters - Regulators - GOV - General configuration - Stand-alone configuration error - Information - GOV stand-alone configuration error | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30162 |  | 330163 | Parameters - Regulators - AVR - General configuration - Stand-alone configuration error - Information - AVR stand-alone configuration error | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30163 |  | 330164 | Required hardware card(s) not found | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30164 |  | 330165 | Software mismatch on hardware module(s) | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30165 |  | 330166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Mains L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30165 |  | 330166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Busbar L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Triggered value | 30165 |  | 330166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Busbar B L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30166 |  | 330167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Generator L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  | X | X
Alarm status: Triggered value | 30166 |  | 330167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Busbar A L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30166 |  | 330167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Mains L1-L2-L3 wire break | INT16 | X * 1 | X * 1 | [5 empty] | X
Alarm status: Triggered value | 30167 |  | 330168 | Parameters - Mains - AC setup - L1 wire break - Information - Mains L1 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30167 |  | 330168 | Parameters - Busbar - AC setup - L1 wire break - Information - Busbar L1 wire break | INT16 | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Triggered value | 30167 |  | 330168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Busbar B L1 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30168 |  | 330169 | Parameters - Mains - AC setup - L2 wire break - Information - Mains L2 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30168 |  | 330169 | Parameters - Busbar - AC setup - L2 wire break - Information - Busbar L2 wire break | INT16 | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Triggered value | 30168 |  | 330169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Busbar B L2 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30169 |  | 330170 | Parameters - Mains - AC setup - L3 wire break - Information - Mains L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30169 |  | 330170 | Parameters - Busbar - AC setup - L3 wire break - Information - Busbar L3 wire break | INT16 | X * 1 | X * 1 |  |  |  | X |  | X
Alarm status: Triggered value | 30169 |  | 330170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Busbar B L3 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30170 |  | 330171 | Parameters - Generator - AC setup - L1 wire break - Information - Generator L1 wire break | INT16 | X * 1 | X * 1 |  |  | X | X
Alarm status: Triggered value | 30170 |  | 330171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Busbar A L1 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30170 |  | 330171 | Parameters - Mains - AC setup - L1 wire break - Information - Mains L1 wire break | INT16 | X * 1 | X * 1 | [5 empty] | X
Alarm status: Triggered value | 30171 |  | 330172 | Parameters - Generator - AC setup - L2 wire break - Information - Generator L2 wire break | INT16 | X * 1 | X * 1 |  |  | X | X
Alarm status: Triggered value | 30171 |  | 330172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Busbar A L2 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30171 |  | 330172 | Parameters - Mains - AC setup - L2 wire break - Information - Mains L2 wire break | INT16 | X * 1 | X * 1 | [5 empty] | X
Alarm status: Triggered value | 30172 |  | 330173 | Parameters - Generator - AC setup - L3 wire break - Information - Generator L3 wire break | INT16 | X * 1 | X * 1 |  |  | X | X
Alarm status: Triggered value | 30172 |  | 330173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Busbar A L3 wire break | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30172 |  | 330173 | Parameters - Mains - AC setup - L3 wire break - Information - Mains L3 wire break | INT16 | X * 1 | X * 1 | [5 empty] | X
Alarm status: Triggered value | 30173 |  | 330174 | Parameters - Hardware - GAM3.2 1 - Status not OK alarm - Information - GAM3.2 1 status not OK | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30174 |  | 330175 | Parameters - Hardware - GAM3.2 2 - Status not OK alarm - Information - GAM3.2 2 status not OK | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30175 |  | 330176 | Parameters - Hardware - GAM3.2 3 - Status not OK alarm - Information - GAM3.2 3 status not OK | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30176 |  | 330177 | Parameters - Breakers - Generator breaker monitoring - No synchronisation signal - Information - No synchronisation signal for asynchronous generator | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30177 |  | 330178 | Parameters - Generator - Voltage protections - Asynchronous over-voltage - Information - Asynchronous generator over-voltage | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30178 |  | 330179 | Parameters - Mains - AC setup - Supervision alarm - Information - Mains supervision alarm | INT16 | X * 1 | X * 1 |  | X | X |  |  | X | X
Alarm status: Triggered value | 30179 |  | 330180 | Parameters - Engine - Emergency stop - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30180 |  | 330181 | Clock battery failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30181 |  | 330182 | Controller temperature too high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30182 |  | 330183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - PSM3.1 1 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30183 |  | 330184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - PSM3.1 1 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30184 |  | 330185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - PSM3.2 1 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30185 |  | 330186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - PSM3.2 1 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30186 |  | 330187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - PSM3.2 2 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30187 |  | 330188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - PSM3.2 2 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30188 |  | 330189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - PSM3.2 3 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30189 |  | 330190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - PSM3.2 3 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30190 |  | 330191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - EIM3.1 1 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30191 |  | 330192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - EIM3.1 1 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30192 |  | 330193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - EIM3.1 2 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30193 |  | 330194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - EIM3.1 2 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30194 |  | 330195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - EIM3.1 3 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30195 |  | 330196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - EIM3.1 3 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30196 |  | 330197 | EIM3.1 4 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30197 |  | 330198 | EIM3.1 4 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30198 |  | 330199 | EIM3.1 5 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30199 |  | 330200 | EIM3.1 5 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30200 |  | 330201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - EIM3.1 1 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30201 |  | 330202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - EIM3.1 2 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30202 |  | 330203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - EIM3.1 3 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30203 |  | 330204 | EIM3.1 4 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30204 |  | 330205 | EIM3.1 5 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30205 |  | 330206 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30206 |  | 330207 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30207 |  | 330208 | AC protections not running (differential current) | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30208 |  | 330209 | AC data is missing (differential current) | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30209 |  | 330210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - GAM3.2 1 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30210 |  | 330211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - GAM3.2 1 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30211 |  | 330212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - GAM3.2 2 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30212 |  | 330213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - GAM3.2 2 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30213 |  | 330214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - GAM3.2 3 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30214 |  | 330215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - GAM3.2 3 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30215 |  | 330216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - PSM3.2 4 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30216 |  | 330217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - PSM3.2 4 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30217 |  | 330218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - PSM3.2 5 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30218 |  | 330219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - PSM3.2 5 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30219 |  | 330220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - PSM3.2 6 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30220 |  | 330221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - PSM3.2 6 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30221 |  | 330222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - PSM3.2 7 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30222 |  | 330223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - PSM3.2 7 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30223 |  | 330224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - PSM3.2 8 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30224 |  | 330225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - PSM3.2 8 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30225 |  | 330226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - PSM3.2 9 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30226 |  | 330227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - PSM3.2 9 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30227 |  | 330228 | Parameters - System - Monitoring - Any bus tie breaker position failure - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30228 |  | 330229 | Parameters - System - Monitoring - Duplicate controller ID - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30229 |  | 330230 | Parameters - System - Monitoring - Missing all controllers - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30230 |  | 330231 | Parameters - System - Monitoring - Missing any controller - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30231 |  | 330232 | Controller ID not configured | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30232 |  | 330233 | Parameters - System - Monitoring - Any mains breaker position failure - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30233 |  | 330234 | Parameters - System - Monitoring - Data loss from a controller - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30234 |  | 330235 | Parameters - System - Monitoring - Data loss on DEIF network - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30235 |  | 330236 | Parameters - System - Monitoring - High traffic on DEIF network - Information - High traffic to DEIF network | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30236 |  | 330237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30237 |  | 330238 | Parameters - System - Monitoring - Blackout detection mismatch - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30239 |  | 330240 | Parameters - System - Monitoring - Group alarm - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30240 |  | 330241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - NTP server 1 could not connect | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30241 |  | 330242 | Parameters - Communication - NTP - NTP server 1 no response - Information - NTP server 1 is not responding | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30242 |  | 330243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - NTP server 2 could not connect | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30243 |  | 330244 | Parameters - Communication - NTP - NTP server 2 no response - Information - NTP server 2 is not responding | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30244 |  | 330245 | Parameters - Communication - NTP - No NTP server time synchronisation - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30245 |  | 330246 | Parameters - Communication - NTP - No NTP server(s) connected - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30246 |  | 330247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30247 |  | 330248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30248 |  | 330249 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30249 |  | 330250 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30250 |  | 330251 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30251 |  | 330252 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30252 |  | 330253 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30253 |  | 330254 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30254 |  | 330255 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30255 |  | 330256 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30256 |  | 330257 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30257 |  | 330258 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30258 |  | 330259 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30259 |  | 330260 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30260 |  | 330261 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30261 |  | 330262 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30262 |  | 330263 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30263 |  | 330264 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30264 |  | 330265 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30265 |  | 330266 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30266 |  | 330267 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30267 |  | 330268 | Missing controller(s) in group | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30268 |  | 330269 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30269 |  | 330270 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30270 |  | 330271 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30271 |  | 330272 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30272 |  | 330273 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30273 |  | 330274 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30274 |  | 330275 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30275 |  | 330276 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30276 |  | 330277 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30277 |  | 330278 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30278 |  | 330279 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30279 |  | 330280 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30280 |  | 330281 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30281 |  | 330282 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30282 |  | 330283 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30283 |  | 330284 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30284 |  | 330285 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30285 |  | 330286 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30286 |  | 330287 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30287 |  | 330288 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30288 |  | 330289 | Parameters - Breakers - Breaker 1 feedback monitoring - Position failure - Information - Breaker 1 position failure | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Triggered value | 30289 |  | 330290 | Parameters - Breakers - Breaker 1 feedback monitoring - Feedback mismatch - Information - Breaker 1 feedback mismatch | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Triggered value | 30290 |  | 330291 | Parameters - Breakers - Breaker 2 feedback monitoring - Position failure - Information - Breaker 2 position failure | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Triggered value | 30290 |  | 330291 | Parameters - Breakers - BTB 1 feedback monitoring - Position failure - Information - BTB 1 position failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30291 |  | 330292 | Parameters - Breakers - Breaker 2 feedback monitoring - Feedback mismatch - Information - Breaker 2 feedback mismatch | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Triggered value | 30291 |  | 330292 | Parameters - Breakers - BTB 1 feedback monitoring - Feedback mismatch - Information - BTB 1 feedback mismatch | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30292 |  | 330293 | Parameters - Breakers - Breaker 3 feedback monitoring - Position failure - Information - Breaker 3 position failure | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Triggered value | 30292 |  | 330293 | Parameters - Breakers - BTB 2 feedback monitoring - Position failure - Information - BTB 2 position failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30293 |  | 330294 | Parameters - Breakers - Breaker 3 feedback monitoring - Feedback mismatch - Information - Breaker 3 feedback mismatch | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Triggered value | 30293 |  | 330294 | Parameters - Breakers - BTB 2 feedback monitoring - Feedback mismatch - Information - BTB 2 feedback mismatch | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30294 |  | 330295 | Parameters - Breakers - Breaker 4 feedback monitoring - Position failure - Information - Breaker 4 position failure | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Triggered value | 30294 |  | 330295 | Parameters - Breakers - BTB 3 feedback monitoring - Position failure - Information - BTB 3 position failure | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30295 |  | 330296 | Parameters - Breakers - Breaker 4 feedback monitoring - Feedback mismatch - Information - Breaker 4 feedback mismatch | INT16 | X * 1 | X * 1 |  |  |  | X | X | X
Alarm status: Triggered value | 30295 |  | 330296 | Parameters - Breakers - BTB 3 feedback monitoring - Feedback mismatch - Information - BTB 3 feedback mismatch | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30296 |  | 330297 | Controller not part of system | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30297 |  | 330298 | Different single-line configurations | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30298 |  | 330299 | Single-line missing/none active | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30299 |  | 330300 | Parameters - Communication - Modbus - Modbus communication timeout - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30300 |  | 330301 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - CODESYS configuration conflict | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30301 |  | 330302 | Parameters - CODESYS - Monitoring - Application not OK - Information - CODESYS application not OK | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30302 |  | 330303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30303 |  | 330304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30304 |  | 330305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30305 |  | 330306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30306 |  | 330307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30307 |  | 330308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30308 |  | 330309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30309 |  | 330310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30310 |  | 330311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30311 |  | 330312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30312 |  | 330313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30313 |  | 330314 | Emulation disabled (live power) | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30315 |  | 330316 | Parameters - Local - CustomLogic - Configuration invalid - Information - CustomLogic configuration invalid | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30316 |  | 330317 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Digital AVR communication error | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30317 |  | 330318 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30318 |  | 330319 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30319 |  | 330320 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30320 |  | 330321 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30321 |  | 330322 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30322 |  | 330323 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30323 |  | 330324 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30324 |  | 330325 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30325 |  | 330326 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30326 |  | 330327 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30327 |  | 330328 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30328 |  | 330329 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30329 |  | 330330 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30330 |  | 330331 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30331 |  | 330332 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30332 |  | 330333 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30333 |  | 330334 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30334 |  | 330335 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30335 |  | 330336 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30336 |  | 330337 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30337 |  | 330338 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30338 |  | 330339 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30339 |  | 330340 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30340 |  | 330341 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30341 |  | 330342 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30342 |  | 330343 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30343 |  | 330344 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30344 |  | 330345 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30345 |  | 330346 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30346 |  | 330347 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30347 |  | 330348 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30348 |  | 330349 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30349 |  | 330350 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30350 |  | 330351 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30351 |  | 330352 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30352 |  | 330353 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30353 |  | 330354 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30354 |  | 330355 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30355 |  | 330356 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30356 |  | 330357 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30357 |  | 330358 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30358 |  | 330359 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30359 |  | 330360 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30360 |  | 330361 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30361 |  | 330362 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30362 |  | 330363 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30363 |  | 330364 | DAVR unsupported AC configuration | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30364 |  | 330365 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Illegal DAVR configuration | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30365 |  | 330366 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Generator under-voltage 1 | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30365 |  | 330366 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Busbar A under-voltage 1 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30365 |  | 330366 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Mains under-voltage 1 | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30366 |  | 330367 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Generator under-voltage 2 | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30366 |  | 330367 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Busbar A under-voltage 2 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30366 |  | 330367 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Mains under-voltage 2 | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30367 |  | 330368 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Generator under-voltage 3 | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30367 |  | 330368 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Busbar A under-voltage 3 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30367 |  | 330368 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Mains under-voltage 3 | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30368 |  | 330369 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Generator over-voltage 1 | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30368 |  | 330369 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Busbar A over-voltage 1 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30368 |  | 330369 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Mains over-voltage 1 | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30369 |  | 330370 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Generator over-voltage 2 | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30369 |  | 330370 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Busbar A over-voltage 2 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30369 |  | 330370 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Mains over-voltage 2 | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30370 |  | 330371 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Generator voltage unbalance | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30370 |  | 330371 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Busbar A voltage unbalance | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30370 |  | 330371 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Mains voltage unbalance | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30371 |  | 330372 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Generator negative sequence voltage | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30371 |  | 330372 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Busbar A negative sequence voltage | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30371 |  | 330372 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Mains negative sequence voltage | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30372 |  | 330373 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Generator zero sequence voltage | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30372 |  | 330373 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Busbar A zero sequence voltage | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30372 |  | 330373 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Mains zero sequence voltage | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30373 |  | 330374 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Generator positive sequence under-voltage | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30373 |  | 330374 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Busbar A positive sequence under-voltage | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30373 |  | 330374 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Mains positive sequence under-voltage | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30374 |  | 330375 | Parameters - Generator - Current protections - Over-current 1 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30374 |  | 330375 | Parameters - Busbar A - Current protections - Over-current 1 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30374 |  | 330375 | Parameters - Mains - Current protections - Over-current 1 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30375 |  | 330376 | Parameters - Generator - Current protections - Over-current 2 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30375 |  | 330376 | Parameters - Busbar A - Current protections - Over-current 2 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30375 |  | 330376 | Parameters - Mains - Current protections - Over-current 2 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30376 |  | 330377 | Parameters - Generator - Current protections - Over-current 3 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30376 |  | 330377 | Parameters - Busbar A - Current protections - Over-current 3 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30376 |  | 330377 | Parameters - Mains - Current protections - Over-current 3 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30377 |  | 330378 | Parameters - Generator - Current protections - Over-current 4 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30377 |  | 330378 | Parameters - Busbar A - Current protections - Over-current 4 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30377 |  | 330378 | Parameters - Mains - Current protections - Over-current 4 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30378 |  | 330379 | Parameters - Generator - Current protections - Fast over-current 1 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30378 |  | 330379 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30378 |  | 330379 | Parameters - Mains - Current protections - Fast over-current 1 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30379 |  | 330380 | Parameters - Generator - Current protections - Fast over-current 2 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30379 |  | 330380 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30379 |  | 330380 | Parameters - Mains - Current protections - Fast over-current 2 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30380 |  | 330381 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30380 |  | 330381 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30380 |  | 330381 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30381 |  | 330382 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30381 |  | 330382 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30381 |  | 330382 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30382 |  | 330383 | Parameters - Generator - Current protections - Directional over-current 1 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30382 |  | 330383 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30382 |  | 330383 | Parameters - Mains - Current protections - Directional over-current 1 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30383 |  | 330384 | Parameters - Generator - Current protections - Directional over-current 2 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30383 |  | 330384 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30383 |  | 330384 | Parameters - Mains - Current protections - Directional over-current 2 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30384 |  | 330385 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30385 |  | 330386 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30386 |  | 330387 | Parameters - Generator - Current protections - Negative sequence current - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30386 |  | 330387 | Parameters - Busbar A - Current protections - Negative sequence current - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30386 |  | 330387 | Parameters - Mains - Current protections - Negative sequence current - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30387 |  | 330388 | Parameters - Generator - Current protections - Zero sequence current - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30387 |  | 330388 | Parameters - Busbar A - Current protections - Zero sequence current - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30387 |  | 330388 | Parameters - Mains - Current protections - Zero sequence current - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30388 |  | 330389 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Generator over-frequency 1 | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30388 |  | 330389 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Busbar A over-frequency 1 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30388 |  | 330389 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Mains over-frequency 1 | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30389 |  | 330390 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Generator over-frequency 2 | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30389 |  | 330390 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Busbar A over-frequency 2 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30389 |  | 330390 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Mains over-frequency 2 | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30390 |  | 330391 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Generator over-frequency 3 | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30390 |  | 330391 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Busbar A over-frequency 3 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30390 |  | 330391 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Mains over-frequency 3 | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30391 |  | 330392 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Generator under-frequency 1 | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30391 |  | 330392 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Busbar A under-frequency 1 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30391 |  | 330392 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Mains under-frequency 1 | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30392 |  | 330393 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Generator under-frequency 2 | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30392 |  | 330393 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Busbar A under-frequency 2 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30392 |  | 330393 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Mains under-frequency 2 | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30393 |  | 330394 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Generator under-frequency 3 | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30393 |  | 330394 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Busbar A under-frequency 3 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30393 |  | 330394 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Mains under-frequency 3 | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30394 |  | 330395 | Parameters - Generator - Power protections - Overload 1 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30394 |  | 330395 | Parameters - Busbar A - Power protections - Power export 1 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30394 |  | 330395 | Parameters - Mains - Power protections - Overload 1 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30395 |  | 330396 | Parameters - Generator - Power protections - Overload 2 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30395 |  | 330396 | Parameters - Busbar A - Power protections - Power export 2 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30395 |  | 330396 | Parameters - Mains - Power protections - Overload 2 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30396 |  | 330397 | Parameters - Generator - Power protections - Overload 3 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30396 |  | 330397 | Parameters - Busbar A - Power protections - Power export 3 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30396 |  | 330397 | Parameters - Mains - Power protections - Overload 3 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30397 |  | 330398 | Parameters - Generator - Power protections - Overload 4 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30397 |  | 330398 | Parameters - Busbar A - Power protections - Power export 4 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30397 |  | 330398 | Parameters - Mains - Power protections - Overload 4 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30398 |  | 330399 | Parameters - Generator - Power protections - Overload 5 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30398 |  | 330399 | Parameters - Busbar A - Power protections - Power export 5 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30398 |  | 330399 | Parameters - Mains - Power protections - Overload 5 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30399 |  | 330400 | Parameters - Generator - Power protections - Reverse power 1 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30399 |  | 330400 | Parameters - Busbar A - Power protections - Power import 1 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30399 |  | 330400 | Parameters - Mains - Power protections - Reverse power 1 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30400 |  | 330401 | Parameters - Generator - Power protections - Reverse power 2 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30400 |  | 330401 | Parameters - Busbar A - Power protections - Power import 2 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30400 |  | 330401 | Parameters - Mains - Power protections - Reverse power 2 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30401 |  | 330402 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30401 |  | 330402 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30401 |  | 330402 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30402 |  | 330403 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30402 |  | 330403 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30402 |  | 330403 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30403 |  | 330404 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30403 |  | 330404 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30403 |  | 330404 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30404 |  | 330405 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 10 | X * 0.1 |  | X | X | X
Alarm status: Triggered value | 30404 |  | 330405 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30404 |  | 330405 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 10 | X * 0.1 | [5 empty] | X | X
Alarm status: Triggered value | 30405 |  | 330406 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Mains over-voltage 1 | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30405 |  | 330406 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Busbar over-voltage 1 | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30405 |  | 330406 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Busbar B over-voltage 1 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30406 |  | 330407 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Mains over-voltage 2 | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30406 |  | 330407 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Busbar over-voltage 2 | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30406 |  | 330407 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Busbar B over-voltage 2 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30407 |  | 330408 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Mains over-voltage 3 | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30407 |  | 330408 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Busbar over-voltage 3 | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30407 |  | 330408 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Busbar B over-voltage 3 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30408 |  | 330409 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Mains under-voltage 1 | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30408 |  | 330409 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Busbar under-voltage 1 | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30408 |  | 330409 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Busbar B under-voltage 1 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30409 |  | 330410 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Mains under-voltage 2 | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30409 |  | 330410 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Busbar under-voltage 2 | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30409 |  | 330410 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Busbar B under-voltage 2 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30410 |  | 330411 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Mains under-voltage 3 | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30410 |  | 330411 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Busbar under-voltage 3 | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30410 |  | 330411 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Busbar B under-voltage 3 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30411 |  | 330412 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Mains under-voltage 4 | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30411 |  | 330412 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Busbar under-voltage 4 | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30411 |  | 330412 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Busbar B under-voltage 4 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30412 |  | 330413 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Mains voltage unbalance | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30412 |  | 330413 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Busbar voltage unbalance | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30412 |  | 330413 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Busbar B voltage unbalance | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30413 |  | 330414 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Mains over-frequency 1 | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30413 |  | 330414 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Busbar over-frequency 1 | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30413 |  | 330414 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Busbar B over-frequency 1 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30414 |  | 330415 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Mains over-frequency 2 | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30414 |  | 330415 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Busbar over-frequency 2 | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30414 |  | 330415 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Busbar B over-frequency 2 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30415 |  | 330416 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Mains over-frequency 3 | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30415 |  | 330416 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Busbar over-frequency 3 | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30415 |  | 330416 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Busbar B over-frequency 3 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30416 |  | 330417 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Mains under-frequency 1 | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30416 |  | 330417 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Busbar under-frequency 1 | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30416 |  | 330417 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Busbar B under-frequency 1 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30417 |  | 330418 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Mains under-frequency 2 | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30417 |  | 330418 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Busbar under-frequency 2 | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30417 |  | 330418 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Busbar B under-frequency 2 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30418 |  | 330419 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Mains under-frequency 3 | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30418 |  | 330419 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Busbar under-frequency 3 | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30418 |  | 330419 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Busbar B under-frequency 3 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30419 |  | 330420 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Mains under-frequency 4 | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30419 |  | 330420 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Busbar under-frequency 4 | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30419 |  | 330420 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Busbar B under-frequency 4 | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30420 |  | 330421 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Busbar negative sequence voltage | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30420 |  | 330421 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Busbar negative sequence voltage | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30420 |  | 330421 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Busbar B negative sequence voltage | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30421 |  | 330422 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Busbar zero sequence voltage | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30421 |  | 330422 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Busbar zero sequence voltage | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30421 |  | 330422 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Busbar B zero sequence voltage | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30422 |  | 330423 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Busbar positive sequence under-voltage | INT16 | X * 10 | X * 0.1 |  | X | X
Alarm status: Triggered value | 30422 |  | 330423 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Busbar positive sequence under-voltage | INT16 | X * 10 | X * 0.1 |  |  |  | X |  | X | X
Alarm status: Triggered value | 30422 |  | 330423 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Busbar B positive sequence under-voltage | INT16 | X * 10 | X * 0.1 |  |  |  |  | X
Alarm status: Triggered value | 30423 |  | 330424 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30424 |  | 330425 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30425 |  | 330426 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30426 |  | 330427 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30427 |  | 330428 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30428 |  | 330429 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30429 |  | 330430 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30430 |  | 330431 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30431 |  | 330432 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30432 |  | 330433 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30433 |  | 330434 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30434 |  | 330435 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30435 |  | 330436 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30436 |  | 330437 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30437 |  | 330438 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30438 |  | 330439 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30439 |  | 330440 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30440 |  | 330441 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30441 |  | 330442 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30442 |  | 330443 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30443 |  | 330444 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30444 |  | 330445 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30445 |  | 330446 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30446 |  | 330447 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30447 |  | 330448 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30448 |  | 330449 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30449 |  | 330450 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30450 |  | 330451 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30451 |  | 330452 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30452 |  | 330453 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30453 |  | 330454 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30454 |  | 330455 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30455 |  | 330456 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30456 |  | 330457 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30457 |  | 330458 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30458 |  | 330459 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30459 |  | 330460 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30460 |  | 330461 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30461 |  | 330462 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30462 |  | 330463 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30463 |  | 330464 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30464 |  | 330465 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30465 |  | 330466 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30466 |  | 330467 | Missing controller | INT16 | X * 1 | X * 1 |  |  |  | X | X | X | X
Alarm status: Triggered value | 30600 |  | 330601 | Parameters - Communication - DEIF network - DEIF network fork detected - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30602 |  | 330603 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30604 |  | 330605 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30604 |  | 330605 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30604 |  | 330605 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | [5 empty] | X | X
Alarm status: Triggered value | 30605 |  | 330606 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 |  | X
Alarm status: Triggered value | 30605 |  | 330606 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30607 |  | 330608 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30608 |  | 330609 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30609 |  | 330610 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30610 |  | 330611 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30611 |  | 330612 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30612 |  | 330613 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30613 |  | 330614 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30614 |  | 330615 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30615 |  | 330616 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30616 |  | 330617 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30617 |  | 330618 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30618 |  | 330619 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30619 |  | 330620 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30620 |  | 330621 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30621 |  | 330622 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30622 |  | 330623 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30623 |  | 330624 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30624 |  | 330625 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30625 |  | 330626 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30626 |  | 330627 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30628 |  | 330629 | Internal issue detected. A restart is required soon! | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30630 |  | 330631 | Card issue detected | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30631 |  | 330632 | Card configuration failed | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30632 |  | 330633 | Unknown traffic on DEIF network | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30633 |  | 330634 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30634 |  | 330635 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30635 |  | 330636 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X | X | X
Alarm status: Triggered value | 30636 |  | 330637 | Local IO service error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30637 |  | 330638 | App logging failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30638 |  | 330639 | Event logging failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30639 |  | 330640 | Licence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 30640 |  | 330641 | Brightness is dimmed according to temperature | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31500 |  | 331501 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31501 |  | 331502 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31502 |  | 331503 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31503 |  | 331504 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31504 |  | 331505 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31505 |  | 331506 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31506 |  | 331507 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31507 |  | 331508 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31508 |  | 331509 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31509 |  | 331510 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31510 |  | 331511 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31511 |  | 331512 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31512 |  | 331513 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31513 |  | 331514 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31514 |  | 331515 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31515 |  | 331516 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31516 |  | 331517 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31517 |  | 331518 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31518 |  | 331519 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31519 |  | 331520 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31520 |  | 331521 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31521 |  | 331522 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31522 |  | 331523 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31523 |  | 331524 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31524 |  | 331525 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31525 |  | 331526 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31526 |  | 331527 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31527 |  | 331528 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31528 |  | 331529 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31529 |  | 331530 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31530 |  | 331531 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31531 |  | 331532 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31532 |  | 331533 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31533 |  | 331534 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31534 |  | 331535 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31535 |  | 331536 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31536 |  | 331537 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31537 |  | 331538 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31538 |  | 331539 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31539 |  | 331540 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31540 |  | 331541 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31541 |  | 331542 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31542 |  | 331543 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31543 |  | 331544 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31544 |  | 331545 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31545 |  | 331546 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31546 |  | 331547 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31547 |  | 331548 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31548 |  | 331549 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31549 |  | 331550 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31600 |  | 331601 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31601 |  | 331602 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31602 |  | 331603 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31603 |  | 331604 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31604 |  | 331605 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31605 |  | 331606 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31606 |  | 331607 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31607 |  | 331608 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31608 |  | 331609 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31609 |  | 331610 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31610 |  | 331611 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31611 |  | 331612 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31612 |  | 331613 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31613 |  | 331614 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31614 |  | 331615 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31615 |  | 331616 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31616 |  | 331617 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31617 |  | 331618 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31618 |  | 331619 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31619 |  | 331620 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31620 |  | 331621 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31621 |  | 331622 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31622 |  | 331623 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31623 |  | 331624 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31624 |  | 331625 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31625 |  | 331626 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31626 |  | 331627 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31627 |  | 331628 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31628 |  | 331629 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31629 |  | 331630 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31630 |  | 331631 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31631 |  | 331632 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31632 |  | 331633 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31633 |  | 331634 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31634 |  | 331635 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31635 |  | 331636 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31636 |  | 331637 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31637 |  | 331638 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31638 |  | 331639 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31639 |  | 331640 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31640 |  | 331641 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31641 |  | 331642 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31642 |  | 331643 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31643 |  | 331644 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31644 |  | 331645 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31645 |  | 331646 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31646 |  | 331647 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31647 |  | 331648 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31648 |  | 331649 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31649 |  | 331650 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31650 |  | 331651 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31651 |  | 331652 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31652 |  | 331653 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31653 |  | 331654 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31654 |  | 331655 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31655 |  | 331656 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31656 |  | 331657 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31657 |  | 331658 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31658 |  | 331659 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31659 |  | 331660 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31660 |  | 331661 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31661 |  | 331662 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31662 |  | 331663 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31663 |  | 331664 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31664 |  | 331665 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31665 |  | 331666 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31666 |  | 331667 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31667 |  | 331668 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31668 |  | 331669 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31669 |  | 331670 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31670 |  | 331671 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31671 |  | 331672 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31672 |  | 331673 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31673 |  | 331674 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31674 |  | 331675 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31675 |  | 331676 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31676 |  | 331677 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31677 |  | 331678 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31678 |  | 331679 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31679 |  | 331680 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31680 |  | 331681 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31681 |  | 331682 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31682 |  | 331683 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31683 |  | 331684 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31684 |  | 331685 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31685 |  | 331686 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31686 |  | 331687 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31687 |  | 331688 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31688 |  | 331689 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31689 |  | 331690 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31690 |  | 331691 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31691 |  | 331692 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31692 |  | 331693 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31693 |  | 331694 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31694 |  | 331695 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31695 |  | 331696 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31696 |  | 331697 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31697 |  | 331698 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31698 |  | 331699 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31699 |  | 331700 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31700 |  | 331701 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31701 |  | 331702 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31702 |  | 331703 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31703 |  | 331704 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31704 |  | 331705 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31705 |  | 331706 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31706 |  | 331707 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31707 |  | 331708 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31708 |  | 331709 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31709 |  | 331710 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31710 |  | 331711 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31711 |  | 331712 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31712 |  | 331713 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31713 |  | 331714 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31714 |  | 331715 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31715 |  | 331716 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31716 |  | 331717 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31717 |  | 331718 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31718 |  | 331719 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31719 |  | 331720 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31720 |  | 331721 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31721 |  | 331722 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31722 |  | 331723 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31723 |  | 331724 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31724 |  | 331725 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31725 |  | 331726 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31726 |  | 331727 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31727 |  | 331728 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31728 |  | 331729 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31729 |  | 331730 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31730 |  | 331731 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31731 |  | 331732 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31732 |  | 331733 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31733 |  | 331734 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31734 |  | 331735 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31735 |  | 331736 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31736 |  | 331737 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31737 |  | 331738 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31738 |  | 331739 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31739 |  | 331740 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31740 |  | 331741 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31741 |  | 331742 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31742 |  | 331743 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31743 |  | 331744 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31744 |  | 331745 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31745 |  | 331746 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31746 |  | 331747 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31747 |  | 331748 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31748 |  | 331749 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31749 |  | 331750 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31750 |  | 331751 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31751 |  | 331752 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31752 |  | 331753 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31753 |  | 331754 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31754 |  | 331755 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31755 |  | 331756 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31756 |  | 331757 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31757 |  | 331758 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31758 |  | 331759 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31759 |  | 331760 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31760 |  | 331761 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31761 |  | 331762 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31762 |  | 331763 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31763 |  | 331764 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31764 |  | 331765 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31765 |  | 331766 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31766 |  | 331767 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31767 |  | 331768 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31768 |  | 331769 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31769 |  | 331770 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31770 |  | 331771 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31771 |  | 331772 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31772 |  | 331773 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31773 |  | 331774 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31774 |  | 331775 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31775 |  | 331776 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31776 |  | 331777 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31777 |  | 331778 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31778 |  | 331779 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31779 |  | 331780 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31780 |  | 331781 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31781 |  | 331782 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31782 |  | 331783 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31783 |  | 331784 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31784 |  | 331785 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31785 |  | 331786 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31786 |  | 331787 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31787 |  | 331788 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31788 |  | 331789 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31789 |  | 331790 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31790 |  | 331791 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31791 |  | 331792 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31792 |  | 331793 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31793 |  | 331794 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31794 |  | 331795 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31795 |  | 331796 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31796 |  | 331797 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31797 |  | 331798 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31798 |  | 331799 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
Alarm status: Triggered value | 31799 |  | 331800 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40000 |  | 340001 | Parameters - Engine - Start sequence - Start prepare - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40001 |  | 340002 | Parameters - Engine - Start sequence - Crank - Crank on - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40002 |  | 340003 | Parameters - Engine - Start sequence - Crank - Crank off - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40003 |  | 340004 | Parameters - Engine - Start sequence - Run coil - Run coil before crank - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40005 |  | 340006 | Parameters - Engine - Start sequence - Start prepare - Extended start prepare - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40006 |  | 340007 | Parameters - Engine - Stop sequence - Cooldown - Cooldown time - Information | INT16 | X * 1 | X * 1 | s | X | X | X
General parameter: Delay timer elapsed time | 40008 |  | 340009 | Parameters - Engine - Stop sequence - Extended stop - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40009 |  | 340010 | Parameters - Engine - Stop sequence - Cooldown - Suppress alarm action - Information | INT16 | X * 1 | X * 1 | s | X | X | X
General parameter: Delay timer elapsed time | 40016 |  | 340017 | Parameters - Engine - Idle run start - Minimum - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40018 |  | 340019 | Parameters - Engine - Idle run start - Maximum - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40025 |  | 340026 | Parameters - Engine - Idle run stop - Minimum - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40027 |  | 340028 | Parameters - Engine - Idle run stop - Maximum - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40033 |  | 340034 | Parameters - Engine - Idle run start - Idle run - Extended inhibit - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40038 |  | 340039 | Parameters - Engine - Running detection - Engine ready - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40045 |  | 340046 | Parameters - Engine - Maintenance - Priming - OFF timer - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40046 |  | 340047 | Parameters - Engine - Maintenance - Priming - ON timer - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40049 |  | 340050 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump OFF delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40050 |  | 340051 | Pump source select | INT16 | X * 10 | X * 0.1 |  | X | X | X
General parameter: Delay timer elapsed time | 40052 |  | 340053 | Parameters - Breakers - Generator breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40052 |  | 340053 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40052 |  | 340053 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer elapsed time | 40053 |  | 340054 | Parameters - Breakers - Generator breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40053 |  | 340054 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40053 |  | 340054 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer elapsed time | 40054 |  | 340055 | Parameters - Breakers - Generator breaker configuration - Configuration - Spring load time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40054 |  | 340055 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Spring load time - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40054 |  | 340055 | Parameters - Breakers - Mains breaker configuration - Configuration - Spring-load time - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer elapsed time | 40057 |  | 340058 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s | X
General parameter: Delay timer elapsed time | 40057 |  | 340058 | Parameters - Breakers - Tie breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
General parameter: Delay timer elapsed time | 40058 |  | 340059 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s | X
General parameter: Delay timer elapsed time | 40058 |  | 340059 | Parameters - Breakers - Tie breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
General parameter: Delay timer elapsed time | 40059 |  | 340060 | Parameters - Breakers - Mains breaker configuration - Configuration - Spring-load time - Information | INT16 | X * 10 | X * 0.1 | s | X
General parameter: Delay timer elapsed time | 40059 |  | 340060 | Parameters - Breakers - Tie breaker configuration - Configuration - Spring-load time - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
General parameter: Delay timer elapsed time | 40200 |  | 340201 | Parameters - Generator - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40200 |  | 340201 | Parameters - Busbar A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40200 |  | 340201 | Parameters - Mains - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer elapsed time | 40202 |  | 340203 | Parameters - Generator - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40202 |  | 340203 | Parameters - Busbar A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40202 |  | 340203 | Parameters - Mains - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer elapsed time | 40204 |  | 340205 | Parameters - Busbar A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40204 |  | 340205 | Parameters - Mains - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer elapsed time | 40206 |  | 340207 | Parameters - Busbar A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40206 |  | 340207 | Parameters - Mains - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer elapsed time | 40208 |  | 340209 | Parameters - Busbar A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40208 |  | 340209 | Parameters - Mains - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer elapsed time | 40210 |  | 340211 | Parameters - Busbar A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40210 |  | 340211 | Parameters - Mains - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer elapsed time | 40225 |  | 340226 | Parameters - Mains - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X
General parameter: Delay timer elapsed time | 40225 |  | 340226 | Parameters - Busbar - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X |  | X | X
General parameter: Delay timer elapsed time | 40225 |  | 340226 | Parameters - Busbar B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40233 |  | 340234 | Blackout delay | INT16 | X * 10 | X * 0.1 | s | X | X
General parameter: Delay timer elapsed time | 40233 |  | 340234 | Parameters - Busbar - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X |  | X | X
General parameter: Delay timer elapsed time | 40233 |  | 340234 | Parameters - Busbar B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40234 |  | 340235 | Parameters - Generator - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40234 |  | 340235 | Parameters - Busbar A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40234 |  | 340235 | Parameters - Mains - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer elapsed time | 40242 |  | 340243 | Blackout delay | INT16 | X * 10 | X * 0.1 | s | X | X | X |  | X | X
General parameter: Delay timer elapsed time | 40242 |  | 340243 | Parameters - Busbar A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40243 |  | 340244 | Parameters - Generator - AC setup - Voltage and frequency OK (blackout) - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40641 |  | 340642 | Parameters - Local - Alarm horn - Horn 1 - Minimum down time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40642 |  | 340643 | Parameters - Local - Alarm horn - Horn 1 - Minimum up time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40645 |  | 340646 | Parameters - Local - Alarm horn - Horn 2 - Minimum down time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40646 |  | 340647 | Parameters - Local - Alarm horn - Horn 2 - Minimum up time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40649 |  | 340650 | Parameters - Local - Alarm horn - Horn 3 - Minimum down time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40650 |  | 340651 | Parameters - Local - Alarm horn - Horn 3 - Minimum up time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40652 |  | 340653 | Parameters - Local - Alive - Alive configuration - Period - Information | INT16 | X * 100 | X * 0.01 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40705 |  | 340706 | Parameters - Regulators - GOV - General configuration - Regulation delay - Regulator delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 40716 |  | 340717 | Parameters - Regulators - AVR - General configuration - Regulation delay - Regulator delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 41041 |  | 341042 | Parameters - Mains - AC setup - Supervision selector - Recovery selector time - Information | INT16 | X * 10 | X * 0.1 | s | X | X |  |  | X | X
General parameter: Delay timer elapsed time | 41042 |  | 341043 | Parameters - Mains - AC setup - Supervision selector - Recovery time fast - Information | INT16 | X * 10 | X * 0.1 | s | X | X |  |  | X | X
General parameter: Delay timer elapsed time | 41043 |  | 341044 | Parameters - Mains - AC setup - Supervision selector - Recovery time slow - Information | INT16 | X * 10 | X * 0.1 | s | X | X |  |  | X | X
General parameter: Delay timer elapsed time | 41070 |  | 341071 | Parameters - Test functions - Lamp test - Duration - Information | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41071 |  | 341072 | Parameters - Test functions - Lamp test - Colour cycle time - Information | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41073 |  | 341074 | Parameters - CODESYS - Monitoring - Application not OK - Startup time - Information | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41076 |  | 341077 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU powerup time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 41106 |  | 341107 | Parameters - Engine - ECU - Controls - Reset - Power off timer - Information | INT16 | X * 1 | X * 1 | s | X | X | X
General parameter: Delay timer elapsed time | 41147 |  | 341148 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Power-up time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 41811 |  | 341812 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41813 |  | 341814 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41815 |  | 341816 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41817 |  | 341818 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41819 |  | 341820 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41821 |  | 341822 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41823 |  | 341824 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41825 |  | 341826 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41827 |  | 341828 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41829 |  | 341830 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41831 |  | 341832 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41833 |  | 341834 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41835 |  | 341836 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41837 |  | 341838 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41839 |  | 341840 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41841 |  | 341842 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41843 |  | 341844 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41845 |  | 341846 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41847 |  | 341848 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41849 |  | 341850 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41851 |  | 341852 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41853 |  | 341854 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41855 |  | 341856 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41857 |  | 341858 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41890 |  | 341891 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41898 |  | 341899 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41899 |  | 341900 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41907 |  | 341908 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41908 |  | 341909 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41916 |  | 341917 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41917 |  | 341918 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41925 |  | 341926 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41926 |  | 341927 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41934 |  | 341935 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41935 |  | 341936 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41943 |  | 341944 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41944 |  | 341945 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41952 |  | 341953 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41953 |  | 341954 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41961 |  | 341962 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41998 |  | 341999 | Parameters - Engine - ECU diagnostic - Time to enable function - Information | INT16 | X * 1 | X * 1 | s | X | X | X
General parameter: Delay timer elapsed time | 42000 |  | 342001 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump ON delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 42004 |  | 342005 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump ON delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 42005 |  | 342006 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump OFF delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 42010 |  | 342011 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump ON delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer elapsed time | 42011 |  | 342012 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump OFF delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46000 |  | 346001 | Parameters - Engine - Start sequence - Start prepare - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46001 |  | 346002 | Parameters - Engine - Start sequence - Crank - Crank on - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46002 |  | 346003 | Parameters - Engine - Start sequence - Crank - Crank off - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46003 |  | 346004 | Parameters - Engine - Start sequence - Run coil - Run coil before crank - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46005 |  | 346006 | Parameters - Engine - Start sequence - Start prepare - Extended start prepare - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46006 |  | 346007 | Parameters - Engine - Stop sequence - Cooldown - Cooldown time - Information | INT16 | X * 1 | X * 1 | s | X | X | X
General parameter: Delay timer remaining time | 46008 |  | 346009 | Parameters - Engine - Stop sequence - Extended stop - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46009 |  | 346010 | Parameters - Engine - Stop sequence - Cooldown - Suppress alarm action - Information | INT16 | X * 1 | X * 1 | s | X | X | X
General parameter: Delay timer remaining time | 46016 |  | 346017 | Parameters - Engine - Idle run start - Minimum - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46018 |  | 346019 | Parameters - Engine - Idle run start - Maximum - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46025 |  | 346026 | Parameters - Engine - Idle run stop - Minimum - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46027 |  | 346028 | Parameters - Engine - Idle run stop - Maximum - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46033 |  | 346034 | Parameters - Engine - Idle run start - Idle run - Extended inhibit - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46038 |  | 346039 | Parameters - Engine - Running detection - Engine ready - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46045 |  | 346046 | Parameters - Engine - Maintenance - Priming - OFF timer - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46046 |  | 346047 | Parameters - Engine - Maintenance - Priming - ON timer - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46049 |  | 346050 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump OFF delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46050 |  | 346051 | Pump source select | INT16 | X * 10 | X * 0.1 |  | X | X | X
General parameter: Delay timer remaining time | 46052 |  | 346053 | Parameters - Breakers - Generator breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46052 |  | 346053 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46052 |  | 346053 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer remaining time | 46053 |  | 346054 | Parameters - Breakers - Generator breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46053 |  | 346054 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46053 |  | 346054 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer remaining time | 46054 |  | 346055 | Parameters - Breakers - Generator breaker configuration - Configuration - Spring load time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46054 |  | 346055 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Spring load time - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46054 |  | 346055 | Parameters - Breakers - Mains breaker configuration - Configuration - Spring-load time - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer remaining time | 46057 |  | 346058 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s | X
General parameter: Delay timer remaining time | 46057 |  | 346058 | Parameters - Breakers - Tie breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
General parameter: Delay timer remaining time | 46058 |  | 346059 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s | X
General parameter: Delay timer remaining time | 46058 |  | 346059 | Parameters - Breakers - Tie breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
General parameter: Delay timer remaining time | 46059 |  | 346060 | Parameters - Breakers - Mains breaker configuration - Configuration - Spring-load time - Information | INT16 | X * 10 | X * 0.1 | s | X
General parameter: Delay timer remaining time | 46059 |  | 346060 | Parameters - Breakers - Tie breaker configuration - Configuration - Spring-load time - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
General parameter: Delay timer remaining time | 46200 |  | 346201 | Parameters - Generator - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46200 |  | 346201 | Parameters - Busbar A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46200 |  | 346201 | Parameters - Mains - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer remaining time | 46202 |  | 346203 | Parameters - Generator - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46202 |  | 346203 | Parameters - Busbar A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46202 |  | 346203 | Parameters - Mains - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer remaining time | 46204 |  | 346205 | Parameters - Busbar A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46204 |  | 346205 | Parameters - Mains - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer remaining time | 46206 |  | 346207 | Parameters - Busbar A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46206 |  | 346207 | Parameters - Mains - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer remaining time | 46208 |  | 346209 | Parameters - Busbar A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46208 |  | 346209 | Parameters - Mains - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer remaining time | 46210 |  | 346211 | Parameters - Busbar A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46210 |  | 346211 | Parameters - Mains - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer remaining time | 46225 |  | 346226 | Parameters - Mains - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X
General parameter: Delay timer remaining time | 46225 |  | 346226 | Parameters - Busbar - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X |  | X | X
General parameter: Delay timer remaining time | 46225 |  | 346226 | Parameters - Busbar B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46233 |  | 346234 | Blackout delay | INT16 | X * 10 | X * 0.1 | s | X | X
General parameter: Delay timer remaining time | 46233 |  | 346234 | Parameters - Busbar - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X |  | X | X
General parameter: Delay timer remaining time | 46233 |  | 346234 | Parameters - Busbar B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46234 |  | 346235 | Parameters - Generator - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46234 |  | 346235 | Parameters - Busbar A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46234 |  | 346235 | Parameters - Mains - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  |  | X | X
General parameter: Delay timer remaining time | 46242 |  | 346243 | Blackout delay | INT16 | X * 10 | X * 0.1 | s | X | X | X |  | X | X
General parameter: Delay timer remaining time | 46242 |  | 346243 | Parameters - Busbar A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46243 |  | 346244 | Parameters - Generator - AC setup - Voltage and frequency OK (blackout) - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46641 |  | 346642 | Parameters - Local - Alarm horn - Horn 1 - Minimum down time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 46642 |  | 346643 | Parameters - Local - Alarm horn - Horn 1 - Minimum up time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 46645 |  | 346646 | Parameters - Local - Alarm horn - Horn 2 - Minimum down time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 46646 |  | 346647 | Parameters - Local - Alarm horn - Horn 2 - Minimum up time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 46649 |  | 346650 | Parameters - Local - Alarm horn - Horn 3 - Minimum down time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 46650 |  | 346651 | Parameters - Local - Alarm horn - Horn 3 - Minimum up time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 46652 |  | 346653 | Parameters - Local - Alive - Alive configuration - Period - Information | INT16 | X * 100 | X * 0.01 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 46705 |  | 346706 | Parameters - Regulators - GOV - General configuration - Regulation delay - Regulator delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 46716 |  | 346717 | Parameters - Regulators - AVR - General configuration - Regulation delay - Regulator delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 47041 |  | 347042 | Parameters - Mains - AC setup - Supervision selector - Recovery selector time - Information | INT16 | X * 10 | X * 0.1 | s | X | X |  |  | X | X
General parameter: Delay timer remaining time | 47042 |  | 347043 | Parameters - Mains - AC setup - Supervision selector - Recovery time fast - Information | INT16 | X * 10 | X * 0.1 | s | X | X |  |  | X | X
General parameter: Delay timer remaining time | 47043 |  | 347044 | Parameters - Mains - AC setup - Supervision selector - Recovery time slow - Information | INT16 | X * 10 | X * 0.1 | s | X | X |  |  | X | X
General parameter: Delay timer remaining time | 47070 |  | 347071 | Parameters - Test functions - Lamp test - Duration - Information | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47071 |  | 347072 | Parameters - Test functions - Lamp test - Colour cycle time - Information | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47073 |  | 347074 | Parameters - CODESYS - Monitoring - Application not OK - Startup time - Information | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47076 |  | 347077 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU powerup time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 47106 |  | 347107 | Parameters - Engine - ECU - Controls - Reset - Power off timer - Information | INT16 | X * 1 | X * 1 | s | X | X | X
General parameter: Delay timer remaining time | 47147 |  | 347148 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Power-up time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 47811 |  | 347812 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47813 |  | 347814 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47815 |  | 347816 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47817 |  | 347818 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47819 |  | 347820 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47821 |  | 347822 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47823 |  | 347824 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47825 |  | 347826 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47827 |  | 347828 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47829 |  | 347830 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47831 |  | 347832 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47833 |  | 347834 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47835 |  | 347836 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47837 |  | 347838 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47839 |  | 347840 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47841 |  | 347842 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47843 |  | 347844 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47845 |  | 347846 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47847 |  | 347848 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47849 |  | 347850 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47851 |  | 347852 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47853 |  | 347854 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47855 |  | 347856 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47857 |  | 347858 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47890 |  | 347891 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47898 |  | 347899 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47899 |  | 347900 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47907 |  | 347908 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47908 |  | 347909 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47916 |  | 347917 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47917 |  | 347918 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47925 |  | 347926 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47926 |  | 347927 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47934 |  | 347935 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47935 |  | 347936 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47943 |  | 347944 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47944 |  | 347945 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47952 |  | 347953 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47953 |  | 347954 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47961 |  | 347962 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47998 |  | 347999 | Parameters - Engine - ECU diagnostic - Time to enable function - Information | INT16 | X * 1 | X * 1 | s | X | X | X
General parameter: Delay timer remaining time | 48000 |  | 348001 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump ON delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 48004 |  | 348005 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump ON delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 48005 |  | 348006 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump OFF delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 48010 |  | 348011 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump ON delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X
General parameter: Delay timer remaining time | 48011 |  | 348012 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump OFF delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X

## Controller text
Text associated to Modbus value
Modbus address | Modbus function code | Controller function name | Modbus output (decimal) | Text
8000 | 04 | Engine state | 0 | Engine not ready to start
|  |  | 1 | Engine ready to start
|  |  | 2 | Pre-running engine
|  |  | 3 | Preparing engine
|  |  | 4 | Crank on
|  |  | 5 | Engine start off
|  |  | 6 | Idle run
|  |  | 7 | Engine running
|  |  | 8 | Engine stopping
|  |  | 9 | Engine cooldown
|  |  | 12 | Extended stop active
8002 | 04 | GB state | 0 | Breaker open
|  | BTB state | 1 | Breaker closed
|  | MB state | 2 | Breaker position unknown
|  |  | 3 | Breaker opening directly
|  |  | 4 | Breaker closing directly
|  |  | 5 | Breaker synchronising
|  |  | 6 | Breaker deloading
8003 | 04 | MB state | 0 | Breaker open
|  |  | 1 | Breaker closed
|  |  | 2 | Breaker position unknown
|  |  | 3 | Breaker opening directly
|  |  | 4 | Breaker closing directly
|  |  | 5 | Breaker synchronising
|  |  | 6 | Breaker deloading
8004 | 04 | Virtual busbar status GB side | 0 | Dead busbar
|  |  | 1 | Busbar not dead and not OK
|  |  | 2 | Busbar OK, and not stable
|  |  | 3 | Live busbar
|  |  | 4 | Unknown state
8005 | 04 | Virtual busbar status MB side | 0 | Dead busbar
|  |  | 1 | Busbar not dead and not OK
|  |  | 2 | Busbar OK, and not stable
|  |  | 3 | Live busbar
|  |  | 4 | Unknown state
8006 | 04 | Mains ¦ State | 0 | Dead busbar
|  | Busbar ¦ State | 1 | Busbar not dead and not OK
|  | Busbar B ¦ State | 2 | Busbar OK, and not stable
|  |  | 3 | Live busbar
|  |  | 4 | Unknown state
8007 | 04 | Generator ¦ State | 0 | Dead busbar
|  | Busbar A ¦ State | 1 | Busbar not dead and not OK
|  | Mains ¦ State | 2 | Busbar OK, and not stable
|  |  | 3 | Live busbar
|  |  | 4 | Unknown state
8008 | 04 | Current command mode | 0 | MANUAL mode
|  |  | 1 | LOCAL mode
|  |  | 2 | Remote mode
8015 | 04 | GOV regulator type | 0 | Frequency synchronisation (analogue)
|  |  | 1 | Phase synchronisation (analogue)
|  |  | 2 | Frequency regulation (analogue)
|  |  | 3 | Power load share (analogue)
|  |  | 4 | Power regulation (analogue)
|  |  | 5 | Manual regulation (analogue)
|  |  | 6 | RPM synchronisation (analogue)
|  |  | 7 | RPM regulation (analogue)
|  |  | 8 | Frequency synchronisation (relay)
|  |  | 9 | Phase synchronisation (relay)
|  |  | 10 | Frequency regulation (relay)
|  |  | 11 | Power load share (relay)
|  |  | 12 | Power regulation (relay)
|  |  | 13 | Manual regulation (relay)
|  |  | 14 | RPM synchronisation (relay)
|  |  | 15 | RPM regulation (relay)
|  |  | 16 | No governor regulator configured
8016 | 04 | AVR regulator type | 0 | Voltage regulation (analogue)
|  |  | 1 | Reactive power load share (analogue)
|  |  | 2 | Reactive power regulation (analogue)
|  |  | 3 | Manual regulation (analogue)
|  |  | 4 | Voltage regulation (relay)
|  |  | 5 | Reactive power load share (relay)
|  |  | 6 | Reactive power regulation (relay)
|  |  | 7 | Manual regulation (relay)
|  |  | 8 | No AVR regulator configured
8027 | 04 | External breaker 1 state | 0 | Breaker open
|  |  | 1 | Breaker closed
|  |  | 2 | Breaker position unknown
8028 | 04 | External breaker 1 busbar A state | 4 | Unknown state
8029 | 04 | External breaker 1 busbar B state | 4 | Unknown state
8030 | 04 | External breaker 2 state | 0 | Breaker open
|  |  | 1 | Breaker closed
|  |  | 2 | Breaker position unknown
8031 | 04 | External breaker 2 busbar A state | 4 | Unknown state
8032 | 04 | External breaker 2 busbar B state | 4 | Unknown state
8033 | 04 | External breaker 3 state | 0 | Breaker open
|  |  | 1 | Breaker closed
|  |  | 2 | Breaker position unknown
8034 | 04 | External breaker 3 busbar A state | 4 | Unknown state
8035 | 04 | External breaker 3 busbar B state | 4 | Unknown state
8036 | 04 | External breaker 4 state | 0 | Breaker open
|  |  | 1 | Breaker closed
|  |  | 2 | Breaker position unknown
8037 | 04 | External breaker 4 busbar A state | 4 | Unknown state
8038 | 04 | External breaker 4 busbar B state | 4 | Unknown state
Note on B4: 04 - Read single or multiple
Note on D4: The controller function name shows the path to the parameter in PICUS. If the function is not visible in PICUS, only the function name is displayed.