## Description
SGC 120 and 121 Modbus descriptions
Row | Hyperlink index
9 | Modbus function codes
19 | Holding register
Back to index | Modbus function codes
| Function code | Description
| 03 | Read a single or multiple 16-bit registers from the server device location.
| 16 | Write a value to a single or multiple 16-bit registers to the server device.
Back to index | Holding register
| Function code | Effect
| 03 | Read
| 16 | Write
| Function group | Description
| AC measurement | Read the operating value of the associated AC measurement.
| Energy counter | Read the counter value.
| Engine measurement | Read the operating value of the associated engine measurement.
| Running hours | Read the running hours value
| Alarm status | Read the alarm status
| Input and output status | Read the state of a digital input or output on the controller. The controller returns 0 (false) when the digital input/output is inactive. The controller returns 1 (true) when the digital input/output is active.
| DG status | Read the status of the genset.
| DG mode change | Write: The controller changes the state of the genset if a valid value is entered.

## Holding register (03;16)
Holding register (03;16)
Function group | Modbus address | Modbus function code | Parameter | Data type | Scaling | Unit
Protocol revision | 0 | 03 | Protocol revision | Unsigned | - | -
AC measurement | 1 | 03 | Generator L1-n voltage | Unsigned | 0.1 | V
AC measurement | 2 | 03 | Generator L2-n voltage | Unsigned | 0.1 | V
AC measurement | 3 | 03 | Generator L3-n voltage | Unsigned | 0.1 | V
AC measurement | 4 | 03 | Generator L1-L2 voltage | Unsigned | 0.1 | V
AC measurement | 5 | 03 | Generator L2-L3 voltage | Unsigned | 0.1 | V
AC measurement | 6 | 03 | Generator L3-L1 voltage | Unsigned | 0.1 | V
AC measurement | 7 | 03 | Generator R frequency | Unsigned | 0.1 | Hz
AC measurement | 8 | 03 | Generator Y frequency | Unsigned | 0.1 | Hz
AC measurement | 9 | 03 | Generator B frequency | Unsigned | 0.1 | Hz
AC measurement | 10 | 03 | Generator power factor L1 | Signed | 0.01 | --
AC measurement | 11 | 03 | Generator power factor L2 | Signed | 0.01 | --
AC measurement | 12 | 03 | Generator power factor L3 | Signed | 0.01 | --
AC measurement | 13 | 03 | Generator average power factor | Signed | 0.01 | --
AC measurement | 14 | 03 | Mains L1-n voltage | Unsigned | 0.1 | V
AC measurement | 15 | 03 | Mains L2-n voltage | Unsigned | 0.1 | V
AC measurement | 16 | 03 | Mains L3-n voltage | Unsigned | 0.1 | V
AC measurement | 17 | 03 | Mains L1-L2 voltage | Unsigned | 0.1 | V
AC measurement | 18 | 03 | Mains L2-L3 voltage | Unsigned | 0.1 | V
AC measurement | 19 | 03 | Mains L3-L1 voltage | Unsigned | 0.1 | V
AC measurement | 20 | 03 | Mains R frequency | Unsigned | 0.1 | Hz
AC measurement | 21 | 03 | Mains Y frequency | Unsigned | 0.1 | Hz
AC measurement | 22 | 03 | Mains B frequency | Unsigned | 0.1 | Hz
AC measurement | 23 | 03 | Load L1 current | Unsigned | 0.1 | A
AC measurement | 24 | 03 | Load L2 current | Unsigned | 0.1 | A
AC measurement | 25 | 03 | Load L3 current | Unsigned | 0.1 | A
AC measurement | 26 | 03 | Load L1 watts | Signed | 0.1 | kW
AC measurement | 27 | 03 | Load L2 watts | Signed | 0.1 | kW
AC measurement | 28 | 03 | Load L3 watts | Signed | 0.1 | kW
AC measurement | 29 | 03 | Load total watts | Signed | 0.1 | kW
AC measurement | 30 | 03 | Percentage Load | Signed | 1 | %
AC measurement | 31 | 03 | Load L1 va | Unsigned | 0.1 | kVA
AC measurement | 32 | 03 | Load L2 va | Unsigned | 0.1 | kVA
AC measurement | 33 | 03 | Load L3 va | Unsigned | 0.1 | kVA
AC measurement | 34 | 03 | Load total va | Unsigned | 0.1 | kVA
AC measurement | 35 | 03 | Load L1 var | Unsigned | 0.1 | kVAR
AC measurement | 36 | 03 | Load L2 var | Unsigned | 0.1 | kVAR
AC measurement | 37 | 03 | Load L3 var | Unsigned | 0.1 | kVAR
AC measurement | 38 | 03 | Load total var | Unsigned | 0.1 | kVAR
Energy counter | 39-40 | 03 | Generator cumulative energy | Unsigned | 0.1 | kWh
Energy counter | 41-42 | 03 | Generator cumulative apparent energy | Unsigned | 0.1 | kVAh
Energy counter | 43-44 | 03 | Generator cumulative reactive energy | Unsigned | 0.1 | kVARh
Energy counter | 45-46 | 03 | Mains cumulative energy | Unsigned | 0.1 | kWh
Energy counter | 47-48 | 03 | Mains cumulative apparent energy | Unsigned | 0.1 | kVAh
Energy counter | 49-50 | 03 | Mains cumulative reactive energy | Unsigned | 0.1 | kVARh
Engine measurement | 51 | 03 | Oil pressure | Unsigned | 0.1 | Bar
Engine measurement | 52 | 03 | Coolant temperature | Signed | 0.1 | Deg C
Engine measurement | 53 | 03 | Fuel level | Unsigned | 1 | %
Engine measurement | 54 | 03 | Fuel level in Lit | Unsigned | 0.1 | lit
Engine measurement | 55 | 03 | Charge alternator voltage | Unsigned | 0.1 | V
Engine measurement | 56 | 03 | Battery voltage | Unsigned | 0.1 | V
Engine measurement | 57 | 03 | Engine speed | Unsigned | 1 | RPM
Engine measurement | 58 | 03 | No of starts | Unsigned | 1 | --
Engine measurement | 59 | 03 | No of trips | Unsigned | 1 | --
Running hours | 60-61 | 03 | Eng run hrs | Unsigned | 1 | Hrs
Running hours | 62 | 03 | Eng run min | Unsigned | 1 | Min
Running hours | 63 | 03 | Mains run hrs | Unsigned | 1 | Hrs
Running hours | 64 | 03 | Mains run min | Unsigned | 1 | Min
Function group | Modbus address | Modbus function code | Parameter | Data type | Scaling | Unit
Alarm Status for Alarm 1 | 65 | 03 | Low oil pressure | 13/16-16/16 | -- | --
Alarm Status for Alarm 1 | 65 | 03 | High coolant temperature | 9/16-12/16 | -- | --
Alarm Status for Alarm 1 | 65 | 03 | Low fuel level | 5/16-8/16 | -- | --
Alarm Status for Alarm 1 | 65 | 03 | Water level switch | 1/16-4/16 | -- | --
Alarm Status for Alarm 2 | 66 | 03 | Under speed | 13/16-16/16 | -- | --
Alarm Status for Alarm 2 | 66 | 03 | Over speed | 9/16-12/16 | -- | --
Alarm Status for Alarm 2 | 66 | 03 | Fail to start | 5/16-8/16 | -- | --
Alarm Status for Alarm 2 | 66 | 03 | Fail to stop | 1/16-4/16 | -- | --
Alarm Status for Alarm 3 | 67 | 03 | Reverse Power Detected | 13/16-16/16 | -- | --
Alarm Status for Alarm 3 | 67 | 03 | Low Load Alarm | 9/16-12/16 | -- | --
Alarm Status for Alarm 3 | 67 | 03 | Generator low frequency | 5/16-8/16 | -- | --
Alarm Status for Alarm 3 | 67 | 03 | Generator high frequency | 1/16-4/16 | -- | --
Alarm Status for Alarm 4 | 68 | 03 | Generator high current | 13/16-16/16 | -- | --
Alarm Status for Alarm 4 | 68 | 03 | Generator overload | 9/16-12/16 | -- | --
Alarm Status for Alarm 4 | 68 | 03 | Unbalanced load | 5/16-8/16 | -- | --
Alarm Status for Alarm 4 | 68 | 03 | Emergency stop | 1/16-4/16 | -- | --
Alarm Status for Alarm 5 | 69 | 03 | Charge alternator failure | 13/16-16/16 | -- | --
Alarm Status for Alarm 5 | 69 | 03 | Maintenance Due | 9/16-12/16
Alarm Status for Alarm 5 | 69 | 03 | AFT Activation Timeout | 5/16-8/16 | -- | --
Alarm Status for Alarm 5 | 69 | 03 | Ash Load Maintenance | 1/16-4/16 | -- | --
Alarm Status for Alarm 6 | 70 | 03 | Battery low voltage | 13/16-16/16 | -- | --
Alarm Status for Alarm 6 | 70 | 03 | Battery high voltage | 9/16-12/16 | -- | --
Alarm Status for Alarm 6 | 70 | 03 | Temperature Circuit open | 5/16-8/16 | -- | --
Alarm Status for Alarm 6 | 70 | 03 | LOP/Pin23-Short to battery | 1/16-4/16 | -- | --
Alarm Status for Alarm 7 | 71 | 03 | Fuel theft | 13/16-16/16 | -- | --
Alarm Status for Alarm 7 | 71 | 03 | Magnetic pick up fault | 9/16-12/16 | -- | --
Alarm Status for Alarm 7 | 71 | 03 | Oil pressure open circuit | 5/16-8/16 | -- | --
Alarm Status for Alarm 7 | 71 | 03 | Auxiliary input I | 1/16-4/16 | -- | --
Alarm Status for Alarm 8 | 72 | 03 | Auxiliary input A | 13/16-16/16 | -- | --
Alarm Status for Alarm 8 | 72 | 03 | Auxiliary input B | 9/16-12/16 | -- | --
Alarm Status for Alarm 8 | 72 | 03 | Auxiliary input C | 5/16-8/16 | -- | --
Alarm Status for Alarm 8 | 72 | 03 | Auxiliary input D | 1/16-4/16 | -- | --
Alarm Status for Alarm 9 | 73 | 03 | Auxiliary input E | 13/16-16/16 | -- | --
Alarm Status for Alarm 9 | 73 | 03 | Auxiliary input F | 9/16-12/16 | -- | --
Alarm Status for Alarm 9 | 73 | 03 | Auxiliary input G | 5/16-8/16 | -- | --
Alarm Status for Alarm 9 | 73 | 03 | Auxiliary input H | 1/16-4/16 | -- | --
Alarm Status for Alarm 10 | 74 | 03 | Gen L1 phase low volt | 13/16-16/16 | -- | --
Alarm Status for Alarm 10 | 74 | 03 | Gen L1 phase high volt | 9/16-12/16 | -- | --
Alarm Status for Alarm 10 | 74 | 03 | Gen L2 phase low volt | 5/16-8/16 | -- | --
Alarm Status for Alarm 10 | 74 | 03 | Gen L2 phase high volt | 1/16-4/16 | -- | --
Alarm Status for Alarm 11 | 75 | 03 | Gen L3 phase low volt | 13/16-16/16 | -- | --
Alarm Status for Alarm 11 | 75 | 03 | Gen L3 phase high volt | 9/16-12/16 | -- | --
Alarm Status for Alarm 11 | 75 | 03 | DG phase rotation | 5/16-8/16 | -- | --
Alarm Status for Alarm 11 | 75 | 03 | Mains phase rotation | 1/16-4/16 | -- | --
Alarm Status for Alarm 12 | 76 | 03 | Fuel level open circuit | 13/16-16/16 | -- | --
Alarm Status for Alarm 12 | 76 | 03 | V belt broken | 9/16-12/16 | -- | --
Alarm Status for Alarm 12 | 76 | 03 | Reserved | 5/16-8/16 | -- | --
Alarm Status for Alarm 12 | 76 | 03 | High oil pressure detected | 1/16-4/16 | -- | --
Interpretation of alarm status results
Value of Register | Interpretation
0 | Alarm disabled
1 | Alarm not active
2 | Warning alarm active
3 | Shutdown alarm active
4 | Electrical trip alarm active
5 | Notification
Function group | Register Address | Modbus function code | Parameter | Data type | Scaling | Unit
Input and output status | 77 | 03 | Digital input A | 16/16 | -- | --
Input and output status |  | 03 | Digital input B | 15/16 | -- | --
Input and output status |  | 03 | Digital input C | 14/16 | -- | --
Input and output status |  | 03 | Digital input D | 13/16 | -- | --
Input and output status |  | 03 | Digital input E | 12-16 | -- | --
Input and output status |  | 03 | Digital input F | 11-16 | -- | --
Input and output status |  | 03 | Digital input G | 10-16 | -- | --
Input and output status |  | 03 | Digital input H | 9-16 | -- | --
Input and output status |  | 03 | Digital input I | 8-16 | -- | --
Input and output status |  | 03 | Digital output A | 7-16 | -- | --
Input and output status |  | 03 | Digital output B | 6-16 | -- | --
Input and output status |  | 03 | Digital output C | 5-16 | -- | --
Input and output status |  | 03 | Digital output D | 4-16 | -- | --
Input and output status |  | 03 | Digital output E | 3-16 | -- | --
Input and output status |  | 03 | Digital output F | 2-16 | -- | --
Input and output status |  | 03 | Unimplemented | 1-16 | -- | --
Function group | Register Address | Modbus function code | Parameter | Data type | Scaling | Unit
DG status | 78 | 03 | SGC Mode | 16/16 | -- | Config (1)/Running or Not running (0)
DG status | 78 | 03 | Mains healthy / unhealthy | 15/16 | -- | True (1) / False(0)
DG status | 78 | 03 | DG operation mode | 14-12/16 | -- | Scheduler-110 Auto-101 Manual-100
DG status | 78 | 03 | Load on Mains | 11-16 | -- | True (1) / False(0)
DG status | 78 | 03 | Load on DG | 10-16 | -- | True (1) / False(0)
DG status | 78 | 03 | Current DG status | 9-16 | -- | Running / stopped
DG status | 78 | 03 | DG stopped normally | 8-16 | -- | True (1) / False(0)
DG status | 78 | 03 | DG stopped with fault | 7-16 | -- | True (1) / False(0)
DG status | 78 | 03 | DG fail to start | 6-16 | -- | True (1) / False(0)
DG status | 78 | 03 | Gen available | 5-16 | -- | True (1) / False(0)
DG status | 78 | 03 | Common shut down | 4-16 | -- | True (1) / False(0)
DG status | 78 | 03 | Common electric trip | 3-16 | -- | True (1) / False(0)
DG status | 78 | 03 | Common warning | 2-16 | -- | True (1) / False(0)
DG status | 78 | 03 | Common notification | 1-16 | -- | True (1) / False(0)
DG status | 79 | 03 | Current time stamp | Hexadecimal | -- | Min Sec
DG status | 80 | 03 | Current time stamp | Hexadecimal | -- | Week day Hour
DG status | 81 | 03 | Current time stamp | Hexadecimal | -- | Month Day
DG status | 82 | 03 | Current time stamp | Unsigned | -- | Year
Function group | Register Address | Modbus function code | Parameter | Data type | Scaling | Unit
DG mode change | 0 | 16 | DG mode change command | Unsigned | -- | SGC STOP KEY (0x01), Decimal value:01 SGC START KEY (0x02), Decimal value:02 SGC AUTO KEY (0x04), Decimal value:04 SGC ACK KEY (0x40), Decimal value:64 Only one value at a time