## Descriptions
MIB 8000 Modbus descriptions
Revision A
Row | Hyperlink index
15 | Framing
21 | Transmission_mode
29 | Modbus function codes
40 | Discrete output coil
48 | Discrete input contact
57 | Output holding register
Back to index | Framing
| Address | 8-bit
| Function | 8-bit
| Data | N x 8-bit
| Check | 16-bit
Back to index | Transmission mode
| Coding system | 8-bit binary
| Start bit | 1
| Data bits | 8
| Parity | No parity
| Stop bit | 1
| Error checking | CRC check
Back to index | Modbus function codes
| Function code | Description
| 01 | Read a single or multiple discrete output coils.
| 02 | Read a single or multiple discrete input contacts.
| 03 | Read a single or multiple output holding registers.
| 05 | Write a value to a single discrete output coil.
| 16 | Write a value to multiple consecutive output holding registers.
Back to index | Discrete output coils
| Function code | Effect
| 01 | Read
| 05 | Write
| Function group | Description
| Digital output state | Read the state of a digital output on the unit. Read: The unit returns 0 when the digital output is OFF and 1 when the unit is ON. Write: The unit executes the command if you write 1.
Back to index | Discrete input contact
| Function code | Effect
| 02 | Read
| Function group | Description
| Digital input | Read the state of a digital input on the unit. The unit returns 0 when the digital output is OFF. The unit returns 1 when the digital output is ON.
Back to index | Holding register
| Function code | Effect
| 03 | Read
| 16 | Write (preset)
| Function group | Description
| Basic measurements | Read the operating value of the associated basic measurement.
| Parameter settings | Read and write the parameter settings of the unit. Read: The unit returns the value of the associated function. Write: The unit changes the value of the associated function if a valid value is entered.
| Power quality measurements | Read the operating value of the associated power quality measurement.
| Real time energy measurements | Read and write the real time energy measurements of the unit. Read: The unit returns the value of the associated measurement. Write (preset): The unit changes the value of the associated measurement if a valid value is entered.
| Statistics measurements | Read the operating value of the associated statistic measurement.
| Run time parameters | Read the operating value of the associated run time parameter.
| Clock parameters | Read and write the time and date values of the unit. Read: The unit returns the value of the associated parameter. Write: The unit changes the value of the associated parameter if a valid value is entered.
| TOU energy: current month (accumulated) | Read and write the TOU energy values of the unit. Read: The unit returns the value of the associated parameter. Write (preset): The unit changes the value of the associated parameter if a valid value is entered.
| TOU energy: current month (incremental) | Read and write the TOU energy values of the controller. Read: The controller returns the value of the associated parameter. Write (preset): The controller changes the value of the associated parameter if a valid value is entered.
| TOU energy: prior month (accumulated) | Read and write the TOU energy values of the controller. Read: The controller returns the value of the associated parameter. Write (preset): The controller changes the value of the associated parameter if a valid value is entered.
| TOU energy: prior month (incremental) | Read and write the TOU energy values of the controller. Read: The controller returns the value of the associated parameter. Write (preset): The controller changes the value of the associated parameter if a valid value is entered.
| TOU energy: daily energy | Read and write the TOU energy values of the unit. Read: The unit returns the value of the associated parameter. Write (preset): The unit changes the value of the associated parameter if a valid value is entered.
| TOU maximum demand parameters | Read the operating value of the associated maximum demand parameter.
| TOU parameters | Read and write the TOU parameters of the unit. Read: The unit returns the value of the associated parameter. Write: The unit changes the value of the associated parameter if a valid value is entered.
| TOU: daylight saving time parameters | Read and write the daylight saving time parameters of the unit. Read: The unit returns the value of the associated parameter. Write: The unit changes the value of the associated parameter if a valid value is entered.
| TOU: ten years holiday | Read and write the ten years holiday values of the unit. Read: The unit returns the value of the associated value. Write: The unit changes the value of the associated value if a valid value is entered.
| Extend I/O parameter settings | Read and write the extend I/O parameter settings of the unit. Read: The unit returns the value of the associated parameter. Write: The unit changes the value of the associated parameter if a valid value is entered.
| Pulse accumulation | Read the operating value of the associated pulse accumulation value.
| SOE event parameters | Read and write the SOE event parameters of the unit. Read: The unit returns the value of the associated parameter. Write (preset): The unit changes the value of the associated parameter if a valid value is entered.

## Discrete output coils (01;05)
Relay status (01;05)
Function group | Modbus address | PLC address | Modbus function code | Controller function name
Digital output state | 0 | 40001 | 01;05 | DO1. 1: ON; 0: OFF
Digital output state | 1 | 40002 | 01;05 | DO2. 1: ON; 0: OFF

## Discrete input contact (02)
Discrete input contact (02)
Function group | Modbus address | PLC address | Modbus function code | Controller function name
Digital input | 0 | 40001 | 02 | DI1. 1: ON; 0: OFF
Digital input | 1 | 40002 | 02 | DI2. 1: ON; 0: OFF
Digital input | 2 | 40003 | 02 | DI3. 1: ON; 0: OFF
Digital input | 3 | 40004 | 02 | DI4. 1: ON; 0: OFF

## Holding register (03;16)
Holding register (03;16)
Function group | Modbus address | PLC address | Modbus function code | Function name | Data type | Data format | Scaling (10⁻ˣ) | Unit
Basic measurements | 8192 | 48193 | 03 | Frequency F | INT16u | AB | 2 | Hz
Basic measurements | 8193 | 48194 | 03 | Phase voltage V1 | INT16u | AB | 0 | V
Basic measurements | 8194 | 48195 | 03 | Phase voltage V2 | INT16u | AB | 0 | V
Basic measurements | 8195 | 48196 | 03 | Phase voltage V3 | INT16u | AB | 0 | V
Basic measurements | 8196 | 48197 | 03 | Uin avg | INT16u | AB | 0 | V
Basic measurements | 8197 | 48198 | 03 | Line voltage V12 | INT16u | AB | 0 | V
Basic measurements | 8198 | 48199 | 03 | Line voltage V23 | INT16u | AB | 0 | V
Basic measurements | 8199 | 48200 | 03 | Line voltage V31 | INT16u | AB | 0 | V
Basic measurements | 8200 | 48201 | 03 | Ull avg | INT16u | AB | 0 | V
Basic measurements | 8201 | 48202 | 03 | Current I1 | INT16u | AB | 0 | A
Basic measurements | 8202 | 48203 | 03 | Current I2 | INT16u | AB | 0 | A
Basic measurements | 8203 | 48204 | 03 | Current I3 | INT16u | AB | 0 | A
Basic measurements | 8204 | 48205 | 03 | Reserved | INT16u | AB | 0
Basic measurements | 8205 | 48206 | 03 | Neutral line current in | INT16u | AB | 0 | A
Basic measurements | 8206 | 48207 | 03 | I total | INT16u | AB | 0 | A
Basic measurements | 8207 | 48208 | 03 | I avg | INT16u | AB | 0 | A
Basic measurements | 8208 | 48209 | 03 | Phase active power Pa | INT16u | AB | 0 | W
Basic measurements | 8209 | 48210 | 03 | Phase active power Pb | INT16u | AB | 0 | W
Basic measurements | 8210 | 48211 | 03 | Phase active power Pc | INT16u | AB | 0 | W
Basic measurements | 8211 | 48212 | 03 | System active power Pcon | INT16u | AB | 0 | W
Basic measurements | 8212 | 48213 | 03 | Phase reactive power Qa | INT16u | AB | 0 | var
Basic measurements | 8213 | 48214 | 03 | Phase reactive power Qb | INT16u | AB | 0 | var
Basic measurements | 8214 | 48125 | 03 | Phase reactive power Qc | INT16u | AB | 0 | var
Basic measurements | 8215 | 48126 | 03 | System reactive power Qcon | INT16u | AB | 0 | var
Basic measurements | 8216 | 48217 | 03 | Phase apparent power Sa | INT16u | AB | 0 | VA
Basic measurements | 8217 | 48218 | 03 | Phase apparent power Sb | INT16u | AB | 0 | VA
Basic measurements | 8218 | 48219 | 03 | Phase apparent power Sc | INT16u | AB | 0 | VA
Basic measurements | 8219 | 48220 | 03 | System apparent power Scon | INT16u | AB | 0 | VA
Basic measurements | 8220 | 48221 | 03 | Phase power factor Pfa | INT16u | AB | 3
Basic measurements | 8221 | 48222 | 03 | Phase power factor Pfb | INT16u | AB | 3
Basic measurements | 8222 | 48223 | 03 | Phase power factor Pfc | INT16u | AB | 3
Basic measurements | 8223 | 48224 | 03 | System power factor Pfcon | INT16u | AB | 3
Basic measurements | 8224 | 48225 | 03 | Voltage unbalance factor U_unbl | INT16u | AB | 1
Basic measurements | 8225 | 48226 | 03 | Current unbalance factor I_unbl | INT16u | AB | 1
Basic measurements | 8226 | 48227 | 03 | Load nature RT (L/C/R) | INT16u | AB | 0
Basic measurements | 8227 | 48228 | 03 | Active power demand P_DEMA | INT16u | AB | 0 | W
Basic measurements | 8228 | 48229 | 03 | Reactive power demand Q_DEMA | INT16u | AB | 0 | var
Basic measurements | 8229 | 48230 | 03 | Apparent power demand S_DEMA | INT16u | AB | 0 | VA
Basic measurements | 8230 | 48231 | 03 | Phase current demand Ia_DEMA | INT16u | AB | 0 | A
Basic measurements | 8231 | 48232 | 03 | Phase current demand Ib_DEMA | INT16u | AB | 0 | A
Basic measurements | 8232 | 48233 | 03 | Phase current demand Ic_DEMA | INT16u | AB | 0 | A
Basic measurements | 8233 | 48234 | 03 | Neutral line current demand IN_DEMA | INT16u | AB | 0 | A
Basic measurements | 8234 | 48235 | 03 | Active power forecasting demand P_DEMA | INT16u | AB | 0 | W
Basic measurements | 8235 | 48236 | 03 | Reactive power forecasting demand Q_DEMA | INT16u | AB | 0 | var
Basic measurements | 8236 | 48237 | 03 | Apparent power forecasting demand S_DEMA | INT16u | AB | 0 | VA
Basic measurements | 8237 | 48238 | 03 | Phase current forecast demand Ia_DEMA | INT16u | AB | 0 | A
Basic measurements | 8238 | 48239 | 03 | Phase current forecast demand Ib_DEMA | INT16u | AB | 0 | A
Basic measurements | 8239 | 48240 | 03 | Phase current forecast demand Ic_DEMA | INT16u | AB | 0 | A
Basic measurements | 8240 | 48241 | 03 | Neutral line current forecast demand IN_DEMA | INT16u | AB | 0 | A
Basic measurements | 8241 | 48242 | 03 | Reserved | INT16u | AB
Power quality measurements | 9152 | 49153 | 03 | Total harmonic distortion of V1 or V12 THD_V1 | INT16u | AB | 2
Power quality measurements | 9153 | 49154 | 03 | Total harmonic distortion of V2 or V31 THD_V2 | INT16u | AB | 2
Power quality measurements | 9154 | 49155 | 03 | Total harmonic distortion of V3 or V23 THD_V3 | INT16u | AB | 2
Power quality measurements | 9155 | 49156 | 03 | Total harmonic distortion voltage average THD_V | INT16u | AB | 2
Power quality measurements | 9156 | 49157 | 03 | Total harmonic distortion I1 of I1 | INT16u | AB | 2
Power quality measurements | 9157 | 49158 | 03 | Total harmonic distortion I2 of I2 | INT16u | AB | 2
Power quality measurements | 9158 | 49159 | 03 | Total harmonic distortion I3 of I3 | INT16u | AB | 2
Power quality measurements | 9159 | 49160 | 03 | Total harmonic distortion I1 of IN | INT16u | AB | 2
Power quality measurements | 9160 | 49161 | 03 | Total harmonic distortion current average THD_I | INT16u | AB | 2
Power quality measurements | 9161 | 49162 | 03 | Odd total harmonic distortion of V1 (or V12) | INT16u | AB | 2
Power quality measurements | 9162 | 49163 | 03 | Even total harmonic distortion of V1 (or V12) | INT16u | AB | 2
Power quality measurements | 9163 | 49164 | 03 | THFF of V1 (or V12) | INT16u | AB | 2
Power quality measurements | 9164 | 49165 | 03 | Crest factor of V1 (or V12) | INT16u | AB | 2
Power quality measurements | 9165 | 49166 | 03 | Odd total harmonic distortion of V2 (or V23) | INT16u | AB | 2
Power quality measurements | 9166 | 49167 | 03 | Even total harmonic distortion of V2 (or V23) | INT16u | AB | 2
Power quality measurements | 9167 | 49168 | 03 | THFF of V2 (or V23) | INT16u | AB | 2
Power quality measurements | 9168 | 49169 | 03 | Crest factor of V2 (or V23) | INT16u | AB | 2
Power quality measurements | 9169 | 49170 | 03 | Odd total harmonic distortion of V3 (or V31) | INT16u | AB | 2
Power quality measurements | 9170 | 49171 | 03 | Even total harmonic distortion of V3 (or V31) | INT16u | AB | 2
Power quality measurements | 9171 | 49172 | 03 | THFF of V3 (or V31) | INT16u | AB | 2
Power quality measurements | 9172 | 49173 | 03 | Crest factor of V3 (or V31) | INT16u | AB | 2
Power quality measurements | 9173 | 49174 | 03 | Crest factor of V1 (or V12) | INT16u | AB | 2
Power quality measurements | 9174 | 49175 | 03 | Odd total harmonic distortion of I1 | INT16u | AB | 2
Power quality measurements | 9175 | 49176 | 03 | Even total harmonic distortion of I1 | INT16u | AB | 2
Power quality measurements | 9176 | 49177 | 03 | K factor of I1 | INT16u | AB | 2
Power quality measurements | 9177 | 49178 | 03 | Odd total harmonic distortion of I2 | INT16u | AB | 2
Power quality measurements | 9178 | 49179 | 03 | Even total harmonic distortion of I2 | INT16u | AB | 2
Power quality measurements | 9179 | 49180 | 03 | K factor of I2 | INT16u | AB | 2
Power quality measurements | 9180 | 49181 | 03 | Odd total harmonic distortion of I3 | INT16u | AB | 2
Power quality measurements | 9181 | 49182 | 03 | Even total harmonic distortion of I3 | INT16u | AB | 2
Power quality measurements | 9182 | 49183 | 03 | K factor of I3 | INT16u | AB | 2
Power quality measurements | 9183 | 49184 | 03 | Odd total harmonic distortion of IN | INT16u | AB | 2
Power quality measurements | 9184 | 49185 | 03 | Even total harmonic distortion of IN | INT16u | AB | 2
Power quality measurements | 9185 | 49186 | 03 | K factor of IN | INT16u | AB | 2
Power quality measurements | 9186 | 49187 | 03 | Harmonic spectrum of V1 (2nd ~ 63rd) | INT16u | AB | 2
Power quality measurements | 9187 | 49188 | 03 | Harmonic spectrum of V2 (2nd ~ 63rd) | INT16u | AB | 2
Power quality measurements | 9188 | 49189 | 03 | Harmonic spectrum of V3 (2nd ~ 63rd) | INT16u | AB | 2
Power quality measurements | 9189 | 49190 | 03 | Harmonic spectrum of I1 (2nd ~ 63rd) | INT16u | AB | 2
Power quality measurements | 9190 | 49191 | 03 | Harmonic spectrum of I2 (2nd ~ 63rd) | INT16u | AB | 2
Power quality measurements | 9191 | 49192 | 03 | Harmonic spectrum of I3 (2nd ~ 63rd) | INT16u | AB | 2
Statistics measurements | 12288 | 412289 | 03 | Time stamp - Year (Max of V1) | INT16u | AB | 0
Statistics measurements | 12288 | 412289 | 03 | Time stamp - Month (Max of V1) | INT16u | AB | 0
Statistics measurements | 12289 | 412290 | 03 | Time stamp - Day (Max of V1) | INT16u | AB | 0
Statistics measurements | 12289 | 412290 | 03 | Time stamp - Hours (Max of V1) | INT16u | AB | 0
Statistics measurements | 12290 | 412291 | 03 | Time stamp - Minute (Max of V1) | INT16u | AB | 0
Statistics measurements | 12290 | 412291 | 03 | Time stamp - Second (Max of V1) | INT16u | AB | 0
Statistics measurements | 12291 | 412292 | 03 | Max of V1 | INT16u | AB | 0 | V
Statistics measurements | 12292 - 12295 | 412293 - 412296 | 03 | Time stamp and max of V2 | INT16u | AB | 0 | V
Statistics measurements | 12296 - 12299 | 412297 - 412300 | 03 | Time stamp and max of V3 | INT16u | AB | 0 | V
Statistics measurements | 12300 - 12303 | 412301 - 412304 | 03 | Time stamp and max of V12 | INT16u | AB | 0 | V
Statistics measurements | 12304 - 12307 | 412305 - 412308 | 03 | Time stamp and max of V23 | INT16u | AB | 0 | V
Statistics measurements | 12308 - 12311 | 412309 - 412312 | 03 | Time stamp and max of V31 | INT16u | AB | 0 | V
Statistics measurements | 12312 - 12315 | 412313 - 412316 | 03 | Time stamp and max of I1 | INT16u | AB | 0 | A
Statistics measurements | 12316 - 12319 | 412317 - 412320 | 03 | Time stamp and max of I2 | INT16u | AB | 0 | A
Statistics measurements | 12320 - 12323 | 412321 - 412324 | 03 | Time stamp and max of I3 | INT16u | AB | 0 | A
Statistics measurements | 12324 - 12327 | 412325 - 412328 | 03 | Time stamp and max of IN | INT16u | AB | 0 | A
Statistics measurements | 12328 - 12331 | 412329 - 412332 | 03 | Time stamp and max of system power | INT16u | AB | 0 | W
Statistics measurements | 12332 - 12335 | 412333 - 412336 | 03 | Time stamp and max of system reactive power | INT16u | AB | 0 | var
Statistics measurements | 12336 - 12339 | 412337 - 412340 | 03 | Time stamp and max of system apparent power | INT16u | AB | 0 | VA
Statistics measurements | 12340 - 12343 | 412341 - 412344 | 03 | Time stamp and max of system power factor | INT16u | AB | 0
Statistics measurements | 12344 - 12347 | 412345 - 412348 | 03 | Time stamp and max of system frequency | INT16u | AB | 0 | V
Statistics measurements | 12348 - 12351 | 412349 - 412352 | 03 | Time stamp and max of unbalance voltage | INT16u | AB | 0 | A
Statistics measurements | 12352 - 12355 | 412352 - 412356 | 03 | Time stamp and max of unbalance current | INT16u | AB | 0
Statistics measurements | 12356 - 12359 | 412357 - 412360 | 03 | Time stamp and max of thermal distortion harmonics (THD) V1 | INT16u | AB | 0
Statistics measurements | 12360 - 12363 | 412361 - 412364 | 03 | Time stamp and max of thermal distortion harmonics (THD) V2 | INT16u | AB | 0
Statistics measurements | 12364 - 12367 | 412365 - 412368 | 03 | Time stamp and max of thermal distortion harmonics (THD) V3 | INT16u | AB | 0
Statistics measurements | 12368 - 12371 | 412369 - 412372 | 03 | Time stamp and max of thermal distortion harmonics (THD) I1 | INT16u | AB | 0
Statistics measurements | 12372 - 12375 | 412373 - 412376 | 03 | Time stamp and max of thermal distortion harmonics (THD) I2 | INT16u | AB | 0
Statistics measurements | 12376 - 12379 | 412377 - 412380 | 03 | Time stamp and max of thermal distortion harmonics (THD) I3 | INT16u | AB | 0
Statistics measurements | 12380 - 12383 | 412381 - 412384 | 03 | Time stamp and max of thermal distortion harmonics (THD) IN | INT16u | AB | 0
Statistics measurements | 12384 - 12387 | 412385 - 412388 | 03 | Time stamp and max of power demand | INT16u | AB | 0 | W
Statistics measurements | 12388 - 12391 | 412389 - 412392 | 03 | Time stamp and max of reactive power demand | INT16u | AB | 0 | var
Statistics measurements | 12392 - 12395 | 412393 - 412396 | 03 | Time stamp and max of apparent power demand | INT16u | AB | 0 | VA
Statistics measurements | 12396 - 12399 | 412397 - 412400 | 03 | Time stamp and max of I1 demand | INT16u | AB | 0 | A
Statistics measurements | 12400 - 12403 | 412401 - 412406 | 03 | Time stamp and max of I2 demand | INT16u | AB | 0 | A
Statistics measurements | 12404 - 12407 | 412405 - 412408 | 03 | Time stamp and max of I3 demand | INT16u | AB | 0 | A
Statistics measurements | 12408 - 12411 | 412409 - 412412 | 03 | Time stamp and max of IN demand | INT16u | AB | 0 | A
Statistics measurements | 12412 - 12415 | 412413 - 412416 | 03 | Time stamp and min of V1 | INT16u | AB | 0 | V
Statistics measurements | 12416 - 12419 | 412417 - 412420 | 03 | Time stamp and min of V2 | INT16u | AB | 0 | V
Statistics measurements | 12420 - 12423 | 412421 - 412424 | 03 | Time stamp and min of V3 | INT16u | AB | 0 | V
Statistics measurements | 12424 - 12427 | 412425 - 412428 | 03 | Time stamp and min of V12 | INT16u | AB | 0 | V
Statistics measurements | 12428 - 12431 | 412429 - 412432 | 03 | Time stamp and min of V23 | INT16u | AB | 0 | V
Statistics measurements | 12432 - 12435 | 412433 - 412436 | 03 | Time stamp and min of V31 | INT16u | AB | 0 | V
Statistics measurements | 12436 - 12439 | 412437 - 412440 | 03 | Time stamp and min of I1 | INT16u | AB | 0 | A
Statistics measurements | 12440 - 12443 | 412441 - 412444 | 03 | Time stamp and min of I2 | INT16u | AB | 0 | A
Statistics measurements | 12444 - 12447 | 412445 - 412448 | 03 | Time stamp and min of I3 | INT16u | AB | 0 | A
Statistics measurements | 12448 - 12451 | 412449 - 412452 | 03 | Time stamp and min of IN | INT16u | AB | 0 | A
Statistics measurements | 12452 - 12455 | 412453 - 412456 | 03 | Time stamp and min of system power | INT16u | AB | 0 | W
Statistics measurements | 12456 - 12459 | 412457 - 412460 | 03 | Time stamp and min of system reactive power | INT16u | AB | 0 | var
Statistics measurements | 12460 - 12463 | 412461 - 412464 | 03 | Time stamp and min of system of apparent power | INT16u | AB | 0 | VA
Statistics measurements | 12464 - 12467 | 412465 - 412468 | 03 | Time stamp and min of system power factor | INT16u | AB | 0 | W
Statistics measurements | 12468 - 12471 | 412469 - 412472 | 03 | Time stamp and min of system frequency | INT16u | AB | 0 | Hz
Statistics measurements | 12472 - 12475 | 412473 - 412476 | 03 | Time stamp and min of unbalance voltage | INT16u | AB | 0 | V
Statistics measurements | 12476 - 12479 | 412477 - 412480 | 03 | Time stamp and min of unbalance current | INT16u | AB | 0 | A
Statistics measurements | 12480 - 12483 | 412481 - 412484 | 03 | Time stamp and min of thermal distortion harmonics V1 | INT16u | AB | 0
Statistics measurements | 12484 - 12487 | 412485 - 412488 | 03 | Time stamp and min of thermal distortion harmonics V2 | INT16u | AB | 0
Statistics measurements | 12488 - 12491 | 412489 - 412492 | 03 | Time stamp and min of thermal distortion harmonics V3 | INT16u | AB | 0
Statistics measurements | 12492 - 12495 | 412493 - 412496 | 03 | Time stamp and min of thermal distortion harmonics I1 | INT16u | AB | 0
Statistics measurements | 12496 - 12499 | 412497 - 412500 | 03 | Time stamp and min of thermal distortion harmonics I2 | INT16u | AB | 0
Statistics measurements | 12500 - 12503 | 412501 - 412504 | 03 | Time stamp and min of thermal distortion harmonics I3 | INT16u | AB | 0
Statistics measurements | 12504 - 12507 | 412505 - 412508 | 03 | Time stamp and min of thermal distortion harmonics IN | INT16u | AB | 0
Run time parameters | 384 | 4385 | 03 | Meter run time (high 16 bit) | INT32u | ABCD | 2 | H
Run time parameters | 385 | 4386 | 03 | Meter run time (low 16 bit) | INT32u | ABCD | 2 | H
Run time parameters | 386 | 4387 | 03 | Load run time (high 16 bit) | INT32u | ABCD | 2 | H
Run time parameters | 387 | 4388 | 03 | Load run time (low 16 bit) | INT32u | ABCD | 2 | H
Parameter settings | 4096 | 44097 | 03;16 | Access code | INT16u | AB | 0
Parameter settings | 4097 | 44098 | 03;16 | Communication address | INT16u | AB | 0
Parameter settings | 4098 | 44099 | 03;16 | Baud rate | INT16u | AB | 0
Parameter settings | 4099 | 44100 | 03;16 | Parity mode. 0:EVEN; 1:ODD; 2:NONE2; 3: NONE1 | INT16u | AB | 0
Parameter settings | 4100 | 44101 | 03;16 | Voltage input wiring type. 0: 3Ln; 1: 3LL; 2: 2LL; 3: 1Ln; 4: 1LL | INT16u | AB | 0
Parameter settings | 4101 | 44102 | 03;16 | Current input wiring type. 0: 3CT; 1: 2CT; 2: 1 CT | INT16u | AB | 0
Parameter settings | 4102 | 44103 | 03;16 | PT1 (high 16 bit) | INT16u | AB | 0
Parameter settings | 4103 | 44104 | 03;16 | PT1 (low 16 bit) | INT16u | AB | 0
Parameter settings | 4104 | 44105 | 03;16 | PT2 | INT16u | AB | 0
Parameter settings | 4105 | 44106 | 03;16 | CT1 | INT16u | AB | 0
Parameter settings | 4106 | 44107 | 03;16 | CT2 | INT16u | AB | 0
Parameter settings | 4107 | 44108 | 03;16 | CTN1 | INT16u | AB | 0
Parameter settings | 4108 | 44109 | 03;16 | CTN2 | INT16u | AB | 0
Parameter settings | 4109 | 44110 | 03;16 | Definition of middle line current. 0: calculated; 1: measured | INT16u | AB | 0
Parameter settings | 4110 | 44111 | 03;16 | Definition of reactive power. 0: sinusoidal; 1: non-sinusoidal | INT16u | AB | 0
Parameter settings | 4111 | 44112 | 03;16 | Non-standard options of the lead. | INT16u | AB | 0
Parameter settings | 4112 | 44113 | 03;16 | Current I1 direction. 0: positive; 1: negative | INT16u | AB | 0
Parameter settings | 4113 | 44114 | 03;16 | Current I2 direction. 0: positive; 1: negative | INT16u | AB | 0
Parameter settings | 4114 | 44115 | 03;16 | Current I3 direction. 0: positive; 1: negative | INT16u | AB | 0
Parameter settings | 4115 | 44116 | 03;16 | Energy calculating mode. 0: primary; 1: secondary | INT16u | AB | 0
Parameter settings | 4116 | 44117 | 03;16 | Demand calculating mode. 0: sliding window demand; 1: fixed window demand; 2: rolling window demand; 3: thermal demand | INT16u | AB | 0
Parameter settings | 4117 | 44118 | 03;16 | Averaging interval window | INT16u | AB | 0
Parameter settings | 4118 | 44119 | 03;16 | Sub-interval | INT16u | AB | 0
Parameter settings | 4119 | 44120 | 03;16 | VAR/PF convention. =: IEC; 1: IEEE | INT16u | AB | 0
Parameter settings | 4120 | 44121 | 03;16 | Demand clear. Only 0AH work | INT16u | AB | 0
Parameter settings | 4121 | 44122 | 03;16 | Energy calculating mode. 0: disable. 1: enable | INT16u | AB | 0
Parameter settings | 4122 | 44123 | 03;16 | Energy clear. Only 0AH work | INT16u | AB | 0
Parameter settings | 4123 | 44124 | 03;16 | Reset total run time. Only 0AH work | INT16u | AB | 0
Parameter settings | 4124 | 44125 | 03;16 | Reset load time clear. Only 0AH work | INT16u | AB | 0
Parameter settings | 4125 | 44126 | 03;16 | Reset run time. Only 0AH work | INT16u | AB | 0
Parameter settings | 4126 | 44127 | 03;16 | Enable holiday years setting | INT16u | AB | 0
Parameter settings | 4127 | 44128 | 03;16 | Sharp demand clear. Only 0AH work | INT16u | AB | 0
Parameter settings | 4128 | 44129 | 03;16 | Peak demand clear. Only 0AH work | INT16u | AB | 0
Parameter settings | 4129 | 44130 | 03;16 | Valley demand clear. Only 0AH work | INT16u | AB | 0
Parameter settings | 4130 | 44131 | 03;16 | Normal demand clear. Only 0AH work | INT16u | AB | 0
Parameter settings | 4131 | 44132 | 03;16 | Total demand clear. Only 0AH work | INT16u | AB | 0
Parameter settings | 4132 | 44133 | 03;16 | Reset max and min. Only 0AH work | INT16u | AB | 0
Parameter settings | 4133 | 44134 | 03;16 | Turn on the backlight | INT16u | AB | 0
Parameter settings | 4134 | 44135 | 03;16 | Reverse. 0: Modbus-RTU; 1: Profibus | INT16u | AB | 0
Parameter settings | 4135 | 44136 | 03;16 | Communication address of channel 2 | INT16u | AB | 0
Parameter settings | 4136 | 44137 | 03;16 | Baud rate of channel 2 | INT16u | AB | 0
Parameter settings | 4137 | 44138 | 03;16 | Parity mode of channel 2. 0:EVEN; 1:ODD; 2:NONE2; 3: NONE1 | INT16u | AB | 0
Parameter settings | 4138 | 44139 | 03;16 | Enable wiring check. Only 0AH work | INT16u | AB | 0
Parameter settings | 4139 | 44140 | 03;16 | Expected power factor. Capacitive: 67; inductive: 76; resistive: 82 | INT16u | AB | 0
Parameter settings | 4140 | 44141 | 03;16 | Expected load type | INT16s | AB | 0
Parameter settings | 4141 | 44142 | 03;16 | Reverse | INT16u | AB | 0
Clock parameters | 8832 | 48833 | 03;16 | Year | INT16u | AB | 0
Clock parameters | 8833 | 48834 | 03;16 | Month | INT16u | AB | 0
Clock parameters | 8834 | 48835 | 03;16 | Day | INT16u | AB | 0
Clock parameters | 8835 | 48836 | 03;16 | Hour | INT16u | AB | 0
Clock parameters | 8836 | 48837 | 03;16 | Minute | INT16u | AB | 0
Clock parameters | 8837 | 48838 | 03;16 | Second | INT16u | AB | 0
Clock parameters | 8838 | 48839 | 03;16 | Week | INT16u | AB | 0
Clock parameters | 8839 | 48840 | 03;16 | Total run time (high) | INT16u | AB | 0
Clock parameters | 8840 | 48841 | 03;16 | Total run time (low) | INT16u | AB | 0
Clock parameters | 8841 | 48842 | 03;16 | Load run time (high) | INT16u | AB | 0
Clock parameters | 8842 | 48843 | 03;16 | Load run time (low) | INT16u | AB | 0
Clock parameters | 8843 | 48844 | 03;16 | Run time (high) | INT16u | AB | 0
Clock parameters | 8844 | 48845 | 03;16 | Run time (low) | INT16u | AB | 0
Clock parameters | 8845 | 48846 | 03;16 | Reverse | INT16u | AB | 0
Real time energy measurements | 8320 - 8321 | 48321 - 48322 | 03;16 | Energy import Ep_imp (primary) | INT32u | ABCD | 1 | kWh
Real time energy measurements | 8320 - 8321 | 48321 - 48322 | 03;16 | Energy import Ep_imp (secondary) | INT32u | ABCD | 3 | kWh
Real time energy measurements | 8322 - 8323 | 48323 - 48324 | 03;16 | Energy export Ep_exp (primary) | INT32u | ABCD | 1 | kWh
Real time energy measurements | 8322 - 8323 | 48323 - 48324 | 03;16 | Energy export Ep_exp (secondary) | INT32u | ABCD | 3 | kWh
Real time energy measurements | 8324 - 8325 | 48325 - 48326 | 03;16 | Energy total Ep_total (primary) | INT32u | ABCD | 1 | kWh
Real time energy measurements | 8324 - 8325 | 48325 - 48326 | 03;16 | Energy total Ep_total (secondary) | INT32u | ABCD | 3 | kWh
Real time energy measurements | 8326 - 8327 | 48327 - 48328 | 03;16 | Energy net Ep_net (primary) | INT32u | ABCD | 1 | kWh
Real time energy measurements | 8326 - 8327 | 48327 - 48328 | 03;16 | Energy net Ep_net (secondary) | INT32u | ABCD | 3 | kWh
Real time energy measurements | 8328 - 8329 | 48329 - 48330 | 03;16 | First quartile energy Ep_q1 (primary) | INT32u | ABCD | 1 | kWh
Real time energy measurements | 8328 - 8329 | 48329 - 48330 | 03;16 | First quartile energy Ep_q1 (secondary) | INT32u | ABCD | 3 | kWh
Real time energy measurements | 8330 - 8331 | 48331 - 48332 | 03;16 | Second quartile energy Ep_q2 (primary) | INT32u | ABCD | 1 | kWh
Real time energy measurements | 8330 - 8331 | 48331 - 48332 | 03;16 | Second quartile energy Ep_q2 (secondary) | INT32u | ABCD | 3 | kWh
Real time energy measurements | 8332 - 8333 | 48333 - 48334 | 03;16 | Third quartile energy Ep_q3 (primary) | INT32u | ABCD | 1 | kWh
Real time energy measurements | 8332 - 8333 | 48333 - 48334 | 03;16 | Third quartile energy Ep_q3 (secondary) | INT32u | ABCD | 3 | kWh
Real time energy measurements | 8334 - 8335 | 48335 - 48336 | 03;16 | Fourth quartile energy Ep_q4 (primary) | INT32u | ABCD | 1 | kWh
Real time energy measurements | 8334 - 8335 | 48335 - 48336 | 03;16 | Fourth quartile energy Ep_q4 (secondary) | INT32u | ABCD | 3 | kWh
Real time energy measurements | 8336 - 8337 | 48337 - 48338 | 03;16 | Inductive reactive energy Eq_imp (primary) | INT32u | ABCD | 1 | KVARh
Real time energy measurements | 8336 - 8337 | 48337 - 48338 | 03;16 | Inductive reactive energy Eq_imp (secondary) | INT32u | ABCD | 3 | KVARh
Real time energy measurements | 8338 - 8339 | 48339 - 48340 | 03;16 | Capacitive reactive energy Eq_imp (primary) | INT32u | ABCD | 1 | KVARh
Real time energy measurements | 8338 - 8339 | 48339 - 48340 | 03;16 | Capacitive reactive energy Eq_imp (secondary) | INT32u | ABCD | 3 | KVARh
Real time energy measurements | 8340 - 8341 | 48341 - 48342 | 03;16 | Reactive energy total Eq_total (primary) | INT32u | ABCD | 1 | KVARh
Real time energy measurements | 8340 - 8341 | 48341 - 48342 | 03;16 | Reactive energy total Eq_total (secondary) | INT32u | ABCD | 3 | KVARh
Real time energy measurements | 8342 - 8343 | 48343 - 48344 | 03;16 | Reactive energy net Eq_net (primary) | INT32u | ABCD | 1 | KVARh
Real time energy measurements | 8342 - 8343 | 48343 - 48344 | 03;16 | Reactive energy net Eq_net (secondary) | INT32u | ABCD | 3 | KVARh
Real time energy measurements | 8344 - 8345 | 48345 - 48346 | 03;16 | First quartile reactive energy Eq_q1 (primary) | INT32u | ABCD | 1 | KVARh
Real time energy measurements | 8344 - 8345 | 48345 - 48346 | 03;16 | First quartile reactive energy Eq_q1 (secondary) | INT32u | ABCD | 3 | KVARh
Real time energy measurements | 8346 - 8347 | 48347 - 48348 | 03;16 | Second quartile reactive energy Eq_q2 (primary) | INT32u | ABCD | 1 | KVARh
Real time energy measurements | 8346 - 8347 | 48347 - 48348 | 03;16 | Second quartile reactive energy Eq_q2 (secondary) | INT32u | ABCD | 3 | KVARh
Real time energy measurements | 8348 - 8349 | 48349 - 48350 | 03;16 | Third quartile reactive energy Eq_q3 (primary) | INT32u | ABCD | 1 | KVARh
Real time energy measurements | 8348 - 8349 | 48349 - 48350 | 03;16 | Third quartile reactive energy Eq_q3 (secondary) | INT32u | ABCD | 3 | KVARh
Real time energy measurements | 8350 - 8351 | 48351 - 48352 | 03;16 | Fourth quartile reactive energy Eq_q4 (primary) | INT32u | ABCD | 1 | KVARh
Real time energy measurements | 8350 - 8351 | 48351 - 48352 | 03;16 | Fourth quartile reactive energy Eq_q4 (secondary) | INT32u | ABCD | 3 | KVARh
Real time energy measurements | 8352 - 8353 | 48353 - 48354 | 03;16 | Apparent energy import Es_imp (primary) | INT32u | ABCD | 1 | KVAh
Real time energy measurements | 8352 - 8353 | 48353 - 48354 | 03;16 | Apparent energy import Es_imp (secondary) | INT32u | ABCD | 3 | KVAh
Real time energy measurements | 8354 - 8355 | 48355 - 48356 | 03;16 | Apparent energy export Es_exp (primary) | INT32u | ABCD | 1 | KVAh
Real time energy measurements | 8354 - 8355 | 48355 - 48356 | 03;16 | Apparent energy export Es_exp (secondary) | INT32u | ABCD | 3 | KVAh
Real time energy measurements | 8356 - 8357 | 48357 - 48358 | 03;16 | Apparent total energy Es_total (primary) | INT32u | ABCD | 1 | KVAh
Real time energy measurements | 8356 - 8357 | 48357 - 48358 | 03;16 | Apparent total energy Es_total (secondary) | INT32u | ABCD | 3 | KVAh
Real time energy measurements | 8358 - 8359 | 48359 - 48360 | 03;16 | Apparent energy net Es_net (primary) | INT32u | ABCD | 1 | KVAh
Real time energy measurements | 8358 - 8359 | 48359 - 48360 | 03;16 | Apparent energy net Es_net (secondary) | INT32u | ABCD | 3 | KVAh
Real time energy measurements | 8360 - 8361 | 48361 - 48362 | 03;16 | First quartile apparent energy Es_q1 (primary) | INT32u | ABCD | 1 | KVAh
Real time energy measurements | 8360 - 8361 | 48361 - 48362 | 03;16 | First quartile apparent energy Es_q1 (secondary) | INT32u | ABCD | 3 | KVAh
Real time energy measurements | 8362 - 8363 | 48363 - 48364 | 03;16 | Second quartile apparent energy Es_q2 (primary) | INT32u | ABCD | 1 | KVAh
Real time energy measurements | 8362 - 8363 | 48363 - 48364 | 03;16 | Second quartile apparent energy Es_q2 (secondary) | INT32u | ABCD | 3 | KVAh
Real time energy measurements | 8364 - 8365 | 48365 - 48366 | 03;16 | Third quartile apparent energy Es_q3 (primary) | INT32u | ABCD | 1 | KVAh
Real time energy measurements | 8364 - 8365 | 48365 - 48366 | 03;16 | Third quartile apparent energy Es_q3 (secondary) | INT32u | ABCD | 3 | KVAh
Real time energy measurements | 8366 - 8367 | 48367 - 48368 | 03;16 | Fourth quartile apparent energy Es_q4 (primary) | INT32u | ABCD | 1 | KVAh
Real time energy measurements | 8366 - 8367 | 48367 - 48368 | 03;16 | Fourth quartile apparent energy Es_q4 (secondary) | INT32u | ABCD | 3 | KVAh
Real time energy measurements | 8368 - 8369 | 48369 - 48370 | 03;16 | Phase A energy import Ep_imp (primary) | INT32u | ABCD | 1 | kWh
Real time energy measurements | 8368 - 8369 | 48369 - 48370 | 03;16 | Phase A energy import Ep_imp (secondary) | INT32u | ABCD | 3 | kWh
Real time energy measurements | 8370 - 8371 | 48371 - 48372 | 03;16 | Phase A energy export Ep_exp (primary) | INT32u | ABCD | 1 | kWh
Real time energy measurements | 8370 - 8371 | 48371 - 48372 | 03;16 | Phase A energy export Ep_exp (secondary) | INT32u | ABCD | 3 | kWh
Real time energy measurements | 8372 - 8373 | 48373 - 48374 | 03;16 | Phase B energy import Ep_imp (primary) | INT32u | ABCD | 1 | kWh
Real time energy measurements | 8372 - 8373 | 48373 - 48374 | 03;16 | Phase B energy import Ep_imp (secondary) | INT32u | ABCD | 3 | kWh
Real time energy measurements | 8374 - 8375 | 48375 - 48376 | 03;16 | Phase B energy export Ep_exp (primary) | INT32u | ABCD | 1 | kWh
Real time energy measurements | 8374 - 8375 | 48375 - 48376 | 03;16 | Phase B energy export Ep_exp (secondary) | INT32u | ABCD | 3 | kWh
Real time energy measurements | 8376 - 8377 | 48377 - 48378 | 03;16 | Phase C energy import Ep_imp (primary) | INT32u | ABCD | 1 | kWh
Real time energy measurements | 8376 - 8377 | 48377 - 48378 | 03;16 | Phase C energy import Ep_imp (secondary) | INT32u | ABCD | 3 | kWh
Real time energy measurements | 8378 - 8379 | 48379 - 48380 | 03;16 | Phase C energy export Ep_exp (primary) | INT32u | ABCD | 1 | kWh
Real time energy measurements | 8378 - 8379 | 48379 - 48380 | 03;16 | Phase C energy export Ep_exp (secondary) | INT32u | ABCD | 3 | kWh
Real time energy measurements | 8380 - 8381 | 48381 - 48382 | 03;16 | Phase A reactive energy import Ep_imp (primary) | INT32u | ABCD | 1 | KVARh
Real time energy measurements | 8380 - 8381 | 48381 - 48382 | 03;16 | Phase A reactive energy import Ep_imp (secondary) | INT32u | ABCD | 3 | KVARh
Real time energy measurements | 8382 - 8383 | 48383 - 48384 | 03;16 | Phase A reactive energy export Ep_exp (primary) | INT32u | ABCD | 1 | KVARh
Real time energy measurements | 8382 - 8383 | 48383 - 48384 | 03;16 | Phase A reactive energy export Ep_exp (secondary) | INT32u | ABCD | 3 | KVARh
Real time energy measurements | 8384 - 8385 | 48385 - 48386 | 03;16 | Phase B reactive energy import Ep_imp (primary) | INT32u | ABCD | 1 | KVARh
Real time energy measurements | 8384 - 8385 | 48385 - 48386 | 03;16 | Phase B reactive energy import Ep_imp (secondary) | INT32u | ABCD | 3 | KVARh
Real time energy measurements | 8386 - 8387 | 48387 - 48388 | 03;16 | Phase B reactive energy export Ep_exp (primary) | INT32u | ABCD | 1 | KVARh
Real time energy measurements | 8386 - 8387 | 48387 - 48388 | 03;16 | Phase B reactive energy export Ep_exp (secondary) | INT32u | ABCD | 3 | KVARh
Real time energy measurements | 8388 - 8389 | 48389 - 48390 | 03;16 | Phase C reactive energy import Ep_imp (primary) | INT32u | ABCD | 1 | KVARh
Real time energy measurements | 8388 - 8389 | 48389 - 48390 | 03;16 | Phase C reactive energy import Ep_imp (secondary) | INT32u | ABCD | 3 | KVARh
Real time energy measurements | 8390 - 8391 | 48391 - 48392 | 03;16 | Phase C reactive energy export Ep_exp (primary) | INT32u | ABCD | 1 | KVARh
Real time energy measurements | 8390 - 8391 | 48391 - 48392 | 03;16 | Phase C reactive energy export Ep_exp (secondary) | INT32u | ABCD | 3 | KVARh
Real time energy measurements | 8392 - 8393 | 48393 - 48394 | 03;16 | Phase A apparent energy import Ep_imp (primary) | INT32u | ABCD | 1 | KVAh
Real time energy measurements | 8392 - 8393 | 48393 - 48394 | 03;16 | Phase A apparent energy import Ep_imp (secondary) | INT32u | ABCD | 3 | KVAh
Real time energy measurements | 8394 - 8395 | 48395 - 48396 | 03;16 | Phase A apparent energy export Ep_imp (primary) | INT32u | ABCD | 1 | KVAh
Real time energy measurements | 8394 - 8395 | 48395 - 48396 | 03;16 | Phase A apparent energy export Ep_imp (secondary) | INT32u | ABCD | 3 | KVAh
Real time energy measurements | 8396 - 8397 | 48397 - 48398 | 03;16 | Phase B apparent energy import Ep_imp (primary) | INT32u | ABCD | 1 | KVAh
Real time energy measurements | 8396 - 8397 | 48397 - 48398 | 03;16 | Phase B apparent energy import Ep_imp (secondary) | INT32u | ABCD | 3 | KVAh
Real time energy measurements | 8398 - 8399 | 48399 - 48400 | 03;16 | Phase B apparent energy export Ep_imp (primary) | INT32u | ABCD | 1 | KVAh
Real time energy measurements | 8398 - 8399 | 48399 - 48400 | 03;16 | Phase B apparent energy export Ep_imp (secondary) | INT32u | ABCD | 3 | KVAh
Real time energy measurements | 8400 - 8401 | 48401 - 48402 | 03;16 | Phase C apparent energy import Ep_imp (primary) | INT32u | ABCD | 1 | KVAh
Real time energy measurements | 8400 - 8401 | 48401 - 48402 | 03;16 | Phase C apparent energy import Ep_imp (secondary) | INT32u | ABCD | 3 | KVAh
Real time energy measurements | 8402 - 8403 | 48403 - 48404 | 03;16 | Phase C apparent energy export Ep_imp(primary) | INT32u | ABCD | 1 | KVAh
Real time energy measurements | 8402 - 8403 | 48403 - 48404 | 03;16 | Phase C apparent energy export Ep_imp (secondary) | INT32u | ABCD | 3 | KVAh
TOU energy: current month (accumulated) | 13568 - 13569 | 413569 - 413570 | 03;16 | Import Energy Ep_imp (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13570 - 13571 | 413571 - 413572 | 03;16 | Import Energy Ep_imp (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13572 - 13573 | 413573 - 413574 | 03;16 | Import Energy Ep_imp (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13574 - 13575 | 413575 - 413576 | 03;16 | Import Energy Ep_imp (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13576 - 13577 | 413577 - 413578 | 03;16 | Import Energy Ep_imp (total) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13578 - 13579 | 413579 - 413580 | 03;16 | Export energy Ep_exp (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13580 - 13581 | 413581 - 413582 | 03;16 | Export energy Ep_exp (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13582 - 13583 | 413583 - 413584 | 03;16 | Export energy Ep_exp (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13584 - 13585 | 413585 - 413586 | 03;16 | Export energy Ep_exp (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13586 - 13587 | 413587 - 413588 | 03;16 | Export energy Ep_exp (total) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13588 - 13589 | 413589 - 413590 | 03;16 | Total energy Ep_total (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13590 - 13591 | 413591 - 413592 | 03;16 | Total energy Ep_total (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13592 - 13593 | 413593 - 413594 | 03;16 | Total energy Ep_total (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13594 - 13595 | 413595 - 413596 | 03;16 | Total energy Ep_total (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13596 - 13597 | 413597 - 413598 | 03;16 | Total energy Ep_total (total) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13598 - 13599 | 413599 - 413600 | 03;16 | Net energy Ep_net (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13600 - 13601 | 413601 - 413602 | 03;16 | Net energy Ep_net (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13602 - 13603 | 413603 - 413604 | 03;16 | Net energy Ep_net (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13604 - 13605 | 413605 - 413606 | 03;16 | Net energy Ep_net (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13606 - 13607 | 413607 - 413608 | 03;16 | Net energy Ep_net (total) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13608 - 13609 | 413609 - 413610 | 03;16 | First quartile energy Ep_q1 (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13610 - 13611 | 413611 - 413612 | 03;16 | First quartile energy Ep_q1 (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13612 - 13613 | 413613 - 413614 | 03;16 | First quartile energy Ep_q1 (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13614 - 13615 | 413615 - 413616 | 03;16 | First quartile energy Ep_q1 (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13616 - 13617 | 413617 - 413618 | 03;16 | First quartile energy Ep_q1 (total) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13618 - 13619 | 413619 - 413620 | 03;16 | Second quartile energy Ep_q2 (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13620 - 13621 | 413621 - 413622 | 03;16 | Second quartile energy Ep_q2 (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13622 - 13623 | 413623 - 413624 | 03;16 | Second quartile energy Ep_q2 (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13624 - 13625 | 413625 - 413626 | 03;16 | Second quartile energy Ep_q2 (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13626 - 13627 | 413627 - 413628 | 03;16 | Second quartile energy Ep_q2 (total) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13628 - 13629 | 413629 - 413630 | 03;16 | Third quartile energy Ep_q3 (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13630 - 13631 | 413631 - 413632 | 03;16 | Third quartile energy Ep_q3 (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13632 - 13633 | 413633 - 413634 | 03;16 | Third quartile energy Ep_q3 (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13634 - 13635 | 413635 - 413636 | 03;16 | Third quartile energy Ep_q3 (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13636 - 13637 | 413637 - 413638 | 03;16 | Third quartile energy Ep_q3 (total) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13638 - 13639 | 413639 - 413640 | 03;16 | Fourth quartile energy Ep_q4 (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13640 - 13641 | 413641 - 413642 | 03;16 | Fourth quartile energy Ep_q4 (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13642 - 13643 | 413643 - 413644 | 03;16 | Fourth quartile energy Ep_q4 (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13644 - 13645 | 413645 - 413646 | 03;16 | Fourth quartile energy Ep_q4 (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13646 - 13647 | 413647 - 413648 | 03;16 | Fourth quartile energy Ep_q4 (total) | INT32u | ABCD |  | kWh
TOU energy: current month (accumulated) | 13648 - 13649 | 413649 - 413650 | 03;16 | Inductive reactive energy (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13650 - 13651 | 413651 - 413652 | 03;16 | Inductive reactive energy (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13652 - 13653 | 413653 - 413654 | 03;16 | Inductive reactive energy (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13654 - 13655 | 413655 - 413656 | 03;16 | Inductive reactive energy (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13656 - 13657 | 413657 - 413658 | 03;16 | Inductive reactive energy (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13658 - 13659 | 413659 - 413660 | 03;16 | Capacitive reactive energy (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13660 - 13661 | 413661 - 413662 | 03;16 | Capacitive reactive energy (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13662 - 13663 | 413663 - 413664 | 03;16 | Capacitive reactive energy (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13664 - 13665 | 413665 - 413666 | 03;16 | Capacitive reactive energy (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13666 - 13667 | 413667 - 413668 | 03;16 | Capacitive reactive energy (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13668 - 13669 | 413669 - 413670 | 03;16 | Reactive energy total Eq_total (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13670 - 13671 | 413671 - 413672 | 03;16 | Reactive energy total Eq_total (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13672 - 13673 | 413673 - 413674 | 03;16 | Reactive energy total Eq_total (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13674 - 13675 | 413675 - 413676 | 03;16 | Reactive energy total Eq_total (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13676 - 13677 | 413677 - 413678 | 03;16 | Reactive energy total Eq_total (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13678 - 13679 | 413679 - 413680 | 03;16 | Reactive energy net Eq_net (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13680 - 13681 | 413681 - 413682 | 03;16 | Reactive energy net Eq_net (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13682 - 13683 | 413683 - 413684 | 03;16 | Reactive energy net Eq_net (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13684 - 13685 | 413685 - 413686 | 03;16 | Reactive energy net Eq_net (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13686 - 13687 | 413687 - 413688 | 03;16 | Reactive energy net Eq_net (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13688 - 13689 | 413689 - 413690 | 03;16 | First quartile reactive energy Eq_q1 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13690 - 13691 | 413691 - 413692 | 03;16 | First quartile reactive energy Eq_q1 (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13692 - 13693 | 413693 - 413694 | 03;16 | First quartile reactive energy Eq_q1 (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13694 - 13695 | 413695 - 413696 | 03;16 | First quartile reactive energy Eq_q1 (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13696 - 13697 | 413697 - 413698 | 03;16 | First quartile reactive energy Eq_q1 (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13698 - 13699 | 413699 - 413700 | 03;16 | Second quartile reactive energy Eq_q2 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13700 - 13701 | 413701 - 413702 | 03;16 | Second quartile reactive energy Eq_q2 (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13702 - 13703 | 413703 - 413704 | 03;16 | Second quartile reactive energy Eq_q2 (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13704 - 13705 | 413705 - 413706 | 03;16 | Second quartile reactive energy Eq_q2 (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13706 - 13707 | 413707 - 413708 | 03;16 | Second quartile reactive energy Eq_q2 (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13708 - 13709 | 413709 - 413710 | 03;16 | Third quartile reactive energy Eq_q3 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13710 - 13711 | 413711 - 413712 | 03;16 | Third quartile reactive energy Eq_q3 (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13712 - 13713 | 413713 - 413714 | 03;16 | Third quartile reactive energy Eq_q3 (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13714 - 13715 | 413715 - 413716 | 03;16 | Third quartile reactive energy Eq_q3 (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13716 - 13717 | 413717 - 413718 | 03;16 | Third quartile reactive energy Eq_q3 (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13718 - 13719 | 413719 - 413720 | 03;16 | Fourth quartile reactive energy Eq_q4 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13720 - 13721 | 413721 - 413722 | 03;16 | Fourth quartile reactive energy Eq_q4 (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13722 - 13723 | 413723 - 413724 | 03;16 | Fourth quartile reactive energy Eq_q4 (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13724 - 13725 | 413725 - 413726 | 03;16 | Fourth quartile reactive energy Eq_q4 (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13726 - 13727 | 413727 - 413728 | 03;16 | Fourth quartile reactive energy Eq_q4 (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (accumulated) | 13728 - 13729 | 413729 - 413730 | 03;16 | Apparent energy import Es_imp (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13730 - 13731 | 413731 - 413732 | 03;16 | Apparent energy import Es_imp (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13732 - 13733 | 413733 - 413734 | 03;16 | Apparent energy import Es_imp (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13734 - 13735 | 413735 - 413736 | 03;16 | Apparent energy import Es_imp (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13736 - 13737 | 413737 - 413738 | 03;16 | Apparent energy import Es_imp (total) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13738 - 13739 | 413739 - 413740 | 03;16 | Apparent energy export Es_exp (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13740 - 13741 | 413741 - 413742 | 03;16 | Apparent energy export Es_exp (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13742 - 13743 | 413743 - 413744 | 03;16 | Apparent energy export Es_exp (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13744 - 13745 | 413745 - 413746 | 03;16 | Apparent energy export Es_exp (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13746 - 13747 | 413747 - 413748 | 03;16 | Apparent energy export Es_exp (total) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13748 - 13749 | 413749 - 413750 | 03;16 | Apparent energy total Es_total (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13750 - 13751 | 413751 - 413752 | 03;16 | Apparent energy total Es_total (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13752 - 13753 | 413753 - 413754 | 03;16 | Apparent energy total Es_total (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13754 - 13755 | 413755 - 413756 | 03;16 | Apparent energy total Es_total (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13756 - 13757 | 413757 - 413758 | 03;16 | Apparent energy total Es_total (total) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13758 - 13759 | 413759 - 413760 | 03;16 | Apparent energy net Es_net (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13760 - 13761 | 413761 - 413762 | 03;16 | Apparent energy net Es_net (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13762 - 13763 | 413763 - 413764 | 03;16 | Apparent energy net Es_net (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13764 - 13765 | 413765 - 413766 | 03;16 | Apparent energy net Es_net (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13766 - 13767 | 413767 - 413768 | 03;16 | Apparent energy net Es_net (total) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13768 - 13769 | 413769 - 413770 | 03;16 | First quartile apparent energy Es_q1 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13770 - 13771 | 413771 - 413772 | 03;16 | First quartile apparent energy Es_q1 (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13772 - 13773 | 413773 - 413774 | 03;16 | First quartile apparent energy Es_q1 (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13774 - 13775 | 413775 - 413776 | 03;16 | First quartile apparent energy Es_q1 (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13776 - 13777 | 413777 - 413778 | 03;16 | First quartile apparent energy Es_q1 (total) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13778 - 13779 | 413779 - 413780 | 03;16 | Second quartile apparent energy Es_q2 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13780 - 13781 | 413781 - 413782 | 03;16 | Second quartile apparent energy Es_q2 (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13782 - 13783 | 413783 - 413784 | 03;16 | Second quartile apparent energy Es_q2 (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13784 - 13785 | 413785 - 413786 | 03;16 | Second quartile apparent energy Es_q2 (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13786 - 13787 | 413787 - 413788 | 03;16 | Second quartile apparent energy Es_q2 (total) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13788 - 13789 | 413789 - 413790 | 03;16 | Third quartile apparent energy Es_q3 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13790 - 13791 | 413791 - 413792 | 03;16 | Third quartile apparent energy Es_q3 (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13792 - 13793 | 413793 - 413794 | 03;16 | Third quartile apparent energy Es_q3 (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13794 - 13795 | 413795 - 413796 | 03;16 | Third quartile apparent energy Es_q3 (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13796 - 13797 | 413797 - 413798 | 03;16 | Third quartile apparent energy Es_q3 (total) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13798 - 13799 | 413799 - 413800 | 03;16 | Fourth quartile apparent energy Es_q4 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13800 - 13801 | 413801 - 413802 | 03;16 | Fourth quartile apparent energy Es_q4 (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13802 - 13803 | 413803 - 413804 | 03;16 | Fourth quartile apparent energy Es_q4 (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13804 - 13805 | 413805 - 413806 | 03;16 | Fourth quartile apparent energy Es_q4 (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (accumulated) | 13806 - 13807 | 413807 - 413808 | 03;16 | Fourth quartile apparent energy Es_q4 (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13808 - 13809 | 413809 - 413810 | 03;16 | Import Energy Ep_imp (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13810 - 13811 | 413811 - 413812 | 03;16 | Import Energy Ep_imp (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13812 - 13813 | 413813 - 413814 | 03;16 | Import Energy Ep_imp (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13814 - 13815 | 413815 - 413816 | 03;16 | Import Energy Ep_imp (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13816 - 13817 | 413817 - 413818 | 03;16 | Import Energy Ep_imp (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13818 - 13819 | 413819 - 413820 | 03;16 | Export energy Ep_exp (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13820 - 13821 | 413821 - 413822 | 03;16 | Export energy Ep_exp (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13822 - 13823 | 413823 - 413824 | 03;16 | Export energy Ep_exp (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13824 - 13825 | 413825 - 413826 | 03;16 | Export energy Ep_exp (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13826 - 13827 | 413827 - 413828 | 03;16 | Export energy Ep_exp (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13828 - 13829 | 413829 - 413830 | 03;16 | Total energy Ep_total (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13830 - 13831 | 413831 - 413832 | 03;16 | Total energy Ep_total (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13832 - 13833 | 413833 - 413834 | 03;16 | Total energy Ep_total (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13834 - 13835 | 413835 - 413836 | 03;16 | Total energy Ep_total (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13836 - 13837 | 413837 - 413838 | 03;16 | Total energy Ep_total (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13838 - 13839 | 413839 - 413840 | 03;16 | Net energy Ep_net (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13840 - 13841 | 413841 - 413842 | 03;16 | Net energy Ep_net (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13842 - 13843 | 413843 - 413844 | 03;16 | Net energy Ep_net (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13844 - 13845 | 413845 - 413846 | 03;16 | Net energy Ep_net (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13846 - 13847 | 413847 - 413848 | 03;16 | Net energy Ep_net (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13848 - 13849 | 413849 - 413850 | 03;16 | First quartile energy Ep_q1 (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13850 - 13851 | 413851 - 413852 | 03;16 | First quartile energy Ep_q1 (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13852 - 13853 | 413853 - 413854 | 03;16 | First quartile energy Ep_q1 (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13854 - 13855 | 413855 - 413856 | 03;16 | First quartile energy Ep_q1 (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13856 - 13857 | 413857 - 413858 | 03;16 | First quartile energy Ep_q1 (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13858 - 13859 | 413859 - 413860 | 03;16 | Second quartile energy Ep_q2 (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13860 - 13861 | 413861 - 413862 | 03;16 | Second quartile energy Ep_q2 (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13862 - 13863 | 413863 - 413864 | 03;16 | Second quartile energy Ep_q2 (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13864 - 13865 | 413865 - 413866 | 03;16 | Second quartile energy Ep_q2 (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13866 - 13867 | 413867 - 413868 | 03;16 | Second quartile energy Ep_q2 (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13868 - 13869 | 413869 - 413870 | 03;16 | Third quartile energy Ep_q3 (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13870 - 13871 | 413871 - 413872 | 03;16 | Third quartile energy Ep_q3 (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13872 - 13873 | 413873 - 413874 | 03;16 | Third quartile energy Ep_q3 (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13874 - 13875 | 413875 - 413876 | 03;16 | Third quartile energy Ep_q3 (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13876 - 13877 | 413877 - 413878 | 03;16 | Third quartile energy Ep_q3 (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13878 - 13879 | 413879 - 413880 | 03;16 | Fourth quartile energy Ep_q4 (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13880 - 13881 | 413881 - 413882 | 03;16 | Fourth quartile energy Ep_q4 (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13882 - 13883 | 413883 - 413884 | 03;16 | Fourth quartile energy Ep_q4 (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13884 - 13885 | 413885 - 413886 | 03;16 | Fourth quartile energy Ep_q4 (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13886 - 13887 | 413887 - 413888 | 03;16 | Fourth quartile energy Ep_q4 (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13888 - 13889 | 413889 - 413890 | 03;16 | Inductive reactive energy (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (accumulated) | 13890 - 13891 | 413891 - 413892 | 03;16 | Inductive reactive energy (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13892 - 13893 | 413893 - 413894 | 03;16 | Inductive reactive energy (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13894 - 13895 | 413895 - 413896 | 03;16 | Inductive reactive energy (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13896 - 13897 | 413897 - 413898 | 03;16 | Inductive reactive energy (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13898 - 13899 | 413899 - 413900 | 03;16 | Capacitive reactive energy (sharp) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13900 - 13901 | 413901 - 413902 | 03;16 | Capacitive reactive energy (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13902 - 13903 | 413903 - 413904 | 03;16 | Capacitive reactive energy (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13904 - 13905 | 413905 - 413906 | 03;16 | Capacitive reactive energy (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13906 - 13907 | 413907 - 413908 | 03;16 | Capacitive reactive energy (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13908 - 13909 | 413909 - 413910 | 03;16 | Reactive energy total Eq_total (sharp) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13910 - 13911 | 413911 - 413912 | 03;16 | Reactive energy total Eq_total (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13912 - 13913 | 413913 - 413914 | 03;16 | Reactive energy total Eq_total (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13914 - 13915 | 413915 - 413916 | 03;16 | Reactive energy total Eq_total (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13916 - 13917 | 413917 - 413918 | 03;16 | Reactive energy total Eq_total (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13918 - 13919 | 413919 - 413920 | 03;16 | Reactive energy net Eq_net (sharp) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13920 - 13921 | 413921 - 413922 | 03;16 | Reactive energy net Eq_net (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13922 - 13923 | 413923 - 413924 | 03;16 | Reactive energy net Eq_net (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13924 - 13925 | 413925 - 413926 | 03;16 | Reactive energy net Eq_net (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13926 - 13927 | 413927 - 413928 | 03;16 | Reactive energy net Eq_net (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13928 - 13929 | 413929 - 413930 | 03;16 | First quartile reactive energy Eq_q1 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13930 - 13931 | 413931 - 413932 | 03;16 | First quartile reactive energy Eq_q1 (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13932 - 13933 | 413933 - 413934 | 03;16 | First quartile reactive energy Eq_q1 (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13934 - 13935 | 413935 - 413936 | 03;16 | First quartile reactive energy Eq_q1 (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13936 - 13937 | 413937 - 413938 | 03;16 | First quartile reactive energy Eq_q1 (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13938 - 13939 | 413939 - 413940 | 03;16 | Second quartile reactive energy Eq_q2 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13940 - 13941 | 413941 - 413942 | 03;16 | Second quartile reactive energy Eq_q2 (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13942 - 13943 | 413943 - 413944 | 03;16 | Second quartile reactive energy Eq_q2 (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13944 - 13945 | 413945 - 413946 | 03;16 | Second quartile reactive energy Eq_q2 (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13946 - 13947 | 413947 - 413948 | 03;16 | Second quartile reactive energy Eq_q2 (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13948 - 13949 | 413949 - 413950 | 03;16 | Third quartile reactive energy Eq_q3 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13950 - 13951 | 413951 - 413952 | 03;16 | Third quartile reactive energy Eq_q3 (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13952 - 13953 | 413953 - 413954 | 03;16 | Third quartile reactive energy Eq_q3 (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13954 - 13955 | 413955 - 413956 | 03;16 | Third quartile reactive energy Eq_q3 (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13956 - 13957 | 413957 - 413958 | 03;16 | Third quartile reactive energy Eq_q3 (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13958 - 13959 | 413959 - 413960 | 03;16 | Fourth quartile reactive energy Eq_q4 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13960 - 13961 | 413961 - 413962 | 03;16 | Fourth quartile reactive energy Eq_q4 (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13962 - 13963 | 413963 - 413964 | 03;16 | Fourth quartile reactive energy Eq_q4 (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13964 - 13965 | 413965 - 413966 | 03;16 | Fourth quartile reactive energy Eq_q4 (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13966 - 13967 | 413967 - 413968 | 03;16 | Fourth quartile reactive energy Eq_q4 (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (accumulated) | 13968 - 13969 | 413969 - 413970 | 03;16 | Apparent energy import Es_imp (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13970 - 13971 | 413971 - 413972 | 03;16 | Apparent energy import Es_imp (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13972 - 13973 | 413973 - 413974 | 03;16 | Apparent energy import Es_imp (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13974 - 13975 | 413975 - 413976 | 03;16 | Apparent energy import Es_imp (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13976 - 13977 | 413977 - 413978 | 03;16 | Apparent energy import Es_imp (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13978 - 13979 | 413979 - 413980 | 03;16 | Apparent energy export Es_exp (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13980 - 13981 | 413981 - 413982 | 03;16 | Apparent energy export Es_exp (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13982 - 13983 | 413983 - 413984 | 03;16 | Apparent energy export Es_exp (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13984 - 13985 | 413985 - 413986 | 03;16 | Apparent energy export Es_exp (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13986 - 13987 | 413987 - 413988 | 03;16 | Apparent energy export Es_exp (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13988 - 13989 | 413989 - 413990 | 03;16 | Apparent energy total Es_total (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13990 - 13991 | 413991 - 413992 | 03;16 | Apparent energy total Es_total (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13992 - 13993 | 413993 - 413994 | 03;16 | Apparent energy total Es_total (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13994 - 13995 | 413995 - 413996 | 03;16 | Apparent energy total Es_total (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13996 - 13997 | 413997 - 413998 | 03;16 | Apparent energy total Es_total (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 13998 - 13999 | 413999 - 414000 | 03;16 | Apparent energy net Es_net (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14000 - 14001 | 414001 - 414002 | 03;16 | Apparent energy net Es_net (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14002 - 14003 | 414003 - 414004 | 03;16 | Apparent energy net Es_net (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14004 - 14005 | 414005 - 414006 | 03;16 | Apparent energy net Es_net (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14006 - 14007 | 414007 - 414008 | 03;16 | Apparent energy net Es_net (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14008 - 14009 | 414009 - 414010 | 03;16 | First quartile apparent energy Es_q1 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14010 - 14011 | 414011 - 414012 | 03;16 | First quartile apparent energy Es_q1 (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14012 - 14013 | 414013 - 414014 | 03;16 | First quartile apparent energy Es_q1 (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14014 - 14015 | 414015 - 414016 | 03;16 | First quartile apparent energy Es_q1 (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14016 - 14017 | 414017 - 414018 | 03;16 | First quartile apparent energy Es_q1 (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14018 - 14019 | 414019 - 414020 | 03;16 | Second quartile apparent energy Es_q2 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14020 - 14021 | 414021 - 414022 | 03;16 | Second quartile apparent energy Es_q2 (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14022 - 14023 | 414023 - 414024 | 03;16 | Second quartile apparent energy Es_q2 (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14024 - 14025 | 414025 - 414026 | 03;16 | Second quartile apparent energy Es_q2 (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14026 - 14027 | 414027 - 414028 | 03;16 | Second quartile apparent energy Es_q2 (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14028 - 14029 | 414029 - 414030 | 03;16 | Third quartile apparent energy Es_q3 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14030 - 14031 | 414031 - 414032 | 03;16 | Third quartile apparent energy Es_q3 (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14032 - 14033 | 414033 - 414034 | 03;16 | Third quartile apparent energy Es_q3 (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14034 - 14035 | 414035 - 414036 | 03;16 | Third quartile apparent energy Es_q3 (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14036 - 14037 | 414037 - 414038 | 03;16 | Third quartile apparent energy Es_q3 (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14038 - 14039 | 414039 - 414040 | 03;16 | Fourth quartile apparent energy Es_q4 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14040 - 14041 | 414041 - 414042 | 03;16 | Fourth quartile apparent energy Es_q4 (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14042 - 14043 | 414043 - 414044 | 03;16 | Fourth quartile apparent energy Es_q4 (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14044 - 14045 | 414045 - 414046 | 03;16 | Fourth quartile apparent energy Es_q4 (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (accumulated) | 14046 - 14047 | 414047 - 414048 | 03;16 | Fourth quartile apparent energy Es_q4 (total) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14336 - 14337 | 414337 - 414338 | 03;16 | Import Energy Ep_imp (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14338 - 14339 | 414339 - 414340 | 03;16 | Import Energy Ep_imp (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14340 - 14341 | 414341 - 414342 | 03;16 | Import Energy Ep_imp (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14342 - 14343 | 414343 - 414344 | 03;16 | Import Energy Ep_imp (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14344 - 14345 | 414345 - 414346 | 03;16 | Import Energy Ep_imp (total) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14346 - 14347 | 414347 - 414348 | 03;16 | Export energy Ep_exp (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14348 - 14349 | 414349 - 414350 | 03;16 | Export energy Ep_exp (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14350 - 14351 | 414351 - 414352 | 03;16 | Export energy Ep_exp (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14352 - 14353 | 414353 - 414354 | 03;16 | Export energy Ep_exp (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14354 - 14355 | 414355 - 414356 | 03;16 | Export energy Ep_exp (total) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14356 - 14357 | 414357 - 414358 | 03;16 | Total energy Ep_total (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14358 - 14359 | 414359 - 414360 | 03;16 | Total energy Ep_total (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14360 - 14361 | 414361 - 414362 | 03;16 | Total energy Ep_total (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14362 - 14363 | 414363 - 414364 | 03;16 | Total energy Ep_total (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14364 - 14365 | 414365 - 414366 | 03;16 | Total energy Ep_total (total) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14366 - 14367 | 414367 - 414368 | 03;16 | Net energy Ep_net (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14368 - 14369 | 414369 - 414370 | 03;16 | Net energy Ep_net (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14370 - 14371 | 414371 - 414372 | 03;16 | Net energy Ep_net (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14372 - 14373 | 414373 - 414374 | 03;16 | Net energy Ep_net (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14374 - 14375 | 414375 - 414376 | 03;16 | Net energy Ep_net (total) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14376 - 14377 | 414377 - 414378 | 03;16 | First quartile energy Ep_q1 (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14378 - 14379 | 414379 - 414380 | 03;16 | First quartile energy Ep_q1 (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14380 - 14381 | 414381 - 414382 | 03;16 | First quartile energy Ep_q1 (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14382 - 14383 | 414383 - 414384 | 03;16 | First quartile energy Ep_q1 (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14384 - 14385 | 414385 - 414386 | 03;16 | First quartile energy Ep_q1 (total) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14386 - 14387 | 414387 - 414388 | 03;16 | Second quartile energy Ep_q2 (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14388 - 14389 | 414389 - 414390 | 03;16 | Second quartile energy Ep_q2 (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14390 - 14391 | 414391 - 414392 | 03;16 | Second quartile energy Ep_q2 (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14392 - 14393 | 414393 - 414394 | 03;16 | Second quartile energy Ep_q2 (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14394 - 14395 | 414395 - 414396 | 03;16 | Second quartile energy Ep_q2 (total) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14396 - 14397 | 414397 - 414398 | 03;16 | Third quartile energy Ep_q3 (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14398 - 14399 | 414399 - 414400 | 03;16 | Third quartile energy Ep_q3 (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14400 - 14401 | 414401 - 414402 | 03;16 | Third quartile energy Ep_q3 (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14402 - 14403 | 414403 - 414404 | 03;16 | Third quartile energy Ep_q3 (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14404 - 14405 | 414405 - 414406 | 03;16 | Third quartile energy Ep_q3 (total) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14406 - 14407 | 414407 - 414408 | 03;16 | Fourth quartile energy Ep_q4 (sharp) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14408 - 14409 | 414409 - 414410 | 03;16 | Fourth quartile energy Ep_q4 (peak) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14410 - 14411 | 414411 - 414412 | 03;16 | Fourth quartile energy Ep_q4 (valley) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14412 - 14413 | 414413 - 414414 | 03;16 | Fourth quartile energy Ep_q4 (normal) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14414 - 14415 | 414415 - 414416 | 03;16 | Fourth quartile energy Ep_q4 (total) | INT32u | ABCD |  | kWh
TOU energy: current month (incremental) | 14416 - 14417 | 414417 - 414418 | 03;16 | Inductive reactive energy (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14418 - 14419 | 414419 - 414420 | 03;16 | Inductive reactive energy (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14420 - 14421 | 414421 - 414422 | 03;16 | Inductive reactive energy (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14422 - 14423 | 414423 - 414424 | 03;16 | Inductive reactive energy (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14424 - 14425 | 414425 - 414426 | 03;16 | Inductive reactive energy (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14426 - 14427 | 414427 - 414428 | 03;16 | Capacitive reactive energy (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14428 - 14429 | 414429 - 414430 | 03;16 | Capacitive reactive energy (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14430 - 14431 | 414431 - 414432 | 03;16 | Capacitive reactive energy (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14432 - 14433 | 414433 - 414434 | 03;16 | Capacitive reactive energy (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14434 - 14435 | 414435 - 414436 | 03;16 | Capacitive reactive energy (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14436 - 14437 | 414437 - 414438 | 03;16 | Reactive energy total Eq_total (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14438 - 14439 | 414439 - 414440 | 03;16 | Reactive energy total Eq_total (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14440 - 14441 | 414441 - 414442 | 03;16 | Reactive energy total Eq_total (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14442 - 14443 | 414443 - 414444 | 03;16 | Reactive energy total Eq_total (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14444 - 14445 | 414445 - 414446 | 03;16 | Reactive energy total Eq_total (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14446 - 14447 | 414447 - 414448 | 03;16 | Reactive energy net Eq_net (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14448 - 14449 | 414449 - 414450 | 03;16 | Reactive energy net Eq_net (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14450 - 14451 | 414451 - 414452 | 03;16 | Reactive energy net Eq_net (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14452 - 14453 | 414453 - 414454 | 03;16 | Reactive energy net Eq_net (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14454 - 14455 | 414455 - 414456 | 03;16 | Reactive energy net Eq_net (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14456 - 14457 | 414457 - 414458 | 03;16 | First quartile reactive energy Eq_q1 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14458 - 14459 | 414459 - 414460 | 03;16 | First quartile reactive energy Eq_q1 (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14460 - 14461 | 414461 - 414462 | 03;16 | First quartile reactive energy Eq_q1 (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14462 - 14463 | 414463 - 414464 | 03;16 | First quartile reactive energy Eq_q1 (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14464 - 14465 | 414465 - 414466 | 03;16 | First quartile reactive energy Eq_q1 (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14466 - 14467 | 414467 - 414468 | 03;16 | Second quartile reactive energy Eq_q2 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14468 - 14469 | 414469 - 414470 | 03;16 | Second quartile reactive energy Eq_q2 (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14470 - 14471 | 414471 - 414472 | 03;16 | Second quartile reactive energy Eq_q2 (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14472 - 14473 | 414473 - 414474 | 03;16 | Second quartile reactive energy Eq_q2 (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14474 - 14475 | 414475 - 414476 | 03;16 | Second quartile reactive energy Eq_q2 (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14476 - 14477 | 414477 - 414478 | 03;16 | Third quartile reactive energy Eq_q3 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14478 - 14479 | 414479 - 414480 | 03;16 | Third quartile reactive energy Eq_q3 (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14480 - 14481 | 414481 - 414482 | 03;16 | Third quartile reactive energy Eq_q3 (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14482 - 14483 | 414483 - 414484 | 03;16 | Third quartile reactive energy Eq_q3 (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14484 - 14485 | 414485 - 414486 | 03;16 | Third quartile reactive energy Eq_q3 (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14486 - 14487 | 414487 - 414488 | 03;16 | Fourth quartile reactive energy Eq_q4 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14488 - 14489 | 414489 - 414490 | 03;16 | Fourth quartile reactive energy Eq_q4 (peak) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14490 - 14491 | 414491 - 414492 | 03;16 | Fourth quartile reactive energy Eq_q4 (valley) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14492 - 14493 | 414493 - 414494 | 03;16 | Fourth quartile reactive energy Eq_q4 (normal) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14494 - 14495 | 414495 - 414496 | 03;16 | Fourth quartile reactive energy Eq_q4 (total) | INT32u | ABCD |  | KVARh
TOU energy: current month (incremental) | 14496 - 14497 | 414497 - 414498 | 03;16 | Apparent energy import Es_imp (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14498 - 14499 | 414499 - 414500 | 03;16 | Apparent energy import Es_imp (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14500 - 14501 | 414501 - 414502 | 03;16 | Apparent energy import Es_imp (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14502 - 14503 | 414503 - 414504 | 03;16 | Apparent energy import Es_imp (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14504 - 14505 | 414505 - 414506 | 03;16 | Apparent energy import Es_imp (total) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14506 - 14507 | 414507 - 414508 | 03;16 | Apparent energy export Es_exp (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14508 - 14509 | 414509 - 414510 | 03;16 | Apparent energy export Es_exp (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14510 - 14511 | 414511 - 414512 | 03;16 | Apparent energy export Es_exp (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14512 - 14513 | 414513 - 414514 | 03;16 | Apparent energy export Es_exp (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14514 - 14515 | 414515 - 414516 | 03;16 | Apparent energy export Es_exp (total) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14516 - 14517 | 414517 - 414518 | 03;16 | Apparent energy total Es_total (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14518 - 14519 | 414519 - 414520 | 03;16 | Apparent energy total Es_total (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14520 - 14521 | 414521 - 414522 | 03;16 | Apparent energy total Es_total (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14522 - 14523 | 414523 - 414524 | 03;16 | Apparent energy total Es_total (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14524 - 14525 | 414525 - 414526 | 03;16 | Apparent energy total Es_total (total) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14526 - 14527 | 414527 - 414528 | 03;16 | Apparent energy net Es_net (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14528 - 14529 | 414529 - 414530 | 03;16 | Apparent energy net Es_net (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14530 - 14531 | 414531 - 414532 | 03;16 | Apparent energy net Es_net (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14532 - 14533 | 414533 - 414534 | 03;16 | Apparent energy net Es_net (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14534 - 14535 | 414535 - 414536 | 03;16 | Apparent energy net Es_net (total) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14536 - 14537 | 414537 - 414538 | 03;16 | First quartile apparent energy Es_q1 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14538 - 14539 | 414539 - 414540 | 03;16 | First quartile apparent energy Es_q1 (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14540 - 14541 | 414541 - 414542 | 03;16 | First quartile apparent energy Es_q1 (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14542 - 14543 | 414543 - 414544 | 03;16 | First quartile apparent energy Es_q1 (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14544 - 14545 | 414545 - 414546 | 03;16 | First quartile apparent energy Es_q1 (total) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14546 - 14547 | 414547 - 414548 | 03;16 | Second quartile apparent energy Es_q2 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14548 - 14549 | 414549 - 414550 | 03;16 | Second quartile apparent energy Es_q2 (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14550 - 14551 | 414551 - 414552 | 03;16 | Second quartile apparent energy Es_q2 (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14552 - 14553 | 414553 - 414554 | 03;16 | Second quartile apparent energy Es_q2 (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14554 - 14555 | 414555 - 414556 | 03;16 | Second quartile apparent energy Es_q2 (total) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14556 - 14557 | 414557 - 414558 | 03;16 | Third quartile apparent energy Es_q3 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14558 - 14559 | 414559 - 414560 | 03;16 | Third quartile apparent energy Es_q3 (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14560 - 14561 | 414561 - 414562 | 03;16 | Third quartile apparent energy Es_q3 (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14562 - 14563 | 414563 - 414564 | 03;16 | Third quartile apparent energy Es_q3 (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14564 - 14565 | 414565 - 414566 | 03;16 | Third quartile apparent energy Es_q3 (total) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14566 - 14567 | 414567 - 414568 | 03;16 | Fourth quartile apparent energy Es_q4 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14568 - 14569 | 414569 - 414570 | 03;16 | Fourth quartile apparent energy Es_q4 (peak) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14570 - 14571 | 414571 - 414572 | 03;16 | Fourth quartile apparent energy Es_q4 (valley) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14572 - 14573 | 414573 - 414574 | 03;16 | Fourth quartile apparent energy Es_q4 (normal) | INT32u | ABCD |  | KVAh
TOU energy: current month (incremental) | 14574 - 14575 | 414575 - 414576 | 03;16 | Fourth quartile apparent energy Es_q4 (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14576 - 14577 | 414577 - 414578 | 03;16 | Import Energy Ep_imp (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14578 - 14579 | 414579 - 414580 | 03;16 | Import Energy Ep_imp (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14580 - 14581 | 414581 - 414582 | 03;16 | Import Energy Ep_imp (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14582 - 14583 | 414583 - 414584 | 03;16 | Import Energy Ep_imp (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14584 - 14585 | 414585 - 414586 | 03;16 | Import Energy Ep_imp (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14586 - 14587 | 414587 - 414588 | 03;16 | Export energy Ep_exp (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14588 - 14589 | 414589 - 414590 | 03;16 | Export energy Ep_exp (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14590 - 14591 | 414591 - 414592 | 03;16 | Export energy Ep_exp (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14592 - 14593 | 414593 - 414594 | 03;16 | Export energy Ep_exp (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14594 - 14595 | 414595 - 414596 | 03;16 | Export energy Ep_exp (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14596 - 14597 | 414597 - 414598 | 03;16 | Total energy Ep_total (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14598 - 14599 | 414599 - 414600 | 03;16 | Total energy Ep_total (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14600 - 14601 | 414601 - 414602 | 03;16 | Total energy Ep_total (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14602 - 14603 | 414603 - 414604 | 03;16 | Total energy Ep_total (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14604 - 14605 | 414605 - 414606 | 03;16 | Total energy Ep_total (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14606 - 14607 | 414607 - 414608 | 03;16 | Net energy Ep_net (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14608 - 14609 | 414609 - 414610 | 03;16 | Net energy Ep_net (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14610 - 14611 | 414611 - 414612 | 03;16 | Net energy Ep_net (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14612 - 14613 | 414613 - 414614 | 03;16 | Net energy Ep_net (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14614 - 14615 | 414615 - 414616 | 03;16 | Net energy Ep_net (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14616 - 14617 | 414617 - 414618 | 03;16 | First quartile energy Ep_q1 (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14618 - 14619 | 414619 - 414620 | 03;16 | First quartile energy Ep_q1 (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14620 - 14621 | 414621 - 414622 | 03;16 | First quartile energy Ep_q1 (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14622 - 14623 | 414623 - 414624 | 03;16 | First quartile energy Ep_q1 (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14624 - 14625 | 414625 - 414626 | 03;16 | First quartile energy Ep_q1 (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14626 - 14627 | 414627 - 414628 | 03;16 | Second quartile energy Ep_q2 (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14628 - 14629 | 414629 - 414630 | 03;16 | Second quartile energy Ep_q2 (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14630 - 14631 | 414631 - 414632 | 03;16 | Second quartile energy Ep_q2 (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14632 - 14633 | 414633 - 414634 | 03;16 | Second quartile energy Ep_q2 (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14634 - 14635 | 414635 - 414636 | 03;16 | Second quartile energy Ep_q2 (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14636 - 14637 | 414637 - 414638 | 03;16 | Third quartile energy Ep_q3 (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14638 - 14639 | 414639 - 414640 | 03;16 | Third quartile energy Ep_q3 (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14640 - 14641 | 414641 - 414642 | 03;16 | Third quartile energy Ep_q3 (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14642 - 14643 | 414643 - 414644 | 03;16 | Third quartile energy Ep_q3 (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14644 - 14645 | 414645 - 414646 | 03;16 | Third quartile energy Ep_q3 (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14646 - 14647 | 414647 - 414648 | 03;16 | Fourth quartile energy Ep_q4 (sharp) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14648 - 14649 | 414649 - 414650 | 03;16 | Fourth quartile energy Ep_q4 (peak) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14650 - 14651 | 414651 - 414652 | 03;16 | Fourth quartile energy Ep_q4 (valley) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14652 - 14653 | 414653 - 414654 | 03;16 | Fourth quartile energy Ep_q4 (normal) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14654 - 14655 | 414655 - 414656 | 03;16 | Fourth quartile energy Ep_q4 (total) | INT32u | ABCD |  | kWh
TOU energy: prior month (incremental) | 14656 - 14657 | 414657 - 414658 | 03;16 | Inductive reactive energy (sharp) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14658 - 14659 | 414659 - 414660 | 03;16 | Inductive reactive energy (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14660 - 14661 | 414661 - 414662 | 03;16 | Inductive reactive energy (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14662 - 14663 | 414663 - 414664 | 03;16 | Inductive reactive energy (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14664 - 14665 | 414665 - 414666 | 03;16 | Inductive reactive energy (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14666 - 14667 | 414667 - 414668 | 03;16 | Capacitive reactive energy (sharp) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14668 - 14669 | 414669 - 414670 | 03;16 | Capacitive reactive energy (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14670 - 14671 | 414671 - 414672 | 03;16 | Capacitive reactive energy (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14672 - 14673 | 414673 - 414674 | 03;16 | Capacitive reactive energy (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14674 - 14675 | 414675 - 414676 | 03;16 | Capacitive reactive energy (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14676 - 14677 | 414677 - 414678 | 03;16 | Reactive energy total Eq_total (sharp) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14678 - 14679 | 414679 - 414680 | 03;16 | Reactive energy total Eq_total (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14680 - 14681 | 414681 - 414682 | 03;16 | Reactive energy total Eq_total (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14682 - 14683 | 414683 - 414684 | 03;16 | Reactive energy total Eq_total (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14684 - 14685 | 414685 - 414686 | 03;16 | Reactive energy total Eq_total (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14686 - 14687 | 414687 - 414688 | 03;16 | Reactive energy net Eq_net (sharp) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14688 - 14689 | 414689 - 414690 | 03;16 | Reactive energy net Eq_net (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14690 - 14691 | 414691 - 414692 | 03;16 | Reactive energy net Eq_net (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14692 - 14693 | 414693 - 414694 | 03;16 | Reactive energy net Eq_net (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14694 - 14695 | 414695 - 414696 | 03;16 | Reactive energy net Eq_net (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14696 - 14697 | 414697 - 414698 | 03;16 | First quartile reactive energy Eq_q1 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14698 - 14699 | 414699 - 414700 | 03;16 | First quartile reactive energy Eq_q1 (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14700 - 14701 | 414701 - 414702 | 03;16 | First quartile reactive energy Eq_q1 (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14702 - 14703 | 414703 - 414704 | 03;16 | First quartile reactive energy Eq_q1 (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14704 - 14705 | 414705 - 414706 | 03;16 | First quartile reactive energy Eq_q1 (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14706 - 14707 | 414707 - 414708 | 03;16 | Second quartile reactive energy Eq_q2 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14708 - 14709 | 414709 - 414710 | 03;16 | Second quartile reactive energy Eq_q2 (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14710 - 14711 | 414711 - 414712 | 03;16 | Second quartile reactive energy Eq_q2 (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14712 - 14713 | 414713 - 414714 | 03;16 | Second quartile reactive energy Eq_q2 (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14714 - 14715 | 414715 - 414716 | 03;16 | Second quartile reactive energy Eq_q2 (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14716 - 14717 | 414717 - 414718 | 03;16 | Third quartile reactive energy Eq_q3 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14718 - 14719 | 414719 - 414720 | 03;16 | Third quartile reactive energy Eq_q3 (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14720 - 14721 | 414721 - 414722 | 03;16 | Third quartile reactive energy Eq_q3 (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14722 - 14723 | 414723 - 414724 | 03;16 | Third quartile reactive energy Eq_q3 (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14724 - 14725 | 414725 - 414726 | 03;16 | Third quartile reactive energy Eq_q3 (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14726 - 14727 | 414727 - 414728 | 03;16 | Fourth quartile reactive energy Eq_q4 (sharp) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14728 - 14729 | 414729 - 414730 | 03;16 | Fourth quartile reactive energy Eq_q4 (peak) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14730 - 14731 | 414731 - 414732 | 03;16 | Fourth quartile reactive energy Eq_q4 (valley) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14732 - 14733 | 414733 - 414734 | 03;16 | Fourth quartile reactive energy Eq_q4 (normal) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14734 - 14735 | 414735 - 414736 | 03;16 | Fourth quartile reactive energy Eq_q4 (total) | INT32u | ABCD |  | KVARh
TOU energy: prior month (incremental) | 14736 - 14737 | 414737 - 414738 | 03;16 | Apparent energy import Es_imp (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14738 - 14739 | 414739 - 414740 | 03;16 | Apparent energy import Es_imp (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14740 - 14741 | 414741 - 414742 | 03;16 | Apparent energy import Es_imp (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14742 - 14743 | 414743 - 414744 | 03;16 | Apparent energy import Es_imp (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14744 - 14745 | 414745 - 414746 | 03;16 | Apparent energy import Es_imp (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14746 - 14747 | 414747 - 414748 | 03;16 | Apparent energy export Es_exp (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14748 - 14749 | 414749 - 414750 | 03;16 | Apparent energy export Es_exp (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14750 - 14751 | 414751 - 414752 | 03;16 | Apparent energy export Es_exp (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14752 - 14753 | 414753 - 414754 | 03;16 | Apparent energy export Es_exp (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14754 - 14755 | 414755 - 414756 | 03;16 | Apparent energy export Es_exp (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14756 - 14757 | 414757 - 414758 | 03;16 | Apparent energy total Es_total (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14758 - 14759 | 414759 - 414760 | 03;16 | Apparent energy total Es_total (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14760 - 14761 | 414761 - 414762 | 03;16 | Apparent energy total Es_total (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14762 - 14763 | 414763 - 414764 | 03;16 | Apparent energy total Es_total (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14764 - 14765 | 414765 - 414766 | 03;16 | Apparent energy total Es_total (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14766 - 14767 | 414767 - 414768 | 03;16 | Apparent energy net Es_net (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14768 - 14769 | 414769 - 414770 | 03;16 | Apparent energy net Es_net (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14770 - 14771 | 414771 - 414772 | 03;16 | Apparent energy net Es_net (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14772 - 14773 | 414773 - 414774 | 03;16 | Apparent energy net Es_net (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14774 - 14775 | 414775 - 414776 | 03;16 | Apparent energy net Es_net (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14776 - 14777 | 414777 - 414778 | 03;16 | First quartile apparent energy Es_q1 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14778 - 14779 | 414779 - 414780 | 03;16 | First quartile apparent energy Es_q1 (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14780 - 14781 | 414781 - 414782 | 03;16 | First quartile apparent energy Es_q1 (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14782 - 14783 | 414783 - 414784 | 03;16 | First quartile apparent energy Es_q1 (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14784 - 14785 | 414785 - 414786 | 03;16 | First quartile apparent energy Es_q1 (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14786 - 14787 | 414787 - 414788 | 03;16 | Second quartile apparent energy Es_q2 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14788 - 14789 | 414789 - 414790 | 03;16 | Second quartile apparent energy Es_q2 (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14790 - 14791 | 414791 - 414792 | 03;16 | Second quartile apparent energy Es_q2 (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14792 - 14793 | 414793 - 414794 | 03;16 | Second quartile apparent energy Es_q2 (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14794 - 14795 | 414795 - 414796 | 03;16 | Second quartile apparent energy Es_q2 (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14796 - 14797 | 414797 - 414798 | 03;16 | Third quartile apparent energy Es_q3 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14798 - 14799 | 414799 - 414800 | 03;16 | Third quartile apparent energy Es_q3 (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14800 - 14801 | 414801 - 414802 | 03;16 | Third quartile apparent energy Es_q3 (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14802 - 14803 | 414803 - 414804 | 03;16 | Third quartile apparent energy Es_q3 (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14804 - 14805 | 414805 - 414806 | 03;16 | Third quartile apparent energy Es_q3 (total) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14806 - 14807 | 414807 - 414808 | 03;16 | Fourth quartile apparent energy Es_q4 (sharp) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14808 - 14809 | 414809 - 414810 | 03;16 | Fourth quartile apparent energy Es_q4 (peak) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14810 - 14811 | 414811 - 414812 | 03;16 | Fourth quartile apparent energy Es_q4 (valley) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14812 - 14813 | 414813 - 414814 | 03;16 | Fourth quartile apparent energy Es_q4 (normal) | INT32u | ABCD |  | KVAh
TOU energy: prior month (incremental) | 14814 - 14815 | 414815 - 414816 | 03;16 | Fourth quartile apparent energy Es_q4 (total) | INT32u | ABCD |  | KVAh
TOU energy: Daily energy | 15360 - 15361 | 415361 - 415362 | 03 | Ep_imp (Yesterday) | INT32u | ABCD |  | kWh
TOU energy: Daily energy | 15362 - 15363 | 415363 - 415364 | 03 | Ep_exp (Yesterday) | INT32u | ABCD |  | kWh
TOU energy: Daily energy | 15364 - 15365 | 415365 - 415366 | 03 | Ep_total (Yesterday) | INT32u | ABCD |  | kWh
TOU energy: Daily energy | 15366 - 15367 | 415367 - 415368 | 03 | Ep_net (Yesterday) | INT32u | ABCD |  | kWh
TOU energy: Daily energy | 15368 - 15369 | 415369 - 415370 | 03 | Ep_q1 (Yesterday) | INT32u | ABCD |  | kWh
TOU energy: Daily energy | 15370 - 15371 | 415371 - 415372 | 03 | Ep_q2 (Yesterday) | INT32u | ABCD |  | kWh
TOU energy: Daily energy | 15372 - 15373 | 415373 - 415374 | 03 | Ep_q3 (Yesterday) | INT32u | ABCD |  | kWh
TOU energy: Daily energy | 15374 - 15375 | 415375 - 415376 | 03 | Ep_q4 (Yesterday) | INT32u | ABCD |  | kWh
TOU energy: Daily energy | 15376 - 15377 | 415377 - 415378 | 03 | Eq_imp (Yesterday) | INT32u | ABCD |  | KVARh
TOU energy: Daily energy | 15378 - 15379 | 415379 - 415380 | 03 | Eq_exp (Yesterday) | INT32u | ABCD |  | KVARh
TOU energy: Daily energy | 15380 - 15381 | 415381 - 415382 | 03 | Eq_total (Yesterday) | INT32u | ABCD |  | KVARh
TOU energy: Daily energy | 15382 - 15383 | 415383 - 415384 | 03 | Eq_net (Yesterday) | INT32u | ABCD |  | KVARh
TOU energy: Daily energy | 15384 - 15385 | 415385 - 415386 | 03 | Eq_q1 (Yesterday) | INT32u | ABCD |  | KVARh
TOU energy: Daily energy | 15386 - 15387 | 415387 - 415388 | 03 | Eq_q2 (Yesterday) | INT32u | ABCD |  | KVARh
TOU energy: Daily energy | 15388 - 15389 | 415389 - 415390 | 03 | Eq_q3 (Yesterday) | INT32u | ABCD |  | KVARh
TOU energy: Daily energy | 15390 - 15391 | 415391 - 415392 | 03 | Eq_q4 (Yesterday) | INT32u | ABCD |  | KVARh
TOU energy: Daily energy | 15392 - 15393 | 415393 - 415394 | 03 | Es_imp (Yesterday) | INT32u | ABCD |  | KVAh
TOU energy: Daily energy | 15394 - 15395 | 415395 - 415396 | 03 | Es_exp (Yesterday) | INT32u | ABCD |  | KVAh
TOU energy: Daily energy | 15396 - 15397 | 415397 - 415398 | 03 | Es_total (Yesterday) | INT32u | ABCD |  | KVAh
TOU energy: Daily energy | 15398 - 15399 | 415399 - 415400 | 03 | Es_net (Yesterday) | INT32u | ABCD |  | KVAh
TOU energy: Daily energy | 15400 - 15401 | 415401 - 415402 | 03 | Es_q1 (Yesterday) | INT32u | ABCD |  | KVAh
TOU energy: Daily energy | 15402 - 15403 | 415403 - 415404 | 03 | Es_q2 (Yesterday) | INT32u | ABCD |  | KVAh
TOU energy: Daily energy | 15404 - 15405 | 415405 - 415406 | 03 | Es_q3 (Yesterday) | INT32u | ABCD |  | KVAh
TOU energy: Daily energy | 15406 - 15407 | 415407 - 415408 | 03 | Es_q4 (Yesterday) | INT32u | ABCD |  | KVAh
TOU energy: Daily energy | 15408 - 15455 | 415409 - 415456 | 03 | Daily Energy (Day before yesterday) | INT32u | ABCD
TOU energy: Daily energy | 15456 - 15503 | 415457 - 415504 | 03 | Daily Energy (Three days ago) | INT32u | ABCD
TOU energy: Daily energy | 15504 - 15551 | 415505 - 415552 | 03 | Daily Energy (Four days ago) | INT32u | ABCD
TOU energy: Daily energy | 15552 - 15599 | 415553 - 415600 | 03 | Daily Energy (Five days ago) | INT32u | ABCD
TOU energy: Daily energy | 15600 - 15647 | 415601 - 415648 | 03 | Daily Energy (Six days ago) | INT32u | ABCD
TOU energy: Daily energy | 15648 - 15695 | 415649 - 415696 | 03 | Daily Energy (Seven days ago) | INT32u | ABCD
TOU maximum demand parameters | 15104 | 415105 | 03 | Time stamp - Year of max import power demand (Sharp) | INT16u | AB
TOU maximum demand parameters | 15104 | 415105 | 03 | Time Stamp - Month of max import power demand (Sharp) | INT16u | AB
TOU maximum demand parameters | 15105 | 415106 | 03 | Time Stamp - Day of max import power demand (Sharp) | INT16u | AB
TOU maximum demand parameters | 15105 | 415106 | 03 | Time Stamp - Hour of max import power demand (Sharp) | INT16u | AB
TOU maximum demand parameters | 15106 | 415107 | 03 | Time Stamp - Minute of max import power demand (Sharp) | INT16u | AB
TOU maximum demand parameters | 15106 | 415107 | 03 | Time Stamp - Second of max import power demand (Sharp) | INT16u | AB
TOU maximum demand parameters | 15107 | 415108 | 03 | Max import power demand (Sharp) | INT16s | AB
TOU maximum demand parameters | 15108 - 15111 | 415109 - 415112 | 03 | Time stamp and max import power demand (peak) | INT16s | AB |  | W
TOU maximum demand parameters | 15112 - 15115 | 415113 - 415116 | 03 | Time stamp and max import power demand (valley) | INT16s | AB |  | W
TOU maximum demand parameters | 15116 - 15119 | 415117 - 415120 | 03 | Time stamp and max import power demand (normal) | INT16s | AB |  | W
TOU maximum demand parameters | 15120 - 15123 | 415121 - 415124 | 03 | Time stamp and max import power demand (total) | INT16s | AB |  | W
TOU maximum demand parameters | 15124 - 15127 | 415125 - 415128 | 03 | Time stamp and max export power demand (sharp) | INT16s | AB |  | W
TOU maximum demand parameters | 15128 - 15131 | 415129 - 415132 | 03 | Time stamp and max export power demand (peak) | INT16s | AB |  | W
TOU maximum demand parameters | 15132 - 15135 | 415133 - 415136 | 03 | Time stamp and max export power demand (valley) | INT16s | AB |  | W
TOU maximum demand parameters | 15136 - 15139 | 415137 - 415140 | 03 | Time stamp and max export power demand (normal) | INT16s | AB |  | W
TOU maximum demand parameters | 15140 - 15143 | 415141 - 415144 | 03 | Time stamp and max export power demand (total) | INT16s | AB |  | W
TOU maximum demand parameters | 15144 - 15147 | 415145 - 415148 | 03 | Time stamp and max inductive reactive demand (sharp) | INT16s | AB |  | var
TOU maximum demand parameters | 15148 - 15151 | 415149 - 415152 | 03 | Time stamp and max inductive reactive demand (peak) | INT16s | AB |  | var
TOU maximum demand parameters | 15152 - 15155 | 415153 - 415156 | 03 | Time stamp and max inductive reactive demand (valley) | INT16s | AB |  | var
TOU maximum demand parameters | 15156 - 15159 | 415157 - 415160 | 03 | Time stamp and max inductive reactive demand (normal) | INT16s | AB |  | var
TOU maximum demand parameters | 15160 - 15163 | 415161 - 415164 | 03 | Time stamp and max inductive reactive demand (total) | INT16s | AB |  | var
TOU maximum demand parameters | 15164 - 15167 | 415165 - 415168 | 03 | Time stamp and max capacitive reactive demand (sharp) | INT16s | AB |  | var
TOU maximum demand parameters | 15168 - 15171 | 415169 - 415172 | 03 | Time stamp and max capacitive reactive demand (peak) | INT16s | AB |  | var
TOU maximum demand parameters | 15172 - 15175 | 415173 - 415176 | 03 | Time stamp and max capacitive reactive demand (valley) | INT16s | AB |  | var
TOU maximum demand parameters | 15176 - 15179 | 415177 - 415180 | 03 | Time stamp and max capacitive reactive demand (normal) | INT16s | AB |  | var
TOU maximum demand parameters | 15180 - 15183 | 415181 - 415184 | 03 | Time stamp and max capacitive reactive demand (total) | INT16s | AB |  | var
TOU maximum demand parameters | 15184 - 15187 | 415185 - 415188 | 03 | Time stamp and max import apparent demand (sharp) | INT16s | AB |  | VA
TOU maximum demand parameters | 15188 - 15191 | 415189 - 415192 | 03 | Time stamp and max import apparent demand (peak) | INT16s | AB |  | VA
TOU maximum demand parameters | 15192 - 15195 | 415193 - 415196 | 03 | Time stamp and max import apparent demand (valley) | INT16s | AB |  | VA
TOU maximum demand parameters | 15196 - 15199 | 415197 - 415200 | 03 | Time stamp and max import apparent demand (normal) | INT16s | AB |  | VA
TOU maximum demand parameters | 15200 - 15203 | 415201 - 415204 | 03 | Time stamp and max import apparent demand (total) | INT16s | AB |  | VA
TOU maximum demand parameters | 15204 - 15207 | 415205 - 415208 | 03 | Time stamp and max export apparent demand (sharp) | INT16s | AB |  | VA
TOU maximum demand parameters | 15208 - 15211 | 415209 - 415212 | 03 | Time stamp and max export apparent demand (peak) | INT16s | AB |  | VA
TOU maximum demand parameters | 15212 - 15215 | 415213 - 415216 | 03 | Time stamp and max export apparent demand (valley) | INT16s | AB |  | VA
TOU maximum demand parameters | 15216 - 15219 | 415217 - 415220 | 03 | Time stamp and max export apparent demand (normal) | INT16s | AB |  | VA
TOU maximum demand parameters | 15220 - 15223 | 415221 - 415224 | 03 | Time stamp and max export apparent demand (total) | INT16s | AB |  | VA
TOU maximum demand parameters | 15224 - 15227 | 415225 - 415228 | 03 | Time stamp and max I1 demand (sharp) | INT16s | AB |  | A
TOU maximum demand parameters | 15228 - 15231 | 415229 - 415232 | 03 | Time stamp and max I1 demand (peak) | INT16s | AB |  | A
TOU maximum demand parameters | 15232 - 15235 | 415233 - 415236 | 03 | Time stamp and max I1 demand (valley) | INT16s | AB |  | A
TOU maximum demand parameters | 15236 - 15239 | 415237 - 415240 | 03 | Time stamp and max I1 demand (normal) | INT16s | AB |  | A
TOU maximum demand parameters | 15240 - 15243 | 415241 - 415244 | 03 | Time stamp and max I1 demand (total) | INT16s | AB |  | A
TOU maximum demand parameters | 15244 - 15247 | 415245 - 415248 | 03 | Time stamp and max I2 demand (sharp) | INT16s | AB |  | A
TOU maximum demand parameters | 15248 - 15251 | 415249 - 415252 | 03 | Time stamp and max I2 demand (peak) | INT16s | AB |  | A
TOU maximum demand parameters | 15252 - 15255 | 415253 - 415256 | 03 | Time stamp and max I2 demand (valley) | INT16s | AB |  | A
TOU maximum demand parameters | 15256 - 15259 | 415257 - 415260 | 03 | Time stamp and max I2 demand (normal) | INT16s | AB |  | A
TOU maximum demand parameters | 15260 - 15263 | 415261 - 415264 | 03 | Time stamp and max I2 demand (total) | INT16s | AB |  | A
TOU maximum demand parameters | 15264 - 15267 | 415265 - 415268 | 03 | Time stamp and max I3 demand (sharp) | INT16s | AB |  | A
TOU maximum demand parameters | 15268 - 15271 | 415269 - 415272 | 03 | Time stamp and max I3 demand (peak) | INT16s | AB |  | A
TOU maximum demand parameters | 15272 - 15275 | 415273 - 415276 | 03 | Time stamp and max I3 demand (valley) | INT16s | AB |  | A
TOU maximum demand parameters | 15276 - 15279 | 415277 - 415280 | 03 | Time stamp and max I3 demand (normal) | INT16s | AB |  | A
TOU maximum demand parameters | 15280 - 15283 | 415281 - 415284 | 03 | Time stamp and max I3 demand (total) | INT16s | AB |  | A
TOU maximum demand parameters | 15284 - 15287 | 415285 - 415288 | 03 | Time stamp and max IN demand (sharp) | INT16s | AB |  | A
TOU maximum demand parameters | 15288 - 15291 | 415289 - 415292 | 03 | Time stamp and max IN demand (peak) | INT16s | AB |  | A
TOU maximum demand parameters | 15292 - 15295 | 415293 - 415296 | 03 | Time stamp and max IN demand (valley) | INT16s | AB |  | A
TOU maximum demand parameters | 15296 - 15299 | 415297 - 415300 | 03 | Time stamp and max IN demand (normal) | INT16s | AB |  | A
TOU maximum demand parameters | 15300 - 15303 | 415301 - 415304 | 03 | Time stamp and max IN demand (total) | INT16s | AB |  | A
TOU parameters | 4384 | 44385 | 03;16 | The Number of Season | INT16u | AB
TOU parameters | 4385 | 44386 | 03;16 | The Number of TOU Schedule | INT16u | AB
TOU parameters | 4386 | 44387 | 03;16 | The Number of TOU Segment | INT16u | AB
TOU parameters | 4387 | 44388 | 03;16 | The Number of Tariff | INT16u | AB
TOU parameters | 4388 | 44389 | 03;16 | Weekend setting. (bit0---Sun: bit1~bit6: Mon ~ Sat; 0: Disable; 1: Enable) | INT16u | AB
TOU parameters | 4389 | 44390 | 03;16 | Weekend Schedule | INT16u | AB
TOU parameters | 4390 | 44391 | 03;16 | Holiday Setting | INT16u | AB
TOU parameters | 4391 | 44392 | 03;16 | Enable TOU. 1: Enable; Others: Disable | INT16u | AB
TOU parameters | 4392 | 44393 | 03;16 | Restore to defaults. 1: Enable; Others: Disable | INT16u | AB
TOU parameters | 4393 | 44394 | 03;16 | Monthly billing mode. 0: End of Month; 1: Assign | INT16u | AB
TOU parameters | 4394 | 44395 | 03;16 | Billing Time - Day | INT16u | AB
TOU parameters | 4395 | 44396 | 03;16 | Billing Time - Hour | INT16u | AB
TOU parameters | 4396 | 44397 | 03;16 | Billing Time - Minute | INT16u | AB
TOU parameters | 4397 | 44398 | 03;16 | Billing Time - Second | INT16u | AB
TOU parameters | 4398 | 44399 | 03;16 | Fault status word. 0: No Error; 1: Tariff Error; 2: Season Error; 4: Segment Error; 8: The Number of Season Error; 16: Season Setting Error; 32: The Number of Holiday Error; 64: Holiday Setting Error; 256: Tariff in TOU Schedule Error; 512: Time In TOU Schedule Error; 1024: Time Segment In TOU Schedule Error; 2048: Weekend Schedule Error; 4096: Weekend Error | INT16u | AB
TOU parameters | 4399 | 44400 | 03;16 | Enable Holiday Years Setting | INT16u | AB
TOU parameters | 4400 | 44401 | 03;16 | Start Year of Holiday Years | INT16u | AB
TOU parameters | 4401 | 44402 | 03;16 | End Year of Holiday Years | INT16u | AB
TOU parameters | 4416 - 4418 | 44417 - 44419 | 03;16 | TOU Seasons 1 Start Time (Month, Day, and Hour) | INT16u | AB
TOU parameters | 4419 - 4421 | 44420 - 44422 | 03;16 | TOU Seasons 2 Start Time (Month, Day, and Hour) | INT16u | AB
TOU parameters | 4422 - 4424 | 44423 - 44425 | 03;16 | TOU Seasons 3 Start Time (Month, Day, and Hour) | INT16u | AB
TOU parameters | 4425 - 4427 | 44426 - 44428 | 03;16 | TOU Seasons 4 Start Time (Month, Day, and Hour) | INT16u | AB
TOU parameters | 4428 - 4430 | 44429 - 44431 | 03;16 | TOU Seasons 5 Start Time (Month, Day, and Hour) | INT16u | AB
TOU parameters | 4431 - 4433 | 44432 - 44434 | 03;16 | TOU Seasons 6 Start Time (Month, Day, and Hour) | INT16u | AB
TOU parameters | 4434 - 4436 | 44435 - 44437 | 03;16 | TOU Seasons 7 Start Time (Month, Day, and Hour) | INT16u | AB
TOU parameters | 4437 - 4439 | 44438 - 44440 | 03;16 | TOU Seasons 8 Start Time (Month, Day, and Hour) | INT16u | AB
TOU parameters | 4440 - 4442 | 44441 - 44443 | 03;16 | TOU Seasons 9 Start Time (Month, Day, and Hour) | INT16u | AB
TOU parameters | 4443 - 4445 | 44444 - 44446 | 03;16 | TOU Seasons 10 Start Time (Month, Day, and Hour) | INT16u | AB
TOU parameters | 4446 - 4448 | 44447 - 44449 | 03;16 | TOU Seasons 11 Start Time (Month, Day, and Hour) | INT16u | AB
TOU parameters | 4449 - 4451 | 44450 - 44452 | 03;16 | TOU Seasons 12 Start Time (Month, Day, and Hour) | INT16u | AB
TOU parameters | 4452 - 4454 | 44453 - 44455 | 03;16 | First TOU schedule 1 Segment start time (hour, minute and tariff) | INT16u | AB
TOU parameters | 4455 - 4457 | 44456 - 44458 | 03;16 | First TOU schedule 2 Segment start time (hour, minute and tariff) | INT16u | AB
TOU parameters | 4458 - 4460 | 44459 - 44461 | 03;16 | First TOU schedule 3 Segment start time (hour, minute and tariff) | INT16u | AB
TOU parameters | 4461 - 4463 | 44462 - 44464 | 03;16 | First TOU schedule 4 Segment start time (hour, minute and tariff) | INT16u | AB
TOU parameters | 4464 - 4466 | 44465 - 44467 | 03;16 | First TOU Schedule 5 Segment start time (hour, minute and tariff) | INT16u | AB
TOU parameters | 4467 - 4469 | 44468 - 44470 | 03;16 | First TOU schedule 6 Segment start time (hour, minute and tariff) | INT16u | AB
TOU parameters | 4470 - 4472 | 44471 - 44473 | 03;16 | First TOU schedule 7 Segment start time (hour, minute and tariff) | INT16u | AB
TOU parameters | 4473 - 4475 | 44474 - 44476 | 03;16 | First TOU schedule 8 Segment start time (hour, minute and tariff) | INT16u | AB
TOU parameters | 4476 - 4478 | 44477 - 44479 | 03;16 | First TOU schedule 9 Segment start time (hour, minute and tariff) | INT16u | AB
TOU parameters | 4479 - 4481 | 44480 - 44482 | 03;16 | First TOU schedule 10 Segment start time (hour, minute and tariff) | INT16u | AB
TOU parameters | 4482 - 4484 | 44483 - 44485 | 03;16 | First TOU schedule 11 Segment start time (hour, minute and tariff) | INT16u | AB
TOU parameters | 4485 - 4487 | 44486 - 44488 | 03;16 | First TOU schedule 12 Segment start time (hour, minute and tariff) | INT16u | AB
TOU parameters | 4488 - 4490 | 44489 - 44491 | 03;16 | First TOU schedule 13 Segment start time (hour, minute and tariff) | INT16u | AB
TOU parameters | 4491 - 4493 | 44492 - 44494 | 03;16 | First TOU schedule 14 Segment start time (hour, minute and tariff) | INT16u | AB
TOU parameters | 4494 - 4535 | 44495 - 44536 | 03;16 | Second TOU schedule 1~14 Segment start time (hour, minute, and tariff) | INT16u | AB
TOU parameters | 4536 - 4577 | 44537 - 44578 | 03;16 | Third TOU schedule 1~14 Segment start time (hour, minute, and tariff) | INT16u | AB
TOU parameters | 4578 - 4619 | 44579 - 44620 | 03;16 | Fourth TOU schedule 1~14 Segment start time (hour, minute, and tariff) | INT16u | AB
TOU parameters | 4620 - 4661 | 44621 - 44662 | 03;16 | Fifth TOU schedule 1~14 Segment start time (hour, minute, and tariff) | INT16u | AB
TOU parameters | 4662 - 4703 | 44663 - 44704 | 03;16 | Sixth TOU schedule 1~14 Segment start time (hour, minute, and tariff) | INT16u | AB
TOU parameters | 4704 - 4745 | 44705 - 44746 | 03;16 | Seventh TOU schedule 1~14 Segment start time (hour, minute, and tariff) | INT16u | AB
TOU parameters | 4746 - 4787 | 44747 - 44788 | 03;16 | Eighth TOU schedule 1~14 Segment start time (hour, minute, and tariff) | INT16u | AB
TOU parameters | 4788 - 4829 | 44789 - 44830 | 03;16 | Ninth TOU schedule 1~14 Segment start time (hour, minute, and tariff) | INT16u | AB
TOU parameters | 4830 - 4871 | 44831 - 44872 | 03;16 | Tenth TOU schedule 1~14 Segment start time (hour, minute, and tariff) | INT16u | AB
TOU parameters | 4872 - 4913 | 44873 - 44914 | 03;16 | Eleventh TOU schedule 1~14 Segment start time (hour, minute, and tariff) | INT16u | AB
TOU parameters | 4914 - 4955 | 44915 - 44956 | 03;16 | Twelfth TOU schedule 1~14 Segment start time (hour, minute, and tariff) | INT16u | AB
TOU parameters | 4956 - 4997 | 44957 - 44998 | 03;16 | Thirteenth TOU schedule 1~14 Segment start time (hour, minute, and tariff) | INT16u | AB
TOU parameters | 4998 - 5039 | 44999 - 45040 | 03;16 | Fourteenth TOU schedule 1~14 Segment start time (hour, minute, and tariff) | INT16u | AB
TOU parameters | 5040 - 5042 | 45041 - 45043 | 03;16 | Holidays 1 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5043 - 5045 | 45044 - 45046 | 03;16 | Holidays 2 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5046 - 5048 | 45047 - 45049 | 03;16 | Holidays 3 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5049 - 5051 | 45050 - 45052 | 03;16 | Holidays 4 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5052 - 5054 | 45053 - 45055 | 03;16 | Holidays 5 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5055 - 5057 | 45056 - 45058 | 03;16 | Holidays 6 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5058 - 5060 | 45059 - 45061 | 03;16 | Holidays 7 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5061 - 5063 | 45062 - 45064 | 03;16 | Holidays 8 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5064 - 5066 | 45065 - 45067 | 03;16 | Holidays 9 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5067 - 5069 | 45068 - 45070 | 03;16 | Holidays 10 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5070 - 5072 | 45071 - 45073 | 03;16 | Holidays 11 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5073 - 5075 | 45074 - 45076 | 03;16 | Holidays 12 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5076 - 5078 | 45077 - 45079 | 03;16 | Holidays 13 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5079 - 5081 | 45080 - 45082 | 03;16 | Holidays 14 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5082 - 5084 | 45083 - 45085 | 03;16 | Holidays 15 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5085 - 5087 | 45086 - 45088 | 03;16 | Holidays 16 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5088 - 5090 | 45089 - 45091 | 03;16 | Holidays 17 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5091 - 5093 | 45092 - 45094 | 03;16 | Holidays 18 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5094 - 5096 | 45095 - 45097 | 03;16 | Holidays 19 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5097 - 5099 | 45098 - 45100 | 03;16 | Holidays 20 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5100 - 5102 | 45101 - 45103 | 03;16 | Holidays 21 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5103 - 5105 | 45104 - 45106 | 03;16 | Holidays 22 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5106 - 5108 | 45107 - 45109 | 03;16 | Holidays 23 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5109 - 5111 | 45110 - 45112 | 03;16 | Holidays 24 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5112 - 5114 | 45113 - 45115 | 03;16 | Holidays 25 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5115 - 5117 | 45116 - 45118 | 03;16 | Holidays 26 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5118 - 5120 | 45119 - 45121 | 03;16 | Holidays 27 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5121 - 5123 | 45122 - 45124 | 03;16 | Holidays 28 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5124 - 5126 | 45125 - 45127 | 03;16 | Holidays 29 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5127 - 5129 | 45128 - 45130 | 03;16 | Holidays 30 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU parameters | 5130 - 5375 | 45131 - 45376 | 03;16 | Reserve | INT16u | AB
TOU: ten years holiday (first year) | 5376 - 5378 | 45377 - 45379 | 03;16 | Holidays 1 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5379 - 5381 | 45380 - 45382 | 03;16 | Holidays 2 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5382 - 5384 | 45383 - 45385 | 03;16 | Holidays 3 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5385 - 5387 | 45386 - 45388 | 03;16 | Holidays 4 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5388 - 5390 | 45389 - 45391 | 03;16 | Holidays 5 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5391 - 5393 | 45392 - 45394 | 03;16 | Holidays 6 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5394 - 5396 | 45395 - 45397 | 03;16 | Holidays 7 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5397 - 5399 | 45398 - 45400 | 03;16 | Holidays 8 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5400 - 5402 | 45401 - 45403 | 03;16 | Holidays 9 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5403 - 5405 | 45404 - 45406 | 03;16 | Holidays 10 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5406 - 5408 | 45407 - 45409 | 03;16 | Holidays 11 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5409 - 5411 | 45410 - 45412 | 03;16 | Holidays 12 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5412 - 5414 | 45413 - 45415 | 03;16 | Holidays 13 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5415 - 5417 | 45416 - 45418 | 03;16 | Holidays 14 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5418 - 5420 | 45419 - 45421 | 03;16 | Holidays 15 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5421 - 5423 | 45422 - 45424 | 03;16 | Holidays 16 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5424 - 5426 | 45425 - 45427 | 03;16 | Holidays 17 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5427 - 5429 | 45428 - 45430 | 03;16 | Holidays 18 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5430 - 5432 | 45431 - 45433 | 03;16 | Holidays 19 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5433 - 5435 | 45434 - 45436 | 03;16 | Holidays 20 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5436 - 5438 | 45437 - 45439 | 03;16 | Holidays 21 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5439 - 5441 | 45440 - 45442 | 03;16 | Holidays 22 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5442 - 5444 | 45443 - 45445 | 03;16 | Holidays 23 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5445 - 5447 | 45446 - 45448 | 03;16 | Holidays 24 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5448 - 5450 | 45449 - 45451 | 03;16 | Holidays 25 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5451 - 5453 | 45452 - 45454 | 03;16 | Holidays 26 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5454 - 5456 | 45455 - 45457 | 03;16 | Holidays 27 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5457 - 5459 | 45458 - 45460 | 03;16 | Holidays 28 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5460 - 5462 | 45461 - 45463 | 03;16 | Holidays 29 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5463 - 5465 | 45464 - 45466 | 03;16 | Holidays 30 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (first year) | 5466 | 45467 | 03;16 | The first year | INT16u | AB
TOU: ten years holiday (first year) | 5467 | 45468 | 03;16 | The amount number of holidays in first year | INT16u | AB
TOU: ten years holiday (first year) | 5468 - 5470 | 45469 - 45471 | 03;16 | Holidays 1 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5471 - 5473 | 45472 - 45474 | 03;16 | Holidays 2 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5474 - 5476 | 45475 - 45477 | 03;16 | Holidays 3 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5477 - 5479 | 45478 - 45480 | 03;16 | Holidays 4 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5480 - 5482 | 45481 - 45483 | 03;16 | Holidays 5 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5483 - 5485 | 45484 - 45486 | 03;16 | Holidays 6 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5486 - 5488 | 45487 - 45489 | 03;16 | Holidays 7 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5489 - 5491 | 45490 - 45492 | 03;16 | Holidays 8 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5492 - 5494 | 45493 - 45495 | 03;16 | Holidays 9 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5495 - 5497 | 45496 - 45498 | 03;16 | Holidays 10 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5498 - 5500 | 45499 - 45501 | 03;16 | Holidays 11 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5501 - 5503 | 45502 - 45504 | 03;16 | Holidays 12 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5504 - 5506 | 45505 - 45507 | 03;16 | Holidays 13 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5507 - 5509 | 45508 - 45510 | 03;16 | Holidays 14 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5510 - 5512 | 45511 - 45513 | 03;16 | Holidays 15 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5513 - 5515 | 45514 - 45516 | 03;16 | Holidays 16 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5516 - 5518 | 45517 - 45519 | 03;16 | Holidays 17 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5519 - 5521 | 45520 - 45522 | 03;16 | Holidays 18 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5522 - 5524 | 45523 - 45525 | 03;16 | Holidays 19 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5525 - 5527 | 45526 - 45528 | 03;16 | Holidays 20 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5528 - 5530 | 45529 - 45531 | 03;16 | Holidays 21 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5531 - 5533 | 45532 - 45534 | 03;16 | Holidays 22 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5534 - 5536 | 45535 - 45537 | 03;16 | Holidays 23 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5537 - 5539 | 45538 - 45540 | 03;16 | Holidays 24 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5540 - 5542 | 45541 - 45543 | 03;16 | Holidays 25 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5543 - 5545 | 45544 - 45546 | 03;16 | Holidays 26 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5546 - 5548 | 45547 - 45549 | 03;16 | Holidays 27 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5549 - 5551 | 45550 - 45552 | 03;16 | Holidays 28 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5552 - 5554 | 45553 - 45555 | 03;16 | Holidays 29 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5555 - 5557 | 45556 - 45558 | 03;16 | Holidays 30 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (second year) | 5558 | 45559 | 03;16 | The second year | INT16u | AB
TOU: ten years holiday (second year) | 5559 | 45560 | 03;16 | The amount number of holidays in second year | INT16u | AB
TOU: ten years holiday (third year) | 5560 - 5562 | 45561 - 45563 | 03;16 | Holidays 1 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5563 - 5565 | 45564 - 45566 | 03;16 | Holidays 2 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5566 - 5568 | 45567 - 45569 | 03;16 | Holidays 3 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5569 - 5571 | 45570 - 45572 | 03;16 | Holidays 4 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5572 - 5574 | 45573 - 45575 | 03;16 | Holidays 5 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5575 - 5577 | 45576 - 45578 | 03;16 | Holidays 6 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5578 - 5580 | 45579 - 45581 | 03;16 | Holidays 7 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5581 - 5583 | 45582 - 45584 | 03;16 | Holidays 8 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5584 - 5586 | 45585 - 45587 | 03;16 | Holidays 9 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5587 - 5589 | 45588 - 45590 | 03;16 | Holidays 10 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5590 - 5592 | 45591 - 45593 | 03;16 | Holidays 11 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5593 - 5595 | 45594 - 45596 | 03;16 | Holidays 12 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5596 - 5598 | 45597 - 45599 | 03;16 | Holidays 13 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5599 - 5601 | 45600 - 45602 | 03;16 | Holidays 14 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5602 - 5604 | 45603 - 45605 | 03;16 | Holidays 15 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5605 - 5607 | 45606 - 45608 | 03;16 | Holidays 16 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5608 - 5610 | 45609 - 45611 | 03;16 | Holidays 17 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5611 - 5613 | 45612 - 45614 | 03;16 | Holidays 18 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5614 - 5616 | 45615 - 45617 | 03;16 | Holidays 19 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5617 - 5619 | 45618 - 45620 | 03;16 | Holidays 20 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5620 - 5622 | 45621 - 45623 | 03;16 | Holidays 21 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5623 - 5625 | 45624 - 45626 | 03;16 | Holidays 22 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5626 - 5628 | 45627 - 45629 | 03;16 | Holidays 23 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5629 - 5631 | 45630 - 45632 | 03;16 | Holidays 24 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5632 - 5634 | 45633 - 45635 | 03;16 | Holidays 25 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5635 - 5637 | 45636 - 45638 | 03;16 | Holidays 26 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5638 - 5640 | 45639 - 45641 | 03;16 | Holidays 27 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5641 - 5643 | 45642 - 45644 | 03;16 | Holidays 28 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5644 - 5646 | 45645 - 45647 | 03;16 | Holidays 29 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5647 - 5649 | 45648 - 45650 | 03;16 | Holidays 30 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (third year) | 5650 | 45651 | 03;16 | The third year | INT16u | AB
TOU: ten years holiday (third year) | 5651 | 45652 | 03;16 | The amount number of holidays in third year | INT16u | AB
TOU: ten years holiday (fourth year) | 5652 - 5654 | 45653 - 45655 | 03;16 | Holidays 1 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5655 - 5657 | 45656 - 45658 | 03;16 | Holidays 2 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5658 - 5660 | 45659 - 45661 | 03;16 | Holidays 3 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5661 - 5663 | 45662 - 45664 | 03;16 | Holidays 4 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5664 - 5666 | 45665 - 45667 | 03;16 | Holidays 5 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5667 - 5669 | 45668 - 45670 | 03;16 | Holidays 6 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5670 - 5672 | 45671 - 45673 | 03;16 | Holidays 7 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5673 - 5675 | 45674 - 45676 | 03;16 | Holidays 8 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5676 - 5678 | 45677 - 45679 | 03;16 | Holidays 9 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5679 - 5681 | 45680 - 45682 | 03;16 | Holidays 10 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5682 - 5684 | 45683 - 45685 | 03;16 | Holidays 11 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5685 - 5687 | 45686 - 45688 | 03;16 | Holidays 12 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5688 - 5690 | 45689 - 45691 | 03;16 | Holidays 13 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5691 - 5693 | 45692 - 45694 | 03;16 | Holidays 14 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5694 - 5696 | 45695 - 45697 | 03;16 | Holidays 15 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5697 - 5699 | 45698 - 45700 | 03;16 | Holidays 16 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5700 - 5702 | 45701 - 45703 | 03;16 | Holidays 17 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5703 - 5705 | 45704 - 45706 | 03;16 | Holidays 18 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5706 - 5708 | 45707 - 45709 | 03;16 | Holidays 19 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5709 - 5711 | 45710 - 45712 | 03;16 | Holidays 20 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5712 - 5714 | 45713 - 45715 | 03;16 | Holidays 21 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5715 - 5717 | 45716 - 45718 | 03;16 | Holidays 22 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5718 - 5720 | 45719 - 45721 | 03;16 | Holidays 23 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5721 - 5723 | 45722 - 45724 | 03;16 | Holidays 24 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5724 - 5726 | 45725 - 45727 | 03;16 | Holidays 25 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5727 - 5729 | 45728 - 45730 | 03;16 | Holidays 26 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5730 - 5732 | 45731 - 45733 | 03;16 | Holidays 27 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5733 - 5735 | 45734 - 45736 | 03;16 | Holidays 28 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5736 - 5738 | 45737 - 45739 | 03;16 | Holidays 29 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5739 - 5741 | 45740 - 45742 | 03;16 | Holidays 30 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fourth year) | 5742 | 45743 | 03;16 | The fourth year | INT16u | AB
TOU: ten years holiday (fourth year) | 5743 | 45744 | 03;16 | The amount number of holidays in fourth year | INT16u | AB
TOU: ten years holiday (fifth year) | 5744 - 5746 | 45745 - 45747 | 03;16 | Holidays 1 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5747 - 5749 | 45748 - 45750 | 03;16 | Holidays 2 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5750 - 5752 | 45751 - 45753 | 03;16 | Holidays 3 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5753 - 5755 | 45754 - 45756 | 03;16 | Holidays 4 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5756 - 5758 | 45757 - 45759 | 03;16 | Holidays 5 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5759 - 5761 | 45760 - 45762 | 03;16 | Holidays 6 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5762 - 5764 | 45763 - 45765 | 03;16 | Holidays 7 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5765 - 5767 | 45766 - 45768 | 03;16 | Holidays 8 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5768 - 5770 | 45769 - 45771 | 03;16 | Holidays 9 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5771 - 5773 | 45772 - 45774 | 03;16 | Holidays 10 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5774 - 5776 | 45775 - 45777 | 03;16 | Holidays 11 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5777 - 5779 | 45778 - 45780 | 03;16 | Holidays 12 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5780 - 5782 | 45781 - 45783 | 03;16 | Holidays 13 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5783 - 5785 | 45784 - 45786 | 03;16 | Holidays 14 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5786 - 5788 | 45787 - 45789 | 03;16 | Holidays 15 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5789 - 5791 | 45790 - 45792 | 03;16 | Holidays 16 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5792 - 5794 | 45793 - 45795 | 03;16 | Holidays 17 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5795 - 5797 | 45796 - 45798 | 03;16 | Holidays 18 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5798 - 5800 | 45799 - 45801 | 03;16 | Holidays 19 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5801 - 5803 | 45802 - 45804 | 03;16 | Holidays 20 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5804 - 5806 | 45805 - 45807 | 03;16 | Holidays 21 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5807 - 5809 | 45808 - 45810 | 03;16 | Holidays 22 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5810 - 5812 | 45811 - 45813 | 03;16 | Holidays 23 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5813 - 5815 | 45814 - 45816 | 03;16 | Holidays 24 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5816 - 5818 | 45817 - 45819 | 03;16 | Holidays 25 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5819 - 5821 | 45820 - 45822 | 03;16 | Holidays 26 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5822 - 5824 | 45823 - 45825 | 03;16 | Holidays 27 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5825 - 5827 | 45826 - 45828 | 03;16 | Holidays 28 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5828 - 5830 | 45829 - 45831 | 03;16 | Holidays 29 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5831 - 5833 | 45832 - 45834 | 03;16 | Holidays 30 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (fifth year) | 5834 | 45835 | 03;16 | The fifth year | INT16u | AB
TOU: ten years holiday (fifth year) | 5835 | 45836 | 03;16 | The amount number of holidays in fifth year | INT16u | AB
TOU: ten years holiday (sixth year) | 5836 - 5838 | 45837 - 45839 | 03;16 | Holidays 1 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5839 - 5841 | 45840 - 45842 | 03;16 | Holidays 2 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5842 - 5844 | 45843 - 45845 | 03;16 | Holidays 3 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5845 - 5847 | 45846 - 45848 | 03;16 | Holidays 4 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5848 - 5850 | 45849 - 45851 | 03;16 | Holidays 5 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5851 - 5853 | 45852 - 45854 | 03;16 | Holidays 6 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5854 - 5856 | 45855 - 45857 | 03;16 | Holidays 7 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5857 - 5859 | 45858 - 45860 | 03;16 | Holidays 8 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5860 - 5862 | 45861 - 45863 | 03;16 | Holidays 9 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5863 - 5865 | 45864 - 45866 | 03;16 | Holidays 10 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5866 - 5868 | 45867 - 45869 | 03;16 | Holidays 11 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5869 - 5871 | 45870 - 45872 | 03;16 | Holidays 12 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5872 - 5874 | 45873 - 45875 | 03;16 | Holidays 13 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5875 - 5877 | 45876 - 45878 | 03;16 | Holidays 14 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5878 - 5880 | 45879 - 45881 | 03;16 | Holidays 15 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5881 - 5883 | 45882 - 45884 | 03;16 | Holidays 16 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5884 - 5886 | 45885 - 45887 | 03;16 | Holidays 17 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5887 - 5889 | 45888 - 45890 | 03;16 | Holidays 18 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5890 - 5892 | 45891 - 45893 | 03;16 | Holidays 19 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5893 - 5895 | 45894 - 45896 | 03;16 | Holidays 20 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5896 - 5898 | 45897 - 45899 | 03;16 | Holidays 21 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5899 - 5901 | 45900 - 45902 | 03;16 | Holidays 22 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5902 - 5904 | 45903 - 45905 | 03;16 | Holidays 23 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5905 - 5907 | 45906 - 45908 | 03;16 | Holidays 24 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5908 - 5910 | 45909 - 45911 | 03;16 | Holidays 25 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5911 - 5913 | 45912 - 45914 | 03;16 | Holidays 26 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5914 - 5916 | 45915 - 45917 | 03;16 | Holidays 27 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5917 - 5919 | 45918 - 45920 | 03;16 | Holidays 28 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5920 - 5922 | 45921 - 45923 | 03;16 | Holidays 29 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5923 - 5925 | 45924 - 45926 | 03;16 | Holidays 30 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (sixth year) | 5926 | 45927 | 03;16 | The sixth year | INT16u | AB
TOU: ten years holiday (sixth year) | 5927 | 45928 | 03;16 | The amount number of holidays in sixth year | INT16u | AB
TOU: ten years holiday (seventh year) | 5928 - 5930 | 45929 - 45931 | 03;16 | Holidays 1 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5931 - 5933 | 45932 - 45934 | 03;16 | Holidays 2 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5934 - 5936 | 45935 - 45937 | 03;16 | Holidays 3 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5937 - 5939 | 45938 - 45940 | 03;16 | Holidays 4 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5940 - 5942 | 45941 - 45943 | 03;16 | Holidays 5 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5943 - 5945 | 45944 - 45946 | 03;16 | Holidays 6 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5946 - 5948 | 45947 - 45949 | 03;16 | Holidays 7 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5949 - 5951 | 45950 - 45952 | 03;16 | Holidays 8 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5952 - 5954 | 45953 - 45955 | 03;16 | Holidays 9 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5955 - 5957 | 45956 - 45958 | 03;16 | Holidays 10 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5958 - 5960 | 45959 - 45961 | 03;16 | Holidays 11 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5961 - 5963 | 45962 - 45964 | 03;16 | Holidays 12 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5964 - 5966 | 45965 - 45967 | 03;16 | Holidays 13 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5967 - 5969 | 45968 - 45970 | 03;16 | Holidays 14 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5970 - 5972 | 45971 - 45973 | 03;16 | Holidays 15 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5973 - 5975 | 45974 - 45976 | 03;16 | Holidays 16 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5976 - 5978 | 45977 - 45979 | 03;16 | Holidays 17 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5979 - 5981 | 45980 - 45982 | 03;16 | Holidays 18 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5982 - 5984 | 45983 - 45985 | 03;16 | Holidays 19 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5985 - 5987 | 45986 - 45988 | 03;16 | Holidays 20 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5988 - 5990 | 45989 - 45991 | 03;16 | Holidays 21 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5991 - 5993 | 45992 - 45994 | 03;16 | Holidays 22 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5994 - 5996 | 45995 - 45997 | 03;16 | Holidays 23 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 5997 - 5999 | 45998 - 46000 | 03;16 | Holidays 24 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 6000 - 6002 | 46001 - 46003 | 03;16 | Holidays 25 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 6003 - 6005 | 46004 - 46006 | 03;16 | Holidays 26 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 6006 - 6008 | 46007 - 46009 | 03;16 | Holidays 27 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 6009 - 6011 | 46010 - 46012 | 03;16 | Holidays 28 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 6012 - 6014 | 46013 - 46015 | 03;16 | Holidays 29 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 6015 - 6017 | 46016 - 46018 | 03;16 | Holidays 30 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (seventh year) | 6018 | 6019 | 03;16 | The seventh year | INT16u | AB
TOU: ten years holiday (seventh year) | 6019 | 6020 | 03;16 | The amount number of holidays in seventh year | INT16u | AB
TOU: ten years holiday (eighth year) | 6020 - 6022 | 46021 - 46023 | 03;16 | Holidays 1 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6023 - 6025 | 46024 - 46026 | 03;16 | Holidays 2 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6026 - 6028 | 46027 - 46029 | 03;16 | Holidays 3 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6029 - 6031 | 46030 - 46032 | 03;16 | Holidays 4 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6032 - 6034 | 46033 - 46035 | 03;16 | Holidays 5 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6035 - 6037 | 46036 - 46038 | 03;16 | Holidays 6 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6038 - 6040 | 46039 - 46041 | 03;16 | Holidays 7 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6041 - 6043 | 46042 - 46044 | 03;16 | Holidays 8 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6044 - 6046 | 46045 - 46047 | 03;16 | Holidays 9 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6047 - 6049 | 46048 - 46050 | 03;16 | Holidays 10 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6050 - 6052 | 46051 - 46053 | 03;16 | Holidays 11 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6053 - 6055 | 46054 - 46056 | 03;16 | Holidays 12 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6056 - 6058 | 46057 - 46059 | 03;16 | Holidays 13 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6059 - 6061 | 46060 - 46062 | 03;16 | Holidays 14 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6062 - 6064 | 46063 - 46065 | 03;16 | Holidays 15 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6065 - 6067 | 46066 - 46068 | 03;16 | Holidays 16 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6068 - 6070 | 46069 - 46071 | 03;16 | Holidays 17 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6071 - 6073 | 46072 - 46074 | 03;16 | Holidays 18 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6074 - 6076 | 46075 - 46077 | 03;16 | Holidays 19 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6077 - 6079 | 46078 - 46080 | 03;16 | Holidays 20 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6080 - 6082 | 46081 - 46083 | 03;16 | Holidays 21 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6083 - 6085 | 46084 - 46086 | 03;16 | Holidays 22 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6086 - 6088 | 46087 - 46089 | 03;16 | Holidays 23 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6089 - 6091 | 46090 - 46092 | 03;16 | Holidays 24 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6092 - 6094 | 46093 - 46095 | 03;16 | Holidays 25 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6095 - 6097 | 46096 - 46098 | 03;16 | Holidays 26 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6098 - 6100 | 46099 - 46101 | 03;16 | Holidays 27 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6101 - 6103 | 46102 - 46104 | 03;16 | Holidays 28 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6104 - 6106 | 46105 - 46107 | 03;16 | Holidays 29 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6107 - 6109 | 46108 - 46110 | 03;16 | Holidays 30 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (eighth year) | 6110 | 46111 | 03;16 | The eighth year | INT16u | AB
TOU: ten years holiday (eighth year) | 6111 | 46112 | 03;16 | The amount number of holidays in eighth year | INT16u | AB
TOU: ten years holiday (ninth year) | 6112 - 6114 | 46113 - 46115 | 03;16 | Holidays 1 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6115 - 6117 | 46116 - 46118 | 03;16 | Holidays 2 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6118 - 6120 | 46119 - 46121 | 03;16 | Holidays 3 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6121 - 6123 | 46122 - 46124 | 03;16 | Holidays 4 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6124 - 6126 | 46125 - 46127 | 03;16 | Holidays 5 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6127 - 6129 | 46128 - 46130 | 03;16 | Holidays 6 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6130 - 6132 | 46131 - 46133 | 03;16 | Holidays 7 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6133 - 6135 | 46134 - 46136 | 03;16 | Holidays 8 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6136 - 6138 | 46137 - 46139 | 03;16 | Holidays 9 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6139 - 6141 | 46140 - 46142 | 03;16 | Holidays 10 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6142 - 6144 | 46143 - 46145 | 03;16 | Holidays 11 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6145 - 6147 | 46146 - 46148 | 03;16 | Holidays 12 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6148 - 6150 | 46149 - 46151 | 03;16 | Holidays 13 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6151 - 6153 | 46152 - 46154 | 03;16 | Holidays 14 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6154 - 6156 | 46155 - 46157 | 03;16 | Holidays 15 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6157 - 6159 | 46158 - 46160 | 03;16 | Holidays 16 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6160 - 6162 | 46161 - 46163 | 03;16 | Holidays 17 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6163 - 6165 | 46164 - 46166 | 03;16 | Holidays 18 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6166 - 6168 | 46167 - 46169 | 03;16 | Holidays 19 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6169 - 6171 | 46170 - 46172 | 03;16 | Holidays 20 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6172 - 6174 | 46173 - 46175 | 03;16 | Holidays 21 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6175 - 6177 | 46176 - 46178 | 03;16 | Holidays 22 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6178 - 6180 | 46179 - 46181 | 03;16 | Holidays 23 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6181 - 6183 | 46182 - 46184 | 03;16 | Holidays 24 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6184 - 6186 | 46185 - 46187 | 03;16 | Holidays 25 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6187 - 6189 | 46188 - 46190 | 03;16 | Holidays 26 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6190 - 6192 | 46191 - 46193 | 03;16 | Holidays 27 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6193 - 6195 | 46194 - 46196 | 03;16 | Holidays 28 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6196 - 6198 | 46197 - 46199 | 03;16 | Holidays 29 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6199 - 6201 | 46200 - 46202 | 03;16 | Holidays 30 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (ninth year) | 6202 | 46203 | 03;16 | The ninth year | INT16u | AB
TOU: ten years holiday (ninth year) | 6203 | 46204 | 03;16 | The amount number of holidays in ninth year | INT16u | AB
TOU: ten years holiday (tenth year) | 6204 - 6206 | 46205 - 46207 | 03;16 | Holidays 1 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6207 - 6209 | 46208 - 46210 | 03;16 | Holidays 2 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6210 - 6212 | 46211 - 46213 | 03;16 | Holidays 3 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6213 - 6215 | 46214 - 46216 | 03;16 | Holidays 4 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6216 - 6218 | 46217 - 46219 | 03;16 | Holidays 5 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6219 - 6221 | 46220 - 46222 | 03;16 | Holidays 6 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6222 - 6224 | 46223 - 46225 | 03;16 | Holidays 7 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6225 - 6227 | 46226 - 46228 | 03;16 | Holidays 8 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6228 - 6230 | 46229 - 46231 | 03;16 | Holidays 9 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6231 - 6233 | 46232 - 46234 | 03;16 | Holidays 10 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6234 - 6236 | 46235 - 46237 | 03;16 | Holidays 11 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6237 - 6239 | 46238 - 46240 | 03;16 | Holidays 12 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6240 - 6242 | 46241 - 46243 | 03;16 | Holidays 13 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6243 - 6245 | 46244 - 46246 | 03;16 | Holidays 14 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6246 - 6248 | 46247 - 46249 | 03;16 | Holidays 15 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6249 - 6251 | 46250 - 46252 | 03;16 | Holidays 16 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6252 - 6254 | 46253 - 46255 | 03;16 | Holidays 17 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6255 - 6257 | 46256 - 46258 | 03;16 | Holidays 18 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6258 - 6260 | 46259 - 46261 | 03;16 | Holidays 19 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6261 - 6263 | 46262 - 46264 | 03;16 | Holidays 20 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6264 - 6266 | 46265 - 46267 | 03;16 | Holidays 21 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6267 - 6269 | 46268 - 46270 | 03;16 | Holidays 22 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6270 - 6272 | 46271 - 46273 | 03;16 | Holidays 23 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6273 - 6275 | 46274 - 46276 | 03;16 | Holidays 24 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6276 - 6278 | 46277 - 46279 | 03;16 | Holidays 25 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6279 - 6281 | 46280 - 46282 | 03;16 | Holidays 26 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6282 - 6284 | 46283 - 46285 | 03;16 | Holidays 27 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6285 - 6287 | 46286 - 46288 | 03;16 | Holidays 28 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6288 - 6290 | 46289 - 46291 | 03;16 | Holidays 29 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6291 - 6293 | 46292 - 46294 | 03;16 | Holidays 30 table (month, day, and the number of TOU schedule) | INT16u | AB
TOU: ten years holiday (tenth year) | 6294 | 4295 | 03;16 | The tenth year | INT16u | AB
TOU: ten years holiday (tenth year) | 9295 | 4296 | 03;16 | The amount number of holidays in tenth year | INT16u | AB
TOU: daylight saving time parameters | 4352 | 44353 | 03;16 | Enable DST. 0: Disable; 1: Enable | INT16u | AB
TOU: daylight saving time parameters | 4353 | 44354 | 03;16 | DST format | INT16u | AB
TOU: daylight saving time parameters (format 1) | 4354 | 44355 | 03;16 | DST start month | INT16u | AB
TOU: daylight saving time parameters (format 1) | 4355 | 44356 | 03;16 | DST start day | INT16u | AB
TOU: daylight saving time parameters (format 1) | 4356 | 44357 | 03;16 | DST start house | INT16u | AB
TOU: daylight saving time parameters (format 1) | 4357 | 44358 | 03;16 | DST start minute | INT16u | AB
TOU: daylight saving time parameters (format 1) | 4358 | 44359 | 03;16 | Adjust time of DST start (unit: minute) | INT16u | AB
TOU: daylight saving time parameters (format 1) | 4359 | 44360 | 03;16 | DST ending month | INT16u | AB
TOU: daylight saving time parameters (format 1) | 4360 | 44361 | 03;16 | DST ending day | INT16u | AB
TOU: daylight saving time parameters (format 1) | 4361 | 44362 | 03;16 | DST ending house | INT16u | AB
TOU: daylight saving time parameters (format 1) | 4362 | 44363 | 03;16 | DST ending minute | INT16u | AB
TOU: daylight saving time parameters (format 1) | 4363 | 44364 | 03;16 | Adjust time of DST ending (unit: minute) | INT16u | AB
TOU: daylight saving time parameters (format 2) | 4364 | 44365 | 03;16 | DST start month | INT16u | AB
TOU: daylight saving time parameters (format 2) | 4365 | 44366 | 03;16 | DST start day (Mon/Tue/Wed/Thu/Fri/Sat/Sun). 0: Sun; 1 ~ 6: Mon ~ Sat | INT16u | AB
TOU: daylight saving time parameters (format 2) | 4366 | 44367 | 03;16 | DST start week | INT16u | AB
TOU: daylight saving time parameters (format 2) | 4367 | 44368 | 03;16 | DST start house | INT16u | AB
TOU: daylight saving time parameters (format 2) | 4368 | 44369 | 03;16 | DST start minute | INT16u | AB
TOU: daylight saving time parameters (format 2) | 4369 | 44370 | 03;16 | Adjust time of DST start (unit: minute) | INT16u | AB
TOU: daylight saving time parameters (format 2) | 4370 | 44371 | 03;16 | DST ending month | INT16u | AB
TOU: daylight saving time parameters (format 2) | 4371 | 44372 | 03;16 | DST ending day (Mon/Tue/Wed/Thu/Fri/Sat/Sun). 0: Sun; 1 ~ 6: Mon ~ Sat | INT16u | AB
TOU: daylight saving time parameters (format 2) | 4372 | 44373 | 03;16 | DST ending week | INT16u | AB
TOU: daylight saving time parameters (format 2) | 4373 | 44374 | 03;16 | DST ending house | INT16u | AB
TOU: daylight saving time parameters (format 2) | 4374 | 44375 | 03;16 | DST ending minute | INT16u | AB
TOU: daylight saving time parameters (format 2) | 4375 | 44376 | 03;16 | Adjust time of DST ending (unit: minute) | INT16u | AB
Extend I/O parameter settings | 6400 | 46401 | 03;16 | DI type. Bit0:DI1; Bit1:DI2; Bit2:DI3; Bit3:DI4(0: SOE; 1: Pulse Counter) | INT16u | AB
Extend I/O parameter settings | 6401 | 46402 | 03;16 | DI pulse constant | INT16u | AB
Extend I/O parameter settings | 6402 | 46403 | 03;16 | Clear DI counters. Only 0AH works. | INT16u | AB
Extend I/O parameter settings | 6403 | 46404 | 03;16 | Work mode of DO1. 0: Pulse Output; 1: Alarm on Channel 1; 2: Alarm on Channel 2; 3: Alarm on Channel 1 and Channel 2; 4: Communication control | INT16u | AB
Extend I/O parameter settings | 6404 | 46405 | 03;16 | Work mode of DO2. 0: Pulse Output; 1: Alarm on Channel 1; 2: Alarm on Channel 2; 3: Alarm on Channel 1 and Channel 2; 4: Communication control | INT16u | AB
Extend I/O parameter settings | 6405 | 46406 | 03;16 | Pulse constant | INT16u | AB
Extend I/O parameter settings | 6406 | 46407 | 03;16 | DO pulse width | INT16u | AB
Extend I/O parameter settings | 6407 | 46408 | 03;16 | DO1 energy output. 0: NONE; 1: Ep_imp; 2: Ep_exp; 3: Eq_imp; 4: Eq_ exp | INT16u | AB
Extend I/O parameter settings | 6408 | 46409 | 03;16 | DO2 energy output. 0: NONE; 1: Ep_imp; 2: Ep_exp; 3: Eq_imp; 4: Eq_ exp | INT16u | AB
Extend I/O parameter settings | 6409 | 46410 | 03;16 | Alarm delay time | INT16u | AB
Extend I/O parameter settings | 6410 | 46411 | 03;16 | The alarm parameter of channel 1. 0 ~ 51: 0: Disable; 1: Frequency; 2: A-phase voltage ; 3: B-phase voltage ; 4: B-phase voltage; 5: Phase voltage average; 6: Line voltage V12; 7: Line voltage V23 ; 8: Line voltage V31; 9: Line voltage average; 10: Phase (line) current I1; 11: Phase (line) current I2; 12: Phase (line) current I3; 13: Reversed; 14: Middle line current In; 15: Total current; 16: Average current; 17: Phase A power Pa; 18: Phase B power Pb; 19: Phase C power Pc; 20: System power Pcon; 21: Phase A reactive power Qa; 22: Phase B reactive power Qb; 23: Phase C reactive power Qc; 24: System reactive power Qcon; 25: Phase A apparent power Sa; 26: Phase B apparent power Sb; 27: Phase C apparent power Sc; 28: System apparent power Scon; 29: Phase A power factor PFa; 30: Phase B power factor PFb; 31: Phase C power factor PFc; 32: System power factor PFcon; 33: Voltage unbalance factor U_unbl; 34: Current unbalance factor I_unbl; 35: Power demand P_DEMA; 36: Reactive Power demand Q_DEMA; 37: Apparent power demand S_DEMA; 38: Phase A current demand Ia_DEMA; 39: Phase B current demand Ib_DEMA; 40: Phase C current demand Ic_DEMA; 41: Neutral line current demand IN_DEMA; 42: THD_V1; 43: THD_V2; 44: THD_V3; 45: THD_Voltage_ Average; 46: THD_ I1; 47: THD_ I2; 48: THD_ I3; 49: THD_IN; 50: THD_Current_Average; 51: Reverse Phase Sequence. | INT16u | AB
Extend I/O parameter settings | 6411 | 46412 | 03;16 | The alarm mode of channel 1 | INT16u | AB
Extend I/O parameter settings | 6412 | 46413 | 03;16 | The alarm threshold of channel 1 | INT16u | AB
Extend I/O parameter settings | 6413 | 46414 | 03;16 | The alarm parameter of channel 2. 0 ~ 51: 0: Disable; 1: Frequency; 2: A-phase voltage ; 3: B-phase voltage ; 4: B-phase voltage; 5: Phase voltage average; 6: Line voltage V12; 7: Line voltage V23 ; 8: Line voltage V31; 9: Line voltage average; 10: Phase (line) current I1; 11: Phase (line) current I2; 12: Phase (line) current I3; 13: Reversed; 14: Middle line current In; 15: Total current; 16: Average current; 17: Phase A power Pa; 18: Phase B power Pb; 19: Phase C power Pc; 20: System power Pcon; 21: Phase A reactive power Qa; 22: Phase B reactive power Qb; 23: Phase C reactive power Qc; 24: System reactive power Qcon; 25: Phase A apparent power Sa; 26: Phase B apparent power Sb; 27: Phase C apparent power Sc; 28: System apparent power Scon; 29: Phase A power factor PFa; 30: Phase B power factor PFb; 31: Phase C power factor PFc; 32: System power factor PFcon; 33: Voltage unbalance factor U_unbl; 34: Current unbalance factor I_unbl; 35: Power demand P_DEMA; 36: Reactive Power demand Q_DEMA; 37: Apparent power demand S_DEMA; 38: Phase A current demand Ia_DEMA; 39: Phase B current demand Ib_DEMA; 40: Phase C current demand Ic_DEMA; 41: Neutral line current demand IN_DEMA; 42: THD_V1; 43: THD_V2; 44: THD_V3; 45: THD_Voltage_ Average; 46: THD_ I1; 47: THD_ I2; 48: THD_ I3; 49: THD_IN; 50: THD_Current_Average; 51: Reverse Phase Sequence. | INT16u | AB
Extend I/O parameter settings | 6414 | 46415 | 03;16 | The alarm mode of channel 2 | INT16u | AB
Extend I/O parameter settings | 6415 | 46416 | 03;16 | The alarm threshold of channel 2 | INT16u | AB
Extend I/O parameter settings | 6416 | 46417 | 03;16 | Alarm backlight flash. 0: Backlight flash when Alarm status; 1: Backlight don’t flash when alarm status | INT16u | AB
Extend I/O parameter settings | 6417 | 46418 | 03;16 | Clear alarm record. Only 0AH works. | INT16u | AB
Extend I/O parameter settings | 6418 | 46419 | 03;16 | DO output model by communication control. 0x01: Level; 0x02: Pulse | INT16u | AB
Pulse accumulation | 8544 - 8545 | 48545 - 48546 | 03 | DI1 counter number | INT32u | ABCD
Pulse accumulation | 8546 - 8547 | 48547 - 48548 | 03 | DI2 counter number | INT32u | ABCD
Pulse accumulation | 8548 - 8549 | 48549 - 48550 | 03 | DI3 counter number | INT32u | ABCD
Pulse accumulation | 8550 - 8551 | 48551 - 48552 | 03 | DI4 counter number | INT32u | ABCD
SOE event parameters | 12800 | 412801 | 03 | Time stamp - Year (SOE record 1) (High) | INT16u | AB
SOE event parameters | 12800 | 412801 | 03 | Time stamp - Month (SOE record 1) (Low) | INT16u | AB
SOE event parameters | 12801 | 412802 | 03 | Time stamp - Day (SOE record 1) (High) | INT16u | AB
SOE event parameters | 12801 | 412802 | 03 | Time stamp - Hours (SOE record 1) (Low) | INT16u | AB
SOE event parameters | 12802 | 412803 | 03 | Time stamp - Minute (SOE record 1) (High) | INT16u | AB
SOE event parameters | 12802 | 412803 | 03 | Time stamp - Second (SOE record 1) (Low) | INT16u | AB
SOE event parameters | 12803 | 412803 | 03 | Time stamp - Millisecond (SOE record 1) (Low) | INT16u | AB
SOE event parameters | 12804 | 412805 | 03 | IO block of SOE record 1 | INT16u | AB
SOE event parameters | 12805 - 12809 | 412806 - 412810 | 03 | SOE record 2 | INT16u | AB
SOE event parameters | 12810 - 12814 | 412811 - 412815 | 03 | SOE record 3 | INT16u | AB
SOE event parameters | 12815 - 12819 | 412816 - 412820 | 03 | SOE record 4 | INT16u | AB
SOE event parameters | 12820 - 12824 | 412821 - 412825 | 03 | SOE record 5 | INT16u | AB
SOE event parameters | 12825 - 12829 | 412826 - 412830 | 03 | SOE record 6 | INT16u | AB
SOE event parameters | 12830 - 12834 | 412831 - 412835 | 03 | SOE record 7 | INT16u | AB
SOE event parameters | 12835 - 12839 | 412836 - 412840 | 03 | SOE record 8 | INT16u | AB
SOE event parameters | 12840 - 12844 | 412841 - 412845 | 03 | SOE record 9 | INT16u | AB
SOE event parameters | 12845 - 12849 | 412846 - 412850 | 03 | SOE record 10 | INT16u | AB
SOE event parameters | 12850 - 12854 | 412851 - 412855 | 03 | SOE record 11 | INT16u | AB
SOE event parameters | 12855 - 12859 | 412856 - 412860 | 03 | SOE record 12 | INT16u | AB
SOE event parameters | 12860 - 12864 | 412861 - 412865 | 03 | SOE record 13 | INT16u | AB
SOE event parameters | 12865 - 12869 | 412866 - 412870 | 03 | SOE record 14 | INT16u | AB
SOE event parameters | 12870 - 12874 | 412871 - 412875 | 03 | SOE record 15 | INT16u | AB
SOE event parameters | 12875 - 12879 | 412876 - 412880 | 03 | SOE record 16 | INT16u | AB
SOE event parameters | 12880 - 12884 | 412881 - 412885 | 03 | SOE record 17 | INT16u | AB
SOE event parameters | 12885 - 12889 | 412886 - 412890 | 03 | SOE record 18 | INT16u | AB
SOE event parameters | 12890 - 12894 | 412891 - 412895 | 03 | SOE record 19 | INT16u | AB
SOE event parameters | 12895 - 12899 | 412896 - 412900 | 03 | SOE record 20 | INT16u | AB
Single SOE event parameters | 12992 | 412993 | 03 | Time stamp - Year (SOE record 1) (High) | INT16u | AB
Single SOE event parameters | 12992 | 412993 | 03 | Time stamp - Month (SOE record 1) (Low) | INT16u | AB
Single SOE event parameters | 12993 | 412994 | 03 | Time stamp - Day (SOE record 1) (High) | INT16u | AB
Single SOE event parameters | 12993 | 412994 | 03 | Time stamp - Hours (SOE record 1) (Low) | INT16u | AB
Single SOE event parameters | 12994 | 412995 | 03 | Time stamp - Minute (SOE record 1) (High) | INT16u | AB
Single SOE event parameters | 12994 | 412995 | 03 | Time stamp - Second (SOE record 1) (Low) | INT16u | AB
Single SOE event parameters | 12995 | 412996 | 03 | Time stamp - Millisecond (SOE record 1) | INT16u | AB
Single SOE event parameters | 12996 | 412997 | 03 | IO block of SOE record 1 | INT16u | AB
Single SOE event parameters | 12997 | 412998 | 03 | The last SOE record number | INT16u | AB
Single SOE event parameters | 12998 | 412999 | 03;16 | The number of SOE records | INT16u | AB