## Descriptions
ASC 150 Modbus descriptions
Software version
The information contained in these tables (Revision I) is applicable to software version 1.22.0 of the ASC 150.
Row | Hyperlink index
13 | Modbus function codes
24 | Discrete output coil
32 | Discrete input contact
41 | Output holding register
55 | Input register
Back to index | Modbus function codes
| Function code | Description
| 01 | Read a single or multiple discrete output coils.
| 02 | Read a single or multiple discrete input contacts.
| 03 | Read a single or multiple output holding registers.
| 04 | Read a single or multiple input registers.
| 05 | Write a value to a single discrete output coil.
| 06 | Write a value to a single output holding register.
| 15 | Write a value to multiple consecutive discrete output coils.
| 16 | Write a value to multiple consecutive output holding registers.
Back to index | Discrete output coil
| Function code | Effect
| 01 | Read
| 05 or 15 | Write
| Function group | Description
| Command flag | Activate a command in the controller. Read: The controller always returns 0 (false). Write: The controller executes the command if you write 1 (true).
Back to index | Discrete input contact
| Function code | Effect
| 02 | Read
| Function group | Description
| Digital input | Read the state of a digital input on the controller. The controller returns 0 (false) when the digital input is inactive. The controller returns 1 (true) when the digital input is active.
| Digital output | Read the state of a digital output on the controller. The controller returns 0 (false) when the digital output is inactive. The controller returns 1 (true) when the digital output is active.
| Status flag | Read whether a status flag is activated. The controller returns 0 (false) when the status flag is not activated. The controller returns 1 (true) when the status flag is activated.
Back to index | Output holding register
| Function code | Effect
| 03 | Read
| 06 or 16 | Write
| Function group | Description
| Control command | Activate a command in the controller. Read: The controller always returns 0 (false) from the bits. Write: The controller executes the command if you write 1 (true) to the address bit.
| Control time command | Read and write the time and date values of the controller. Read: The controller returns the value of the associated function. Write: The controller changes the value of the associated function if a valid value is entered.
| Read area 1 (ASC to PLC/external system) | Part of the DEIF Open protocol. The ASC puts data here for a PLC or external system to read.
| Read area 2 (ASC to PLC/external system) | Part of the DEIF Open protocol. The ASC puts data here for a PLC or external system to read.
| Read/Write (Battery) | Read and write for a battery controller. Read: The controller returns the value of the associated function. Write: The controller changes the value of the associated function if a valid value is entered.
| Weather area | Weather data.
| Write area 1 (PLC/external system to ASC) | Part of the DEIF Open protocol. A PLC or external system writes data here for the ASC to use.
Back to index | Input register
| Function code | Effect
| 04 | Read
| Function group | Description
| AC alarm | Read one bit to see whether the AC alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| AC measurement | Read the operating value of the associated AC measurement.
| Alarm | Read one bit to see whether the alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| Alarm list monitoring | Read the Address for each active alarm. Use the Parameters tab in the utility software to look up which alarm corresponds to each Address. The alarm list monitoring is in Modbus addresses 28000 to 28099. These addresses are not listed in the Input register (04) worksheet.
| APPL version | Read the controller application version.
| Control command state | Read the state of all the bits in the control command address.
| Counter | Read the counter value.
| DC measurement | Read the operating value of the associated measurement.
| Digital input state | Read one bit to see whether the digital input is activated. The controller returns 0 (false) when the digital input is not activated. The controller returns 1 (true) when the digital input is activated.
| Digital output state | Read one bit to see whether the digital output is activated. The controller returns 0 (false) when the digital output is not activated. The controller returns 1 (true) when the digital output is activated.
| M-Logic state | Read one bit to see whether the M-Logic virtual event or flip-flop is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| Modbus configurable area | Read the value of the function assigned to the address using the Modbus configurator. Additional information about the assigned address should be completed by the user. Modbus addresses 0 to 499 are available for configurable Modbus. These addresses are not listed in the Input register (04) worksheet.
| Modes | Read one bit to see whether the mode is activated. The controller returns 0 (false) when the mode is not activated. The controller returns 1 (true) when the mode is activated.
| Plant config | Read the value of the plant configuration.
| Plant logic state | Read one bit to see whether the plant state is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| PM AC measurement | Read the operating value of the associated Power Management measurements and settings.
| PM alarm | Read one bit to see whether the Power Management alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| PM Plant logic state | Read one bit to see whether the Power Management state is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| Power meter area 1 | Read the operating value of the associated power meters.
| Profibus configurable area | Read the value of the function assigned to the address using the Modbus configurator. Additional information about the assigned address should be completed by the user. Modbus addresses 0 to 62 are available for configurable Profibus. These addresses are not listed in the Input register (04) worksheet.
| PV monitoring area | The ASC Modbus client can poll key data from the inverter(s) and place it in the designated Modbus server area for a monitoring system to read. PV monitoring can be used with unicast and broadcast topologies. The number of nodes determines the number of inverters the ASC should poll data from. A maximum of 42 nodes can be monitored. The ASC expects that the ModbusIDs of the inverters are consecutive in order starting from the selected ModbusID and forward. 70 registers are reserved for each inverter. The Modbus addresses are only for the first inverter. Registers for the following inverters are consecutive.
| Relay state | Read one bit to see the relay state. The controller returns 0 (false) when the relay is de-energised. The controller returns 1 (true) when the relay is energised.

## Discrete output coil (01;05;15)
Discrete output coil (01;05;15)
Function group | Modbus address | PLC address | Modbus function code | Controller function name | SOLAR | BATT
Command flag | 0 | 1 | 01; 05; 15 | Remote start | X | X
Command flag | 1 | 2 | 01; 05; 15 | Remote ESB ON |  | X
Command flag | 1 | 2 | 01; 05; 15 | Remote PVB ON | X
Command flag | 2 | 3 | 01; 05; 15 | Remote ESB OFF |  | X
Command flag | 2 | 3 | 01; 05; 15 | Remote PVB OFF | X
Command flag | 3 | 4 | 01; 05; 15 | Remote stop | X | X
Command flag | 4 | 5 | 01; 05; 15 | Alarm inhibit 1 | X | X
Command flag | 5 | 6 | 01; 05; 15 | Alarm inhibit 2 | X | X
Command flag | 6 | 7 | 01; 05; 15 | Alarm inhibit 3 | X | X
Command flag | 9 | 10 | 01; 05; 15 | Alarm ack. | X | X
Command flag | 10 | 11 | 01; 05; 15 | Nominal setting 1 | X | X
Command flag | 11 | 12 | 01; 05; 15 | Nominal setting 2 | X | X
Command flag | 12 | 13 | 01; 05; 15 | Nominal setting 3 | X | X
Command flag | 13 | 14 | 01; 05; 15 | Nominal setting 4 | X | X
Command flag | 16 | 17 | 01; 05; 15 | Island | X | X
Command flag | 17 | 18 | 01; 05; 15 | Automatic mains failure (AMF) | X | X
Command flag | 18 | 19 | 01; 05; 15 | Peak shaving | X | X
Command flag | 19 | 20 | 01; 05; 15 | Fixed power | X | X
Command flag | 20 | 21 | 01; 05; 15 | Mains power export (MPE) | X | X
Command flag | 24 | 25 | 01; 05; 15 | MB ON | X | X
Command flag | 25 | 26 | 01; 05; 15 | MB OFF | X | X
Command flag | 26 | 27 | 01; 05; 15 | Auto start/stop | X | X
Command flag | 28 | 29 | 01; 05; 15 | Semi-auto mode | X | X
Command flag | 29 | 30 | 01; 05; 15 | Auto mode | X | X
Command flag | 33 | 34 | 01; 05; 15 | External power control | X | X
Command flag | 34 | 35 | 01; 05; 15 | External reactive power control | X | X
Command flag | 35 | 36 | 01; 05; 15 | External power factor control | X | X
Command flag | 36 | 37 | 01; 05; 15 | Capacitive PF | X | X
Command flag | 40 | 41 | 01; 05; 15 | Application 1 | X | X
Command flag | 41 | 42 | 01; 05; 15 | Application 2 | X | X
Command flag | 42 | 43 | 01; 05; 15 | Application 3 | X | X
Command flag | 43 | 44 | 01; 05; 15 | Application 4 | X | X
Command flag | 46 | 47 | 01; 05; 15 | Synchronise clock to 4:00 a.m. | X | X
Command flag | 48 | 49 | 01; 05; 15 | Virtual toggle event 1 | X | X
Command flag | 49 | 50 | 01; 05; 15 | Virtual toggle event 2 | X | X
Command flag | 50 | 51 | 01; 05; 15 | Virtual toggle event 3 | X | X
Command flag | 51 | 52 | 01; 05; 15 | Virtual toggle event 4 | X | X
Command flag | 52 | 53 | 01; 05; 15 | Virtual toggle event 5 | X | X
Command flag | 53 | 54 | 01; 05; 15 | Virtual toggle event 6 | X | X
Command flag | 54 | 55 | 01; 05; 15 | Virtual toggle event 7 | X | X
Command flag | 55 | 56 | 01; 05; 15 | Virtual toggle event 8 | X | X
Command flag | 56 | 57 | 01; 05; 15 | Virtual toggle event 9 | X | X
Command flag | 57 | 58 | 01; 05; 15 | Virtual toggle event 10 | X | X
Command flag | 58 | 59 | 01; 05; 15 | Virtual toggle event 11 | X | X
Command flag | 59 | 60 | 01; 05; 15 | Virtual toggle event 12 | X | X
Command flag | 60 | 61 | 01; 05; 15 | Virtual toggle event 13 | X | X
Command flag | 61 | 62 | 01; 05; 15 | Virtual toggle event 14 | X | X
Command flag | 62 | 63 | 01; 05; 15 | Virtual toggle event 15 | X | X
Command flag | 63 | 64 | 01; 05; 15 | Virtual toggle event 16 | X | X
Command flag | 64 | 65 | 01; 05; 15 | Virtual toggle event 17 | X | X
Command flag | 65 | 66 | 01; 05; 15 | Virtual toggle event 18 | X | X
Command flag | 66 | 67 | 01; 05; 15 | Virtual toggle event 19 | X | X
Command flag | 67 | 68 | 01; 05; 15 | Virtual toggle event 20 | X | X
Command flag | 68 | 69 | 01; 05; 15 | Virtual toggle event 21 | X | X
Command flag | 69 | 70 | 01; 05; 15 | Virtual toggle event 22 | X | X
Command flag | 70 | 71 | 01; 05; 15 | Virtual toggle event 23 | X | X
Command flag | 71 | 72 | 01; 05; 15 | Virtual toggle event 24 | X | X
Command flag | 72 | 73 | 01; 05; 15 | Virtual toggle event 25 | X | X
Command flag | 73 | 74 | 01; 05; 15 | Virtual toggle event 26 | X | X
Command flag | 74 | 75 | 01; 05; 15 | Virtual toggle event 27 | X | X
Command flag | 75 | 76 | 01; 05; 15 | Virtual toggle event 28 | X | X
Command flag | 76 | 77 | 01; 05; 15 | Virtual toggle event 29 | X | X
Command flag | 77 | 78 | 01; 05; 15 | Virtual toggle event 30 | X | X
Command flag | 78 | 79 | 01; 05; 15 | Virtual toggle event 31 | X | X
Command flag | 79 | 80 | 01; 05; 15 | Virtual toggle event 32 | X | X
Command flag | 121 | 122 | 01; 05; 15 | Clear log | X | X
Command flag | 122 | 123 | 01; 05; 15 | Clear Parameter edits | X | X
Command flag | 127 | 128 | 01; 05; 15 | Enable external power control | X | X
Command flag | 128 | 129 | 01; 05; 15 | Disable external power control | X | X
Command flag | 129 | 130 | 01; 05; 15 | Enable external VAr control | X | X
Command flag | 130 | 131 | 01; 05; 15 | Disable external VAr control | X | X
Command flag | 131 | 132 | 01; 05; 15 | Enable external CosPhi control | X | X
Command flag | 132 | 133 | 01; 05; 15 | Disable external CosPhi control | X | X
Command flag | 142 | 143 | 01; 05; 15 | Virtual toggle event 33 | X | X
Command flag | 143 | 144 | 01; 05; 15 | Virtual toggle event 34 | X | X
Command flag | 144 | 145 | 01; 05; 15 | Virtual toggle event 35 | X | X
Command flag | 145 | 146 | 01; 05; 15 | Virtual toggle event 36 | X | X
Command flag | 146 | 147 | 01; 05; 15 | Virtual toggle event 37 | X | X
Command flag | 147 | 148 | 01; 05; 15 | Virtual toggle event 38 | X | X
Command flag | 148 | 149 | 01; 05; 15 | Virtual toggle event 39 | X | X
Command flag | 149 | 150 | 01; 05; 15 | Virtual toggle event 40 | X | X
Command flag | 150 | 151 | 01; 05; 15 | Virtual toggle event 41 | X | X
Command flag | 151 | 152 | 01; 05; 15 | Virtual toggle event 42 | X | X
Command flag | 152 | 153 | 01; 05; 15 | Virtual toggle event 43 | X | X
Command flag | 153 | 154 | 01; 05; 15 | Virtual toggle event 44 | X | X
Command flag | 154 | 155 | 01; 05; 15 | Virtual toggle event 45 | X | X
Command flag | 155 | 156 | 01; 05; 15 | Virtual toggle event 46 | X | X
Command flag | 156 | 157 | 01; 05; 15 | Virtual toggle event 47 | X | X
Command flag | 157 | 158 | 01; 05; 15 | Virtual toggle event 48 | X | X
Command flag | 158 | 159 | 01; 05; 15 | Virtual toggle event 49 | X | X
Command flag | 159 | 160 | 01; 05; 15 | Virtual toggle event 50 | X | X
Command flag | 160 | 161 | 01; 05; 15 | Virtual toggle event 51 | X | X
Command flag | 161 | 162 | 01; 05; 15 | Virtual toggle event 52 | X | X
Command flag | 162 | 163 | 01; 05; 15 | Virtual toggle event 53 | X | X
Command flag | 163 | 164 | 01; 05; 15 | Virtual toggle event 54 | X | X
Command flag | 164 | 165 | 01; 05; 15 | Virtual toggle event 55 | X | X
Command flag | 165 | 166 | 01; 05; 15 | Virtual toggle event 56 | X | X
Command flag | 166 | 167 | 01; 05; 15 | Virtual toggle event 57 | X | X
Command flag | 167 | 168 | 01; 05; 15 | Virtual toggle event 58 | X | X
Command flag | 168 | 169 | 01; 05; 15 | Virtual toggle event 59 | X | X
Command flag | 169 | 170 | 01; 05; 15 | Virtual toggle event 60 | X | X
Command flag | 170 | 171 | 01; 05; 15 | Virtual toggle event 61 | X | X
Command flag | 171 | 172 | 01; 05; 15 | Virtual toggle event 62 | X | X
Command flag | 172 | 173 | 01; 05; 15 | Virtual toggle event 63 | X | X
Command flag | 173 | 174 | 01; 05; 15 | Virtual toggle event 64 | X | X
Command flag | 174 | 175 | 01; 05; 15 | Virtual toggle event 65 | X | X
Command flag | 175 | 176 | 01; 05; 15 | Virtual toggle event 66 | X | X
Command flag | 176 | 177 | 01; 05; 15 | Virtual toggle event 67 | X | X
Command flag | 177 | 178 | 01; 05; 15 | Virtual toggle event 68 | X | X
Command flag | 178 | 179 | 01; 05; 15 | Virtual toggle event 69 | X | X
Command flag | 179 | 180 | 01; 05; 15 | Virtual toggle event 70 | X | X
Command flag | 180 | 181 | 01; 05; 15 | Virtual toggle event 71 | X | X
Command flag | 181 | 182 | 01; 05; 15 | Virtual toggle event 72 | X | X
Command flag | 182 | 183 | 01; 05; 15 | Virtual toggle event 73 | X | X
Command flag | 183 | 184 | 01; 05; 15 | Virtual toggle event 74 | X | X
Command flag | 184 | 185 | 01; 05; 15 | Virtual toggle event 75 | X | X
Command flag | 185 | 186 | 01; 05; 15 | Virtual toggle event 76 | X | X
Command flag | 186 | 187 | 01; 05; 15 | Virtual toggle event 77 | X | X
Command flag | 187 | 188 | 01; 05; 15 | Virtual toggle event 78 | X | X
Command flag | 188 | 189 | 01; 05; 15 | Virtual toggle event 79 | X | X
Command flag | 189 | 190 | 01; 05; 15 | Virtual toggle event 80 | X | X
Command flag | 190 | 191 | 01; 05; 15 | Virtual toggle event 81 | X | X
Command flag | 191 | 192 | 01; 05; 15 | Virtual toggle event 82 | X | X
Command flag | 192 | 193 | 01; 05; 15 | Virtual toggle event 83 | X | X
Command flag | 193 | 194 | 01; 05; 15 | Virtual toggle event 84 | X | X
Command flag | 194 | 195 | 01; 05; 15 | Virtual toggle event 85 | X | X
Command flag | 195 | 196 | 01; 05; 15 | Virtual toggle event 86 | X | X
Command flag | 196 | 197 | 01; 05; 15 | Virtual toggle event 87 | X | X
Command flag | 197 | 198 | 01; 05; 15 | Virtual toggle event 88 | X | X
Command flag | 198 | 199 | 01; 05; 15 | Virtual toggle event 89 | X | X
Command flag | 199 | 200 | 01; 05; 15 | Virtual toggle event 90 | X | X
Command flag | 200 | 201 | 01; 05; 15 | Virtual toggle event 91 | X | X
Command flag | 201 | 202 | 01; 05; 15 | Virtual toggle event 92 | X | X
Command flag | 202 | 203 | 01; 05; 15 | Virtual toggle event 93 | X | X
Command flag | 203 | 204 | 01; 05; 15 | Virtual toggle event 94 | X | X
Command flag | 204 | 205 | 01; 05; 15 | Virtual toggle event 95 | X | X
Command flag | 205 | 206 | 01; 05; 15 | Virtual toggle event 96 | X | X
Command flag | 206 | 207 | 01; 05; 15 | Set flipflop 01 | X | X
Command flag | 207 | 208 | 01; 05; 15 | Set flipflop 02 | X | X
Command flag | 208 | 209 | 01; 05; 15 | Set flipflop 03 | X | X
Command flag | 209 | 210 | 01; 05; 15 | Set flipflop 04 | X | X
Command flag | 210 | 211 | 01; 05; 15 | Set flipflop 05 | X | X
Command flag | 211 | 212 | 01; 05; 15 | Set flipflop 06 | X | X
Command flag | 212 | 213 | 01; 05; 15 | Set flipflop 07 | X | X
Command flag | 213 | 214 | 01; 05; 15 | Set flipflop 08 | X | X
Command flag | 214 | 215 | 01; 05; 15 | Set flipflop 09 | X | X
Command flag | 215 | 216 | 01; 05; 15 | Set flipflop 10 | X | X
Command flag | 216 | 217 | 01; 05; 15 | Set flipflop 11 | X | X
Command flag | 217 | 218 | 01; 05; 15 | Set flipflop 12 | X | X
Command flag | 218 | 219 | 01; 05; 15 | Set flipflop 13 | X | X
Command flag | 219 | 220 | 01; 05; 15 | Set flipflop 14 | X | X
Command flag | 220 | 221 | 01; 05; 15 | Set flipflop 15 | X | X
Command flag | 221 | 222 | 01; 05; 15 | Set flipflop 16 | X | X
Command flag | 222 | 223 | 01; 05; 15 | Reset flipflop 01 | X | X
Command flag | 223 | 224 | 01; 05; 15 | Reset flipflop 02 | X | X
Command flag | 224 | 225 | 01; 05; 15 | Reset flipflop 03 | X | X
Command flag | 225 | 226 | 01; 05; 15 | Reset flipflop 04 | X | X
Command flag | 226 | 227 | 01; 05; 15 | Reset flipflop 05 | X | X
Command flag | 227 | 228 | 01; 05; 15 | Reset flipflop 06 | X | X
Command flag | 228 | 229 | 01; 05; 15 | Reset flipflop 07 | X | X
Command flag | 229 | 230 | 01; 05; 15 | Reset flipflop 08 | X | X
Command flag | 230 | 231 | 01; 05; 15 | Reset flipflop 09 | X | X
Command flag | 231 | 232 | 01; 05; 15 | Reset flipflop 10 | X | X
Command flag | 232 | 233 | 01; 05; 15 | Reset flipflop 11 | X | X
Command flag | 233 | 234 | 01; 05; 15 | Reset flipflop 12 | X | X
Command flag | 234 | 235 | 01; 05; 15 | Reset flipflop 13 | X | X
Command flag | 235 | 236 | 01; 05; 15 | Reset flipflop 14 | X | X
Command flag | 236 | 237 | 01; 05; 15 | Reset flipflop 15 | X | X
Command flag | 237 | 238 | 01; 05; 15 | Reset flipflop 16 | X | X
Command flag | 238 | 239 | 01; 05; 15 | Toggle flipflop 01 | X | X
Command flag | 239 | 240 | 01; 05; 15 | Toggle flipflop 02 | X | X
Command flag | 240 | 241 | 01; 05; 15 | Toggle flipflop 03 | X | X
Command flag | 241 | 242 | 01; 05; 15 | Toggle flipflop 04 | X | X
Command flag | 242 | 243 | 01; 05; 15 | Toggle flipflop 05 | X | X
Command flag | 243 | 244 | 01; 05; 15 | Toggle flipflop 06 | X | X
Command flag | 244 | 245 | 01; 05; 15 | Toggle flipflop 07 | X | X
Command flag | 245 | 246 | 01; 05; 15 | Toggle flipflop 08 | X | X
Command flag | 246 | 247 | 01; 05; 15 | Toggle flipflop 09 | X | X
Command flag | 247 | 248 | 01; 05; 15 | Toggle flipflop 10 | X | X
Command flag | 248 | 249 | 01; 05; 15 | Toggle flipflop 11 | X | X
Command flag | 249 | 250 | 01; 05; 15 | Toggle flipflop 12 | X | X
Command flag | 250 | 251 | 01; 05; 15 | Toggle flipflop 13 | X | X
Command flag | 251 | 252 | 01; 05; 15 | Toggle flipflop 14 | X | X
Command flag | 252 | 253 | 01; 05; 15 | Toggle flipflop 15 | X | X
Command flag | 253 | 254 | 01; 05; 15 | Toggle flipflop 16 | X | X
Command flag | 307 | 308 | 01; 05; 15 | Virtual switch event 1 | X | X
Command flag | 308 | 309 | 01; 05; 15 | Virtual switch event 2 | X | X
Command flag | 309 | 310 | 01; 05; 15 | Virtual switch event 3 | X | X
Command flag | 310 | 311 | 01; 05; 15 | Virtual switch event 4 | X | X
Command flag | 311 | 312 | 01; 05; 15 | Virtual switch event 5 | X | X
Command flag | 312 | 313 | 01; 05; 15 | Virtual switch event 6 | X | X
Command flag | 313 | 314 | 01; 05; 15 | Virtual switch event 7 | X | X
Command flag | 314 | 315 | 01; 05; 15 | Virtual switch event 8 | X | X
Command flag | 315 | 316 | 01; 05; 15 | Virtual switch event 9 | X | X
Command flag | 316 | 317 | 01; 05; 15 | Virtual switch event 10 | X | X
Command flag | 317 | 318 | 01; 05; 15 | Virtual switch event 11 | X | X
Command flag | 318 | 319 | 01; 05; 15 | Virtual switch event 12 | X | X
Command flag | 319 | 320 | 01; 05; 15 | Virtual switch event 13 | X | X
Command flag | 320 | 321 | 01; 05; 15 | Virtual switch event 14 | X | X
Command flag | 321 | 322 | 01; 05; 15 | Virtual switch event 15 | X | X
Command flag | 322 | 323 | 01; 05; 15 | Virtual switch event 16 | X | X
Command flag | 323 | 324 | 01; 05; 15 | Virtual switch event 17 | X | X
Command flag | 324 | 325 | 01; 05; 15 | Virtual switch event 18 | X | X
Command flag | 325 | 326 | 01; 05; 15 | Virtual switch event 19 | X | X
Command flag | 326 | 327 | 01; 05; 15 | Virtual switch event 20 | X | X
Command flag | 327 | 328 | 01; 05; 15 | Virtual switch event 21 | X | X
Command flag | 328 | 329 | 01; 05; 15 | Virtual switch event 22 | X | X
Command flag | 329 | 330 | 01; 05; 15 | Virtual switch event 23 | X | X
Command flag | 330 | 331 | 01; 05; 15 | Virtual switch event 24 | X | X
Command flag | 331 | 332 | 01; 05; 15 | Virtual switch event 25 | X | X
Command flag | 332 | 333 | 01; 05; 15 | Virtual switch event 26 | X | X
Command flag | 333 | 334 | 01; 05; 15 | Virtual switch event 27 | X | X
Command flag | 334 | 335 | 01; 05; 15 | Virtual switch event 28 | X | X
Command flag | 335 | 336 | 01; 05; 15 | Virtual switch event 29 | X | X
Command flag | 336 | 337 | 01; 05; 15 | Virtual switch event 30 | X | X
Command flag | 337 | 338 | 01; 05; 15 | Virtual switch event 31 | X | X
Command flag | 338 | 339 | 01; 05; 15 | Virtual switch event 32 | X | X

## Discrete input contact (02)
Discrete input contact (02)
Function group | Modbus address | PLC address | Modbus function code | Controller function name | SOLAR | BATT
Status flag | 0 | 100001 | 02 | ESB position ON |  | X
Status flag | 0 | 100001 | 02 | PVB position ON | X
Status flag | 1 | 100002 | 02 | MB position ON | X | X
Status flag | 5 | 100006 | 02 | Mains failure (Single DG) | X | X
Status flag | 8 | 100009 | 02 | Semi-auto mode | X | X
Status flag | 9 | 100010 | 02 | Auto mode | X | X
Status flag | 13 | 100014 | 02 | Island | X | X
Status flag | 14 | 100015 | 02 | Automatic mains failure (AMF) | X | X
Status flag | 15 | 100016 | 02 | Peak shaving | X | X
Status flag | 16 | 100017 | 02 | Fixed power | X | X
Status flag | 17 | 100018 | 02 | Mains power export (MPE) | X | X
Status flag | 19 | 100020 | 02 | Power management | X | X
Status flag | 20 | 100021 | 02 | Any alarm on PMS ID1 | X | X
Status flag | 21 | 100022 | 02 | Any alarm on PMS ID2 | X | X
Status flag | 22 | 100023 | 02 | Any alarm on PMS ID3 | X | X
Status flag | 23 | 100024 | 02 | Any alarm on PMS ID4 | X | X
Status flag | 24 | 100025 | 02 | Any alarm on PMS ID5 | X | X
Status flag | 25 | 100026 | 02 | Any alarm on PMS ID6 | X | X
Status flag | 26 | 100027 | 02 | Any alarm on PMS ID7 | X | X
Status flag | 27 | 100028 | 02 | Any alarm on PMS ID8 | X | X
Status flag | 28 | 100029 | 02 | Any alarm mains (Mains Command Unit) | X | X
Status flag | 31 | 100032 | 02 | Ready auto-start DG1 | X | X
Status flag | 32 | 100033 | 02 | Ready auto-start DG2 | X | X
Status flag | 33 | 100034 | 02 | Ready auto-start DG3 | X | X
Status flag | 34 | 100035 | 02 | Ready auto-start DG4 | X | X
Status flag | 35 | 100036 | 02 | Ready auto-start DG5 | X | X
Status flag | 36 | 100037 | 02 | Ready auto-start DG6 | X | X
Status flag | 37 | 100038 | 02 | Ready auto-start DG7 | X | X
Status flag | 38 | 100039 | 02 | Ready auto-start DG8 | X | X
Status flag | 53 | 100054 | 02 | Mains sync. inhibit | X | X
Status flag | 54 | 100055 | 02 | Any mains sync. inhibit | X | X
Digital input | 22500 | 122501 | 02 | Digital input 39 | X | X
Digital input | 22501 | 122502 | 02 | Digital input 40 | X | X
Digital input | 22502 | 122503 | 02 | Digital input 41 | X | X
Digital input | 22503 | 122504 | 02 | Digital input 42 | X | X
Digital input | 22504 | 122505 | 02 | Digital input 43 | X | X
Digital input | 22505 | 122506 | 02 | Digital input 44 | X | X
Digital input | 22506 | 122507 | 02 | Digital input 45 | X | X
Digital input | 22507 | 122508 | 02 | Digital input 46 | X | X
Digital input | 22513 | 122514 | 02 | Emergency stop input 4 | X | X
Digital input | 22590 | 122591 | 02 | Binary in 23 | X | X
Digital input | 22591 | 122592 | 02 | Binary in 22 | X | X
Digital input | 22592 | 122593 | 02 | Binary in 21 | X | X
Digital input | 22593 | 122594 | 02 | Binary in 20 | X | X
Digital input | 22594 | 122595 | 02 | CIO 116 no. 1. Input 10 | X | X
Digital input | 22595 | 122596 | 02 | CIO 116 no. 1. Input 11 | X | X
Digital input | 22596 | 122597 | 02 | CIO 116 no. 1. Input 12 | X | X
Digital input | 22597 | 122598 | 02 | CIO 116 no. 1. Input 13 | X | X
Digital input | 22598 | 122599 | 02 | CIO 116 no. 1. Input 14 | X | X
Digital input | 22599 | 122600 | 02 | CIO 116 no. 1. Input 15 | X | X
Digital input | 22600 | 122601 | 02 | CIO 116 no. 1. Input 16 | X | X
Digital input | 22601 | 122602 | 02 | CIO 116 no. 1. Input 17 | X | X
Digital input | 22602 | 122603 | 02 | CIO 116 no. 1. Input 19 | X | X
Digital input | 22603 | 122604 | 02 | CIO 116 no. 1. Input 20 | X | X
Digital input | 22604 | 122605 | 02 | CIO 116 no. 1. Input 21 | X | X
Digital input | 22605 | 122606 | 02 | CIO 116 no. 1. Input 22 | X | X
Digital input | 22606 | 122607 | 02 | CIO 116 no. 1. Input 23 | X | X
Digital input | 22607 | 122608 | 02 | CIO 116 no. 1. Input 24 | X | X
Digital input | 22608 | 122609 | 02 | CIO 116 no. 1. Input 25 | X | X
Digital input | 22609 | 122610 | 02 | CIO 116 no. 1. Input 26 | X | X
Digital input | 22610 | 122611 | 02 | CIO 116 no. 2. Input 10 | X | X
Digital input | 22611 | 122612 | 02 | CIO 116 no. 2. Input 11 | X | X
Digital input | 22612 | 122613 | 02 | CIO 116 no. 2. Input 12 | X | X
Digital input | 22613 | 122614 | 02 | CIO 116 no. 2. Input 13 | X | X
Digital input | 22614 | 122615 | 02 | CIO 116 no. 2. Input 14 | X | X
Digital input | 22615 | 122616 | 02 | CIO 116 no. 2. Input 15 | X | X
Digital input | 22616 | 122617 | 02 | CIO 116 no. 2. Input 16 | X | X
Digital input | 22617 | 122618 | 02 | CIO 116 no. 2. Input 17 | X | X
Digital input | 22618 | 122619 | 02 | CIO 116 no. 2. Input 19 | X | X
Digital input | 22619 | 122620 | 02 | CIO 116 no. 2. Input 20 | X | X
Digital input | 22620 | 122621 | 02 | CIO 116 no. 2. Input 21 | X | X
Digital input | 22621 | 122622 | 02 | CIO 116 no. 2. Input 22 | X | X
Digital input | 22622 | 122623 | 02 | CIO 116 no. 2. Input 23 | X | X
Digital input | 22623 | 122624 | 02 | CIO 116 no. 2. Input 24 | X | X
Digital input | 22624 | 122625 | 02 | CIO 116 no. 2. Input 25 | X | X
Digital input | 22625 | 122626 | 02 | CIO 116 no. 2. Input 26 | X | X
Digital input | 22626 | 122627 | 02 | CIO 116 no. 3. Input 10 | X | X
Digital input | 22627 | 122628 | 02 | CIO 116 no. 3. Input 11 | X | X
Digital input | 22628 | 122629 | 02 | CIO 116 no. 3. Input 12 | X | X
Digital input | 22629 | 122630 | 02 | CIO 116 no. 3. Input 13 | X | X
Digital input | 22630 | 122631 | 02 | CIO 116 no. 3. Input 14 | X | X
Digital input | 22631 | 122632 | 02 | CIO 116 no. 3. Input 15 | X | X
Digital input | 22632 | 122633 | 02 | CIO 116 no. 3. Input 16 | X | X
Digital input | 22633 | 122634 | 02 | CIO 116 no. 3. Input 17 | X | X
Digital input | 22634 | 122635 | 02 | CIO 116 no. 3. Input 19 | X | X
Digital input | 22635 | 122636 | 02 | CIO 116 no. 3. Input 20 | X | X
Digital input | 22636 | 122637 | 02 | CIO 116 no. 3. Input 21 | X | X
Digital input | 22637 | 122638 | 02 | CIO 116 no. 3. Input 22 | X | X
Digital input | 22638 | 122639 | 02 | CIO 116 no. 3. Input 23 | X | X
Digital input | 22639 | 122640 | 02 | CIO 116 no. 3. Input 24 | X | X
Digital input | 22640 | 122641 | 02 | CIO 116 no. 3. Input 25 | X | X
Digital input | 22641 | 122642 | 02 | CIO 116 no. 3. Input 26 | X | X
Digital input | 22674 | 122675 | 02 | CIO 308 no. 1. Input 8 | X | X
Digital input | 22675 | 122676 | 02 | CIO 308 no. 1. Input 11 | X | X
Digital input | 22676 | 122677 | 02 | CIO 308 no. 1. Input 14 | X | X
Digital input | 22677 | 122678 | 02 | CIO 308 no. 1. Input 17 | X | X
Digital input | 22678 | 122679 | 02 | CIO 308 no. 1. Input 20 | X | X
Digital input | 22679 | 122680 | 02 | CIO 308 no. 1. Input 23 | X | X
Digital input | 22680 | 122681 | 02 | CIO 308 no. 1. Input 26 | X | X
Digital input | 22681 | 122682 | 02 | CIO 308 no. 1. Input 29 | X | X
Digital input | 22682 | 122683 | 02 | CIO 308 no. 2. Input 8 | X | X
Digital input | 22683 | 122684 | 02 | CIO 308 no. 2. Input 11 | X | X
Digital input | 22684 | 122685 | 02 | CIO 308 no. 2. Input 14 | X | X
Digital input | 22685 | 122686 | 02 | CIO 308 no. 2. Input 17 | X | X
Digital input | 22686 | 122687 | 02 | CIO 308 no. 2. Input 20 | X | X
Digital input | 22687 | 122688 | 02 | CIO 308 no. 2. Input 23 | X | X
Digital input | 22688 | 122689 | 02 | CIO 308 no. 2. Input 26 | X | X
Digital input | 22689 | 122690 | 02 | CIO 308 no. 2. Input 29 | X | X
Digital input | 22690 | 122691 | 02 | CIO 308 no. 3. Input 8 | X | X
Digital input | 22691 | 122692 | 02 | CIO 308 no. 3. Input 11 | X | X
Digital input | 22692 | 122693 | 02 | CIO 308 no. 3. Input 14 | X | X
Digital input | 22693 | 122694 | 02 | CIO 308 no. 3. Input 17 | X | X
Digital input | 22694 | 122695 | 02 | CIO 308 no. 3. Input 20 | X | X
Digital input | 22695 | 122696 | 02 | CIO 308 no. 3. Input 23 | X | X
Digital input | 22696 | 122697 | 02 | CIO 308 no. 3. Input 26 | X | X
Digital input | 22697 | 122698 | 02 | CIO 308 no. 3. Input 29 | X | X
Digital output | 23003 | 123004 | 02 | Relay 9 | X | X
Digital output | 23004 | 123005 | 02 | Relay 10 | X | X
Digital output | 23005 | 123006 | 02 | Relay 11 | X | X
Digital output | 23006 | 123007 | 02 | Relay 12 | X | X
Digital output | 23007 | 123008 | 02 | Relay 13 | X | X
Digital output | 23008 | 123009 | 02 | Relay 14 | X | X
Digital output | 23026 | 123027 | 02 | Relay 16 | X | X
Digital output | 23027 | 123028 | 02 | Relay 15 | X | X
Digital output | 23028 | 123029 | 02 | Relay 18 | X | X
Digital output | 23029 | 123030 | 02 | Relay 17 | X | X
Digital output | 23030 | 123031 | 02 | Relay 5 | X | X
Digital output | 23031 | 123032 | 02 | Relay 6 | X | X
Digital output | 23056 | 123057 | 02 | CIO 208 no. 1. Output 9 | X | X
Digital output | 23057 | 123058 | 02 | CIO 208 no. 1. Output 11 | X | X
Digital output | 23058 | 123059 | 02 | CIO 208 no. 1. Output 13 | X | X
Digital output | 23059 | 123060 | 02 | CIO 208 no. 1. Output 15 | X | X
Digital output | 23060 | 123061 | 02 | CIO 208 no. 1. Output 18 | X | X
Digital output | 23061 | 123062 | 02 | CIO 208 no. 1. Output 21 | X | X
Digital output | 23062 | 123063 | 02 | CIO 208 no. 1. Output 24 | X | X
Digital output | 23063 | 123064 | 02 | CIO 208 no. 1. Output 27 | X | X
Digital output | 23064 | 123065 | 02 | CIO 208 no. 2. Output 9 | X | X
Digital output | 23065 | 123066 | 02 | CIO 208 no. 2. Output 11 | X | X
Digital output | 23066 | 123067 | 02 | CIO 208 no. 2. Output 13 | X | X
Digital output | 23067 | 123068 | 02 | CIO 208 no. 2. Output 15 | X | X
Digital output | 23068 | 123069 | 02 | CIO 208 no. 2. Output 18 | X | X
Digital output | 23069 | 123070 | 02 | CIO 208 no. 2. Output 21 | X | X
Digital output | 23070 | 123071 | 02 | CIO 208 no. 2. Output 24 | X | X
Digital output | 23071 | 123072 | 02 | CIO 208 no. 2. Output 27 | X | X
Digital output | 23072 | 123073 | 02 | CIO 208 no. 3. Output 9 | X | X
Digital output | 23073 | 123074 | 02 | CIO 208 no. 3. Output 11 | X | X
Digital output | 23074 | 123075 | 02 | CIO 208 no. 3. Output 13 | X | X
Digital output | 23075 | 123076 | 02 | CIO 208 no. 3. Output 15 | X | X
Digital output | 23076 | 123077 | 02 | CIO 208 no. 3. Output 18 | X | X
Digital output | 23077 | 123078 | 02 | CIO 208 no. 3. Output 21 | X | X
Digital output | 23078 | 123079 | 02 | CIO 208 no. 3. Output 24 | X | X
Digital output | 23079 | 123080 | 02 | CIO 208 no. 3. Output 27 | X | X
Digital output | 23080 | 123081 | 02 | CIO 116 no. 1 conf. status out | X | X
Digital output | 23081 | 123082 | 02 | CIO 116 no. 2 conf. status out | X | X
Digital output | 23082 | 123083 | 02 | CIO 116 no. 3 conf. status out | X | X
Digital output | 23083 | 123084 | 02 | CIO 208 no. 1 conf. status out | X | X
Digital output | 23084 | 123085 | 02 | CIO 208 no. 2 conf. status out | X | X
Digital output | 23085 | 123086 | 02 | CIO 208 no. 3 conf. status out | X | X
Digital output | 23086 | 123087 | 02 | CIO 308 no. 1 conf. status out | X | X
Digital output | 23087 | 123088 | 02 | CIO 308 no. 2 conf. status out | X | X
Digital output | 23088 | 123089 | 02 | CIO 308 no. 3 conf. status out | X | X

## Holding register (03;06;16)
Holding register (03;06;16)
Function group | Modbus address | Bit | PLC address | Modbus function code | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | SOLAR | BATT
Control command | 0 |  | 400001 | 03; 06; 16 | Power regulator setpoint - 0...100% of nominal power. Activated in menu 7501 | INT16s | AB | 0 |  | X | X
Control command | 1 |  | 400002 | 03; 06; 16 | cosPhi regulator setpoint - 60...100 stated as cosPhi value/100. The value 100 means cosPhi = 1.00 Activated in menu 7504 | INT16s | AB | 0 |  | X | X
Control command | 2 |  | 400003 | 03; 06; 16 | Reactive power regulator setpoint - +/-100% of nominal power. A negative value means capacitive reactive power, and a positive value means inductive reactive power. Activated in menu 7505 | INT16s | AB | 0 |  | X | X
Read area 1 (ASC to PLC/external system) | 46000 |  | 446001 | 03; 06; 16 | PV active power reference. | INT32s | ABCD | 0 | kW | X | X
Read area 1 (ASC to PLC/external system) | 46002 |  | 446003 | 03; 06; 16 | PV reactive power reference. | INT32s | ABCD | 0 | kVAr | X | X
Read area 1 (ASC to PLC/external system) | 46004 |  | 446005 | 03; 06; 16 | Emergency stop request to PV. 100: Activate emergency stop. 200: Deactivate emergency stop. | INT32s | ABCD | 0 |  | X | X
Read area 1 (ASC to PLC/external system) | 46008 |  | 446009 | 03; 06; 16 | Watch dog will increment continuously. To be used for PV/DEIF communication supervision on PV side. | INT32s | ABCD | 0 |  | X | X
Read area 1 (ASC to PLC/external system) | 46010 |  | 446011 | 03; 06; 16 | Active power delivered by the gensets. | INT32s | ABCD | 0 | kW* | X | X
Read area 1 (ASC to PLC/external system) | 46012 |  | 446013 | 03; 06; 16 | Online nominal genset power. | INT32s | ABCD | 0 | kW* | X | X
Read area 1 (ASC to PLC/external system) | 46014 |  | 446015 | 03; 06; 16 | Reactive power delivered by the gensets. | INT32s | ABCD | 0 | kVAr | X | X
Read area 1 (ASC to PLC/external system) | 46016 |  | 446017 | 03; 06; 16 | Minimum genset load required. | INT32s | ABCD | 0 | kW | X | X
Read area 1 (ASC to PLC/external system) | 46018 |  | 446019 | 03; 06; 16 | Mains active power. | INT32s | ABCD | 0 | kW | X | X
Read area 1 (ASC to PLC/external system) | 46020 |  | 446021 | 03; 06; 16 | Mains reactive power. | INT32s | ABCD | 0 | kVAr | X | X
Read area 1 (ASC to PLC/external system) | 46022 |  | 446023 | 03; 06; 16 | Amount of diesel used since last reset. | INT32s | ABCD | 0 | liter | X | X
Read area 1 (ASC to PLC/external system) | 46024 |  | 446025 | 03; 06; 16 | Diesel consumption. | INT32s | ABCD | 1 | liter/h | X | X
Read area 1 (ASC to PLC/external system) | 46026 |  | 446027 | 03; 06; 16 | PV active power reference. | INT16s | AB | 0 | % | X
Read area 1 (ASC to PLC/external system) | 46027 |  | 446028 | 03; 06; 16 | PV curtailment active. 0: Inactive. 1: Active | INT16s | AB | 0 |  | X
Read area 1 (ASC to PLC/external system) | 46028 |  | 446029 | 03; 06; 16 | Curtailed energy counter total. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 46030 |  | 446031 | 03; 06; 16 | Curtailed energy counter month. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 46032 |  | 446033 | 03; 06; 16 | Curtailed energy counter week. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 46034 |  | 446035 | 03; 06; 16 | Curtailed energy counter day. | INT32s | ABCD | 0 | kW | X
Read area 1 (ASC to PLC/external system) | 46036 |  | 446037 | 03; 06; 16 | Plane of array irradiation sensor 1 | INT16s | AB | 0 | W/m2 | X
Read area 1 (ASC to PLC/external system) | 46037 |  | 446038 | 03; 06; 16 | Plane of array irradiation sensor 2 | INT16s | AB | 0 | W/m2 | X
Read area 1 (ASC to PLC/external system) | 46038 |  | 446039 | 03; 06; 16 | Plane of array irradiation sensor 3 | INT16s | AB | 0 | W/m2 | X
Read area 1 (ASC to PLC/external system) | 46039 |  | 446040 | 03; 06; 16 | Plane of array irradiation sensor weighted | INT16s | AB | 0 | W/m2 | X
Read area 1 (ASC to PLC/external system) | 46040 |  | 446041 | 03; 06; 16 | Back of module temperature sensor 1 | INT16s | AB | 1 | Deg C | X
Read area 1 (ASC to PLC/external system) | 46041 |  | 446042 | 03; 06; 16 | Back of module temperature sensor 2 | INT16s | AB | 1 | Deg C | X
Read area 1 (ASC to PLC/external system) | 46042 |  | 446043 | 03; 06; 16 | Back of module temperature sensor 3 | INT16s | AB | 1 | Deg C | X
Read area 1 (ASC to PLC/external system) | 46042 |  | 446043 | 03; 06; 16 | Back of module temperature sensor weighted | INT16s | AB | 1 | Deg C | X
Read area 1 (ASC to PLC/external system) | 46044 |  | 446045 | 03; 06; 16 | Instant maximum active power that can be generated by PV panels. | INT32s | ABCD | 0 | kW | X
Read area 1 (ASC to PLC/external system) | 46046 |  | 446047 | 03; 06; 16 | Instant maximum apparent power that can be generated by inverter(s). | INT32s | ABCD | 0 | kVA | X
Read area 1 (ASC to PLC/external system) | 46048 |  | 446049 | 03; 06; 16 | Instant maximum reactive power that can be generated by inverter(s) in first quadrant. | INT32s | ABCD | 0 | kVAr | X
Read area 1 (ASC to PLC/external system) | 46050 |  | 446051 | 03; 06; 16 | Instant maximum reactive power that can be generated by inverter(s) in fourth quadrant. | INT32s | ABCD | 0 | kVAr | X
Read area 1 (ASC to PLC/external system) | 46052 |  | 446053 | 03; 06; 16 | Active PV power production. | INT32s | ABCD | 0 | kW | X | X
Read area 1 (ASC to PLC/external system) | 46054 |  | 446055 | 03; 06; 16 | Active PV apparent power production. | INT32s | ABCD | 0 | kVA | X | X
Read area 1 (ASC to PLC/external system) | 46056 |  | 446057 | 03; 06; 16 | Active PV reactive power production. | INT32s | ABCD | 0 | kVAr | X | X
Read area 1 (ASC to PLC/external system) | 46058 |  | 446059 | 03; 06; 16 | Spinning reserve generated by this PV. | INT32s | ABCD | 0 | kW | X
Read area 1 (ASC to PLC/external system) | 46060 |  | 446061 | 03; 06; 16 | Spinning reserve generated by all the PV’s | INT32s | ABCD | 0 | kW | X
Read area 1 (ASC to PLC/external system) | 46062 |  | 446063 | 03; 06; 16 | Global horizontal irradiation | INT16s | AB | 0 | W/m2 | X
Read area 1 (ASC to PLC/external system) | 46063 |  | 446064 | 03; 06; 16 | Ambient temperature | INT16s | AB | 1 | Deg C | X
Read area 1 (ASC to PLC/external system) | 46064 |  | 446065 | 03; 06; 16 | Relative humidity | INT16s | AB | 0 | % | X
Read area 1 (ASC to PLC/external system) | 46065 |  | 446066 | 03; 06; 16 | Barometric pressure | INT16s | AB | 0 | hPa | X
Read area 1 (ASC to PLC/external system) | 46066 |  | 446067 | 03; 06; 16 | Wind speed | INT16s | AB | 0 | m/s | X
Read area 1 (ASC to PLC/external system) | 46067 |  | 446068 | 03; 06; 16 | Wind direction | INT16s | AB | 0 | deg | X
Read area 1 (ASC to PLC/external system) | 46068 |  | 446069 | 03; 06; 16 | Rain fall | INT16s | AB | 0 | mm | X
Read area 1 (ASC to PLC/external system) | 46069 |  | 446070 | 03; 06; 16 | Snow depth | INT16s | AB | 0 | mm | X
Read area 1 (ASC to PLC/external system) | 46070 |  | 446071 | 03; 06; 16 | Curtailed energy counter year. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 46072 |  | 446073 | 03; 06; 16 | Performance ratio total | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 46073 |  | 446074 | 03; 06; 16 | Performance ratio year | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 46074 |  | 446075 | 03; 06; 16 | Performance ratio month | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 46075 |  | 446076 | 03; 06; 16 | Performance ratio week | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 46076 |  | 446077 | 03; 06; 16 | Performance ratio day | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 46077 |  | 446078 | 03; 06; 16 | Total genset energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 46079 |  | 446080 | 03; 06; 16 | Yearly genset energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 46081 |  | 446082 | 03; 06; 16 | Monthly genset energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 46083 |  | 446084 | 03; 06; 16 | Weekly genset energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 46085 |  | 446086 | 03; 06; 16 | Daily genset energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 46087 |  | 446088 | 03; 06; 16 | PV penetration total | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 46088 |  | 446089 | 03; 06; 16 | Yearly PV penetration | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 46089 |  | 446090 | 03; 06; 16 | Monthly PV penetration | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 46090 |  | 446091 | 03; 06; 16 | Weekly PV penetration | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 46091 |  | 446092 | 03; 06; 16 | Daily PV penetration | INT16s | AB | 1 | % | X
Write area 1 (PLC/external system to ASC) | 46100 |  | 446101 | 03; 06; 16 | Available PV power. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_P_available will be used by logics. | INT32s | ABCD | 0 | kW* | X | X
Write area 1 (PLC/external system to ASC) | 46102 |  | 446103 | 03; 06; 16 | Active PV power. | INT32s | ABCD | 0 | kW* | X | X
Write area 1 (PLC/external system to ASC) | 46110 |  | 446111 | 03; 06; 16 | Available PV apparent power. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_S_available will be used by logics. | INT32s | ABCD | 0 | kVA* | X
Write area 1 (PLC/external system to ASC) | 46112 |  | 446113 | 03; 06; 16 | External PV spinning reserve request | INT32s | ABCD | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 46114 |  | 446115 | 03; 06; 16 | Current operation mode of the PV plant: 200: Ready for operation | INT32s | ABCD | 0 |  | X
Write area 1 (PLC/external system to ASC) | 46116 |  | 446117 | 03; 06; 16 | Watch dog will increment continuously. To be used for PV/DEIF communication supervision on DEIF side. | INT32s | ABCD | 0 |  | X | X
Write area 1 (PLC/external system to ASC) | 46120 |  | 446121 | 03; 06; 16 | To raise warning and shutdown alarms on DEIF side 100: Warning. 200: Shutdown. 300: Warning & Shutdown. | INT32s | ABCD | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46122 |  | 446123 | 03; 06; 16 | Reactive PV power | INT32s | ABCD | 0 | kvar* | X | X
Write area 1 (PLC/external system to ASC) | 46124 |  | 446125 | 03; 06; 16 | Apparent PV power | INT32s | ABCD | 0 | kVA* | X | X
Write area 1 (PLC/external system to ASC) | 46128 |  | 446129 | 03; 06; 16 | Available PV reactive power in Q1. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_Q_available_Q1 will be used by logics. | INT32s | ABCD | 0 | kVAr* | X
Write area 1 (PLC/external system to ASC) | 46130 |  | 446131 | 03; 06; 16 | Plane of array irradiation sensor 1 | INT16s | AB | 0 | W/m2 | X
Write area 1 (PLC/external system to ASC) | 46131 |  | 446132 | 03; 06; 16 | Plane of array irradiation sensor 2 | INT16s | AB | 0 | W/m2 | X
Write area 1 (PLC/external system to ASC) | 46132 |  | 446133 | 03; 06; 16 | Plane of array irradiation sensor 3 | INT16s | AB | 0 | W/m2 | X
Write area 1 (PLC/external system to ASC) | 46133 |  | 446134 | 03; 06; 16 | Back of module temperature sensor 1 | INT16s | AB | 1 | Deg C | X
Write area 1 (PLC/external system to ASC) | 46134 |  | 446135 | 03; 06; 16 | Back of module temperature sensor 2 | INT16s | AB | 1 | Deg C | X
Write area 1 (PLC/external system to ASC) | 46135 |  | 446136 | 03; 06; 16 | Back of module temperature sensor 3 | INT16s | AB | 1 | Deg C | X
Write area 1 (PLC/external system to ASC) | 46136 |  | 446137 | 03; 06; 16 | Global horizontal irradiation [W/m2] | INT16s | AB | 0 | W/m2 | X
Write area 1 (PLC/external system to ASC) | 46137 |  | 446138 | 03; 06; 16 | Ambient temperature [C] | INT16s | AB | 1 | Deg C | X
Write area 1 (PLC/external system to ASC) | 46138 |  | 446139 | 03; 06; 16 | Relative humidity [%] | INT16s | AB | 0 | % | X
Write area 1 (PLC/external system to ASC) | 46139 |  | 446140 | 03; 06; 16 | Barometric pressure [hPa] | INT16s | AB | 0 | hPa | X
Write area 1 (PLC/external system to ASC) | 46140 |  | 446141 | 03; 06; 16 | Wind speed [m/s] | INT16s | AB | 0 | m/s | X
Write area 1 (PLC/external system to ASC) | 46141 |  | 446142 | 03; 06; 16 | Wind direction [deg] | INT16s | AB | 0 | deg | X
Write area 1 (PLC/external system to ASC) | 46142 |  | 446143 | 03; 06; 16 | Rain fall [mm] | INT16s | AB | 0 | mm | X
Write area 1 (PLC/external system to ASC) | 46143 |  | 446144 | 03; 06; 16 | Snow depth [mm] | INT16s | AB | 0 | mm | X
Write area 1 (PLC/external system to ASC) | 46144 |  | 446145 | 03; 06; 16 | Available PV reactive power in Q2. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_Q_available_Q2 will be used by logics. | INT32s | ABCD | 0 |  | X
Write area 1 (PLC/external system to ASC) | 46146 |  | 446147 | 03; 06; 16 | Available PV reactive power [kVAr*] in Q3. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_Q_available_Q3 will be used by logics. | INT32s | ABCD | 0 |  | X
Write area 1 (PLC/external system to ASC) | 46148 |  | 446149 | 03; 06; 16 | Available PV reactive power [kVAr*] in Q4. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_Q_available_Q4 will be used by logics. | INT32s | ABCD | 0 |  | X
Write area 1 (PLC/external system to ASC) | 46150 |  | 446151 | 03; 06; 16 | Active power of genset 1. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46151 |  | 446152 | 03; 06; 16 | Active power of genset 2. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46152 |  | 446153 | 03; 06; 16 | Active power of genset 3. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46153 |  | 446154 | 03; 06; 16 | Active power of genset 4. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46154 |  | 446155 | 03; 06; 16 | Active power of genset 5. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46155 |  | 446156 | 03; 06; 16 | Active power of genset 6. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46156 |  | 446157 | 03; 06; 16 | Active power of genset 7. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46157 |  | 446158 | 03; 06; 16 | Active power of genset 8. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46158 |  | 446159 | 03; 06; 16 | Active power of genset 9. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46159 |  | 446160 | 03; 06; 16 | Active power of genset 10. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46160 |  | 446161 | 03; 06; 16 | Active power of genset 11. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46161 |  | 446162 | 03; 06; 16 | Active power of genset 12. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46162 |  | 446163 | 03; 06; 16 | Active power of genset 13. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46163 |  | 446164 | 03; 06; 16 | Active power of genset 14. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46164 |  | 446165 | 03; 06; 16 | Active power of genset 15. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46165 |  | 446166 | 03; 06; 16 | Active power of genset 16. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46166 |  | 446167 | 03; 06; 16 | Reactive power of genset 1. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46167 |  | 446168 | 03; 06; 16 | Reactive power of genset 2. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46168 |  | 446169 | 03; 06; 16 | Reactive power of genset 3. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46169 |  | 446170 | 03; 06; 16 | Reactive power of genset 4. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46170 |  | 446171 | 03; 06; 16 | Reactive power of genset 5. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46171 |  | 446172 | 03; 06; 16 | Reactive power of genset 6. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46172 |  | 446173 | 03; 06; 16 | Reactive power of genset 7. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46173 |  | 446174 | 03; 06; 16 | Reactive power of genset 8. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46174 |  | 446175 | 03; 06; 16 | Reactive power of genset 9. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46175 |  | 446176 | 03; 06; 16 | Reactive power of genset 10. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46176 |  | 446177 | 03; 06; 16 | Reactive power of genset 11. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46177 |  | 446178 | 03; 06; 16 | Reactive power of genset 12. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46178 |  | 446179 | 03; 06; 16 | Reactive power of genset 13. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46179 |  | 446180 | 03; 06; 16 | Reactive power of genset 14. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46180 |  | 446181 | 03; 06; 16 | Reactive power of genset 15. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46181 |  | 446182 | 03; 06; 16 | Reactive power of genset 16. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46182 |  | 446183 | 03; 06; 16 | Active mains power. | INT16s | AB | 0 | kW | X | X
Write area 1 (PLC/external system to ASC) | 46183 |  | 446184 | 03; 06; 16 | Reactive mains power. | INT16s | AB | 0 | kvar | X | X
Write area 1 (PLC/external system to ASC) | 46184 |  | 446185 | 03; 06; 16 | GB closed feedback bitwise from genset 01..16 | INT16s | AB | 0 |  | X | X
Write area 1 (PLC/external system to ASC) | 46185 |  | 446186 | 03; 06; 16 | MB closed feedback bitwise from genset 01..16 | INT16s | AB | 0 |  | X | X
Write area 1 (PLC/external system to ASC) | 46186 |  | 446187 | 03; 06; 16 | MB open feedback bitwise from genset 01..16 | INT16s | AB | 0 |  | X | X
Read area 2 (ASC to PLC/external system) | 46200 |  | 446201 | 03; 06; 16 | Total mains imported energy counter. | INT32s | ABCD | 0 | kWh | X | X
Read area 2 (ASC to PLC/external system) | 46202 |  | 446203 | 03; 06; 16 | Yearly mains imported energy counter. | INT32s | ABCD | 0 | kWh | X | X
Read area 2 (ASC to PLC/external system) | 46204 |  | 446205 | 03; 06; 16 | Monthly mains imported energy counter. | INT32s | ABCD | 0 | kWh | X | X
Read area 2 (ASC to PLC/external system) | 46206 |  | 446207 | 03; 06; 16 | Weekly mains imported energy counter. | INT32s | ABCD | 0 | kWh | X | X
Read area 2 (ASC to PLC/external system) | 46208 |  | 446209 | 03; 06; 16 | Daily mains imported energy counter. | INT32s | ABCD | 0 | kWh | X | X
Read area 2 (ASC to PLC/external system) | 46210 |  | 446211 | 03; 06; 16 | Total mains exported energy counter. | INT32s | ABCD | 0 | kWh | X | X
Read area 2 (ASC to PLC/external system) | 46212 |  | 446213 | 03; 06; 16 | Yearly mains exported energy counter. | INT32s | ABCD | 0 | kWh | X | X
Read area 2 (ASC to PLC/external system) | 46214 |  | 446215 | 03; 06; 16 | Monthly mains exported energy counter. | INT32s | ABCD | 0 | kWh | X | X
Read area 2 (ASC to PLC/external system) | 46216 |  | 446217 | 03; 06; 16 | Weekly mains exported energy counter. | INT32s | ABCD | 0 | kWh | X | X
Read area 2 (ASC to PLC/external system) | 46218 |  | 446219 | 03; 06; 16 | Daily mains exported energy counter. | INT32s | ABCD | 0 | kWh | X | X
Read area 2 (ASC to PLC/external system) | 46220 |  | 446221 | 03; 06; 16 | PV power available and inteded for charging | INT32s | ABCD | 0 | kW | X
Read area 2 (ASC to PLC/external system) | 46222 |  | 446223 | 03; 06; 16 | Mains power available and inteded for charging | INT32s | ABCD | 0 | kW | X | X
Read area 2 (ASC to PLC/external system) | 46224 |  | 446225 | 03; 06; 16 | DG power available and inteded for charging | INT32s | ABCD | 0 | kW | X | X
Read area 2 (ASC to PLC/external system) | 46226 |  | 446227 | 03; 06; 16 | PV power charging active | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 46227 |  | 446228 | 03; 06; 16 | MAINS power charging active | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 46228 |  | 446229 | 03; 06; 16 | DG power charging active | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 46229 |  | 446230 | 03; 06; 16 | Power charging active | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 46230 |  | 446231 | 03; 06; 16 | Battery fully charged | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 46231 |  | 446232 | 03; 06; 16 | Energy source functionality OK | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 46232 |  | 446233 | 03; 06; 16 | Power source functionality OK | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 46233 |  | 446234 | 03; 06; 16 | FUNC MODE: 0: Dispatch only. 1: Power. 2: Energy. | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 46234 |  | 446235 | 03; 06; 16 | REG MODE: 0: Volt/Freq. 1: Droop. 2: P/Q | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 46300 |  | 446301 | 03; 06; 16 | State of charge (SOC) | INT16s | AB | 0 | % |  | X
Read/Write (Battery) | 46301 |  | 446302 | 03; 06; 16 | State of energy (SOE) | INT32s | ABCD | 0 | kWh |  | X
Read/Write (Battery) | 46303 |  | 446304 | 03; 06; 16 | Full charged energy | INT32s | ABCD | 0 | kWh |  | X
Read/Write (Battery) | 46307 |  | 446308 | 03; 06; 16 | State of energy (SOE) TEMPCOMP | INT32s | ABCD | 0 | kWh |  | X
Read/Write (Battery) | 46309 |  | 446310 | 03; 06; 16 | Discharging capacity | INT32s | ABCD | 0 | kW |  | X
Read/Write (Battery) | 46311 |  | 446312 | 03; 06; 16 | Charging capacity | INT32s | ABCD | 0 | kW |  | X
Read/Write (Battery) | 46313 |  | 446314 | 03; 06; 16 | Apparent power capacity | INT32s | ABCD | 0 | kVA |  | X
Read/Write (Battery) | 46315 |  | 446316 | 03; 06; 16 | Frequency droop slope (Tesla: No decimals) | INT16s | AB | 1 | %P/Hz |  | X
Read/Write (Battery) | 46316 |  | 446317 | 03; 06; 16 | Voltage droop slope (Tesla: No decimals) | INT16s | AB | 1 | %Q/V |  | X
Read/Write (Battery) | 46317 |  | 446318 | 03; 06; 16 | State of health (SOH) | INT16s | AB | 0 | % |  | X
Read/Write (Battery) | 46318 |  | 446319 | 03; 06; 16 | BMS DC output voltage | INT16s | AB | 0 | Vdc |  | X
Read/Write (Battery) | 46319 |  | 446320 | 03; 06; 16 | Charging total | INT32s | ABCD | 1 | kWh |  | X
Read/Write (Battery) | 46321 |  | 446322 | 03; 06; 16 | Discharging total | INT32s | ABCD | 1 | kWh |  | X
Read/Write (Battery) | 46323 |  | 446324 | 03; 06; 16 | BMS state | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 46324 |  | 446325 | 03; 06; 16 | PCS state | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 46325 |  | 446326 | 03; 06; 16 | PCS DC input voltage from the battery | INT16s | AB | 1 | V |  | X
Read/Write (Battery) | 46326 |  | 446327 | 03; 06; 16 | DC current battery | INT16s | AB | 1 | A |  | X
Read/Write (Battery) | 46327 |  | 446328 | 03; 06; 16 | Temperature battery | INT16s | AB | 1 | Deg C |  | X
Read/Write (Battery) | 46328 |  | 446329 | 03; 06; 16 | Charge AH | INT32s | ABCD | 0 | kW |  | X
Read/Write (Battery) | 46330 |  | 446331 | 03; 06; 16 | Discharge AH | INT32s | ABCD | 0 | kW |  | X
Read/Write (Battery) | 46332 |  | 446333 | 03; 06; 16 | Energy absorbed | INT32s | ABCD | 0 | Wh |  | X
Read/Write (Battery) | 46334 |  | 446335 | 03; 06; 16 | Energy FED | INT32s | ABCD | 0 | Wh |  | X
Read/Write (Battery) | 46336 |  | 446337 | 03; 06; 16 | ESS Voltage L1-L2 | INT16s | AB | 0 | V |  | X
Read/Write (Battery) | 46337 |  | 446338 | 03; 06; 16 | ESS Voltage L2-L3 | INT16s | AB | 0 | V |  | X
Read/Write (Battery) | 46338 |  | 446339 | 03; 06; 16 | ESS Voltage L3-L1 | INT16s | AB | 0 | V |  | X
Read/Write (Battery) | 46339 |  | 446340 | 03; 06; 16 | ESS Voltage L1-N | INT16s | AB | 0 | V |  | X
Read/Write (Battery) | 46340 |  | 446341 | 03; 06; 16 | ESS Voltage L2-N | INT16s | AB | 0 | V |  | X
Read/Write (Battery) | 46341 |  | 446342 | 03; 06; 16 | ESS Voltage L3-N | INT16s | AB | 0 | V |  | X
Read/Write (Battery) | 46342 |  | 446343 | 03; 06; 16 | Frequency | INT16s | AB | 2 | Hz |  | X
Read/Write (Battery) | 46343 |  | 446344 | 03; 06; 16 | BCU/PCS alarm status | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 46344 |  | 446345 | 03; 06; 16 | Max Charge voltage | INT16s | AB | 1 | V |  | X
Read/Write (Battery) | 46345 |  | 446346 | 03; 06; 16 | BMS max charge current | INT32s | AB | 2 | A |  | X
Read/Write (Battery) | 46347 |  | 446348 | 03; 06; 16 | min. discharge voltage | INT16s | AB | 1 | V |  | X
Read/Write (Battery) | 46348 |  | 446349 | 03; 06; 16 | max discharge current | INT32s | AB | 2 | A |  | X
Read/Write (Battery) | 46350 |  | 446351 | 03; 06; 16 | Inductive Q capacity | INT32s | ABCD | 0 | kvar |  | X
Read/Write (Battery) | 46352 |  | 446353 | 03; 06; 16 | Capacitive Q capacity | INT32s | ABCD | 0 | kvar |  | X
Read/Write (Battery) | 46354 |  | 446355 | 03; 06; 16 | PDS/Sub-module 1 power | INT32s | ABCD | 1 | kW |  | X
Read/Write (Battery) | 46356 |  | 446357 | 03; 06; 16 | Sub-module 2 power | INT32s | ABCD | 1 | kW |  | X
Read/Write (Battery) | 46358 |  | 446359 | 03; 06; 16 | PDS/Sub-module 1 state | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 46359 |  | 446360 | 03; 06; 16 | Sub-module 2 state | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 46360 |  | 446361 | 03; 06; 16 | BMS alarm status | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 46361 |  | 446362 | 03; 06; 16 | PCS internal contactor state | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 46362 |  | 446363 | 03; 06; 16 | BMS rack contactor state 0 = Open, 1 = Closed | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 46364 |  | 446365 | 03; 06; 16 | Active power mode: 0 = Internal, 1 = P/Q mode, 2 = V/f mode, 3 = Droop, 0xFF = Unknown | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 46365 |  | 446366 | 03; 06; 16 | ESS identifier | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 46366 |  | 446367 | 03; 06; 16 | PCS DC current | INT32s | AB | 2 | A |  | X
Read/Write (Battery) | 46368 |  | 446369 | 03; 06; 16 | PDS alarm status | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 46369 |  | 446370 | 03; 06; 16 | ESS configuration | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 46370 |  | 446371 | 03; 06; 16 | BMS configuration | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 46371 |  | 446372 | 03; 06; 16 | Minimum battery cell voltage | INT16s | AB | 3 | V |  | X
Read/Write (Battery) | 46372 |  | 446373 | 03; 06; 16 | Average battery cell voltage | INT16s | AB | 3 | V |  | X
Read/Write (Battery) | 46373 |  | 446374 | 03; 06; 16 | Maximum battery cell voltage | INT16s | AB | 3 | V |  | X
Read/Write (Battery) | 46374 |  | 446375 | 03; 06; 16 | Minimum cell temperature | INT16s | AB | 1 | Deg C |  | X
Read/Write (Battery) | 46375 |  | 446376 | 03; 06; 16 | Average cell temperature | INT16s | AB | 1 | Deg C |  | X
Read/Write (Battery) | 46376 |  | 446377 | 03; 06; 16 | Maximum cell temperature | INT16s | AB | 1 | Deg C |  | X
Read/Write (Battery) | 46377 |  | 446378 | 03; 06; 16 | PCS fault flags | INT32u | AB | 0 |  |  | X
Read/Write (Battery) | 46379 |  | 446380 | 03; 06; 16 | PCS warning flags | INT32u | AB | 0 |  |  | X
Read/Write (Battery) | 46381 |  | 446382 | 03; 06; 16 | Ext. PDS/Sub-module 1 input DC voltage | INT16u | AB | 1 | V |  | X
Read/Write (Battery) | 46382 |  | 446383 | 03; 06; 16 | Int. PDS/Sub-module 2 input DC voltage | INT16u | AB | 1 | V |  | X
Read/Write (Battery) | 46383 |  | 446384 | 03; 06; 16 | Ext. PDS/Sub-module 1 output DC voltage | INT16u | AB | 1 | V |  | X
Read/Write (Battery) | 46384 |  | 446385 | 03; 06; 16 | Int. PDS/Sub-module 2 output DC voltage | INT16u | AB | 1 | V |  | X
Read/Write (Battery) | 46385 |  | 446386 | 03; 06; 16 | Ext. PDS/Sub-module 1 output DC current | INT32s | AB | 2 | A |  | X
Read/Write (Battery) | 46387 |  | 446388 | 03; 06; 16 | Int. PDS/Sub-module 2 output DC current | INT32s | AB | 2 | A |  | X
Read/Write (Battery) | 46389 |  | 446390 | 03; 06; 16 | ESS L1 current | INT16s | AB | 0 | A |  | X
Read/Write (Battery) | 46390 |  | 446391 | 03; 06; 16 | ESS L2 current | INT16s | AB | 0 | A |  | X
Read/Write (Battery) | 46391 |  | 446392 | 03; 06; 16 | ESS L3 current | INT16s | AB | 0 | A |  | X
Weather area | 46400 |  | 446401 | 03; 06; 16 | Weather serial number 01-02 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46401 |  | 446402 | 03; 06; 16 | Weather serial number 03-04 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46402 |  | 446403 | 03; 06; 16 | Weather serial number 05-06 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46403 |  | 446404 | 03; 06; 16 | Weather serial number 07-08 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46404 |  | 446405 | 03; 06; 16 | Weather serial number 09-10 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46405 |  | 446406 | 03; 06; 16 | Weather serial number 11-12 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46406 |  | 446407 | 03; 06; 16 | Weather serial number 13-14 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46407 |  | 446408 | 03; 06; 16 | Weather serial number 15-16 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46408 |  | 446409 | 03; 06; 16 | Weather serial number 17-18 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46409 |  | 446410 | 03; 06; 16 | Weather serial number 19-20 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46410 |  | 446411 | 03; 06; 16 | Weather serial number 21-22 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46411 |  | 446412 | 03; 06; 16 | Weather serial number 23-24 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46412 |  | 446413 | 03; 06; 16 | Weather serial number 25-26 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46413 |  | 446414 | 03; 06; 16 | Weather serial number 27-28 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46414 |  | 446415 | 03; 06; 16 | Weather serial number 29-30 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46415 |  | 446416 | 03; 06; 16 | Weather serial number 31-32 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46416 |  | 446417 | 03; 06; 16 | Weather model 01-02 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46417 |  | 446418 | 03; 06; 16 | Weather model 03-04 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46418 |  | 446419 | 03; 06; 16 | Weather model 05-06 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46419 |  | 446420 | 03; 06; 16 | Weather model 07-08 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46420 |  | 446421 | 03; 06; 16 | Weather model 09-10 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46421 |  | 446422 | 03; 06; 16 | Weather model 11-12 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46422 |  | 446423 | 03; 06; 16 | Weather model 13-14 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46423 |  | 446424 | 03; 06; 16 | Weather model 15-16 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46424 |  | 446425 | 03; 06; 16 | Weather model 17-18 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46425 |  | 446426 | 03; 06; 16 | Weather model 19-20 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46426 |  | 446427 | 03; 06; 16 | Weather model 21-22 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46427 |  | 446428 | 03; 06; 16 | Weather model 23-24 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46428 |  | 446429 | 03; 06; 16 | Weather model 25-26 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46429 |  | 446430 | 03; 06; 16 | Weather model 27-28 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46430 |  | 446431 | 03; 06; 16 | Weather model 29-30 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46431 |  | 446432 | 03; 06; 16 | Weather model 31-32 (format maker-dependent) | string | AB | 0 |  | X
Weather area | 46432 |  | 446433 | 03; 06; 16 | Plane of array irradiation sensor 1 | INT16s | AB | 0 | W/m2 | X
Weather area | 46433 |  | 446434 | 03; 06; 16 | Plane of array irradiation sensor 2 | INT16s | AB | 0 | W/m2 | X
Weather area | 46434 |  | 446435 | 03; 06; 16 | Plane of array irradiation sensor 3 | INT16s | AB | 0 | W/m2 | X
Weather area | 46435 |  | 446436 | 03; 06; 16 | Global horizontal irradiation | INT16s | AB | 0 | W/m2 | X
Weather area | 46436 |  | 446437 | 03; 06; 16 | Back of module temperature sensor 1 | INT16s | AB | 0 | Deg C | X
Weather area | 46437 |  | 446438 | 03; 06; 16 | Back of module temperature sensor 2 | INT16s | AB | 0 | Deg C | X
Weather area | 46438 |  | 446439 | 03; 06; 16 | Back of module temperature sensor 3 | INT16s | AB | 0 | Deg C | X
Weather area | 46439 |  | 446440 | 03; 06; 16 | Back of module temperature sensor - global | INT16s | AB | 0 | Deg C | X
Weather area | 46440 |  | 446441 | 03; 06; 16 | Global horizontal irradiation | INT16s | AB | 0 | W/m2 | X
Weather area | 46441 |  | 446442 | 03; 06; 16 | Ambient temperature | INT16s | AB | 1 | Deg C | X
Weather area | 46442 |  | 446443 | 03; 06; 16 | Relative humidity | INT16s | AB | 0 | % | X
Weather area | 46443 |  | 446444 | 03; 06; 16 | Barometric pressure | INT16s | AB | 0 | hPa | X
Weather area | 46444 |  | 446445 | 03; 06; 16 | Wind speed | INT16s | AB | 0 | m/s | X
Weather area | 46445 |  | 446446 | 03; 06; 16 | Wind direction | INT16s | AB | 0 | deg | X
Weather area | 46446 |  | 446447 | 03; 06; 16 | Rain fall | INT16s | AB | 0 | mm | X
Weather area | 46447 |  | 446448 | 03; 06; 16 | Snow depth | INT16s | AB | 0 | mm | X
Weather area | 46448 |  | 446449 | 03; 06; 16 | Solar cell production 1 | INT16s | AB | 0 | W/m2 | X
Weather area | 46449 |  | 446450 | 03; 06; 16 | Solar cell production 2 | INT16s | AB | 0 | W/m2 | X
Control time command | 58000 |  | 458001 | 03; 06; 16 | Year (2003-2099) | INT16s | AB | 0 |  | X | X
Control time command | 58001 |  | 458002 | 03; 06; 16 | Month (1-12) | INT16s | AB | 0 |  | X | X
Control time command | 58002 |  | 458003 | 03; 06; 16 | Date (1-31) | INT16s | AB | 0 |  | X | X
Control time command | 58003 |  | 458004 | 03; 06; 16 | Day (1-7, Monday - Sunday) | INT16s | AB | 0 |  | X | X
Control time command | 58004 |  | 458005 | 03; 06; 16 | Hour (0-23) | INT16s | AB | 0 |  | X | X
Control time command | 58005 |  | 458006 | 03; 06; 16 | Min (0-59) | INT16s | AB | 0 |  | X | X
Control time command | 58006 |  | 458007 | 03; 06; 16 | Sec (0-59) | INT16s | AB | 0 |  | X | X

## Input register (04)
Input register (04)
Function group | Modbus address | Bit | PLC address | Modbus function code | Channel | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | SOLAR | BATT
APPL version | 500 |  | 300501 | 04 |  | Application version | INT16s | AB | 0 |  | X | X
AC measurement | 501 |  | 300502 | 04 |  | PV/ESS Voltage L1-L2 | INT16s | AB | 0 | V | X | X
AC measurement | 502 |  | 300503 | 04 |  | PV/ESS Voltage L2-L3 | INT16s | AB | 0 | V | X | X
AC measurement | 503 |  | 300504 | 04 |  | PV/ESS Voltage L3-L1 | INT16s | AB | 0 | V | X | X
AC measurement | 504 |  | 300505 | 04 |  | PV/ESS voltage L1-N | INT16s | AB | 0 | V | X | X
AC measurement | 505 |  | 300506 | 04 |  | PV/ESS voltage L2-N | INT16s | AB | 0 | V | X | X
AC measurement | 506 |  | 300507 | 04 |  | PV/ESS voltage L3-N | INT16s | AB | 0 | V | X | X
AC measurement | 507 |  | 300508 | 04 |  | PV/ESS frequency L1 | INT16s | AB | 2 | Hz | X | X
AC measurement | 508 |  | 300509 | 04 |  | PV/ESS frequency L2 | INT16s | AB | 2 | Hz | X | X
AC measurement | 509 |  | 300510 | 04 |  | PV/ESS frequency L3 | INT16s | AB | 2 | Hz | X | X
AC measurement | 510 |  | 300511 | 04 |  | PV/ESS voltage phase angle L1-L2 | INT16s | AB | 1 | Deg | X | X
AC measurement | 511 |  | 300512 | 04 |  | PV/ESS voltage phase angle L2-L3 | INT16s | AB | 1 | Deg | X | X
AC measurement | 512 |  | 300513 | 04 |  | PV/ESS voltage phase angle L3-L1 | INT16s | AB | 1 | Deg | X | X
AC measurement | 513 |  | 300514 | 04 |  | PV/ESS current L1 | INT16s | AB | 0 | A | X | X
AC measurement | 514 |  | 300515 | 04 |  | PV/ESS current L2 | INT16s | AB | 0 | A | X | X
AC measurement | 515 |  | 300516 | 04 |  | PV/ESS current L3 | INT16s | AB | 0 | A | X | X
AC measurement | 516 |  | 300517 | 04 |  | PV/ESS power L1 | INT16s | AB | 0 | kW | X | X
AC measurement | 517 |  | 300518 | 04 |  | PV/ESS power L2 | INT16s | AB | 0 | kW | X | X
AC measurement | 518 |  | 300519 | 04 |  | PV/ESS power L3 | INT16s | AB | 0 | kW | X | X
AC measurement | 519 |  | 300520 | 04 |  | PV/ESS power | INT16s | AB | 0 | kW | X | X
AC measurement | 520 |  | 300521 | 04 |  | PV/ESS reactive power L1 | INT16s | AB | 0 | kVAr | X | X
AC measurement | 521 |  | 300522 | 04 |  | PV/ESS reactive power L2 | INT16s | AB | 0 | kVAr | X | X
AC measurement | 522 |  | 300523 | 04 |  | PV/ESS reactive power L3 | INT16s | AB | 0 | kVAr | X | X
AC measurement | 523 |  | 300524 | 04 |  | PV/ESS reactive power | INT16s | AB | 0 | kVAr | X | X
AC measurement | 524 |  | 300525 | 04 |  | PV/ESS apparent power L1 | INT16s | AB | 0 | kVA | X | X
AC measurement | 525 |  | 300526 | 04 |  | PV/ESS apparent power L2 | INT16s | AB | 0 | kVA | X | X
AC measurement | 526 |  | 300527 | 04 |  | PV/ESS apparent power L3 | INT16s | AB | 0 | kVA | X | X
AC measurement | 527 |  | 300528 | 04 |  | PV/ESS apparent power | INT16s | AB | 0 | kVA | X | X
Counter | 528 |  | 300529 | 04 |  | PV/ESS reactive energy counter, total | INT32s | ABCD | 0 | kVArh | X | X
Counter | 530 |  | 300531 | 04 |  | PV/ESS, active energy counter, day | INT32s | ABCD | 0 | kWh | X | X
Counter | 532 |  | 300533 | 04 |  | PV/ESS, active energy counter, week | INT32s | ABCD | 0 | kWh | X | X
Counter | 534 |  | 300535 | 04 |  | PV/ESS, active energy counter, month | INT32s | ABCD | 0 | kWh | X | X
Counter | 536 |  | 300537 | 04 |  | PV/ESS, active energy counter, total | INT32s | ABCD | 0 | kWh | X | X
AC measurement | 538 |  | 300539 | 04 |  | PV/ESS PF | INT16s | AB | 2 | PF | X | X
AC measurement | 539 |  | 300540 | 04 |  | Bus B voltage L1-L2 | INT16s | AB | 0 | V | X | X
AC measurement | 540 |  | 300541 | 04 |  | Bus B voltage L2-L3 | INT16s | AB | 0 | V | X | X
AC measurement | 541 |  | 300542 | 04 |  | Bus B voltage L3-L1 | INT16s | AB | 0 | V | X | X
AC measurement | 542 |  | 300543 | 04 |  | Bus B voltage L1-N | INT16s | AB | 0 | V | X | X
AC measurement | 543 |  | 300544 | 04 |  | Bus B voltage L2-N | INT16s | AB | 0 | V | X | X
AC measurement | 544 |  | 300545 | 04 |  | Bus B voltage L3-N | INT16s | AB | 0 | V | X | X
AC measurement | 545 |  | 300546 | 04 |  | Bus B frequency L1 | INT16s | AB | 2 | Hz | X | X
AC measurement | 546 |  | 300547 | 04 |  | Bus B frequency L2 | INT16s | AB | 2 | Hz | X | X
AC measurement | 547 |  | 300548 | 04 |  | Bus B frequency L3 | INT16s | AB | 2 | Hz | X | X
AC measurement | 548 |  | 300549 | 04 |  | Bus B voltage phase angle L1-L2 | INT16s | AB | 1 | Deg | X | X
AC measurement | 549 |  | 300550 | 04 |  | Bus B voltage phase angle L2-L3 | INT16s | AB | 1 | Deg | X | X
AC measurement | 550 |  | 300551 | 04 |  | Bus B voltage phase angle L3-L1 | INT16s | AB | 1 | Deg | X | X
AC measurement | 551 |  | 300552 | 04 |  | U BB L1 - U ESS L1 phase angle | INT16s | AB | 1 | Deg |  | X
AC measurement | 551 |  | 300552 | 04 |  | U BB L1 - U PV L1 phase angle | INT16s | AB | 1 | Deg | X
AC measurement | 552 |  | 300553 | 04 |  | U BB L2 - U ESS L2 phase angle | INT16s | AB | 1 | Deg |  | X
AC measurement | 552 |  | 300553 | 04 |  | U BB L2 - U PV L2 phase angle | INT16s | AB | 1 | Deg | X
AC measurement | 553 |  | 300554 | 04 |  | U BB L3 - U ESS L3 phase angle | INT16s | AB | 1 | Deg |  | X
AC measurement | 553 |  | 300554 | 04 |  | U BB L3 - U PV L3 phase angle | INT16s | AB | 1 | Deg | X
Counter | 554 |  | 300555 | 04 |  | Absolute running hours | INT32s | ABCD | 0 |  | X | X
Counter | 558 |  | 300559 | 04 |  | No. of alarms | INT16s | AB | 0 |  | X | X
Counter | 559 |  | 300560 | 04 |  | No. of unacknowledged alarms | INT16s | AB | 0 |  | X | X
Counter | 560 |  | 300561 | 04 |  | No. of active acknowledged alarms | INT16s | AB | 0 |  | X | X
Counter | 563 |  | 300564 | 04 |  | No. of ESB operations | INT16s | AB | 0 |  |  | X
Counter | 563 |  | 300564 | 04 |  | No. of PVB operations | INT16s | AB | 0 |  | X
Counter | 564 |  | 300565 | 04 |  | No. of MB operations | INT16s | AB | 0 |  | X | X
DC measurement | 567 |  | 300568 | 04 |  | DC supply term. 1-2 | INT16s | AB | 1 | V | X | X
AC measurement | 573 |  | 300574 | 04 |  | Cos-phi | INT16s | AB | 2 | cosPhi | X | X
AC measurement | 574 |  | 300575 | 04 |  | Cos-phi Inductive/Capacitive 0=Inductive, 1=Capacitive | INT16s | AB | 0 |  | X | X
AC measurement | 592 |  | 300593 | 04 |  | Mains power | INT16s | AB | 0 | kW |  | X
AC measurement | 593 |  | 300594 | 04 |  | PV P Reference | INT16s | AB | 0 | kW | X | X
AC measurement | 594 |  | 300595 | 04 |  | PV P Reference Ramped incl ClosedLoop | INT16s | AB | 0 | kW | X | X
AC measurement | 595 |  | 300596 | 04 |  | PV Q Reference | INT16s | AB | 0 | kW | X | X
AC measurement | 596 |  | 300597 | 04 |  | PV Q Reference Ramped | INT16s | AB | 0 | kW | X | X
Counter | 597 |  | 300598 | 04 |  | BESS Discharging capacity | INT32s | ABCD | 0 | kW |  | X
Counter | 599 |  | 300600 | 04 |  | BESS Charging capacity | INT32s | ABCD | 0 | kW |  | X
AC measurement | 601 |  | 300602 | 04 |  | Hybrid Instant P Max (power derated) | INT16s | AB | 0 | kW | X | X
AC measurement | 602 |  | 300603 | 04 |  | BESS state of charge (SOC) | INT16s | AB | 0 | % |  | X
AC measurement | 603 |  | 300604 | 04 |  | PDS current limit | INT16s | AB | 0 | A |  | X
AC measurement | 604 |  | 300605 | 04 |  | PDS/Sub-module 1 power | INT16s | AB | 0 | kW |  | X
AC measurement | 605 |  | 300606 | 04 |  | Hybrid DG P total | INT16s | AB | 0 | kW | X | X
AC measurement | 606 |  | 300607 | 04 |  | Hybrid DG Q total | INT16s | AB | 0 | kVAr | X | X
Counter | 607 |  | 300608 | 04 |  | Ext. Generator Export energy counter, total | INT32s | ABCD | 0 | kVArh | X | X
Counter | 609 |  | 300610 | 04 |  | Ext. Generator Export energy counter, year | INT32s | ABCD | 0 | kVArh | X | X
Counter | 611 |  | 300612 | 04 |  | Ext. Generator Export energy counter, month | INT32s | ABCD | 0 | kVArh | X | X
Counter | 613 |  | 300614 | 04 |  | Ext. Generator export energy counter, week | INT32s | ABCD | 0 | kWh | X | X
Counter | 615 |  | 300616 | 04 |  | Ext. Generator export energy counter, day | INT32s | ABCD | 0 | kWh | X | X
AC measurement | 617 |  | 300618 | 04 |  | Below SOC Min counter | INT16s | AB | 0 |  |  | X
AC measurement | 618 |  | 300619 | 04 |  | Below SOC Threshold 1 counter | INT16s | AB | 0 |  |  | X
AC measurement | 619 |  | 300620 | 04 |  | Below SOC Threshold 2 counter | INT16s | AB | 0 |  |  | X
AC measurement | 620 |  | 300621 | 04 |  | Below SOC Max counter | INT16s | AB | 0 |  |  | X
AC measurement | 621 |  | 300622 | 04 |  | Above SOC Min counter | INT16s | AB | 0 |  |  | X
AC measurement | 622 |  | 300623 | 04 |  | Above SOC Threshold 1 counter | INT16s | AB | 0 |  |  | X
AC measurement | 623 |  | 300624 | 04 |  | Above SOC Threshold 2 counter | INT16s | AB | 0 |  |  | X
AC measurement | 624 |  | 300625 | 04 |  | Above SOC Max counter | INT16s | AB | 0 |  |  | X
AC measurement | 627 |  | 300628 | 04 |  | Any ext. mains on busbar - Open PMS | INT16s | AB | 0 |  | X | X
AC measurement | 628 |  | 300629 | 04 |  | Any local ext. mains on busbar - Open PMS | INT16s | AB | 0 |  | X | X
AC measurement | 629 |  | 300630 | 04 |  | Any ext. DG on busbar - Open PMS | INT16s | AB | 0 |  | X | X
AC measurement | 630 |  | 300631 | 04 |  | Any local ext. DG on busbar - Open PMS | INT16s | AB | 0 |  | X | X
AC measurement | 631 |  | 300632 | 04 |  | Hotel load power | INT16s | AB | 0 |  | X | X
AC measurement | 632 |  | 300633 | 04 |  | Ext. GB closed feedback bitwise from genset 01..16 | INT16s | AB | 0 |  | X | X
Control command state | 642 |  | 300643 | 04 |  | Control command address 0 | INT16s | AB | 0 |  | X | X
Control command state | 643 |  | 300644 | 04 |  | Control command address 1 | INT16s | AB | 0 |  | X | X
Control command state | 644 |  | 300645 | 04 |  | Control command address 2 | INT16s | AB | 0 |  | X | X
Control command state | 645 |  | 300646 | 04 |  | Control command address 3 | INT16s | AB | 0 |  | X | X
Control command state | 646 |  | 300647 | 04 |  | Control command address 4 | INT16s | AB | 0 |  | X | X
Control command state | 647 |  | 300648 | 04 |  | Control command address 5 | INT16s | AB | 0 |  | X | X
Control command state | 648 |  | 300649 | 04 |  | Control command address 6 | INT16s | AB | 0 |  | X | X
Control command state | 649 |  | 300650 | 04 |  | Control command address 7 | INT16s | AB | 0 |  | X | X
Control command state | 650 |  | 300651 | 04 |  | Control command address 8 | INT16s | AB | 0 |  | X | X
Control command state | 651 |  | 300652 | 04 |  | Control command address 9 | INT16s | AB | 0 |  | X | X
Control command state | 652 |  | 300653 | 04 |  | Control command address 10 | INT16s | AB | 0 |  | X | X
Control command state | 653 |  | 300654 | 04 |  | Control command address 11 | INT16s | AB | 0 |  | X | X
Control command state | 654 |  | 300655 | 04 |  | Control command address 12 | INT16s | AB | 0 |  | X | X
Control command state | 655 |  | 300656 | 04 |  | Control command address 13 | INT16s | AB | 0 |  | X | X
DC measurement | 660 |  | 300661 | 04 |  | CIO 308 no. 1. Input 8 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 661 |  | 300662 | 04 |  | CIO 308 no. 1. Input 11 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 662 |  | 300663 | 04 |  | CIO 308 no. 1. Input 14 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 663 |  | 300664 | 04 |  | CIO 308 no. 1. Input 17 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 664 |  | 300665 | 04 |  | CIO 308 no. 1. Input 20 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 665 |  | 300666 | 04 |  | CIO 308 no. 1. Input 23 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 666 |  | 300667 | 04 |  | CIO 308 no. 1. Input 26 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 667 |  | 300668 | 04 |  | CIO 308 no. 1. Input 29 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 668 |  | 300669 | 04 |  | CIO 308 no. 2. Input 8 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 669 |  | 300670 | 04 |  | CIO 308 no. 2. Input 11 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 670 |  | 300671 | 04 |  | CIO 308 no. 2. Input 14 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 671 |  | 300672 | 04 |  | CIO 308 no. 2. Input 17 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 672 |  | 300673 | 04 |  | CIO 308 no. 2. Input 20 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 673 |  | 300674 | 04 |  | CIO 308 no. 2. Input 23 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 674 |  | 300675 | 04 |  | CIO 308 no. 2. Input 26 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 675 |  | 300676 | 04 |  | CIO 308 no. 2. Input 29 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 676 |  | 300677 | 04 |  | CIO 308 no. 3. Input 8 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 677 |  | 300678 | 04 |  | CIO 308 no. 3. Input 11 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 678 |  | 300679 | 04 |  | CIO 308 no. 3. Input 14 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 679 |  | 300680 | 04 |  | CIO 308 no. 3. Input 17 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 680 |  | 300681 | 04 |  | CIO 308 no. 3. Input 20 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 681 |  | 300682 | 04 |  | CIO 308 no. 3. Input 23 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 682 |  | 300683 | 04 |  | CIO 308 no. 3. Input 26 [Config] | INT16s | AB | 0 |  | X | X
DC measurement | 683 |  | 300684 | 04 |  | CIO 308 no. 3. Input 29 [Config] | INT16s | AB | 0 |  | X | X
Alarm | 691 |  | 300692 | 04 |  | M-Logic extended timer alarm 1 value | INT16s | AB | 0 | min/day/hrs | X | X
Alarm | 692 |  | 300693 | 04 |  | M-Logic extended timer alarm 2 value | INT16s | AB | 0 | min/day/hrs | X | X
Alarm | 693 |  | 300694 | 04 |  | M-Logic extended timer alarm 3 value | INT16s | AB | 0 | min/day/hrs | X | X
Alarm | 694 |  | 300695 | 04 |  | M-Logic extended timer alarm 4 value | INT16s | AB | 0 | min/day/hrs | X | X
Plant logic state | 701 |  | 300702 | 04 |  | External Mains power reading used | INT16s | AB | 0 |  | X | X
Plant logic state | 758 |  | 300759 | 04 |  | External Mains Q reading used | INT16s | AB | 0 |  |  | X
AC measurement | 759 |  | 300760 | 04 |  | Mains Q | INT16s | AB | 0 | kW |  | X
Counter | 760 |  | 300761 | 04 |  | Absolute running minutes | INT16s | AB | 0 | min | X | X
AC measurement | 765 |  | 300766 | 04 |  | Active Power Load | INT32s | ABCD | 0 | kW | X | X
Counter | 770 |  | 300771 | 04 |  | Controller name letter 1 + 2. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X
Counter | 771 |  | 300772 | 04 |  | Controller name letter 3 + 4. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X
Counter | 772 |  | 300773 | 04 |  | Controller name letter 5 + 6. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X
Counter | 773 |  | 300774 | 04 |  | Controller name letter 7 + 7. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X
Counter | 774 |  | 300775 | 04 |  | Controller name letter 9 + 10. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X
Counter | 775 |  | 300776 | 04 |  | Controller name letter 11 + 12. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X
Counter | 776 |  | 300777 | 04 |  | Multi-input 20 configuration | INT16s | AB | 0 |  | X | X
Counter | 777 |  | 300778 | 04 |  | Multi-input 21 configuration | INT16s | AB | 0 |  | X | X
Counter | 778 |  | 300779 | 04 |  | Multi-input 22 configuration | INT16s | AB | 0 |  | X | X
Counter | 779 |  | 300780 | 04 |  | Multi-input 23 configuration | INT16s | AB | 0 |  | X | X
AC measurement | 786 |  | 300787 | 04 |  | Total available power in PMS | INT16s | AB | 0 | kW | X | X
AC measurement | 787 |  | 300788 | 04 |  | Spinning reserve request ALC | INT16s | AB | 0 | kW | X | X
AC measurement | 788 |  | 300789 | 04 |  | Spinning reserve request ASC | INT16s | AB | 0 | kW | X | X
Counter | 790 |  | 300791 | 04 |  | PV/ESS Export reactive energy counter, month | INT32s | ABCD | 0 | kVArh | X | X
Counter | 792 |  | 300793 | 04 |  | PV/ESS Export reactive energy counter, week | INT32s | ABCD | 0 | kVArh | X | X
Counter | 794 |  | 300795 | 04 |  | PV/ESS Export reactive energy counter, day | INT32s | ABCD | 0 | kVArh | X | X
Counter | 796 |  | 300797 | 04 |  | PV/ESS Import active energy counter, total | INT32s | ABCD | 0 | kWh | X | X
Counter | 798 |  | 300799 | 04 |  | PV/ESS Import active energy counter, month | INT32s | ABCD | 0 | kWh | X | X
Counter | 800 |  | 300801 | 04 |  | PV/ESS Import active energy counter, week | INT32s | ABCD | 0 | kWh | X | X
Counter | 802 |  | 300803 | 04 |  | PV/ESS Import active energy counter, day | INT32s | ABCD | 0 | kWh | X | X
Counter | 804 |  | 300805 | 04 |  | PV/ESS Import reactive energy counter, total | INT32s | ABCD | 0 | kVArh | X | X
Counter | 806 |  | 300807 | 04 |  | PV/ESS Import reactive energy counter, month | INT32s | ABCD | 0 | kVArh | X | X
Counter | 808 |  | 300809 | 04 |  | PV/ESS Import reactive energy counter, week | INT32s | ABCD | 0 | kVArh | X | X
Counter | 810 |  | 300811 | 04 |  | PV/ESS Import reactive energy counter, day | INT32s | ABCD | 0 | kVArh | X | X
Counter | 812 |  | 300813 | 04 |  | Pulse counter 01 | INT32s | ABCD | 0 |  | X | X
Counter | 814 |  | 300815 | 04 |  | Pulse counter 02 | INT32s | ABCD | 0 |  | X | X
Alarm | 1005 | 0 | 301006 | 04 | 2120 | Synchronising window | BOOL |  |  |  | X | X
Alarm | 1005 | 1 | 301006 | 04 | 2130 | Synchronising failure ESB | BOOL |  |  |  |  | X
Alarm | 1005 | 2 | 301006 | 04 | 2140 | Synchronising failure MB | BOOL |  |  |  | X | X
AC alarm | 1005 | 3 | 301006 | 04 | 2150 | Phase seq. failure A | BOOL |  |  |  | X | X
Alarm | 1005 | 4 | 301006 | 04 | 2160 | ESB open failure | BOOL |  |  |  |  | X
Alarm | 1005 | 5 | 301006 | 04 | 2170 | ESB close failure | BOOL |  |  |  |  | X
Alarm | 1005 | 6 | 301006 | 04 | 2180 | ESB pos. failure | BOOL |  |  |  |  | X
Alarm | 1005 | 7 | 301006 | 04 | 2200 | MB open failure | BOOL |  |  |  | X | X
Alarm | 1005 | 8 | 301006 | 04 | 2210 | MB close failure | BOOL |  |  |  | X | X
Alarm | 1005 | 9 | 301006 | 04 | 2220 | MB pos. failure | BOOL |  |  |  | X | X
AC alarm | 1005 | 11 | 301006 | 04 | 2155 | Phase seq. failure B | BOOL |  |  |  | X | X
Alarm | 1007 | 0 | 301008 | 04 | 3000 | Digital alarm input 39 | BOOL |  |  |  | X | X
Alarm | 1007 | 1 | 301008 | 04 | 3010 | Digital alarm input 40 | BOOL |  |  |  | X | X
Alarm | 1007 | 2 | 301008 | 04 | 3020 | Digital alarm input 41 | BOOL |  |  |  | X | X
Alarm | 1007 | 3 | 301008 | 04 | 3030 | Digital alarm input 42 | BOOL |  |  |  | X | X
Alarm | 1007 | 4 | 301008 | 04 | 3040 | Digital alarm input 43 | BOOL |  |  |  | X | X
Alarm | 1007 | 5 | 301008 | 04 | 3050 | Digital alarm input 44 | BOOL |  |  |  | X | X
Alarm | 1007 | 6 | 301008 | 04 | 3060 | Digital alarm input 45 | BOOL |  |  |  | X | X
Alarm | 1007 | 7 | 301008 | 04 | 3070 | Digital alarm input 46 | BOOL |  |  |  | X | X
Alarm | 1007 | 8 | 301008 | 04 | 3080 | Digital alarm input 47 | BOOL |  |  |  | X | X
Alarm | 1007 | 9 | 301008 | 04 | 3090 | Digital alarm input 48 | BOOL |  |  |  | X | X
Alarm | 1007 | 10 | 301008 | 04 | 3100 | Digital alarm input 49 | BOOL |  |  |  | X | X
Alarm | 1007 | 11 | 301008 | 04 | 3110 | Digital alarm input 50 | BOOL |  |  |  | X | X
Alarm | 1011 | 7 | 301012 | 04 | 3570 | M-Logic alarm 1 | BOOL |  |  |  | X | X
Alarm | 1011 | 8 | 301012 | 04 | 3580 | M-Logic alarm 2 | BOOL |  |  |  | X | X
Alarm | 1011 | 9 | 301012 | 04 | 3590 | M-Logic alarm 3 | BOOL |  |  |  | X | X
Alarm | 1011 | 10 | 301012 | 04 | 3600 | M-Logic alarm 4 | BOOL |  |  |  | X | X
Alarm | 1011 | 11 | 301012 | 04 | 3610 | M-Logic alarm 5 | BOOL |  |  |  | X | X
Alarm | 1011 | 12 | 301012 | 04 | 3620 | M-Logic extended alarm 1 | BOOL |  |  |  | X | X
Alarm | 1011 | 13 | 301012 | 04 | 3630 | M-Logic extended alarm 2 | BOOL |  |  |  | X | X
Alarm | 1011 | 14 | 301012 | 04 | 3640 | M-Logic extended alarm 3 | BOOL |  |  |  | X | X
Alarm | 1011 | 15 | 301012 | 04 | 3650 | M-Logic extended alarm 4 | BOOL |  |  |  | X | X
Alarm | 1013 | 0 | 301014 | 04 | 4120 | Multi input terminal 20.1 | BOOL |  |  |  | X | X
Alarm | 1013 | 1 | 301014 | 04 | 4130 | Multi input terminal 20.2 | BOOL |  |  |  | X | X
Alarm | 1013 | 2 | 301014 | 04 | 4140 | W. fail. 20 | BOOL |  |  |  | X | X
Alarm | 1013 | 3 | 301014 | 04 | 4150 | Multi input terminal 21.1 | BOOL |  |  |  | X | X
Alarm | 1013 | 4 | 301014 | 04 | 4160 | Multi input terminal 21.2 | BOOL |  |  |  | X | X
Alarm | 1013 | 5 | 301014 | 04 | 4170 | W. fail. 21 | BOOL |  |  |  | X | X
Alarm | 1013 | 6 | 301014 | 04 | 4180 | Multi input terminal 22.1 | BOOL |  |  |  | X | X
Alarm | 1013 | 7 | 301014 | 04 | 4190 | Multi input terminal 22.2 | BOOL |  |  |  | X | X
Alarm | 1013 | 8 | 301014 | 04 | 4200 | W. fail. 22 | BOOL |  |  |  | X | X
Alarm | 1014 | 1 | 301015 | 04 | 4960 | U< aux. term. 1 | BOOL |  |  |  | X | X
Alarm | 1014 | 2 | 301015 | 04 | 4970 | U> aux. term. 1 | BOOL |  |  |  | X | X
Alarm | 1014 | 6 | 301015 | 04 | 4210 | Multi input terminal 23.1 | BOOL |  |  |  | X | X
Alarm | 1014 | 7 | 301015 | 04 | 4220 | Multi input terminal 23.2 | BOOL |  |  |  | X | X
Alarm | 1014 | 8 | 301015 | 04 | 4230 | W. fail. 23 | BOOL |  |  |  | X | X
Alarm | 1015 | 12 | 301016 | 04 | 6540 | Unit not in auto | BOOL |  |  |  | X | X
Relay state | 1016 | 0 | 301017 | 04 | 5000 | Relay 5 | BOOL |  |  |  | X | X
Relay state | 1016 | 1 | 301017 | 04 | 5000 | Relay 6 | BOOL |  |  |  | X | X
Relay state | 1016 | 2 | 301017 | 04 | 5000 | Relay 9 | BOOL |  |  |  | X | X
Relay state | 1016 | 3 | 301017 | 04 | 5000 | Relay 10 | BOOL |  |  |  | X | X
Relay state | 1016 | 4 | 301017 | 04 | 5000 | Relay 11 | BOOL |  |  |  | X | X
Relay state | 1016 | 5 | 301017 | 04 | 5000 | Relay 12 | BOOL |  |  |  | X | X
Relay state | 1016 | 6 | 301017 | 04 | 5000 | Relay 13 | BOOL |  |  |  | X | X
Relay state | 1016 | 7 | 301017 | 04 | 5000 | Relay 14 | BOOL |  |  |  | X | X
Relay state | 1016 | 8 | 301017 | 04 | 5080 | Relay 15 | BOOL |  |  |  | X | X
Relay state | 1016 | 9 | 301017 | 04 | 8090 | Relay 16 | BOOL |  |  |  | X | X
Relay state | 1016 | 10 | 301017 | 04 | 5100 | Relay 17 | BOOL |  |  |  | X | X
Relay state | 1016 | 11 | 301017 | 04 | 5110 | Relay 18 | BOOL |  |  |  | X | X
Plant logic state | 1018 | 0 | 301019 | 04 |  | Mains failure (Single DG) | BOOL |  |  |  | X | X
Plant logic state | 1018 | 1 | 301019 | 04 |  | MB position ON (Single DG) | BOOL |  |  |  | X | X
Plant logic state | 1018 | 4 | 301019 | 04 |  | ESB position ON | BOOL |  |  |  |  | X
Plant logic state | 1018 | 4 | 301019 | 04 |  | PVB position ON | BOOL |  |  |  | X
Plant logic state | 1018 | 5 | 301019 | 04 |  | ESB synchronising | BOOL |  |  |  |  | X
Plant logic state | 1018 | 5 | 301019 | 04 |  | PVB synchronising | BOOL |  |  |  | X
Plant logic state | 1018 | 6 | 301019 | 04 |  | ESS running | BOOL |  |  |  |  | X
Plant logic state | 1018 | 6 | 301019 | 04 |  | PV running | BOOL |  |  |  | X
Plant logic state | 1018 | 11 | 301019 | 04 |  | ESB position OFF | BOOL |  |  |  |  | X
Plant logic state | 1018 | 11 | 301019 | 04 |  | PVB position OFF | BOOL |  |  |  | X
Plant logic state | 1018 | 12 | 301019 | 04 |  | MB position OFF | BOOL |  |  |  | X | X
Plant logic state | 1018 | 13 | 301019 | 04 |  | BB Hz/V OK | BOOL |  |  |  | X | X
Plant logic state | 1018 | 14 | 301019 | 04 |  | Single DG, MB synchronising | BOOL |  |  |  | X | X
Modes | 1019 | 2 | 301020 | 04 |  | Semi auto mode | BOOL |  |  |  | X | X
Modes | 1019 | 3 | 301020 | 04 |  | Auto mode | BOOL |  |  |  | X | X
Modes | 1019 | 5 | 301020 | 04 |  | Island | BOOL |  |  |  | X | X
Modes | 1019 | 6 | 301020 | 04 |  | AMF | BOOL |  |  |  | X | X
Modes | 1019 | 7 | 301020 | 04 |  | Peak shaving | BOOL |  |  |  | X | X
Modes | 1019 | 8 | 301020 | 04 |  | Fixed power | BOOL |  |  |  | X | X
Modes | 1019 | 9 | 301020 | 04 |  | Mains power export | BOOL |  |  |  | X | X
Modes | 1019 | 11 | 301020 | 04 |  | Power management | BOOL |  |  |  | X | X
Modes | 1019 | 15 | 301020 | 04 |  | AMF active | BOOL |  |  |  | X | X
PM alarm | 1031 | 1 | 301032 | 04 |  | CAN 1 missing ID 1 | BOOL |  |  |  | X | X
PM alarm | 1031 | 2 | 301032 | 04 |  | CAN 1 missing ID 2 | BOOL |  |  |  | X | X
PM alarm | 1031 | 3 | 301032 | 04 |  | CAN 1 missing ID 3 | BOOL |  |  |  | X | X
PM alarm | 1031 | 4 | 301032 | 04 |  | CAN 1 missing ID 4 | BOOL |  |  |  | X | X
PM alarm | 1031 | 5 | 301032 | 04 |  | CAN 1 missing ID 5 | BOOL |  |  |  | X | X
PM alarm | 1031 | 6 | 301032 | 04 |  | CAN 1 missing ID 6 | BOOL |  |  |  | X | X
PM alarm | 1031 | 7 | 301032 | 04 |  | CAN 1 missing ID 7 | BOOL |  |  |  | X | X
PM alarm | 1031 | 8 | 301032 | 04 |  | CAN 1 missing ID 8 | BOOL |  |  |  | X | X
PM alarm | 1031 | 9 | 301032 | 04 |  | CAN 1 missing ID 9 | BOOL |  |  |  | X | X
PM alarm | 1031 | 10 | 301032 | 04 |  | CAN 1 missing ID 10 | BOOL |  |  |  | X | X
PM alarm | 1031 | 11 | 301032 | 04 |  | CAN 1 missing ID 11 | BOOL |  |  |  | X | X
PM alarm | 1031 | 12 | 301032 | 04 |  | CAN 1 missing ID 12 | BOOL |  |  |  | X | X
PM alarm | 1031 | 13 | 301032 | 04 |  | CAN 1 missing ID 13 | BOOL |  |  |  | X | X
PM alarm | 1031 | 14 | 301032 | 04 |  | CAN 1 missing ID 14 | BOOL |  |  |  | X | X
PM alarm | 1031 | 15 | 301032 | 04 |  | CAN 1 missing ID 15 | BOOL |  |  |  | X | X
PM alarm | 1032 | 0 | 301033 | 04 |  | CAN 1 missing ID 16 | BOOL |  |  |  | X | X
PM alarm | 1032 | 2 | 301033 | 04 |  | CAN 2 missing ID 1 | BOOL |  |  |  | X | X
PM alarm | 1032 | 3 | 301033 | 04 |  | CAN 2 missing ID 2 | BOOL |  |  |  | X | X
PM alarm | 1032 | 4 | 301033 | 04 |  | CAN 2 missing ID 3 | BOOL |  |  |  | X | X
PM alarm | 1032 | 5 | 301033 | 04 |  | CAN 2 missing ID 4 | BOOL |  |  |  | X | X
PM alarm | 1032 | 6 | 301033 | 04 |  | CAN 2 missing ID 5 | BOOL |  |  |  | X | X
PM alarm | 1032 | 7 | 301033 | 04 |  | CAN 2 missing ID 6 | BOOL |  |  |  | X | X
PM alarm | 1032 | 8 | 301033 | 04 |  | CAN 2 missing ID 7 | BOOL |  |  |  | X | X
PM alarm | 1032 | 9 | 301033 | 04 |  | CAN 2 missing ID 8 | BOOL |  |  |  | X | X
PM alarm | 1032 | 10 | 301033 | 04 |  | CAN 2 missing ID 9 | BOOL |  |  |  | X | X
PM alarm | 1032 | 11 | 301033 | 04 |  | CAN 2 missing ID 10 | BOOL |  |  |  | X | X
PM alarm | 1032 | 12 | 301033 | 04 |  | CAN 2 missing ID 11 | BOOL |  |  |  | X | X
PM alarm | 1032 | 13 | 301033 | 04 |  | CAN 2 missing ID 12 | BOOL |  |  |  | X | X
PM alarm | 1032 | 14 | 301033 | 04 |  | CAN 2 missing ID 13 | BOOL |  |  |  | X | X
PM alarm | 1033 | 0 | 301034 | 04 |  | CAN 2 missing ID 16 | BOOL |  |  |  | X | X
PM alarm | 1033 | 1 | 301034 | 04 |  | CAN 2 missing ID 15 | BOOL |  |  |  | X | X
Alarm | 1036 | 0 | 301037 | 04 | 12000 | Ext. Analogue in. 1.1 | BOOL |  |  |  | X | X
Alarm | 1036 | 1 | 301037 | 04 | 12010 | Ext. Analogue in. 1.2 | BOOL |  |  |  | X | X
Alarm | 1036 | 3 | 301037 | 04 | 12030 | Ext. Analogue in. 2.1 | BOOL |  |  |  | X | X
Alarm | 1036 | 4 | 301037 | 04 | 12040 | Ext. Analogue in. 2.2 | BOOL |  |  |  | X | X
Alarm | 1036 | 6 | 301037 | 04 | 12060 | Ext. Analogue in. 3.1 | BOOL |  |  |  | X | X
Alarm | 1036 | 7 | 301037 | 04 | 12070 | Ext. Analogue in. 3.2 | BOOL |  |  |  | X | X
Alarm | 1036 | 9 | 301037 | 04 | 12090 | Ext. Analogue in. 4.1 | BOOL |  |  |  | X | X
Alarm | 1036 | 10 | 301037 | 04 | 12100 | Ext. Analogue in. 4.2 | BOOL |  |  |  | X | X
Alarm | 1036 | 12 | 301037 | 04 | 12120 | Ext. Analogue in. 5.1 | BOOL |  |  |  | X | X
Alarm | 1036 | 13 | 301037 | 04 | 12130 | Ext. Analogue in. 5.2 | BOOL |  |  |  | X | X
Alarm | 1036 | 15 | 301037 | 04 | 12150 | Ext. Analogue in. 6.1 | BOOL |  |  |  | X | X
Alarm | 1037 | 0 | 301038 | 04 | 12160 | Ext. Analogue in. 6.2 | BOOL |  |  |  | X | X
Alarm | 1037 | 2 | 301038 | 04 | 12180 | Ext. Analogue in. 7.1 | BOOL |  |  |  | X | X
Alarm | 1037 | 3 | 301038 | 04 | 12190 | Ext. Analogue in. 7.2 | BOOL |  |  |  | X | X
Alarm | 1037 | 5 | 301038 | 04 | 12210 | Ext. Analogue in. 8.1 | BOOL |  |  |  | X | X
Alarm | 1037 | 6 | 301038 | 04 | 12220 | Ext. Analogue in. 8.2 | BOOL |  |  |  | X | X
Alarm | 1038 | 0 | 301039 | 04 | 12540 | External digital input 1/CIO 116-1 digital input 10 | BOOL |  |  |  | X | X
Alarm | 1038 | 1 | 301039 | 04 | 12550 | External digital input 2/CIO 116-1 digital input 11 | BOOL |  |  |  | X | X
Alarm | 1038 | 2 | 301039 | 04 | 12560 | External digital input 3/CIO 116-1 digital input 12 | BOOL |  |  |  | X | X
Alarm | 1038 | 3 | 301039 | 04 | 12570 | External digital input 4/CIO 116-1 digital input 13 | BOOL |  |  |  | X | X
Alarm | 1038 | 4 | 301039 | 04 | 12580 | External digital input 5/CIO 116-1 digital input 14 | BOOL |  |  |  | X | X
Alarm | 1038 | 5 | 301039 | 04 | 12590 | External digital input 6/CIO 116-1 digital input 15 | BOOL |  |  |  | X | X
Alarm | 1038 | 6 | 301039 | 04 | 12600 | External digital input 7/CIO 116-1 digital input 16 | BOOL |  |  |  | X | X
Alarm | 1038 | 7 | 301039 | 04 | 12610 | External digital input 8/CIO 116-1 digital input 17 | BOOL |  |  |  | X | X
Alarm | 1038 | 8 | 301039 | 04 | 12620 | External digital input 9/CIO 116-1 digital input 19 | BOOL |  |  |  | X | X
Alarm | 1038 | 9 | 301039 | 04 | 12630 | External digital input 10/CIO 116-1 digital input 20 | BOOL |  |  |  | X | X
Alarm | 1038 | 10 | 301039 | 04 | 12640 | External digital input 11/CIO 116-1 digital input 21 | BOOL |  |  |  | X | X
Alarm | 1038 | 11 | 301039 | 04 | 12650 | External digital input 12/CIO 116-1 digital input 22 | BOOL |  |  |  | X | X
Alarm | 1038 | 12 | 301039 | 04 | 12660 | External digital input 13/CIO 116-1 digital input 23 | BOOL |  |  |  | X | X
Alarm | 1038 | 13 | 301039 | 04 | 12670 | External digital input 14/CIO 116-1 digital input 24 | BOOL |  |  |  | X | X
Alarm | 1038 | 14 | 301039 | 04 | 12680 | External digital input 15/CIO 116-1 digital input 25 | BOOL |  |  |  | X | X
Alarm | 1038 | 15 | 301039 | 04 | 12690 | External digital input 16/CIO 116 no.1 digital input 26 | BOOL |  |  |  | X | X
Digital output state | 1039 | 0 | 301040 | 04 | 12790 | External digital output 1/CIO 208-1 digital output 9 | BOOL |  |  |  | X | X
Digital output state | 1039 | 1 | 301040 | 04 | 12800 | External digital output 2/CIO 208-1 digital output 11 | BOOL |  |  |  | X | X
Digital output state | 1039 | 2 | 301040 | 04 | 12810 | External digital output 3/CIO 208-1 digital output 13 | BOOL |  |  |  | X | X
Digital output state | 1039 | 3 | 301040 | 04 | 12820 | External digital output 4/CIO 208-1 digital output 15 | BOOL |  |  |  | X | X
Digital output state | 1039 | 4 | 301040 | 04 | 12830 | External digital output 5/CIO 208-1 digital output 18 | BOOL |  |  |  | X | X
Digital output state | 1039 | 5 | 301040 | 04 | 12840 | External digital output 6/CIO 208-1 digital output 21 | BOOL |  |  |  | X | X
Digital output state | 1039 | 6 | 301040 | 04 | 12850 | External digital output 7/CIO 208-1 digital output 24 | BOOL |  |  |  | X | X
Digital output state | 1039 | 7 | 301040 | 04 | 12860 | External digital output 8/CIO 208-1 digital output 27 | BOOL |  |  |  | X | X
Digital output state | 1039 | 8 | 301040 | 04 | 12870 | External digital output 9/CIO 208-2 digital output 9 | BOOL |  |  |  | X | X
Digital output state | 1039 | 9 | 301040 | 04 | 12880 | External digital output 10/CIO 208-2 digital output 11 | BOOL |  |  |  | X | X
Digital output state | 1039 | 10 | 301040 | 04 | 12890 | External digital output 11/CIO 208-2 digital output 13 | BOOL |  |  |  | X | X
Digital output state | 1039 | 11 | 301040 | 04 | 12900 | External digital output 12/CIO 208-2 digital output 15 | BOOL |  |  |  | X | X
Digital output state | 1039 | 12 | 301040 | 04 | 12910 | External digital output 13/CIO 208-2 digital output 18 | BOOL |  |  |  | X | X
Digital output state | 1039 | 13 | 301040 | 04 | 12920 | External digital output 14/CIO 208-2 digital output 21 | BOOL |  |  |  | X | X
Digital output state | 1039 | 14 | 301040 | 04 | 12930 | External digital output 15/CIO 208-2 digital output 24 | BOOL |  |  |  | X | X
Digital output state | 1039 | 15 | 301040 | 04 | 12940 | External digital output 16/CIO 208-2 digital output 27 | BOOL |  |  |  | X | X
PM alarm | 1040 | 0 | 301041 | 04 |  | CAN 1 missing ID 1 | BOOL |  |  |  | X | X
PM alarm | 1040 | 1 | 301041 | 04 |  | CAN 1 missing ID 2 | BOOL |  |  |  | X | X
PM alarm | 1040 | 2 | 301041 | 04 |  | CAN 1 missing ID 3 | BOOL |  |  |  | X | X
PM alarm | 1040 | 3 | 301041 | 04 |  | CAN 1 missing ID 4 | BOOL |  |  |  | X | X
PM alarm | 1040 | 4 | 301041 | 04 |  | CAN 1 missing ID 5 | BOOL |  |  |  | X | X
PM alarm | 1040 | 5 | 301041 | 04 |  | CAN 1 missing ID 6 | BOOL |  |  |  | X | X
PM alarm | 1040 | 6 | 301041 | 04 |  | CAN 1 missing ID 7 | BOOL |  |  |  | X | X
PM alarm | 1040 | 7 | 301041 | 04 |  | CAN 1 missing ID 8 | BOOL |  |  |  | X | X
PM alarm | 1040 | 8 | 301041 | 04 |  | CAN 1 missing ID 9 | BOOL |  |  |  | X | X
PM alarm | 1040 | 9 | 301041 | 04 |  | CAN 1 missing ID 10 | BOOL |  |  |  | X | X
PM alarm | 1040 | 10 | 301041 | 04 |  | CAN 1 missing ID 11 | BOOL |  |  |  | X | X
PM alarm | 1040 | 11 | 301041 | 04 |  | CAN 1 missing ID 12 | BOOL |  |  |  | X | X
PM alarm | 1040 | 12 | 301041 | 04 |  | CAN 1 missing ID 13 | BOOL |  |  |  | X | X
PM alarm | 1040 | 13 | 301041 | 04 |  | CAN 1 missing ID 14 | BOOL |  |  |  | X | X
PM alarm | 1040 | 14 | 301041 | 04 |  | CAN 1 missing ID 15 | BOOL |  |  |  | X | X
PM alarm | 1040 | 15 | 301041 | 04 |  | CAN 1 missing ID 16 | BOOL |  |  |  | X | X
PM alarm | 1041 | 0 | 301042 | 04 |  | CAN 1 missing ID 17 | BOOL |  |  |  | X | X
PM alarm | 1041 | 1 | 301042 | 04 |  | CAN 1 missing ID 18 | BOOL |  |  |  | X | X
PM alarm | 1041 | 2 | 301042 | 04 |  | CAN 1 missing ID 19 | BOOL |  |  |  | X | X
PM alarm | 1041 | 3 | 301042 | 04 |  | CAN 1 missing ID 20 | BOOL |  |  |  | X | X
PM alarm | 1041 | 4 | 301042 | 04 |  | CAN 1 missing ID 21 | BOOL |  |  |  | X | X
PM alarm | 1041 | 5 | 301042 | 04 |  | CAN 1 missing ID 22 | BOOL |  |  |  | X | X
PM alarm | 1041 | 6 | 301042 | 04 |  | CAN 1 missing ID 23 | BOOL |  |  |  | X | X
PM alarm | 1041 | 7 | 301042 | 04 |  | CAN 1 missing ID 24 | BOOL |  |  |  | X | X
PM alarm | 1041 | 8 | 301042 | 04 |  | CAN 1 missing ID 25 | BOOL |  |  |  | X | X
PM alarm | 1041 | 9 | 301042 | 04 |  | CAN 1 missing ID 26 | BOOL |  |  |  | X | X
PM alarm | 1041 | 10 | 301042 | 04 |  | CAN 1 missing ID 27 | BOOL |  |  |  | X | X
PM alarm | 1041 | 11 | 301042 | 04 |  | CAN 1 missing ID 28 | BOOL |  |  |  | X | X
PM alarm | 1041 | 12 | 301042 | 04 |  | CAN 1 missing ID 29 | BOOL |  |  |  | X | X
PM alarm | 1041 | 13 | 301042 | 04 |  | CAN 1 missing ID 30 | BOOL |  |  |  | X | X
PM alarm | 1041 | 14 | 301042 | 04 |  | CAN 1 missing ID 31 | BOOL |  |  |  | X | X
PM alarm | 1041 | 15 | 301042 | 04 |  | CAN 1 missing ID 32 | BOOL |  |  |  | X | X
PM alarm | 1042 | 0 | 301043 | 04 |  | CAN 1 missing ID 33 | BOOL |  |  |  | X | X
PM alarm | 1042 | 1 | 301043 | 04 |  | CAN 1 missing ID 34 | BOOL |  |  |  | X | X
PM alarm | 1042 | 2 | 301043 | 04 |  | CAN 1 missing ID 35 | BOOL |  |  |  | X | X
PM alarm | 1042 | 3 | 301043 | 04 |  | CAN 1 missing ID 36 | BOOL |  |  |  | X | X
PM alarm | 1042 | 4 | 301043 | 04 |  | CAN 1 missing ID 37 | BOOL |  |  |  | X | X
PM alarm | 1042 | 5 | 301043 | 04 |  | CAN 1 missing ID 38 | BOOL |  |  |  | X | X
PM alarm | 1042 | 6 | 301043 | 04 |  | CAN 1 missing ID 39 | BOOL |  |  |  | X | X
PM alarm | 1043 | 0 | 301044 | 04 |  | CAN 2 missing ID 1 | BOOL |  |  |  | X | X
PM alarm | 1043 | 1 | 301044 | 04 |  | CAN 2 missing ID 2 | BOOL |  |  |  | X | X
PM alarm | 1043 | 2 | 301044 | 04 |  | CAN 2 missing ID 3 | BOOL |  |  |  | X | X
PM alarm | 1043 | 3 | 301044 | 04 |  | CAN 2 missing ID 4 | BOOL |  |  |  | X | X
PM alarm | 1043 | 4 | 301044 | 04 |  | CAN 2 missing ID 5 | BOOL |  |  |  | X | X
PM alarm | 1043 | 5 | 301044 | 04 |  | CAN 2 missing ID 6 | BOOL |  |  |  | X | X
PM alarm | 1043 | 6 | 301044 | 04 |  | CAN 2 missing ID 7 | BOOL |  |  |  | X | X
PM alarm | 1043 | 7 | 301044 | 04 |  | CAN 2 missing ID 8 | BOOL |  |  |  | X | X
PM alarm | 1043 | 8 | 301044 | 04 |  | CAN 2 missing ID 9 | BOOL |  |  |  | X | X
PM alarm | 1043 | 9 | 301044 | 04 |  | CAN 2 missing ID 10 | BOOL |  |  |  | X | X
PM alarm | 1043 | 10 | 301044 | 04 |  | CAN 2 missing ID 11 | BOOL |  |  |  | X | X
PM alarm | 1043 | 11 | 301044 | 04 |  | CAN 2 missing ID 12 | BOOL |  |  |  | X | X
PM alarm | 1043 | 12 | 301044 | 04 |  | CAN 2 missing ID 13 | BOOL |  |  |  | X | X
PM alarm | 1043 | 13 | 301044 | 04 |  | CAN 2 missing ID 14 | BOOL |  |  |  | X | X
PM alarm | 1043 | 14 | 301044 | 04 |  | CAN 2 missing ID 15 | BOOL |  |  |  | X | X
PM alarm | 1043 | 15 | 301044 | 04 |  | CAN 2 missing ID 16 | BOOL |  |  |  | X | X
PM alarm | 1044 | 0 | 301045 | 04 |  | CAN 2 missing ID 17 | BOOL |  |  |  | X | X
PM alarm | 1044 | 1 | 301045 | 04 |  | CAN 2 missing ID 18 | BOOL |  |  |  | X | X
PM alarm | 1044 | 2 | 301045 | 04 |  | CAN 2 missing ID 19 | BOOL |  |  |  | X | X
PM alarm | 1044 | 3 | 301045 | 04 |  | CAN 2 missing ID 20 | BOOL |  |  |  | X | X
PM alarm | 1044 | 4 | 301045 | 04 |  | CAN 2 missing ID 21 | BOOL |  |  |  | X | X
PM alarm | 1044 | 5 | 301045 | 04 |  | CAN 2 missing ID 22 | BOOL |  |  |  | X | X
PM alarm | 1044 | 6 | 301045 | 04 |  | CAN 2 missing ID 23 | BOOL |  |  |  | X | X
PM alarm | 1044 | 7 | 301045 | 04 |  | CAN 2 missing ID 24 | BOOL |  |  |  | X | X
PM alarm | 1044 | 8 | 301045 | 04 |  | CAN 2 missing ID 25 | BOOL |  |  |  | X | X
PM alarm | 1044 | 9 | 301045 | 04 |  | CAN 2 missing ID 26 | BOOL |  |  |  | X | X
PM alarm | 1044 | 10 | 301045 | 04 |  | CAN 2 missing ID 27 | BOOL |  |  |  | X | X
PM alarm | 1044 | 11 | 301045 | 04 |  | CAN 2 missing ID 28 | BOOL |  |  |  | X | X
PM alarm | 1044 | 12 | 301045 | 04 |  | CAN 2 missing ID 29 | BOOL |  |  |  | X | X
PM alarm | 1044 | 13 | 301045 | 04 |  | CAN 2 missing ID 30 | BOOL |  |  |  | X | X
PM alarm | 1044 | 14 | 301045 | 04 |  | CAN 2 missing ID 31 | BOOL |  |  |  | X | X
PM alarm | 1044 | 15 | 301045 | 04 |  | CAN 2 missing ID 32 | BOOL |  |  |  | X | X
PM alarm | 1045 | 0 | 301046 | 04 |  | CAN 2 missing ID 33 | BOOL |  |  |  | X | X
PM alarm | 1045 | 1 | 301046 | 04 |  | CAN 2 missing ID 34 | BOOL |  |  |  | X | X
PM alarm | 1045 | 2 | 301046 | 04 |  | CAN 2 missing ID 35 | BOOL |  |  |  | X | X
PM alarm | 1045 | 3 | 301046 | 04 |  | CAN 2 missing ID 36 | BOOL |  |  |  | X | X
PM alarm | 1045 | 4 | 301046 | 04 |  | CAN 2 missing ID 37 | BOOL |  |  |  | X | X
PM alarm | 1045 | 5 | 301046 | 04 |  | CAN 2 missing ID 38 | BOOL |  |  |  | X | X
PM alarm | 1045 | 6 | 301046 | 04 |  | CAN 2 missing ID 39 | BOOL |  |  |  | X | X
PM alarm | 1045 | 7 | 301046 | 04 |  | CAN 2 missing ID 40 | BOOL |  |  |  | X | X
Plant logic state | 1050 | 0 | 301051 | 04 |  | Ready to autostart | BOOL |  |  |  | X | X
Plant logic state | 1050 | 1 | 301051 | 04 |  | ESS U > 30% of U nominal | BOOL |  |  |  |  | X
Plant logic state | 1050 | 2 | 301051 | 04 |  | BB U > 30% of U nominal | BOOL |  |  |  | X | X
M-Logic state | 1051 |  | 301052 | 04 |  | Virtual events 1-16 | INT16s | AB | 0 |  | X | X
M-Logic state | 1052 |  | 301053 | 04 |  | Virtual events 17-32 | INT16s | AB | 0 |  | X | X
Alarm | 1053 | 4 | 301054 | 04 | 4610 | Delta analogue 1 - fail 1 | BOOL |  |  |  | X | X
Alarm | 1053 | 5 | 301054 | 04 | 4620 | Delta analogue 1 - fail 2 | BOOL |  |  |  | X | X
Alarm | 1053 | 6 | 301054 | 04 | 4630 | Delta analogue 2 - fail 1 | BOOL |  |  |  | X | X
Alarm | 1053 | 7 | 301054 | 04 | 4640 | Delta analogue 2 - fail 2 | BOOL |  |  |  | X | X
Alarm | 1053 | 8 | 301054 | 04 | 4650 | Delta analogue 3 - fail 1 | BOOL |  |  |  | X | X
Alarm | 1053 | 9 | 301054 | 04 | 4660 | Delta analogue 3 - fail 2 | BOOL |  |  |  | X | X
Alarm | 1053 | 10 | 301054 | 04 | 4680 | Delta analogue 4 - fail 1 | BOOL |  |  |  | X | X
Alarm | 1053 | 11 | 301054 | 04 | 4690 | Delta analogue 4 - fail 2 | BOOL |  |  |  | X | X
Alarm | 1053 | 12 | 301054 | 04 | 4700 | Delta analogue 5 - fail 1 | BOOL |  |  |  | X | X
Alarm | 1053 | 13 | 301054 | 04 | 4710 | Delta analogue 5 - fail 2 | BOOL |  |  |  | X | X
Alarm | 1053 | 14 | 301054 | 04 | 4720 | Delta analogue 6 - fail 1 | BOOL |  |  |  | X | X
Alarm | 1053 | 15 | 301054 | 04 | 4730 | Delta analogue 6 - fail 2 | BOOL |  |  |  | X | X
Alarm | 1057 | 1 | 301058 | 04 |  | Fail class: Warning | BOOL |  |  |  | X | X
Alarm | 1057 | 2 | 301058 | 04 |  | Fail class: Trip ESB | BOOL |  |  |  |  | X
Alarm | 1057 | 2 | 301058 | 04 |  | Fail class: Trip PVB | BOOL |  |  |  | X
Alarm | 1057 | 4 | 301058 | 04 |  | Fail class: Shutdown | BOOL |  |  |  | X | X
Alarm | 1057 | 5 | 301058 | 04 |  | Fail class: Trip MB | BOOL |  |  |  | X | X
M-Logic state | 1058 |  | 301059 | 04 |  | Virtual events 33-48 | INT16s | AB | 0 |  | X | X
M-Logic state | 1059 |  | 301060 | 04 |  | Virtual events 49-64 | INT16s | AB | 0 |  | X | X
M-Logic state | 1060 |  | 301061 | 04 |  | Virtual events 65-80 | INT16s | AB | 0 |  | X | X
M-Logic state | 1061 |  | 301062 | 04 |  | Virtual events 81-96 | INT16s | AB | 0 |  | X | X
M-Logic state | 1062 |  | 301063 | 04 |  | Flipflop output 1-16 | INT16s | AB | 0 |  | X | X
Alarm | 1130 | 0 | 301131 | 04 |  | CIO 308-2 Analogue input 8.1 | BOOL |  |  |  | X | X
Alarm | 1130 | 1 | 301131 | 04 |  | CIO 308-2 Analogue input 8.2 | BOOL |  |  |  | X | X
Alarm | 1130 | 2 | 301131 | 04 |  | CIO 308-2 Analogue input 11.1 | BOOL |  |  |  | X | X
Alarm | 1130 | 3 | 301131 | 04 |  | CIO 308-2 Analogue input 11.2 | BOOL |  |  |  | X | X
Alarm | 1130 | 4 | 301131 | 04 |  | CIO 308-2 Analogue input 14.1 | BOOL |  |  |  | X | X
Alarm | 1130 | 5 | 301131 | 04 |  | CIO 308-2 Analogue input 14.2 | BOOL |  |  |  | X | X
Alarm | 1130 | 6 | 301131 | 04 |  | CIO 308-2 Analogue input 17.1 | BOOL |  |  |  | X | X
Alarm | 1130 | 7 | 301131 | 04 |  | CIO 308-2 Analogue input 17.2 | BOOL |  |  |  | X | X
Alarm | 1130 | 8 | 301131 | 04 |  | CIO 308-2 Analogue input 20.1 | BOOL |  |  |  | X | X
Alarm | 1130 | 9 | 301131 | 04 |  | CIO 308-2 Analogue input 20.2 | BOOL |  |  |  | X | X
Alarm | 1130 | 10 | 301131 | 04 |  | CIO 308-2 Analogue input 23.1 | BOOL |  |  |  | X | X
Alarm | 1130 | 11 | 301131 | 04 |  | CIO 308-2 Analogue input 23.2 | BOOL |  |  |  | X | X
Alarm | 1130 | 12 | 301131 | 04 |  | CIO 308-2 Analogue input 26.1 | BOOL |  |  |  | X | X
Alarm | 1130 | 13 | 301131 | 04 |  | CIO 308-2 Analogue input 26.2 | BOOL |  |  |  | X | X
Alarm | 1130 | 14 | 301131 | 04 |  | CIO 308-2 Analogue input 29.1 | BOOL |  |  |  | X | X
Alarm | 1130 | 15 | 301131 | 04 |  | CIO 308-2 Analogue input 29.2 | BOOL |  |  |  | X | X
Alarm | 1131 | 0 | 301132 | 04 |  | CIO 308-3 Analogue input 8.1 | BOOL |  |  |  | X | X
Alarm | 1131 | 1 | 301132 | 04 |  | CIO 308-3 Analogue input 8.2 | BOOL |  |  |  | X | X
Alarm | 1131 | 2 | 301132 | 04 |  | CIO 308-3 Analogue input 11.1 | BOOL |  |  |  | X | X
Alarm | 1131 | 3 | 301132 | 04 |  | CIO 308-3 Analogue input 11.2 | BOOL |  |  |  | X | X
Alarm | 1131 | 4 | 301132 | 04 |  | CIO 308-3 Analogue input 14.1 | BOOL |  |  |  | X | X
Alarm | 1131 | 5 | 301132 | 04 |  | CIO 308-3 Analogue input 14.2 | BOOL |  |  |  | X | X
Alarm | 1131 | 6 | 301132 | 04 |  | CIO 308-3 Analogue input 17.1 | BOOL |  |  |  | X | X
Alarm | 1131 | 7 | 301132 | 04 |  | CIO 308-3 Analogue input 17.2 | BOOL |  |  |  | X | X
Alarm | 1131 | 8 | 301132 | 04 |  | CIO 308-3 Analogue input 20.1 | BOOL |  |  |  | X | X
Alarm | 1131 | 9 | 301132 | 04 |  | CIO 308-3 Analogue input 20.2 | BOOL |  |  |  | X | X
Alarm | 1131 | 10 | 301132 | 04 |  | CIO 308-3 Analogue input 23.1 | BOOL |  |  |  | X | X
Alarm | 1131 | 11 | 301132 | 04 |  | CIO 308-3 Analogue input 23.2 | BOOL |  |  |  | X | X
Alarm | 1131 | 12 | 301132 | 04 |  | CIO 308-3 Analogue input 26.1 | BOOL |  |  |  | X | X
Alarm | 1131 | 13 | 301132 | 04 |  | CIO 308-3 Analogue input 26.2 | BOOL |  |  |  | X | X
Alarm | 1131 | 14 | 301132 | 04 |  | CIO 308-3 Analogue input 29.1 | BOOL |  |  |  | X | X
Alarm | 1131 | 15 | 301132 | 04 |  | CIO 308-3 Analogue input 29.2 | BOOL |  |  |  | X | X
Alarm | 1132 | 0 | 301133 | 04 |  | CIO 116-2 digital input 10 | BOOL |  |  |  | X | X
Alarm | 1132 | 1 | 301133 | 04 |  | CIO 116-2 digital input 11 | BOOL |  |  |  | X | X
Alarm | 1132 | 2 | 301133 | 04 |  | CIO 116-2 digital input 12 | BOOL |  |  |  | X | X
Alarm | 1132 | 3 | 301133 | 04 |  | CIO 116-2 digital input 13 | BOOL |  |  |  | X | X
Alarm | 1132 | 4 | 301133 | 04 |  | CIO 116-2 digital input 14 | BOOL |  |  |  | X | X
Alarm | 1132 | 5 | 301133 | 04 |  | CIO 116-2 digital input 15 | BOOL |  |  |  | X | X
Alarm | 1132 | 6 | 301133 | 04 |  | CIO 116-2 digital input 16 | BOOL |  |  |  | X | X
Alarm | 1132 | 7 | 301133 | 04 |  | CIO 116-2 digital input 17 | BOOL |  |  |  | X | X
Alarm | 1132 | 8 | 301133 | 04 |  | CIO 116-2 digital input 18 | BOOL |  |  |  | X | X
Alarm | 1132 | 9 | 301133 | 04 |  | CIO 116-2 digital input 20 | BOOL |  |  |  | X | X
Alarm | 1132 | 10 | 301133 | 04 |  | CIO 116-2 digital input 21 | BOOL |  |  |  | X | X
Alarm | 1132 | 11 | 301133 | 04 |  | CIO 116-2 digital input 22 | BOOL |  |  |  | X | X
Alarm | 1132 | 12 | 301133 | 04 |  | CIO 116-2 digital input 23 | BOOL |  |  |  | X | X
Alarm | 1132 | 13 | 301133 | 04 |  | CIO 116-2 digital input 24 | BOOL |  |  |  | X | X
Alarm | 1132 | 14 | 301133 | 04 |  | CIO 116-2 digital input 25 | BOOL |  |  |  | X | X
Alarm | 1132 | 15 | 301133 | 04 |  | CIO 116-2 digital input 26 | BOOL |  |  |  | X | X
Alarm | 1133 | 0 | 301134 | 04 |  | CIO 116-3 digital input 10 | BOOL |  |  |  | X | X
Alarm | 1133 | 1 | 301134 | 04 |  | CIO 116-3 digital input 11 | BOOL |  |  |  | X | X
Alarm | 1133 | 2 | 301134 | 04 |  | CIO 116-3 digital input 12 | BOOL |  |  |  | X | X
Alarm | 1133 | 3 | 301134 | 04 |  | CIO 116-3 digital input 13 | BOOL |  |  |  | X | X
Alarm | 1133 | 4 | 301134 | 04 |  | CIO 116-3 digital input 14 | BOOL |  |  |  | X | X
Alarm | 1133 | 5 | 301134 | 04 |  | CIO 116-3 digital input 15 | BOOL |  |  |  | X | X
Alarm | 1133 | 6 | 301134 | 04 |  | CIO 116-3 digital input 16 | BOOL |  |  |  | X | X
Alarm | 1133 | 7 | 301134 | 04 |  | CIO 116-3 digital input 17 | BOOL |  |  |  | X | X
Alarm | 1133 | 8 | 301134 | 04 |  | CIO 116-3 digital input 19 | BOOL |  |  |  | X | X
Alarm | 1133 | 9 | 301134 | 04 |  | CIO 116-3 digital input 20 | BOOL |  |  |  | X | X
Alarm | 1133 | 10 | 301134 | 04 |  | CIO 116-3 digital input 21 | BOOL |  |  |  | X | X
Alarm | 1133 | 11 | 301134 | 04 |  | CIO 116-3 digital input 22 | BOOL |  |  |  | X | X
Alarm | 1133 | 12 | 301134 | 04 |  | CIO 116-3 digital input 23 | BOOL |  |  |  | X | X
Alarm | 1133 | 13 | 301134 | 04 |  | CIO 116-3 digital input 24 | BOOL |  |  |  | X | X
Alarm | 1133 | 14 | 301134 | 04 |  | CIO 116-3 digital input 25 | BOOL |  |  |  | X | X
Alarm | 1133 | 15 | 301134 | 04 |  | CIO 116-3 digital input 26 | BOOL |  |  |  | X | X
Digital output state | 1136 | 0 | 301137 | 04 |  | CIO 208-3 digital output 9 | BOOL |  |  |  | X | X
Digital output state | 1136 | 1 | 301137 | 04 |  | CIO 208-3 digital output 11 | BOOL |  |  |  | X | X
Digital output state | 1136 | 2 | 301137 | 04 |  | CIO 208-3 digital output 13 | BOOL |  |  |  | X | X
Digital output state | 1136 | 3 | 301137 | 04 |  | CIO 208-3 digital output 15 | BOOL |  |  |  | X | X
Digital output state | 1136 | 4 | 301137 | 04 |  | CIO 208-3 digital output 18 | BOOL |  |  |  | X | X
Digital output state | 1136 | 5 | 301137 | 04 |  | CIO 208-3 digital output 21 | BOOL |  |  |  | X | X
Digital output state | 1136 | 6 | 301137 | 04 |  | CIO 208-3 digital output 24 | BOOL |  |  |  | X | X
Digital output state | 1136 | 7 | 301137 | 04 |  | CIO 208-3 digital output 27 | BOOL |  |  |  | X | X
Digital input state | 1138 | 0 | 301139 | 04 |  | CIO 116 no. 1. Input 10 | BOOL |  |  |  | X | X
Digital input state | 1138 | 1 | 301139 | 04 |  | CIO 116 no. 1. Input 11 | BOOL |  |  |  | X | X
Digital input state | 1138 | 2 | 301139 | 04 |  | CIO 116 no. 1. Input 12 | BOOL |  |  |  | X | X
Digital input state | 1138 | 3 | 301139 | 04 |  | CIO 116 no. 1. Input 13 | BOOL |  |  |  | X | X
Digital input state | 1138 | 4 | 301139 | 04 |  | CIO 116 no. 1. Input 14 | BOOL |  |  |  | X | X
Digital input state | 1138 | 5 | 301139 | 04 |  | CIO 116 no. 1. Input 15 | BOOL |  |  |  | X | X
Digital input state | 1138 | 6 | 301139 | 04 |  | CIO 116 no. 1. Input 16 | BOOL |  |  |  | X | X
Digital input state | 1138 | 7 | 301139 | 04 |  | CIO 116 no. 1. Input 17 | BOOL |  |  |  | X | X
Digital input state | 1138 | 8 | 301139 | 04 |  | CIO 116 no. 1. Input 19 | BOOL |  |  |  | X | X
Digital input state | 1138 | 9 | 301139 | 04 |  | CIO 116 no. 1. Input 20 | BOOL |  |  |  | X | X
Digital input state | 1138 | 10 | 301139 | 04 |  | CIO 116 no. 1. Input 21 | BOOL |  |  |  | X | X
Digital input state | 1138 | 11 | 301139 | 04 |  | CIO 116 no. 1. Input 22 | BOOL |  |  |  | X | X
Digital input state | 1138 | 12 | 301139 | 04 |  | CIO 116 no. 1. Input 23 | BOOL |  |  |  | X | X
Digital input state | 1138 | 13 | 301139 | 04 |  | CIO 116 no. 1. Input 24 | BOOL |  |  |  | X | X
Digital input state | 1138 | 14 | 301139 | 04 |  | CIO 116 no. 1. Input 25 | BOOL |  |  |  | X | X
Digital input state | 1138 | 15 | 301139 | 04 |  | CIO 116 no. 1. Input 26 | BOOL |  |  |  | X | X
Digital input state | 1139 | 0 | 301140 | 04 |  | CIO 116 no. 2. Input 10 | BOOL |  |  |  | X | X
Digital input state | 1139 | 1 | 301140 | 04 |  | CIO 116 no. 2. Input 11 | BOOL |  |  |  | X | X
Digital input state | 1139 | 2 | 301140 | 04 |  | CIO 116 no. 2. Input 12 | BOOL |  |  |  | X | X
Digital input state | 1139 | 3 | 301140 | 04 |  | CIO 116 no. 2. Input 13 | BOOL |  |  |  | X | X
Digital input state | 1139 | 4 | 301140 | 04 |  | CIO 116 no. 2. Input 14 | BOOL |  |  |  | X | X
Digital input state | 1139 | 5 | 301140 | 04 |  | CIO 116 no. 2. Input 15 | BOOL |  |  |  | X | X
Digital input state | 1139 | 6 | 301140 | 04 |  | CIO 116 no. 2. Input 16 | BOOL |  |  |  | X | X
Digital input state | 1139 | 7 | 301140 | 04 |  | CIO 116 no. 2. Input 17 | BOOL |  |  |  | X | X
Digital input state | 1139 | 8 | 301140 | 04 |  | CIO 116 no. 2. Input 19 | BOOL |  |  |  | X | X
Digital input state | 1139 | 9 | 301140 | 04 |  | CIO 116 no. 2. Input 20 | BOOL |  |  |  | X | X
Digital input state | 1139 | 10 | 301140 | 04 |  | CIO 116 no. 2. Input 21 | BOOL |  |  |  | X | X
Digital input state | 1139 | 11 | 301140 | 04 |  | CIO 116 no. 2. Input 22 | BOOL |  |  |  | X | X
Digital input state | 1139 | 12 | 301140 | 04 |  | CIO 116 no. 2. Input 23 | BOOL |  |  |  | X | X
Digital input state | 1139 | 13 | 301140 | 04 |  | CIO 116 no. 2. Input 24 | BOOL |  |  |  | X | X
Digital input state | 1139 | 14 | 301140 | 04 |  | CIO 116 no. 2. Input 25 | BOOL |  |  |  | X | X
Digital input state | 1139 | 15 | 301140 | 04 |  | CIO 116 no. 2. Input 26 | BOOL |  |  |  | X | X
Digital input state | 1140 | 0 | 301141 | 04 |  | CIO 116 no. 3. Input 10 | BOOL |  |  |  | X | X
Digital input state | 1140 | 1 | 301141 | 04 |  | CIO 116 no. 3. Input 11 | BOOL |  |  |  | X | X
Digital input state | 1140 | 2 | 301141 | 04 |  | CIO 116 no. 3. Input 12 | BOOL |  |  |  | X | X
Digital input state | 1140 | 3 | 301141 | 04 |  | CIO 116 no. 3. Input 13 | BOOL |  |  |  | X | X
Digital input state | 1140 | 4 | 301141 | 04 |  | CIO 116 no. 3. Input 14 | BOOL |  |  |  | X | X
Digital input state | 1140 | 5 | 301141 | 04 |  | CIO 116 no. 3. Input 15 | BOOL |  |  |  | X | X
Digital input state | 1140 | 6 | 301141 | 04 |  | CIO 116 no. 3. Input 16 | BOOL |  |  |  | X | X
Digital input state | 1140 | 7 | 301141 | 04 |  | CIO 116 no. 3. Input 17 | BOOL |  |  |  | X | X
Digital input state | 1140 | 8 | 301141 | 04 |  | CIO 116 no. 3. Input 19 | BOOL |  |  |  | X | X
Digital input state | 1140 | 9 | 301141 | 04 |  | CIO 116 no. 3. Input 20 | BOOL |  |  |  | X | X
Digital input state | 1140 | 10 | 301141 | 04 |  | CIO 116 no. 3. Input 21 | BOOL |  |  |  | X | X
Digital input state | 1140 | 11 | 301141 | 04 |  | CIO 116 no. 3. Input 22 | BOOL |  |  |  | X | X
Digital input state | 1140 | 12 | 301141 | 04 |  | CIO 116 no. 3. Input 23 | BOOL |  |  |  | X | X
Digital input state | 1140 | 13 | 301141 | 04 |  | CIO 116 no. 3. Input 24 | BOOL |  |  |  | X | X
Digital input state | 1140 | 14 | 301141 | 04 |  | CIO 116 no. 3. Input 25 | BOOL |  |  |  | X | X
Digital input state | 1140 | 15 | 301141 | 04 |  | CIO 116 no. 3. Input 26 | BOOL |  |  |  | X | X
Digital output state | 1141 | 0 | 301142 | 04 |  | CIO 116 no. 1 conf. status out | BOOL |  |  |  | X | X
Digital output state | 1141 | 1 | 301142 | 04 |  | CIO 116 no. 2 conf. status out | BOOL |  |  |  | X | X
Digital output state | 1141 | 2 | 301142 | 04 |  | CIO 116 no. 3 conf. status out | BOOL |  |  |  | X | X
Digital output state | 1141 | 3 | 301142 | 04 |  | CIO 208 no. 1 conf. status out | BOOL |  |  |  | X | X
Digital output state | 1141 | 4 | 301142 | 04 |  | CIO 208 no. 2 conf. status out | BOOL |  |  |  | X | X
Digital output state | 1141 | 5 | 301142 | 04 |  | CIO 208 no. 3 conf. status out | BOOL |  |  |  | X | X
Digital output state | 1141 | 6 | 301142 | 04 |  | CIO 308 no. 1 conf. status out | BOOL |  |  |  | X | X
Digital output state | 1141 | 7 | 301142 | 04 |  | CIO 308 no. 2 conf. status out | BOOL |  |  |  | X | X
Digital output state | 1141 | 8 | 301142 | 04 |  | CIO 308 no. 3 conf. status out | BOOL |  |  |  | X | X
Digital input state | 1142 | 0 | 301143 | 04 |  | Digital input 39 | BOOL |  |  |  | X | X
Digital input state | 1142 | 1 | 301143 | 04 |  | Digital input 40 | BOOL |  |  |  | X | X
Digital input state | 1142 | 2 | 301143 | 04 |  | Digital input 41 | BOOL |  |  |  | X | X
Digital input state | 1142 | 3 | 301143 | 04 |  | Digital input 42 | BOOL |  |  |  | X | X
Digital input state | 1142 | 4 | 301143 | 04 |  | Digital input 43 | BOOL |  |  |  | X | X
Digital input state | 1142 | 5 | 301143 | 04 |  | Digital input 44 | BOOL |  |  |  | X | X
Digital input state | 1142 | 6 | 301143 | 04 |  | Digital input 45 | BOOL |  |  |  | X | X
Digital input state | 1142 | 7 | 301143 | 04 |  | Digital input 46 | BOOL |  |  |  | X | X
Digital input state | 1142 | 11 | 301143 | 04 |  | Digital input 47 | BOOL |  |  |  | X | X
Digital input state | 1142 | 12 | 301143 | 04 |  | Digital input 48 | BOOL |  |  |  | X | X
Digital input state | 1142 | 13 | 301143 | 04 |  | Digital input 49 | BOOL |  |  |  | X | X
Digital input state | 1142 | 14 | 301143 | 04 |  | Digital input 50 | BOOL |  |  |  | X | X
Digital input state | 1145 | 0 | 301146 | 04 |  | CIO 308 no. 1. Input 8 | BOOL |  |  |  | X | X
Digital input state | 1145 | 1 | 301146 | 04 |  | CIO 308 no. 1. Input 11 | BOOL |  |  |  | X | X
Digital input state | 1145 | 2 | 301146 | 04 |  | CIO 308 no. 1. Input 14 | BOOL |  |  |  | X | X
Digital input state | 1145 | 3 | 301146 | 04 |  | CIO 308 no. 1. Input 17 | BOOL |  |  |  | X | X
Digital input state | 1145 | 4 | 301146 | 04 |  | CIO 308 no. 1. Input 20 | BOOL |  |  |  | X | X
Digital input state | 1145 | 5 | 301146 | 04 |  | CIO 308 no. 1. Input 23 | BOOL |  |  |  | X | X
Digital input state | 1145 | 6 | 301146 | 04 |  | CIO 308 no. 1. Input 26 | BOOL |  |  |  | X | X
Digital input state | 1145 | 7 | 301146 | 04 |  | CIO 308 no. 1. Input 29 | BOOL |  |  |  | X | X
Digital input state | 1145 | 8 | 301146 | 04 |  | CIO 308 no. 2. Input 8 | BOOL |  |  |  | X | X
Digital input state | 1145 | 9 | 301146 | 04 |  | CIO 308 no. 2. Input 11 | BOOL |  |  |  | X | X
Digital input state | 1145 | 10 | 301146 | 04 |  | CIO 308 no. 2. Input 14 | BOOL |  |  |  | X | X
Digital input state | 1145 | 11 | 301146 | 04 |  | CIO 308 no. 2. Input 17 | BOOL |  |  |  | X | X
Digital input state | 1145 | 12 | 301146 | 04 |  | CIO 308 no. 2. Input 20 | BOOL |  |  |  | X | X
Digital input state | 1145 | 13 | 301146 | 04 |  | CIO 308 no. 2. Input 23 | BOOL |  |  |  | X | X
Digital input state | 1145 | 14 | 301146 | 04 |  | CIO 308 no. 2. Input 26 | BOOL |  |  |  | X | X
Digital input state | 1145 | 15 | 301146 | 04 |  | CIO 308 no. 2. Input 29 | BOOL |  |  |  | X | X
Digital input state | 1146 | 0 | 301147 | 04 |  | CIO 308 no. 3. Input 8 | BOOL |  |  |  | X | X
Digital input state | 1146 | 1 | 301147 | 04 |  | CIO 308 no. 3. Input 11 | BOOL |  |  |  | X | X
Digital input state | 1146 | 2 | 301147 | 04 |  | CIO 308 no. 3. Input 14 | BOOL |  |  |  | X | X
Digital input state | 1146 | 3 | 301147 | 04 |  | CIO 308 no. 3. Input 17 | BOOL |  |  |  | X | X
Digital input state | 1146 | 4 | 301147 | 04 |  | CIO 308 no. 3. Input 20 | BOOL |  |  |  | X | X
Digital input state | 1146 | 5 | 301147 | 04 |  | CIO 308 no. 3. Input 23 | BOOL |  |  |  | X | X
Digital input state | 1146 | 6 | 301147 | 04 |  | CIO 308 no. 3. Input 26 | BOOL |  |  |  | X | X
Digital input state | 1146 | 7 | 301147 | 04 |  | CIO 308 no. 3. Input 29 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 0 | 301151 | 04 |  | M-Logic Output evaluation Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 1 | 301151 | 04 |  | M-Logic Output evaluation Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 2 | 301151 | 04 |  | M-Logic Output evaluation Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 3 | 301151 | 04 |  | M-Logic Output evaluation Line 4 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 4 | 301151 | 04 |  | M-Logic Output evaluation Line 5 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 5 | 301151 | 04 |  | M-Logic Output evaluation Line 6 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 6 | 301151 | 04 |  | M-Logic Output evaluation Line 7 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 7 | 301151 | 04 |  | M-Logic Output evaluation Line 8 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 8 | 301151 | 04 |  | M-Logic Output evaluation Line 9 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 9 | 301151 | 04 |  | M-Logic Output evaluation Line 10 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 10 | 301151 | 04 |  | M-Logic Output evaluation Line 11 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 11 | 301151 | 04 |  | M-Logic Output evaluation Line 12 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 12 | 301151 | 04 |  | M-Logic Output evaluation Line 13 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 13 | 301151 | 04 |  | M-Logic Output evaluation Line 14 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 14 | 301151 | 04 |  | M-Logic Output evaluation Line 15 | BOOL |  |  |  | X | X
M-Logic state | 1150 | 15 | 301151 | 04 |  | M-Logic Output evaluation Line 16 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 0 | 301152 | 04 |  | M-Logic Output evaluation Line 17 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 1 | 301152 | 04 |  | M-Logic Output evaluation Line 18 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 2 | 301152 | 04 |  | M-Logic Output evaluation Line 19 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 3 | 301152 | 04 |  | M-Logic Output evaluation Line 20 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 4 | 301152 | 04 |  | M-Logic Output evaluation Line 21 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 5 | 301152 | 04 |  | M-Logic Output evaluation Line 22 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 6 | 301152 | 04 |  | M-Logic Output evaluation Line 23 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 7 | 301152 | 04 |  | M-Logic Output evaluation Line 24 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 8 | 301152 | 04 |  | M-Logic Output evaluation Line 25 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 9 | 301152 | 04 |  | M-Logic Output evaluation Line 26 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 10 | 301152 | 04 |  | M-Logic Output evaluation Line 27 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 11 | 301152 | 04 |  | M-Logic Output evaluation Line 28 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 12 | 301152 | 04 |  | M-Logic Output evaluation Line 29 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 13 | 301152 | 04 |  | M-Logic Output evaluation Line 30 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 14 | 301152 | 04 |  | M-Logic Output evaluation Line 31 | BOOL |  |  |  | X | X
M-Logic state | 1151 | 15 | 301152 | 04 |  | M-Logic Output evaluation Line 32 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 0 | 301153 | 04 |  | M-Logic Output evaluation Line 33 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 1 | 301153 | 04 |  | M-Logic Output evaluation Line 34 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 2 | 301153 | 04 |  | M-Logic Output evaluation Line 35 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 3 | 301153 | 04 |  | M-Logic Output evaluation Line 36 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 4 | 301153 | 04 |  | M-Logic Output evaluation Line 37 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 5 | 301153 | 04 |  | M-Logic Output evaluation Line 38 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 6 | 301153 | 04 |  | M-Logic Output evaluation Line 39 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 7 | 301153 | 04 |  | M-Logic Output evaluation Line 40 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 8 | 301153 | 04 |  | M-Logic Output evaluation Line 41 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 9 | 301153 | 04 |  | M-Logic Output evaluation Line 42 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 10 | 301153 | 04 |  | M-Logic Output evaluation Line 43 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 11 | 301153 | 04 |  | M-Logic Output evaluation Line 44 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 12 | 301153 | 04 |  | M-Logic Output evaluation Line 45 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 13 | 301153 | 04 |  | M-Logic Output evaluation Line 46 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 14 | 301153 | 04 |  | M-Logic Output evaluation Line 47 | BOOL |  |  |  | X | X
M-Logic state | 1152 | 15 | 301153 | 04 |  | M-Logic Output evaluation Line 48 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 0 | 301154 | 04 |  | M-Logic Output evaluation Line 49 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 1 | 301154 | 04 |  | M-Logic Output evaluation Line 50 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 2 | 301154 | 04 |  | M-Logic Output evaluation Line 51 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 3 | 301154 | 04 |  | M-Logic Output evaluation Line 52 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 4 | 301154 | 04 |  | M-Logic Output evaluation Line 53 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 5 | 301154 | 04 |  | M-Logic Output evaluation Line 54 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 6 | 301154 | 04 |  | M-Logic Output evaluation Line 55 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 7 | 301154 | 04 |  | M-Logic Output evaluation Line 56 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 8 | 301154 | 04 |  | M-Logic Output evaluation Line 57 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 9 | 301154 | 04 |  | M-Logic Output evaluation Line 58 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 10 | 301154 | 04 |  | M-Logic Output evaluation Line 59 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 11 | 301154 | 04 |  | M-Logic Output evaluation Line 60 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 12 | 301154 | 04 |  | M-Logic Output evaluation Line 61 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 13 | 301154 | 04 |  | M-Logic Output evaluation Line 62 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 14 | 301154 | 04 |  | M-Logic Output evaluation Line 63 | BOOL |  |  |  | X | X
M-Logic state | 1153 | 15 | 301154 | 04 |  | M-Logic Output evaluation Line 64 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 0 | 301155 | 04 |  | M-Logic Output evaluation Line 65 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 1 | 301155 | 04 |  | M-Logic Output evaluation Line 66 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 2 | 301155 | 04 |  | M-Logic Output evaluation Line 67 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 3 | 301155 | 04 |  | M-Logic Output evaluation Line 68 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 4 | 301155 | 04 |  | M-Logic Output evaluation Line 69 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 5 | 301155 | 04 |  | M-Logic Output evaluation Line 70 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 6 | 301155 | 04 |  | M-Logic Output evaluation Line 71 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 7 | 301155 | 04 |  | M-Logic Output evaluation Line 72 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 8 | 301155 | 04 |  | M-Logic Output evaluation Line 73 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 9 | 301155 | 04 |  | M-Logic Output evaluation Line 74 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 10 | 301155 | 04 |  | M-Logic Output evaluation Line 75 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 11 | 301155 | 04 |  | M-Logic Output evaluation Line 76 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 12 | 301155 | 04 |  | M-Logic Output evaluation Line 77 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 13 | 301155 | 04 |  | M-Logic Output evaluation Line 78 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 14 | 301155 | 04 |  | M-Logic Output evaluation Line 79 | BOOL |  |  |  | X | X
M-Logic state | 1154 | 15 | 301155 | 04 |  | M-Logic Output evaluation Line 80 | BOOL |  |  |  | X | X
M-Logic state | 1155 | 8 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 1 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1155 | 9 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 1 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1155 | 10 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 1 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1155 | 11 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 2 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1155 | 12 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 2 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1155 | 13 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 2 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1155 | 14 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 3 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1155 | 15 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 3 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 0 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 3 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 1 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 4 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 2 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 4 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 3 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 4 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 4 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 5 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 5 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 5 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 6 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 5 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 7 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 6 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 8 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 6 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 9 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 6 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 10 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 7 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 11 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 7 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 12 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 7 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 13 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 8 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 14 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 8 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1156 | 15 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 8 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 0 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 9 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 1 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 9 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 2 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 9 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 3 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 10 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 4 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 10 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 5 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 10 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 6 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 11 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 7 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 11 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 8 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 11 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 9 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 12 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 10 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 12 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 11 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 12 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 12 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 13 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 13 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 13 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 14 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 13 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1157 | 15 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 14 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 0 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 14 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 1 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 14 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 2 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 15 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 3 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 15 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 4 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 15 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 5 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 16 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 6 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 16 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 7 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 16 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 8 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 1 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 9 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 1 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 10 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 1 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 11 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 2 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 12 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 2 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 13 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 2 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 14 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 3 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1158 | 15 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 3 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 0 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 3 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 1 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 4 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 2 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 4 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 3 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 4 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 4 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 5 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 5 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 5 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 6 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 5 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 7 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 6 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 8 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 6 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 9 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 6 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 10 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 7 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 11 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 7 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 12 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 7 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 13 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 8 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 14 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 8 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1159 | 15 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 8 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 0 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 9 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 1 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 9 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 2 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 9 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 3 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 10 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 4 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 10 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 5 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 10 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 6 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 11 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 7 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 11 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 8 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 11 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 9 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 12 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 10 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 12 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 11 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 12 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 12 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 13 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 13 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 13 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 14 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 13 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1160 | 15 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 14 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1161 | 0 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 14 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1161 | 1 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 14 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1161 | 2 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 15 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1161 | 3 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 15 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1161 | 4 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 15 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1161 | 5 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 16 Line 1 | BOOL |  |  |  | X | X
M-Logic state | 1161 | 6 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 16 Line 2 | BOOL |  |  |  | X | X
M-Logic state | 1161 | 7 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 16 Line 3 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 0 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 1 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 1 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 2 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 2 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 3 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 3 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 4 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 4 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 5 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 5 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 6 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 6 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 7 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 7 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 8 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 8 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 1 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 9 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 2 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 10 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 3 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 11 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 4 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 12 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 5 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 13 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 6 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 14 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 7 | BOOL |  |  |  | X | X
M-Logic state | 1171 | 15 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 8 | BOOL |  |  |  | X | X
M-Logic state | 1173 | 8 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_1 Buzzer 1 | BOOL |  |  |  | X | X
M-Logic state | 1173 | 9 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_1 Buzzer 2 | BOOL |  |  |  | X | X
M-Logic state | 1173 | 10 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_1 Buzzer 3 | BOOL |  |  |  | X | X
M-Logic state | 1173 | 11 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_2 Buzzer 1 | BOOL |  |  |  | X | X
M-Logic state | 1173 | 12 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_2 Buzzer 2 | BOOL |  |  |  | X | X
M-Logic state | 1173 | 13 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_2 Buzzer 3 | BOOL |  |  |  | X | X
M-Logic state | 1174 | 7 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_1 Relay 1 | BOOL |  |  |  | X | X
M-Logic state | 1174 | 8 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_1 Relay 2 | BOOL |  |  |  | X | X
M-Logic state | 1174 | 9 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_1 Relay 3 | BOOL |  |  |  | X | X
M-Logic state | 1174 | 10 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_2 Relay 1 | BOOL |  |  |  | X | X
M-Logic state | 1174 | 11 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_2 Relay 2 | BOOL |  |  |  | X | X
M-Logic state | 1174 | 12 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_2 Relay 3 | BOOL |  |  |  | X | X
AC measurement | 1320 |  | 301321 | 04 |  | ESS power reference | INT16s | AB | 0 | kW |  | X
AC measurement | 1320 |  | 301321 | 04 |  | PV power reference | INT16s | AB | 0 | kW | X
AC measurement | 1321 |  | 301322 | 04 |  | ESS reactive power reference | INT16s | AB | 0 | kW |  | X
AC measurement | 1321 |  | 301322 | 04 |  | PV reactive power reference | INT16s | AB | 0 | kW | X
AC measurement | 1322 |  | 301323 | 04 |  | ESS power actual | INT16s | AB | 0 | kW |  | X
AC measurement | 1322 |  | 301323 | 04 |  | PV power actual | INT16s | AB | 0 | kW | X
AC measurement | 1323 |  | 301324 | 04 |  | ESS reactive power actual | INT16s | AB | 0 | kW |  | X
AC measurement | 1323 |  | 301324 | 04 |  | PV reactive power actual | INT16s | AB | 0 | kW | X
AC measurement | 1324 |  | 301325 | 04 |  | ESS nominal power actual | INT16s | AB | 0 | kW |  | X
AC measurement | 1324 |  | 301325 | 04 |  | PV nominal power actual | INT16s | AB | 0 | kW | X
Plant logic state | 1325 |  | 301326 | 04 |  | ESS breaker status | INT16s | AB | 0 |  |  | X
Plant logic state | 1325 |  | 301326 | 04 |  | PV breaker status | INT16s | AB | 0 |  | X
Alarm | 1326 | 0 | 301327 | 04 |  | ESS running status | BOOL |  |  |  |  | X
Alarm | 1326 | 0 | 301327 | 04 |  | PV running status | BOOL |  |  |  | X
Alarm | 1360 | 0 | 301361 | 04 | 3660 | M-Logic alarm 10 | BOOL |  |  |  | X | X
Alarm | 1360 | 1 | 301361 | 04 | 3670 | M-Logic alarm 11 | BOOL |  |  |  | X | X
Alarm | 1360 | 2 | 301361 | 04 | 3680 | M-Logic alarm 12 | BOOL |  |  |  | X | X
Alarm | 1360 | 3 | 301361 | 04 | 3690 | M-Logic alarm 13 | BOOL |  |  |  | X | X
Alarm | 1360 | 4 | 301361 | 04 | 3700 | M-Logic alarm 14 | BOOL |  |  |  | X | X
PM AC measurement | 1500 |  | 301501 | 04 |  | Total power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1501 |  | 301502 | 04 |  | Available power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1502 |  | 301503 | 04 |  | Total nominal power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1503 |  | 301504 | 04 |  | Total genset power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1504 |  | 301505 | 04 |  | Total reactive power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1505 |  | 301506 | 04 |  | Number of gensets in application | INT16s | AB | 0 |  | X | X
PM AC measurement | 1506 |  | 301507 | 04 |  | Plant type | INT16s | AB | 0 |  | X | X
PM AC measurement | 1510 |  | 301511 | 04 |  | Nominal power ID 1 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1511 |  | 301512 | 04 |  | Nominal power ID 2 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1512 |  | 301513 | 04 |  | Nominal power ID 3 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1513 |  | 301514 | 04 |  | Nominal power ID 4 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1514 |  | 301515 | 04 |  | Nominal power ID 5 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1515 |  | 301516 | 04 |  | Nominal power ID 6 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1516 |  | 301517 | 04 |  | Nominal power ID 7 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1517 |  | 301518 | 04 |  | Nominal power ID 8 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1518 |  | 301519 | 04 |  | Nominal power ID 9 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1519 |  | 301520 | 04 |  | Nominal power ID 10 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1520 |  | 301521 | 04 |  | Nominal power ID 11 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1521 |  | 301522 | 04 |  | Nominal power ID 12 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1522 |  | 301523 | 04 |  | Nominal power ID 13 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1523 |  | 301524 | 04 |  | Nominal power ID 14 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1524 |  | 301525 | 04 |  | Nominal power ID 15 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1525 |  | 301526 | 04 |  | Nominal power ID 16 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1526 |  | 301527 | 04 |  | Active Power ID 1 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1527 |  | 301528 | 04 |  | Active Power ID 2 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1528 |  | 301529 | 04 |  | Active Power ID 3 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1529 |  | 301530 | 04 |  | Active Power ID 4 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1530 |  | 301531 | 04 |  | Active Power ID 5 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1531 |  | 301532 | 04 |  | Active Power ID 6 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1532 |  | 301533 | 04 |  | Active Power ID 7 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1533 |  | 301534 | 04 |  | Active Power ID 8 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1534 |  | 301535 | 04 |  | Active Power ID 9 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1535 |  | 301536 | 04 |  | Active Power ID 10 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1536 |  | 301537 | 04 |  | Active Power ID 11 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1537 |  | 301538 | 04 |  | Active Power ID 12 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1538 |  | 301539 | 04 |  | Active Power ID 13 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1539 |  | 301540 | 04 |  | Active Power ID 14 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1540 |  | 301541 | 04 |  | Active Power ID 15 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1541 |  | 301542 | 04 |  | Active Power ID 16 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1542 |  | 301543 | 04 |  | Reactive Power ID 1 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1543 |  | 301544 | 04 |  | Reactive Power ID 2 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1544 |  | 301545 | 04 |  | Reactive Power ID 3 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1545 |  | 301546 | 04 |  | Reactive Power ID 4 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1546 |  | 301547 | 04 |  | Reactive Power ID 5 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1547 |  | 301548 | 04 |  | Reactive Power ID 6 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1548 |  | 301549 | 04 |  | Reactive Power ID 7 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1549 |  | 301550 | 04 |  | Reactive Power ID 8 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1550 |  | 301551 | 04 |  | Reactive Power ID 9 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1551 |  | 301552 | 04 |  | Reactive Power ID 10 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1552 |  | 301553 | 04 |  | Reactive Power ID 11 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1553 |  | 301554 | 04 |  | Reactive Power ID 12 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1554 |  | 301555 | 04 |  | Reactive Power ID 13 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1555 |  | 301556 | 04 |  | Reactive Power ID 14 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1556 |  | 301557 | 04 |  | Reactive Power ID 15 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1557 |  | 301558 | 04 |  | Reactive Power ID 16 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1560 |  | 301561 | 04 |  | Active Power ID 17 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1561 |  | 301562 | 04 |  | Active Power ID 18 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1562 |  | 301563 | 04 |  | Active Power ID 19 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1563 |  | 301564 | 04 |  | Active Power ID 20 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1565 |  | 301566 | 04 |  | Reactive Power ID 17 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1566 |  | 301567 | 04 |  | Reactive Power ID 18 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1567 |  | 301568 | 04 |  | Reactive Power ID 19 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1568 |  | 301569 | 04 |  | Reactive Power ID 20 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1569 |  | 301570 | 04 |  | Active Power ID 17 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1570 |  | 301571 | 04 |  | Active Power ID 18 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1571 |  | 301572 | 04 |  | Active Power ID 19 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1572 |  | 301573 | 04 |  | Active Power ID 20 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1573 |  | 301574 | 04 |  | Active Power ID 21 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1574 |  | 301575 | 04 |  | Active Power ID 22 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1575 |  | 301576 | 04 |  | Active Power ID 23 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1576 |  | 301577 | 04 |  | Active Power ID 24 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1577 |  | 301578 | 04 |  | Active Power ID 25 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1578 |  | 301579 | 04 |  | Active Power ID 26 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1579 |  | 301580 | 04 |  | Active Power ID 27 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1580 |  | 301581 | 04 |  | Active Power ID 28 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1581 |  | 301582 | 04 |  | Active Power ID 29 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1582 |  | 301583 | 04 |  | Active Power ID 30 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1583 |  | 301584 | 04 |  | Active Power ID 31 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1584 |  | 301585 | 04 |  | Active Power ID 32 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1585 |  | 301586 | 04 |  | Reactive Power ID 17 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1586 |  | 301587 | 04 |  | Reactive Power ID 18 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1587 |  | 301588 | 04 |  | Reactive Power ID 19 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1588 |  | 301589 | 04 |  | Reactive Power ID 20 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1589 |  | 301590 | 04 |  | Reactive Power ID 21 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1590 |  | 301591 | 04 |  | Reactive Power ID 22 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1591 |  | 301592 | 04 |  | Reactive Power ID 23 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1592 |  | 301593 | 04 |  | Reactive Power ID 24 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1593 |  | 301594 | 04 |  | Reactive Power ID 25 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1594 |  | 301595 | 04 |  | Reactive Power ID 26 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1595 |  | 301596 | 04 |  | Reactive Power ID 27 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1596 |  | 301597 | 04 |  | Reactive Power ID 28 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1597 |  | 301598 | 04 |  | Reactive Power ID 29 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1598 |  | 301599 | 04 |  | Reactive Power ID 30 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1599 |  | 301600 | 04 |  | Reactive Power ID 31 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1600 |  | 301601 | 04 |  | Reactive Power ID 32 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1601 |  | 301602 | 04 |  | Active Power ID 33 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1602 |  | 301603 | 04 |  | Active Power ID 34 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1603 |  | 301604 | 04 |  | Active Power ID 35 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1604 |  | 301605 | 04 |  | Active Power ID 36 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1605 |  | 301606 | 04 |  | Active Power ID 37 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1606 |  | 301607 | 04 |  | Active Power ID 38 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1607 |  | 301608 | 04 |  | Active Power ID 39 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1608 |  | 301609 | 04 |  | Active Power ID 40 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1609 |  | 301610 | 04 |  | Reactive Power ID 33 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1610 |  | 301611 | 04 |  | Reactive Power ID 34 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1611 |  | 301612 | 04 |  | Reactive Power ID 35 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1612 |  | 301613 | 04 |  | Reactive Power ID 36 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1613 |  | 301614 | 04 |  | Reactive Power ID 37 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1614 |  | 301615 | 04 |  | Reactive Power ID 38 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1615 |  | 301616 | 04 |  | Reactive Power ID 39 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1616 |  | 301617 | 04 |  | Reactive Power ID 40 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1617 |  | 301618 | 04 |  | Plant mode mains 17 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1618 |  | 301619 | 04 |  | Plant mode mains 18 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1619 |  | 301620 | 04 |  | Plant mode mains 19 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1620 |  | 301621 | 04 |  | Plant mode mains 20 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1621 |  | 301622 | 04 |  | Plant mode mains 21 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1622 |  | 301623 | 04 |  | Plant mode mains 22 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1623 |  | 301624 | 04 |  | Plant mode mains 23 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1624 |  | 301625 | 04 |  | Plant mode mains 24 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1625 |  | 301626 | 04 |  | Plant mode mains 25 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1626 |  | 301627 | 04 |  | Plant mode mains 26 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1627 |  | 301628 | 04 |  | Plant mode mains 27 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1628 |  | 301629 | 04 |  | Plant mode mains 28 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1629 |  | 301630 | 04 |  | Plant mode mains 29 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1630 |  | 301631 | 04 |  | Plant mode mains 30 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1631 |  | 301632 | 04 |  | Plant mode mains 31 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1632 |  | 301633 | 04 |  | Plant mode mains 32 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1633 |  | 301634 | 04 |  | Bus power mains 17 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1634 |  | 301635 | 04 |  | Bus power mains 18 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1635 |  | 301636 | 04 |  | Bus power mains 19 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1636 |  | 301637 | 04 |  | Bus power mains 20 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1637 |  | 301638 | 04 |  | Bus power mains 21 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1638 |  | 301639 | 04 |  | Bus power mains 22 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1639 |  | 301640 | 04 |  | Bus power mains 23 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1640 |  | 301641 | 04 |  | Bus power mains 24 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1641 |  | 301642 | 04 |  | Bus power mains 25 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1642 |  | 301643 | 04 |  | Bus power mains 26 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1643 |  | 301644 | 04 |  | Bus power mains 27 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1644 |  | 301645 | 04 |  | Bus power mains 28 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1645 |  | 301646 | 04 |  | Bus power mains 29 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1646 |  | 301647 | 04 |  | Bus power mains 30 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1647 |  | 301648 | 04 |  | Bus power mains 31 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1648 |  | 301649 | 04 |  | Bus power mains 32 | INT16s | AB | 0 |  | X | X
PM Plant logic state | 1649 | 0 | 301650 | 04 |  | Mains transducer-configured, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 1 | 301650 | 04 |  | Mains transducer-configured, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 2 | 301650 | 04 |  | Mains transducer-configured, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 3 | 301650 | 04 |  | Mains transducer-configured, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 4 | 301650 | 04 |  | Mains transducer-configured, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 5 | 301650 | 04 |  | Mains transducer-configured, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 6 | 301650 | 04 |  | Mains transducer-configured, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 7 | 301650 | 04 |  | Mains transducer-configured, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 8 | 301650 | 04 |  | Mains transducer-configured, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 9 | 301650 | 04 |  | Mains transducer-configured, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 10 | 301650 | 04 |  | Mains transducer-configured, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 11 | 301650 | 04 |  | Mains transducer-configured, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 12 | 301650 | 04 |  | Mains transducer-configured, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 13 | 301650 | 04 |  | Mains transducer-configured, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 14 | 301650 | 04 |  | Mains transducer-configured, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 15 | 301650 | 04 |  | Mains transducer-configured, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 0 | 301651 | 04 |  | TB transducer-configured, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 1 | 301651 | 04 |  | TB transducer-configured, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 2 | 301651 | 04 |  | TB transducer-configured, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 3 | 301651 | 04 |  | TB transducer-configured, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 4 | 301651 | 04 |  | TB transducer-configured, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 5 | 301651 | 04 |  | TB transducer-configured, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 6 | 301651 | 04 |  | TB transducer-configured, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 7 | 301651 | 04 |  | TB transducer-configured, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 8 | 301651 | 04 |  | TB transducer-configured, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 9 | 301651 | 04 |  | TB transducer-configured, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 10 | 301651 | 04 |  | TB transducer-configured, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 11 | 301651 | 04 |  | TB transducer-configured, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 12 | 301651 | 04 |  | TB transducer-configured, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 13 | 301651 | 04 |  | TB transducer-configured, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 14 | 301651 | 04 |  | TB transducer-configured, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 15 | 301651 | 04 |  | TB transducer-configured, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 0 | 301652 | 04 |  | BTB transducer-configured, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 1 | 301652 | 04 |  | BTB transducer-configured, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 2 | 301652 | 04 |  | BTB transducer-configured, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 3 | 301652 | 04 |  | BTB transducer-configured, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 4 | 301652 | 04 |  | BTB transducer-configured, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 5 | 301652 | 04 |  | BTB transducer-configured, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 6 | 301652 | 04 |  | BTB transducer-configured, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 7 | 301652 | 04 |  | BTB transducer-configured, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 0 | 301653 | 04 |  | ID 33 BTB controlled | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 1 | 301653 | 04 |  | ID 34 BTB controlled | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 2 | 301653 | 04 |  | ID 35 BTB controlled | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 3 | 301653 | 04 |  | ID 36 BTB controlled | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 4 | 301653 | 04 |  | ID 37 BTB controlled | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 5 | 301653 | 04 |  | ID 38 BTB controlled | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 6 | 301653 | 04 |  | ID 39 BTB controlled | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 7 | 301653 | 04 |  | ID 40 BTB controlled | BOOL |  |  |  | X | X
PM AC measurement | 1653 |  | 301654 | 04 |  | Nominal power ID 17 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1654 |  | 301655 | 04 |  | Nominal power ID 18 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1655 |  | 301656 | 04 |  | Nominal power ID 19 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1656 |  | 301657 | 04 |  | Nominal power ID 20 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1657 |  | 301658 | 04 |  | Nominal power ID 21 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1658 |  | 301659 | 04 |  | Nominal power ID 22 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1659 |  | 301660 | 04 |  | Nominal power ID 23 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1660 |  | 301661 | 04 |  | Nominal power ID 24 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1661 |  | 301662 | 04 |  | Nominal power ID 25 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1662 |  | 301663 | 04 |  | Nominal power ID 26 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1663 |  | 301664 | 04 |  | Nominal power ID 27 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1664 |  | 301665 | 04 |  | Nominal power ID 28 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1665 |  | 301666 | 04 |  | Nominal power ID 29 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1666 |  | 301667 | 04 |  | Nominal power ID 30 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1667 |  | 301668 | 04 |  | Nominal power ID 31 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1668 |  | 301669 | 04 |  | Nominal power ID 32 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1696 |  | 301697 | 04 |  | Total PV active power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1697 |  | 301698 | 04 |  | Total PV reactive power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1698 |  | 301699 | 04 |  | Total Battery active power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1699 |  | 301700 | 04 |  | Total Battery reactive power | INT16s | AB | 0 |  | X | X
PM Plant logic state | 1700 | 0 | 301701 | 04 |  | TB available | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 1 | 301701 | 04 |  | Mains unit available | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 2 | 301701 | 04 |  | Any MB pos. ON | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 3 | 301701 | 04 |  | All MB pos. OFF | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 4 | 301701 | 04 |  | TB pos. ON (Mains Command Unit) | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 5 | 301701 | 04 |  | TB pos. OFF (Mains Command Unit) | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 6 | 301701 | 04 |  | Any GB pos. ON | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 7 | 301701 | 04 |  | All GB pos. OFF | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 8 | 301701 | 04 |  | Any TB pos. ON | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 9 | 301701 | 04 |  | All TB pos. OFF | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 10 | 301701 | 04 |  | Any BTB pos. ON | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 0 | 301702 | 04 |  | GB pos. ON ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 1 | 301702 | 04 |  | GB pos. ON ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 2 | 301702 | 04 |  | GB pos. ON ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 3 | 301702 | 04 |  | GB pos. ON ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 4 | 301702 | 04 |  | GB pos. ON ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 5 | 301702 | 04 |  | GB pos. ON ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 6 | 301702 | 04 |  | GB pos. ON ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 7 | 301702 | 04 |  | GB pos. ON ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 8 | 301702 | 04 |  | GB pos. ON ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 9 | 301702 | 04 |  | GB pos. ON ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 10 | 301702 | 04 |  | GB pos. ON ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 11 | 301702 | 04 |  | GB pos. ON ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 12 | 301702 | 04 |  | GB pos. ON ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 13 | 301702 | 04 |  | GB pos. ON ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 14 | 301702 | 04 |  | GB pos. ON ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 15 | 301702 | 04 |  | GB pos. ON ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 0 | 301703 | 04 |  | GB pos. OFF ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 1 | 301703 | 04 |  | GB pos. OFF ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 2 | 301703 | 04 |  | GB pos. OFF ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 3 | 301703 | 04 |  | GB pos. OFF ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 4 | 301703 | 04 |  | GB pos. OFF ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 5 | 301703 | 04 |  | GB pos. OFF ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 6 | 301703 | 04 |  | GB pos. OFF ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 7 | 301703 | 04 |  | GB pos. OFF ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 8 | 301703 | 04 |  | GB pos. OFF ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 9 | 301703 | 04 |  | GB pos. OFF ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 10 | 301703 | 04 |  | GB pos. OFF ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 11 | 301703 | 04 |  | GB pos. OFF ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 12 | 301703 | 04 |  | GB pos. OFF ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 13 | 301703 | 04 |  | GB pos. OFF ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 14 | 301703 | 04 |  | GB pos. OFF ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 15 | 301703 | 04 |  | GB pos. OFF ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 0 | 301704 | 04 |  | DG Hz/V OK, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 1 | 301704 | 04 |  | DG Hz/V OK, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 2 | 301704 | 04 |  | DG Hz/V OK, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 3 | 301704 | 04 |  | DG Hz/V OK, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 4 | 301704 | 04 |  | DG Hz/V OK, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 5 | 301704 | 04 |  | DG Hz/V OK, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 6 | 301704 | 04 |  | DG Hz/V OK, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 7 | 301704 | 04 |  | DG Hz/V OK, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 8 | 301704 | 04 |  | DG Hz/V OK, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 9 | 301704 | 04 |  | DG Hz/V OK, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 10 | 301704 | 04 |  | DG Hz/V OK, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 11 | 301704 | 04 |  | DG Hz/V OK, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 12 | 301704 | 04 |  | DG Hz/V OK, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 13 | 301704 | 04 |  | DG Hz/V OK, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 14 | 301704 | 04 |  | DG Hz/V OK, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 15 | 301704 | 04 |  | DG Hz/V OK, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1704 | 0 | 301705 | 04 |  | Mains OK, single mains | BOOL |  |  |  | X | X
PM Plant logic state | 1704 | 1 | 301705 | 04 |  | Mains OK, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1704 | 2 | 301705 | 04 |  | Mains OK, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1704 | 3 | 301705 | 04 |  | Mains OK, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1704 | 4 | 301705 | 04 |  | Mains OK, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 0 | 301706 | 04 |  | Ready for auto start, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 1 | 301706 | 04 |  | Ready for auto start, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 2 | 301706 | 04 |  | Ready for auto start, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 3 | 301706 | 04 |  | Ready for auto start, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 4 | 301706 | 04 |  | Ready for auto start, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 5 | 301706 | 04 |  | Ready for auto start, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 6 | 301706 | 04 |  | Ready for auto start, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 7 | 301706 | 04 |  | Ready for auto start, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 8 | 301706 | 04 |  | Ready for auto start, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 9 | 301706 | 04 |  | Ready for auto start, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 10 | 301706 | 04 |  | Ready for auto start, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 11 | 301706 | 04 |  | Ready for auto start, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 12 | 301706 | 04 |  | Ready for auto start, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 13 | 301706 | 04 |  | Ready for auto start, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 14 | 301706 | 04 |  | Ready for auto start, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 15 | 301706 | 04 |  | Ready for auto start, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1706 | 0 | 301707 | 04 |  | Mains not in semi, single mains | BOOL |  |  |  | X | X
PM Plant logic state | 1706 | 1 | 301707 | 04 |  | Mains not in semi, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1706 | 2 | 301707 | 04 |  | Mains not in semi, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1706 | 3 | 301707 | 04 |  | Mains not in semi, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1706 | 4 | 301707 | 04 |  | Mains not in semi, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 0 | 301708 | 04 |  | Any alarms, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 1 | 301708 | 04 |  | Any alarms, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 2 | 301708 | 04 |  | Any alarms, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 3 | 301708 | 04 |  | Any alarms, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 4 | 301708 | 04 |  | Any alarms, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 5 | 301708 | 04 |  | Any alarms, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 6 | 301708 | 04 |  | Any alarms, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 7 | 301708 | 04 |  | Any alarms, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 8 | 301708 | 04 |  | Any alarms, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 9 | 301708 | 04 |  | Any alarms, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 10 | 301708 | 04 |  | Any alarms, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 11 | 301708 | 04 |  | Any alarms, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 12 | 301708 | 04 |  | Any alarms, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 13 | 301708 | 04 |  | Any alarms, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 14 | 301708 | 04 |  | Any alarms, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 15 | 301708 | 04 |  | Any alarms, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1708 | 0 | 301709 | 04 |  | Any alarms, single mains | BOOL |  |  |  | X | X
PM Plant logic state | 1708 | 1 | 301709 | 04 |  | Any alarms, mains 1A | BOOL |  |  |  | X | X
PM Plant logic state | 1708 | 2 | 301709 | 04 |  | Any alarms, mains 1B | BOOL |  |  |  | X | X
PM Plant logic state | 1708 | 3 | 301709 | 04 |  | Any alarms, mains 2A | BOOL |  |  |  | X | X
PM Plant logic state | 1708 | 4 | 301709 | 04 |  | Any alarms, mains 2B | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 0 | 301710 | 04 |  | Engine running, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 1 | 301710 | 04 |  | Engine running, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 2 | 301710 | 04 |  | Engine running, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 3 | 301710 | 04 |  | Engine running, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 4 | 301710 | 04 |  | Engine running, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 5 | 301710 | 04 |  | Engine running, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 6 | 301710 | 04 |  | Engine running, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 7 | 301710 | 04 |  | Engine running, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 8 | 301710 | 04 |  | Engine running, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 9 | 301710 | 04 |  | Engine running, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 10 | 301710 | 04 |  | Engine running, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 11 | 301710 | 04 |  | Engine running, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 12 | 301710 | 04 |  | Engine running, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 13 | 301710 | 04 |  | Engine running, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 14 | 301710 | 04 |  | Engine running, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 15 | 301710 | 04 |  | Engine running, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 0 | 301711 | 04 |  | MB pos. ON, single mains | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 1 | 301711 | 04 |  | MB pos. ON, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 2 | 301711 | 04 |  | MB pos. ON, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 3 | 301711 | 04 |  | MB pos. ON, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 4 | 301711 | 04 |  | MB pos. ON, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 5 | 301711 | 04 |  | MB pos. OFF, single mains | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 6 | 301711 | 04 |  | MB pos. OFF, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 7 | 301711 | 04 |  | MB pos. OFF, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 8 | 301711 | 04 |  | MB pos. OFF, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 0 | 301712 | 04 |  | GB synchronising, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 1 | 301712 | 04 |  | GB synchronising, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 2 | 301712 | 04 |  | GB synchronising, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 3 | 301712 | 04 |  | GB synchronising, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 4 | 301712 | 04 |  | GB synchronising, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 5 | 301712 | 04 |  | GB synchronising, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 6 | 301712 | 04 |  | GB synchronising, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 7 | 301712 | 04 |  | GB synchronising, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 8 | 301712 | 04 |  | GB synchronising, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 9 | 301712 | 04 |  | GB synchronising, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 10 | 301712 | 04 |  | GB synchronising, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 11 | 301712 | 04 |  | GB synchronising, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 12 | 301712 | 04 |  | GB synchronising, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 13 | 301712 | 04 |  | GB synchronising, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 14 | 301712 | 04 |  | GB synchronising, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 15 | 301712 | 04 |  | GB synchronising, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 0 | 301713 | 04 |  | Mains OK, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 1 | 301713 | 04 |  | Mains OK, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 2 | 301713 | 04 |  | Mains OK, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 3 | 301713 | 04 |  | Mains OK, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 4 | 301713 | 04 |  | Mains OK, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 5 | 301713 | 04 |  | Mains OK, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 6 | 301713 | 04 |  | Mains OK, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 7 | 301713 | 04 |  | Mains OK, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 8 | 301713 | 04 |  | Mains OK, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 9 | 301713 | 04 |  | Mains OK, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 10 | 301713 | 04 |  | Mains OK, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 11 | 301713 | 04 |  | Mains OK, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 12 | 301713 | 04 |  | Mains OK, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 13 | 301713 | 04 |  | Mains OK, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 14 | 301713 | 04 |  | Mains OK, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 15 | 301713 | 04 |  | Mains OK, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 0 | 301714 | 04 |  | Mains not in semi 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 1 | 301714 | 04 |  | Mains not in semi 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 2 | 301714 | 04 |  | Mains not in semi 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 3 | 301714 | 04 |  | Mains not in semi 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 4 | 301714 | 04 |  | Mains not in semi 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 5 | 301714 | 04 |  | Mains not in semi 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 6 | 301714 | 04 |  | Mains not in semi 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 7 | 301714 | 04 |  | Mains not in semi 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 8 | 301714 | 04 |  | Mains not in semi 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 9 | 301714 | 04 |  | Mains not in semi 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 10 | 301714 | 04 |  | Mains not in semi 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 11 | 301714 | 04 |  | Mains not in semi 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 12 | 301714 | 04 |  | Mains not in semi 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 13 | 301714 | 04 |  | Mains not in semi 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 14 | 301714 | 04 |  | Mains not in semi 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 15 | 301714 | 04 |  | Mains not in semi 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 0 | 301715 | 04 |  | Any alarms, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 1 | 301715 | 04 |  | Any alarms, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 2 | 301715 | 04 |  | Any alarms, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 3 | 301715 | 04 |  | Any alarms, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 4 | 301715 | 04 |  | Any alarms, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 5 | 301715 | 04 |  | Any alarms, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 6 | 301715 | 04 |  | Any alarms, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 7 | 301715 | 04 |  | Any alarms, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 8 | 301715 | 04 |  | Any alarms, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 9 | 301715 | 04 |  | Any alarms, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 10 | 301715 | 04 |  | Any alarms, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 11 | 301715 | 04 |  | Any alarms, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 12 | 301715 | 04 |  | Any alarms, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 13 | 301715 | 04 |  | Any alarms, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 14 | 301715 | 04 |  | Any alarms, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 15 | 301715 | 04 |  | Any alarms, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 0 | 301716 | 04 |  | MB pos. ON, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 1 | 301716 | 04 |  | MB pos. ON, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 2 | 301716 | 04 |  | MB pos. ON, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 3 | 301716 | 04 |  | MB pos. ON, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 4 | 301716 | 04 |  | MB pos. ON, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 5 | 301716 | 04 |  | MB pos. ON, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 6 | 301716 | 04 |  | MB pos. ON, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 7 | 301716 | 04 |  | MB pos. ON, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 8 | 301716 | 04 |  | MB pos. ON, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 9 | 301716 | 04 |  | MB pos. ON, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 10 | 301716 | 04 |  | MB pos. ON, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 11 | 301716 | 04 |  | MB pos. ON, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 12 | 301716 | 04 |  | MB pos. ON, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 13 | 301716 | 04 |  | MB pos. ON, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 14 | 301716 | 04 |  | MB pos. ON, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 15 | 301716 | 04 |  | MB pos. ON, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 0 | 301717 | 04 |  | MB pos. OFF, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 1 | 301717 | 04 |  | MB pos. OFF, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 2 | 301717 | 04 |  | MB pos. OFF, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 3 | 301717 | 04 |  | MB pos. OFF, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 4 | 301717 | 04 |  | MB pos. OFF, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 5 | 301717 | 04 |  | MB pos. OFF, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 6 | 301717 | 04 |  | MB pos. OFF, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 7 | 301717 | 04 |  | MB pos. OFF, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 8 | 301717 | 04 |  | MB pos. OFF, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 9 | 301717 | 04 |  | MB pos. OFF, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 10 | 301717 | 04 |  | MB pos. OFF, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 11 | 301717 | 04 |  | MB pos. OFF, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 12 | 301717 | 04 |  | MB pos. OFF, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 13 | 301717 | 04 |  | MB pos. OFF, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 14 | 301717 | 04 |  | MB pos. OFF, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 15 | 301717 | 04 |  | MB pos. OFF, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 0 | 301718 | 04 |  | Mains failure, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 1 | 301718 | 04 |  | Mains failure, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 2 | 301718 | 04 |  | Mains failure, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 3 | 301718 | 04 |  | Mains failure, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 4 | 301718 | 04 |  | Mains failure, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 5 | 301718 | 04 |  | Mains failure, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 6 | 301718 | 04 |  | Mains failure, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 7 | 301718 | 04 |  | Mains failure, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 8 | 301718 | 04 |  | Mains failure, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 9 | 301718 | 04 |  | Mains failure, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 10 | 301718 | 04 |  | Mains failure, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 11 | 301718 | 04 |  | Mains failure, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 12 | 301718 | 04 |  | Mains failure, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 13 | 301718 | 04 |  | Mains failure, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 14 | 301718 | 04 |  | Mains failure, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 15 | 301718 | 04 |  | Mains failure, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 0 | 301719 | 04 |  | MB synchronising, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 1 | 301719 | 04 |  | MB synchronising, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 2 | 301719 | 04 |  | MB synchronising, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 3 | 301719 | 04 |  | MB synchronising, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 4 | 301719 | 04 |  | MB synchronising, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 5 | 301719 | 04 |  | MB synchronising, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 6 | 301719 | 04 |  | MB synchronising, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 7 | 301719 | 04 |  | MB synchronising, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 8 | 301719 | 04 |  | MB synchronising, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 9 | 301719 | 04 |  | MB synchronising, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 10 | 301719 | 04 |  | MB synchronising, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 11 | 301719 | 04 |  | MB synchronising, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 12 | 301719 | 04 |  | MB synchronising, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 13 | 301719 | 04 |  | MB synchronising, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 14 | 301719 | 04 |  | MB synchronising, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 15 | 301719 | 04 |  | MB synchronising, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 0 | 301720 | 04 |  | TB pos. ON, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 1 | 301720 | 04 |  | TB pos. ON, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 2 | 301720 | 04 |  | TB pos. ON, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 3 | 301720 | 04 |  | TB pos. ON, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 4 | 301720 | 04 |  | TB pos. ON, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 5 | 301720 | 04 |  | TB pos. ON, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 6 | 301720 | 04 |  | TB pos. ON, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 7 | 301720 | 04 |  | TB pos. ON, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 8 | 301720 | 04 |  | TB pos. ON, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 9 | 301720 | 04 |  | TB pos. ON, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 10 | 301720 | 04 |  | TB pos. ON, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 11 | 301720 | 04 |  | TB pos. ON, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 12 | 301720 | 04 |  | TB pos. ON, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 13 | 301720 | 04 |  | TB pos. ON, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 14 | 301720 | 04 |  | TB pos. ON, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 15 | 301720 | 04 |  | TB pos. ON, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 0 | 301721 | 04 |  | TB pos. OFF, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 1 | 301721 | 04 |  | TB pos. OFF, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 2 | 301721 | 04 |  | TB pos. OFF, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 3 | 301721 | 04 |  | TB pos. OFF, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 4 | 301721 | 04 |  | TB pos. OFF, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 5 | 301721 | 04 |  | TB pos. OFF, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 6 | 301721 | 04 |  | TB pos. OFF, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 7 | 301721 | 04 |  | TB pos. OFF, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 8 | 301721 | 04 |  | TB pos. OFF, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 9 | 301721 | 04 |  | TB pos. OFF, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 10 | 301721 | 04 |  | TB pos. OFF, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 11 | 301721 | 04 |  | TB pos. OFF, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 12 | 301721 | 04 |  | TB pos. OFF, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 13 | 301721 | 04 |  | TB pos. OFF, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 14 | 301721 | 04 |  | TB pos. OFF, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 15 | 301721 | 04 |  | TB pos. OFF, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 0 | 301722 | 04 |  | TB synchronising, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 1 | 301722 | 04 |  | TB synchronising, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 2 | 301722 | 04 |  | TB synchronising, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 3 | 301722 | 04 |  | TB synchronising, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 4 | 301722 | 04 |  | TB synchronising, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 5 | 301722 | 04 |  | TB synchronising, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 6 | 301722 | 04 |  | TB synchronising, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 7 | 301722 | 04 |  | TB synchronising, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 8 | 301722 | 04 |  | TB synchronising, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 9 | 301722 | 04 |  | TB synchronising, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 10 | 301722 | 04 |  | TB synchronising, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 11 | 301722 | 04 |  | TB synchronising, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 12 | 301722 | 04 |  | TB synchronising, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 13 | 301722 | 04 |  | TB synchronising, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 14 | 301722 | 04 |  | TB synchronising, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 15 | 301722 | 04 |  | TB synchronising, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 0 | 301723 | 04 |  | Any alarms, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 1 | 301723 | 04 |  | Any alarms, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 2 | 301723 | 04 |  | Any alarms, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 3 | 301723 | 04 |  | Any alarms, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 4 | 301723 | 04 |  | Any alarms, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 5 | 301723 | 04 |  | Any alarms, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 6 | 301723 | 04 |  | Any alarms, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 7 | 301723 | 04 |  | Any alarms, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 0 | 301726 | 04 |  | BTB synchronising, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 1 | 301726 | 04 |  | BTB synchronising, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 2 | 301726 | 04 |  | BTB synchronising, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 3 | 301726 | 04 |  | BTB synchronising, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 4 | 301726 | 04 |  | BTB synchronising, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 5 | 301726 | 04 |  | BTB synchronising, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 6 | 301726 | 04 |  | BTB synchronising, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 7 | 301726 | 04 |  | BTB synchronising, ID 40 | BOOL |  |  |  | X | X
PM alarm | 1727 | 0 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 17 | BOOL |  |  |  | X | X
PM alarm | 1727 | 1 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 18 | BOOL |  |  |  | X | X
PM alarm | 1727 | 2 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 19 | BOOL |  |  |  | X | X
PM alarm | 1727 | 3 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 20 | BOOL |  |  |  | X | X
PM alarm | 1727 | 4 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 21 | BOOL |  |  |  | X | X
PM alarm | 1727 | 5 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 22 | BOOL |  |  |  | X | X
PM alarm | 1727 | 6 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 23 | BOOL |  |  |  | X | X
PM alarm | 1727 | 7 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 24 | BOOL |  |  |  | X | X
PM alarm | 1727 | 8 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 25 | BOOL |  |  |  | X | X
PM alarm | 1727 | 9 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 26 | BOOL |  |  |  | X | X
PM alarm | 1727 | 10 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 27 | BOOL |  |  |  | X | X
PM alarm | 1727 | 11 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 28 | BOOL |  |  |  | X | X
PM alarm | 1727 | 12 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 29 | BOOL |  |  |  | X | X
PM alarm | 1727 | 13 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 30 | BOOL |  |  |  | X | X
PM alarm | 1727 | 14 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 31 | BOOL |  |  |  | X | X
PM alarm | 1727 | 15 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 32 | BOOL |  |  |  | X | X
PM alarm | 1728 | 0 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 33 | BOOL |  |  |  | X | X
PM alarm | 1728 | 1 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 34 | BOOL |  |  |  | X | X
PM alarm | 1728 | 2 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 35 | BOOL |  |  |  | X | X
PM alarm | 1728 | 3 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 36 | BOOL |  |  |  | X | X
PM alarm | 1728 | 4 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 37 | BOOL |  |  |  | X | X
PM alarm | 1728 | 5 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 38 | BOOL |  |  |  | X | X
PM alarm | 1728 | 6 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 39 | BOOL |  |  |  | X | X
PM alarm | 1728 | 7 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 0 | 301733 | 04 |  | BB Hz/V OK, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 1 | 301733 | 04 |  | BB Hz/V OK, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 2 | 301733 | 04 |  | BB Hz/V OK, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 3 | 301733 | 04 |  | BB Hz/V OK, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 4 | 301733 | 04 |  | BB Hz/V OK, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 5 | 301733 | 04 |  | BB Hz/V OK, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 6 | 301733 | 04 |  | BB Hz/V OK, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 7 | 301733 | 04 |  | BB Hz/V OK, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 8 | 301733 | 04 |  | BB Hz/V OK, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 9 | 301733 | 04 |  | BB Hz/V OK, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 10 | 301733 | 04 |  | BB Hz/V OK, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 11 | 301733 | 04 |  | BB Hz/V OK, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 12 | 301733 | 04 |  | BB Hz/V OK, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 13 | 301733 | 04 |  | BB Hz/V OK, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 14 | 301733 | 04 |  | BB Hz/V OK, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 15 | 301733 | 04 |  | BB Hz/V OK, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 0 | 301734 | 04 |  | BB Hz/V OK, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 1 | 301734 | 04 |  | BB Hz/V OK, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 2 | 301734 | 04 |  | BB Hz/V OK, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 3 | 301734 | 04 |  | BB Hz/V OK, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 4 | 301734 | 04 |  | BB Hz/V OK, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 5 | 301734 | 04 |  | BB Hz/V OK, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 6 | 301734 | 04 |  | BB Hz/V OK, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 7 | 301734 | 04 |  | BB Hz/V OK, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 8 | 301734 | 04 |  | BB Hz/V OK, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 9 | 301734 | 04 |  | BB Hz/V OK, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 10 | 301734 | 04 |  | BB Hz/V OK, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 11 | 301734 | 04 |  | BB Hz/V OK, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 12 | 301734 | 04 |  | BB Hz/V OK, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 13 | 301734 | 04 |  | BB Hz/V OK, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 14 | 301734 | 04 |  | BB Hz/V OK, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 15 | 301734 | 04 |  | BB Hz/V OK, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 0 | 301735 | 04 |  | BB Hz/V OK, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 1 | 301735 | 04 |  | BB Hz/V OK, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 2 | 301735 | 04 |  | BB Hz/V OK, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 3 | 301735 | 04 |  | BB Hz/V OK, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 4 | 301735 | 04 |  | BB Hz/V OK, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 5 | 301735 | 04 |  | BB Hz/V OK, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 6 | 301735 | 04 |  | BB Hz/V OK, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 7 | 301735 | 04 |  | BB Hz/V OK, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 0 | 301736 | 04 |  | BB Hz/V present, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 1 | 301736 | 04 |  | BB Hz/V present, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 2 | 301736 | 04 |  | BB Hz/V present, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 3 | 301736 | 04 |  | BB Hz/V present, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 4 | 301736 | 04 |  | BB Hz/V present, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 5 | 301736 | 04 |  | BB Hz/V present, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 6 | 301736 | 04 |  | BB Hz/V present, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 7 | 301736 | 04 |  | BB Hz/V present, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 8 | 301736 | 04 |  | BB Hz/V present, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 9 | 301736 | 04 |  | BB Hz/V present, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 10 | 301736 | 04 |  | BB Hz/V present, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 11 | 301736 | 04 |  | BB Hz/V present, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 12 | 301736 | 04 |  | BB Hz/V present, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 13 | 301736 | 04 |  | BB Hz/V present, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 14 | 301736 | 04 |  | BB Hz/V present, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 15 | 301736 | 04 |  | BB Hz/V present, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 0 | 301737 | 04 |  | BB Hz/V present, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 1 | 301737 | 04 |  | BB Hz/V present, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 2 | 301737 | 04 |  | BB Hz/V present, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 3 | 301737 | 04 |  | BB Hz/V present, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 4 | 301737 | 04 |  | BB Hz/V present, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 5 | 301737 | 04 |  | BB Hz/V present, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 6 | 301737 | 04 |  | BB Hz/V present, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 7 | 301737 | 04 |  | BB Hz/V present, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 8 | 301737 | 04 |  | BB Hz/V present, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 9 | 301737 | 04 |  | BB Hz/V present, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 10 | 301737 | 04 |  | BB Hz/V present, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 11 | 301737 | 04 |  | BB Hz/V present, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 12 | 301737 | 04 |  | BB Hz/V present, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 13 | 301737 | 04 |  | BB Hz/V present, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 14 | 301737 | 04 |  | BB Hz/V present, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 15 | 301737 | 04 |  | BB Hz/V present, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 0 | 301738 | 04 |  | BB Hz/V present, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 1 | 301738 | 04 |  | BB Hz/V present, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 2 | 301738 | 04 |  | BB Hz/V present, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 3 | 301738 | 04 |  | BB Hz/V present, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 4 | 301738 | 04 |  | BB Hz/V present, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 5 | 301738 | 04 |  | BB Hz/V present, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 6 | 301738 | 04 |  | BB Hz/V present, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 7 | 301738 | 04 |  | BB Hz/V present, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 0 | 301739 | 04 |  | BA Hz/V OK, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 1 | 301739 | 04 |  | BA Hz/V OK, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 2 | 301739 | 04 |  | BA Hz/V OK, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 3 | 301739 | 04 |  | BA Hz/V OK, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 4 | 301739 | 04 |  | BA Hz/V OK, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 5 | 301739 | 04 |  | BA Hz/V OK, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 6 | 301739 | 04 |  | BA Hz/V OK, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 7 | 301739 | 04 |  | BA Hz/V OK, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 0 | 301740 | 04 |  | DG Hz/V present, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 1 | 301740 | 04 |  | DG Hz/V present, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 2 | 301740 | 04 |  | DG Hz/V present, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 3 | 301740 | 04 |  | DG Hz/V present, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 4 | 301740 | 04 |  | DG Hz/V present, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 5 | 301740 | 04 |  | DG Hz/V present, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 6 | 301740 | 04 |  | DG Hz/V present, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 7 | 301740 | 04 |  | DG Hz/V present, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 8 | 301740 | 04 |  | DG Hz/V present, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 9 | 301740 | 04 |  | DG Hz/V present, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 10 | 301740 | 04 |  | DG Hz/V present, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 11 | 301740 | 04 |  | DG Hz/V present, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 12 | 301740 | 04 |  | DG Hz/V present, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 13 | 301740 | 04 |  | DG Hz/V present, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 14 | 301740 | 04 |  | DG Hz/V present, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 15 | 301740 | 04 |  | DG Hz/V present, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 0 | 301741 | 04 |  | Hz/V present, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 1 | 301741 | 04 |  | Hz/V present, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 2 | 301741 | 04 |  | Hz/V present, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 3 | 301741 | 04 |  | Hz/V present, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 4 | 301741 | 04 |  | Hz/V present, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 5 | 301741 | 04 |  | Hz/V present, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 6 | 301741 | 04 |  | Hz/V present, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 7 | 301741 | 04 |  | Hz/V present, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 8 | 301741 | 04 |  | Hz/V present, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 9 | 301741 | 04 |  | Hz/V present, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 10 | 301741 | 04 |  | Hz/V present, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 11 | 301741 | 04 |  | Hz/V present, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 12 | 301741 | 04 |  | Hz/V present, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 13 | 301741 | 04 |  | Hz/V present, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 14 | 301741 | 04 |  | Hz/V present, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 15 | 301741 | 04 |  | Hz/V present, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 0 | 301742 | 04 |  | BA Hz/V present, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 1 | 301742 | 04 |  | BA Hz/V present, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 2 | 301742 | 04 |  | BA Hz/V present, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 3 | 301742 | 04 |  | BA Hz/V present, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 4 | 301742 | 04 |  | BA Hz/V present, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 5 | 301742 | 04 |  | BA Hz/V present, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 6 | 301742 | 04 |  | BA Hz/V present, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 7 | 301742 | 04 |  | BA Hz/V present, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 0 | 301750 | 04 |  | Dry Mode active on ID1 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 1 | 301750 | 04 |  | Dry Mode active on ID2 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 2 | 301750 | 04 |  | Dry Mode active on ID3 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 3 | 301750 | 04 |  | Dry Mode active on ID4 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 4 | 301750 | 04 |  | Dry Mode active on ID5 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 5 | 301750 | 04 |  | Dry Mode active on ID6 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 6 | 301750 | 04 |  | Dry Mode active on ID7 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 7 | 301750 | 04 |  | Dry Mode active on ID8 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 8 | 301750 | 04 |  | Dry Mode active on ID9 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 9 | 301750 | 04 |  | Dry Mode active on ID10 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 10 | 301750 | 04 |  | Dry Mode active on ID11 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 11 | 301750 | 04 |  | Dry Mode active on ID12 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 12 | 301750 | 04 |  | Dry Mode active on ID13 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 13 | 301750 | 04 |  | Dry Mode active on ID14 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 14 | 301750 | 04 |  | Dry Mode active on ID15 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 15 | 301750 | 04 |  | Dry Mode active on ID16 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 0 | 301751 | 04 |  | GB Pos ON, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 1 | 301751 | 04 |  | GB Pos ON, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 2 | 301751 | 04 |  | GB Pos ON, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 3 | 301751 | 04 |  | GB Pos ON, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 4 | 301751 | 04 |  | GB Pos ON, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 5 | 301751 | 04 |  | GB Pos ON, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 6 | 301751 | 04 |  | GB Pos ON, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 7 | 301751 | 04 |  | GB Pos ON, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 8 | 301751 | 04 |  | GB Pos ON, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 9 | 301751 | 04 |  | GB Pos ON, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 10 | 301751 | 04 |  | GB Pos ON, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 11 | 301751 | 04 |  | GB Pos ON, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 12 | 301751 | 04 |  | GB Pos ON, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 13 | 301751 | 04 |  | GB Pos ON, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 14 | 301751 | 04 |  | GB Pos ON, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 15 | 301751 | 04 |  | GB Pos ON, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 0 | 301752 | 04 |  | GB Pos OFF, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 1 | 301752 | 04 |  | GB Pos OFF, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 2 | 301752 | 04 |  | GB Pos OFF, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 3 | 301752 | 04 |  | GB Pos OFF, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 4 | 301752 | 04 |  | GB Pos OFF, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 5 | 301752 | 04 |  | GB Pos OFF, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 6 | 301752 | 04 |  | GB Pos OFF, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 7 | 301752 | 04 |  | GB Pos OFF, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 8 | 301752 | 04 |  | GB Pos OFF, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 9 | 301752 | 04 |  | GB Pos OFF, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 10 | 301752 | 04 |  | GB Pos OFF, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 11 | 301752 | 04 |  | GB Pos OFF, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 12 | 301752 | 04 |  | GB Pos OFF, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 13 | 301752 | 04 |  | GB Pos OFF, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 14 | 301752 | 04 |  | GB Pos OFF, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 15 | 301752 | 04 |  | GB Pos OFF, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 0 | 301753 | 04 |  | GB synchronising, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 1 | 301753 | 04 |  | GB synchronising, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 2 | 301753 | 04 |  | GB synchronising, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 3 | 301753 | 04 |  | GB synchronising, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 4 | 301753 | 04 |  | GB synchronising, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 5 | 301753 | 04 |  | GB synchronising, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 6 | 301753 | 04 |  | GB synchronising, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 7 | 301753 | 04 |  | GB synchronising, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 8 | 301753 | 04 |  | GB synchronising, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 9 | 301753 | 04 |  | GB synchronising, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 10 | 301753 | 04 |  | GB synchronising, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 11 | 301753 | 04 |  | GB synchronising, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 12 | 301753 | 04 |  | GB synchronising, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 13 | 301753 | 04 |  | GB synchronising, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 14 | 301753 | 04 |  | GB synchronising, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 15 | 301753 | 04 |  | GB synchronising, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 0 | 301754 | 04 |  | Hz/V OK, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 1 | 301754 | 04 |  | Hz/V OK, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 2 | 301754 | 04 |  | Hz/V OK, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 3 | 301754 | 04 |  | Hz/V OK, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 4 | 301754 | 04 |  | Hz/V OK, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 5 | 301754 | 04 |  | Hz/V OK, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 6 | 301754 | 04 |  | Hz/V OK, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 7 | 301754 | 04 |  | Hz/V OK, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 8 | 301754 | 04 |  | Hz/V OK, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 9 | 301754 | 04 |  | Hz/V OK, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 10 | 301754 | 04 |  | Hz/V OK, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 11 | 301754 | 04 |  | Hz/V OK, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 12 | 301754 | 04 |  | Hz/V OK, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 13 | 301754 | 04 |  | Hz/V OK, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 14 | 301754 | 04 |  | Hz/V OK, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 15 | 301754 | 04 |  | Hz/V OK, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 0 | 301755 | 04 |  | Ready for auto start, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 1 | 301755 | 04 |  | Ready for auto start, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 2 | 301755 | 04 |  | Ready for auto start, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 3 | 301755 | 04 |  | Ready for auto start, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 4 | 301755 | 04 |  | Ready for auto start, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 5 | 301755 | 04 |  | Ready for auto start, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 6 | 301755 | 04 |  | Ready for auto start, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 7 | 301755 | 04 |  | Ready for auto start, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 8 | 301755 | 04 |  | Ready for auto start, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 9 | 301755 | 04 |  | Ready for auto start, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 10 | 301755 | 04 |  | Ready for auto start, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 11 | 301755 | 04 |  | Ready for auto start, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 12 | 301755 | 04 |  | Ready for auto start, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 13 | 301755 | 04 |  | Ready for auto start, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 14 | 301755 | 04 |  | Ready for auto start, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 15 | 301755 | 04 |  | Ready for auto start, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 0 | 301756 | 04 |  | Running, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 1 | 301756 | 04 |  | Running, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 2 | 301756 | 04 |  | Running, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 3 | 301756 | 04 |  | Running, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 4 | 301756 | 04 |  | Running, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 5 | 301756 | 04 |  | Running, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 6 | 301756 | 04 |  | Running, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 7 | 301756 | 04 |  | Running, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 8 | 301756 | 04 |  | Running, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 9 | 301756 | 04 |  | Running, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 10 | 301756 | 04 |  | Running, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 11 | 301756 | 04 |  | Running, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 12 | 301756 | 04 |  | Running, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 13 | 301756 | 04 |  | Running, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 14 | 301756 | 04 |  | Running, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 15 | 301756 | 04 |  | Running, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 0 | 301757 | 04 |  | Dry Mode active on ID17 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 1 | 301757 | 04 |  | Dry Mode active on ID18 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 2 | 301757 | 04 |  | Dry Mode active on ID19 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 3 | 301757 | 04 |  | Dry Mode active on ID20 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 4 | 301757 | 04 |  | Dry Mode active on ID21 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 5 | 301757 | 04 |  | Dry Mode active on ID22 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 6 | 301757 | 04 |  | Dry Mode active on ID23 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 7 | 301757 | 04 |  | Dry Mode active on ID24 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 8 | 301757 | 04 |  | Dry Mode active on ID25 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 9 | 301757 | 04 |  | Dry Mode active on ID26 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 10 | 301757 | 04 |  | Dry Mode active on ID27 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 11 | 301757 | 04 |  | Dry Mode active on ID28 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 12 | 301757 | 04 |  | Dry Mode active on ID29 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 13 | 301757 | 04 |  | Dry Mode active on ID30 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 14 | 301757 | 04 |  | Dry Mode active on ID31 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 15 | 301757 | 04 |  | Dry Mode active on ID32 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 0 | 301758 | 04 |  | MB pos. ON, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 1 | 301758 | 04 |  | MB pos. ON, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 2 | 301758 | 04 |  | MB pos. ON, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 3 | 301758 | 04 |  | MB pos. ON, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 4 | 301758 | 04 |  | MB pos. ON, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 5 | 301758 | 04 |  | MB pos. ON, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 6 | 301758 | 04 |  | MB pos. ON, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 7 | 301758 | 04 |  | MB pos. ON, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 8 | 301758 | 04 |  | MB pos. ON, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 9 | 301758 | 04 |  | MB pos. ON, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 10 | 301758 | 04 |  | MB pos. ON, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 11 | 301758 | 04 |  | MB pos. ON, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 12 | 301758 | 04 |  | MB pos. ON, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 13 | 301758 | 04 |  | MB pos. ON, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 14 | 301758 | 04 |  | MB pos. ON, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 15 | 301758 | 04 |  | MB pos. ON, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 0 | 301759 | 04 |  | MB pos. OFF, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 1 | 301759 | 04 |  | MB pos. OFF, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 2 | 301759 | 04 |  | MB pos. OFF, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 3 | 301759 | 04 |  | MB pos. OFF, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 4 | 301759 | 04 |  | MB pos. OFF, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 5 | 301759 | 04 |  | MB pos. OFF, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 6 | 301759 | 04 |  | MB pos. OFF, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 7 | 301759 | 04 |  | MB pos. OFF, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 8 | 301759 | 04 |  | MB pos. OFF, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 9 | 301759 | 04 |  | MB pos. OFF, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 10 | 301759 | 04 |  | MB pos. OFF, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 11 | 301759 | 04 |  | MB pos. OFF, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 12 | 301759 | 04 |  | MB pos. OFF, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 13 | 301759 | 04 |  | MB pos. OFF, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 14 | 301759 | 04 |  | MB pos. OFF, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 15 | 301759 | 04 |  | MB pos. OFF, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 0 | 301760 | 04 |  | MB synchronising, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 1 | 301760 | 04 |  | MB synchronising, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 2 | 301760 | 04 |  | MB synchronising, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 3 | 301760 | 04 |  | MB synchronising, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 4 | 301760 | 04 |  | MB synchronising, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 5 | 301760 | 04 |  | MB synchronising, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 6 | 301760 | 04 |  | MB synchronising, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 7 | 301760 | 04 |  | MB synchronising, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 8 | 301760 | 04 |  | MB synchronising, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 9 | 301760 | 04 |  | MB synchronising, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 10 | 301760 | 04 |  | MB synchronising, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 11 | 301760 | 04 |  | MB synchronising, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 12 | 301760 | 04 |  | MB synchronising, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 13 | 301760 | 04 |  | MB synchronising, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 14 | 301760 | 04 |  | MB synchronising, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 15 | 301760 | 04 |  | MB synchronising, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 0 | 301761 | 04 |  | TB pos. ON, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 1 | 301761 | 04 |  | TB pos. ON, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 2 | 301761 | 04 |  | TB pos. ON, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 3 | 301761 | 04 |  | TB pos. ON, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 4 | 301761 | 04 |  | TB pos. ON, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 5 | 301761 | 04 |  | TB pos. ON, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 6 | 301761 | 04 |  | TB pos. ON, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 7 | 301761 | 04 |  | TB pos. ON, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 8 | 301761 | 04 |  | TB pos. ON, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 9 | 301761 | 04 |  | TB pos. ON, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 10 | 301761 | 04 |  | TB pos. ON, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 11 | 301761 | 04 |  | TB pos. ON, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 12 | 301761 | 04 |  | TB pos. ON, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 13 | 301761 | 04 |  | TB pos. ON, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 14 | 301761 | 04 |  | TB pos. ON, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 15 | 301761 | 04 |  | TB pos. ON, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 0 | 301762 | 04 |  | TB pos. OFF, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 1 | 301762 | 04 |  | TB pos. OFF, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 2 | 301762 | 04 |  | TB pos. OFF, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 3 | 301762 | 04 |  | TB pos. OFF, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 4 | 301762 | 04 |  | TB pos. OFF, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 5 | 301762 | 04 |  | TB pos. OFF, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 6 | 301762 | 04 |  | TB pos. OFF, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 7 | 301762 | 04 |  | TB pos. OFF, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 8 | 301762 | 04 |  | TB pos. OFF, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 9 | 301762 | 04 |  | TB pos. OFF, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 10 | 301762 | 04 |  | TB pos. OFF, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 11 | 301762 | 04 |  | TB pos. OFF, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 12 | 301762 | 04 |  | TB pos. OFF, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 13 | 301762 | 04 |  | TB pos. OFF, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 14 | 301762 | 04 |  | TB pos. OFF, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 15 | 301762 | 04 |  | TB pos. OFF, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 0 | 301763 | 04 |  | TB synchronising, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 1 | 301763 | 04 |  | TB synchronising, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 2 | 301763 | 04 |  | TB synchronising, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 3 | 301763 | 04 |  | TB synchronising, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 4 | 301763 | 04 |  | TB synchronising, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 5 | 301763 | 04 |  | TB synchronising, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 6 | 301763 | 04 |  | TB synchronising, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 7 | 301763 | 04 |  | TB synchronising, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 8 | 301763 | 04 |  | TB synchronising, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 9 | 301763 | 04 |  | TB synchronising, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 10 | 301763 | 04 |  | TB synchronising, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 11 | 301763 | 04 |  | TB synchronising, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 12 | 301763 | 04 |  | TB synchronising, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 13 | 301763 | 04 |  | TB synchronising, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 14 | 301763 | 04 |  | TB synchronising, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 15 | 301763 | 04 |  | TB synchronising, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 0 | 301764 | 04 |  | Mains transducer-configured, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 1 | 301764 | 04 |  | Mains transducer-configured, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 2 | 301764 | 04 |  | Mains transducer-configured, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 3 | 301764 | 04 |  | Mains transducer-configured, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 4 | 301764 | 04 |  | Mains transducer-configured, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 5 | 301764 | 04 |  | Mains transducer-configured, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 6 | 301764 | 04 |  | Mains transducer-configured, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 7 | 301764 | 04 |  | Mains transducer-configured, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 8 | 301764 | 04 |  | Mains transducer-configured, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 9 | 301764 | 04 |  | Mains transducer-configured, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 10 | 301764 | 04 |  | Mains transducer-configured, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 11 | 301764 | 04 |  | Mains transducer-configured, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 12 | 301764 | 04 |  | Mains transducer-configured, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 13 | 301764 | 04 |  | Mains transducer-configured, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 14 | 301764 | 04 |  | Mains transducer-configured, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 15 | 301764 | 04 |  | Mains transducer-configured, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 0 | 301765 | 04 |  | TB transducer-configured, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 1 | 301765 | 04 |  | TB transducer-configured, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 2 | 301765 | 04 |  | TB transducer-configured, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 3 | 301765 | 04 |  | TB transducer-configured, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 4 | 301765 | 04 |  | TB transducer-configured, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 5 | 301765 | 04 |  | TB transducer-configured, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 6 | 301765 | 04 |  | TB transducer-configured, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 7 | 301765 | 04 |  | TB transducer-configured, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 8 | 301765 | 04 |  | TB transducer-configured, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 9 | 301765 | 04 |  | TB transducer-configured, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 10 | 301765 | 04 |  | TB transducer-configured, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 11 | 301765 | 04 |  | TB transducer-configured, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 12 | 301765 | 04 |  | TB transducer-configured, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 13 | 301765 | 04 |  | TB transducer-configured, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 14 | 301765 | 04 |  | TB transducer-configured, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 15 | 301765 | 04 |  | TB transducer-configured, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 0 | 301766 | 04 |  | Mains OK, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 1 | 301766 | 04 |  | Mains OK, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 2 | 301766 | 04 |  | Mains OK, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 3 | 301766 | 04 |  | Mains OK, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 4 | 301766 | 04 |  | Mains OK, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 5 | 301766 | 04 |  | Mains OK, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 6 | 301766 | 04 |  | Mains OK, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 7 | 301766 | 04 |  | Mains OK, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 8 | 301766 | 04 |  | Mains OK, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 9 | 301766 | 04 |  | Mains OK, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 10 | 301766 | 04 |  | Mains OK, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 11 | 301766 | 04 |  | Mains OK, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 12 | 301766 | 04 |  | Mains OK, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 13 | 301766 | 04 |  | Mains OK, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 14 | 301766 | 04 |  | Mains OK, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 15 | 301766 | 04 |  | Mains OK, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 0 | 301767 | 04 |  | Mains not in semi 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 1 | 301767 | 04 |  | Mains not in semi 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 2 | 301767 | 04 |  | Mains not in semi 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 3 | 301767 | 04 |  | Mains not in semi 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 4 | 301767 | 04 |  | Mains not in semi 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 5 | 301767 | 04 |  | Mains not in semi 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 6 | 301767 | 04 |  | Mains not in semi 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 7 | 301767 | 04 |  | Mains not in semi 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 8 | 301767 | 04 |  | Mains not in semi 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 9 | 301767 | 04 |  | Mains not in semi 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 10 | 301767 | 04 |  | Mains not in semi 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 11 | 301767 | 04 |  | Mains not in semi 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 12 | 301767 | 04 |  | Mains not in semi 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 13 | 301767 | 04 |  | Mains not in semi 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 14 | 301767 | 04 |  | Mains not in semi 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 15 | 301767 | 04 |  | Mains not in semi 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 0 | 301768 | 04 |  | Mains failure, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 1 | 301768 | 04 |  | Mains failure, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 2 | 301768 | 04 |  | Mains failure, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 3 | 301768 | 04 |  | Mains failure, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 4 | 301768 | 04 |  | Mains failure, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 5 | 301768 | 04 |  | Mains failure, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 6 | 301768 | 04 |  | Mains failure, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 7 | 301768 | 04 |  | Mains failure, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 8 | 301768 | 04 |  | Mains failure, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 9 | 301768 | 04 |  | Mains failure, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 10 | 301768 | 04 |  | Mains failure, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 11 | 301768 | 04 |  | Mains failure, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 12 | 301768 | 04 |  | Mains failure, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 13 | 301768 | 04 |  | Mains failure, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 14 | 301768 | 04 |  | Mains failure, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 15 | 301768 | 04 |  | Mains failure, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1769 | 0 | 301770 | 04 |  | PV breaker OFF, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1769 | 1 | 301770 | 04 |  | PV breaker OFF, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1769 | 2 | 301770 | 04 |  | PV breaker OFF, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1769 | 3 | 301770 | 04 |  | PV breaker OFF, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1769 | 4 | 301770 | 04 |  | PV breaker OFF, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1769 | 5 | 301770 | 04 |  | PV breaker OFF, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1769 | 6 | 301770 | 04 |  | PV breaker OFF, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1769 | 7 | 301770 | 04 |  | PV breaker OFF, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1770 | 0 | 301771 | 04 |  | Breaker synchronising, PV ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1770 | 1 | 301771 | 04 |  | Breaker synchronising, PV ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1770 | 2 | 301771 | 04 |  | Breaker synchronising, PV ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1770 | 3 | 301771 | 04 |  | Breaker synchronising, PV ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1770 | 4 | 301771 | 04 |  | Breaker synchronising, PV ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1770 | 5 | 301771 | 04 |  | Breaker synchronising, PV ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1770 | 6 | 301771 | 04 |  | Breaker synchronising, PV ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1770 | 7 | 301771 | 04 |  | Breaker synchronising, PV ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 0 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 1 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 2 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 3 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 4 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 5 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 6 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 7 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 8 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 9 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 10 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 11 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 12 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 13 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 14 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 15 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 0 | 301773 | 04 |  | Ready to autostart, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 1 | 301773 | 04 |  | Ready to autostart, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 2 | 301773 | 04 |  | Ready to autostart, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 3 | 301773 | 04 |  | Ready to autostart, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 4 | 301773 | 04 |  | Ready to autostart, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 5 | 301773 | 04 |  | Ready to autostart, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 6 | 301773 | 04 |  | Ready to autostart, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 7 | 301773 | 04 |  | Ready to autostart, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 8 | 301773 | 04 |  | Ready to autostart, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 9 | 301773 | 04 |  | Ready to autostart, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 10 | 301773 | 04 |  | Ready to autostart, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 11 | 301773 | 04 |  | Ready to autostart, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 12 | 301773 | 04 |  | Ready to autostart, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 13 | 301773 | 04 |  | Ready to autostart, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 14 | 301773 | 04 |  | Ready to autostart, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 15 | 301773 | 04 |  | Ready to autostart, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 0 | 301774 | 04 |  | Load Group 1 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 1 | 301774 | 04 |  | Load Group 1 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 2 | 301774 | 04 |  | Load Group 1 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 3 | 301774 | 04 |  | Load Group 1 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 4 | 301774 | 04 |  | Load Group 1 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 5 | 301774 | 04 |  | Load Group 1 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 6 | 301774 | 04 |  | Load Group 1 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 7 | 301774 | 04 |  | Load Group 1 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 8 | 301774 | 04 |  | Load Group 1 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 9 | 301774 | 04 |  | Load Group 1 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 10 | 301774 | 04 |  | Load Group 1 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 11 | 301774 | 04 |  | Load Group 1 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 12 | 301774 | 04 |  | Load Group 1 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 13 | 301774 | 04 |  | Load Group 1 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 14 | 301774 | 04 |  | Load Group 1 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 15 | 301774 | 04 |  | Load Group 1 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 0 | 301775 | 04 |  | Load Group 2 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 1 | 301775 | 04 |  | Load Group 2 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 2 | 301775 | 04 |  | Load Group 2 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 3 | 301775 | 04 |  | Load Group 2 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 4 | 301775 | 04 |  | Load Group 2 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 5 | 301775 | 04 |  | Load Group 2 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 6 | 301775 | 04 |  | Load Group 2 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 7 | 301775 | 04 |  | Load Group 2 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 8 | 301775 | 04 |  | Load Group 2 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 9 | 301775 | 04 |  | Load Group 2 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 10 | 301775 | 04 |  | Load Group 2 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 11 | 301775 | 04 |  | Load Group 2 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 12 | 301775 | 04 |  | Load Group 2 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 13 | 301775 | 04 |  | Load Group 2 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 14 | 301775 | 04 |  | Load Group 2 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 15 | 301775 | 04 |  | Load Group 2 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 0 | 301776 | 04 |  | Load Group 3 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 1 | 301776 | 04 |  | Load Group 3 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 2 | 301776 | 04 |  | Load Group 3 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 3 | 301776 | 04 |  | Load Group 3 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 4 | 301776 | 04 |  | Load Group 3 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 5 | 301776 | 04 |  | Load Group 3 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 6 | 301776 | 04 |  | Load Group 3 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 7 | 301776 | 04 |  | Load Group 3 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 8 | 301776 | 04 |  | Load Group 3 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 9 | 301776 | 04 |  | Load Group 3 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 10 | 301776 | 04 |  | Load Group 3 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 11 | 301776 | 04 |  | Load Group 3 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 12 | 301776 | 04 |  | Load Group 3 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 13 | 301776 | 04 |  | Load Group 3 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 14 | 301776 | 04 |  | Load Group 3 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 15 | 301776 | 04 |  | Load Group 3 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 0 | 301777 | 04 |  | Load Group 4 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 1 | 301777 | 04 |  | Load Group 4 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 2 | 301777 | 04 |  | Load Group 4 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 3 | 301777 | 04 |  | Load Group 4 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 4 | 301777 | 04 |  | Load Group 4 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 5 | 301777 | 04 |  | Load Group 4 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 6 | 301777 | 04 |  | Load Group 4 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 7 | 301777 | 04 |  | Load Group 4 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 8 | 301777 | 04 |  | Load Group 4 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 9 | 301777 | 04 |  | Load Group 4 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 10 | 301777 | 04 |  | Load Group 4 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 11 | 301777 | 04 |  | Load Group 4 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 12 | 301777 | 04 |  | Load Group 4 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 13 | 301777 | 04 |  | Load Group 4 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 14 | 301777 | 04 |  | Load Group 4 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 15 | 301777 | 04 |  | Load Group 4 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 0 | 301778 | 04 |  | Load Group 5 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 1 | 301778 | 04 |  | Load Group 5 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 2 | 301778 | 04 |  | Load Group 5 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 3 | 301778 | 04 |  | Load Group 5 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 4 | 301778 | 04 |  | Load Group 5 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 5 | 301778 | 04 |  | Load Group 5 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 6 | 301778 | 04 |  | Load Group 5 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 7 | 301778 | 04 |  | Load Group 5 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 8 | 301778 | 04 |  | Load Group 5 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 9 | 301778 | 04 |  | Load Group 5 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 10 | 301778 | 04 |  | Load Group 5 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 11 | 301778 | 04 |  | Load Group 5 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 12 | 301778 | 04 |  | Load Group 5 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 13 | 301778 | 04 |  | Load Group 5 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 14 | 301778 | 04 |  | Load Group 5 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 15 | 301778 | 04 |  | Load Group 5 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 0 | 301779 | 04 |  | Load Group 6 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 1 | 301779 | 04 |  | Load Group 6 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 2 | 301779 | 04 |  | Load Group 6 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 3 | 301779 | 04 |  | Load Group 6 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 4 | 301779 | 04 |  | Load Group 6 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 5 | 301779 | 04 |  | Load Group 6 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 6 | 301779 | 04 |  | Load Group 6 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 7 | 301779 | 04 |  | Load Group 6 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 8 | 301779 | 04 |  | Load Group 6 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 9 | 301779 | 04 |  | Load Group 6 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 10 | 301779 | 04 |  | Load Group 6 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 11 | 301779 | 04 |  | Load Group 6 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 12 | 301779 | 04 |  | Load Group 6 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 13 | 301779 | 04 |  | Load Group 6 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 14 | 301779 | 04 |  | Load Group 6 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 15 | 301779 | 04 |  | Load Group 6 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 0 | 301780 | 04 |  | Load Group 7 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 1 | 301780 | 04 |  | Load Group 7 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 2 | 301780 | 04 |  | Load Group 7 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 3 | 301780 | 04 |  | Load Group 7 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 4 | 301780 | 04 |  | Load Group 7 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 5 | 301780 | 04 |  | Load Group 7 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 6 | 301780 | 04 |  | Load Group 7 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 7 | 301780 | 04 |  | Load Group 7 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 8 | 301780 | 04 |  | Load Group 7 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 9 | 301780 | 04 |  | Load Group 7 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 10 | 301780 | 04 |  | Load Group 7 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 11 | 301780 | 04 |  | Load Group 7 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 12 | 301780 | 04 |  | Load Group 7 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 13 | 301780 | 04 |  | Load Group 7 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 14 | 301780 | 04 |  | Load Group 7 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 15 | 301780 | 04 |  | Load Group 7 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 0 | 301781 | 04 |  | Load Group 8 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 1 | 301781 | 04 |  | Load Group 8 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 2 | 301781 | 04 |  | Load Group 8 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 3 | 301781 | 04 |  | Load Group 8 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 4 | 301781 | 04 |  | Load Group 8 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 5 | 301781 | 04 |  | Load Group 8 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 6 | 301781 | 04 |  | Load Group 8 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 7 | 301781 | 04 |  | Load Group 8 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 8 | 301781 | 04 |  | Load Group 8 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 9 | 301781 | 04 |  | Load Group 8 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 10 | 301781 | 04 |  | Load Group 8 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 11 | 301781 | 04 |  | Load Group 8 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 12 | 301781 | 04 |  | Load Group 8 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 13 | 301781 | 04 |  | Load Group 8 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 14 | 301781 | 04 |  | Load Group 8 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 15 | 301781 | 04 |  | Load Group 8 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 0 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 1 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 2 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 3 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 4 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 5 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 6 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 7 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 8 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 9 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 10 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 11 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 12 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 13 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 14 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 15 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 0 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 1 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 2 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 3 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 4 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 5 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 6 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 7 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 8 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 9 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 10 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 11 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 12 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 13 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 14 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 15 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 0 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 1 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 2 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 3 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 4 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 5 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 6 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 7 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 8 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 9 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 10 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 11 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 12 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 13 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 14 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 15 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 0 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 1 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 2 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 3 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 4 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 5 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 6 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 7 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 8 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 9 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 10 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 11 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 12 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 13 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 14 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 15 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 0 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 1 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 2 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 3 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 4 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 5 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 6 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 7 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 8 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 9 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 10 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 11 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 12 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 13 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 14 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 15 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 0 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 1 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 2 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 3 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 4 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 5 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 6 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 7 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 8 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 9 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 10 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 11 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 12 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 13 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 14 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 15 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 0 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 1 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 2 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 3 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 4 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 5 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 6 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 7 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 8 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 9 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 10 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 11 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 12 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 13 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 14 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 15 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 0 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 1 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 2 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 3 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 4 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 5 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 6 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 7 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 8 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 9 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 10 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 11 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 12 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 13 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 14 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 15 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 0 | 301790 | 04 |  | Load Group 1 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 1 | 301790 | 04 |  | Load Group 1 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 2 | 301790 | 04 |  | Load Group 1 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 3 | 301790 | 04 |  | Load Group 1 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 4 | 301790 | 04 |  | Load Group 1 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 5 | 301790 | 04 |  | Load Group 1 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 6 | 301790 | 04 |  | Load Group 1 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 7 | 301790 | 04 |  | Load Group 1 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 8 | 301790 | 04 |  | Load Group 1 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 9 | 301790 | 04 |  | Load Group 1 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 10 | 301790 | 04 |  | Load Group 1 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 11 | 301790 | 04 |  | Load Group 1 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 12 | 301790 | 04 |  | Load Group 1 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 13 | 301790 | 04 |  | Load Group 1 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 14 | 301790 | 04 |  | Load Group 1 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 15 | 301790 | 04 |  | Load Group 1 Enabled - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 0 | 301791 | 04 |  | Load Group 2 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 1 | 301791 | 04 |  | Load Group 2 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 2 | 301791 | 04 |  | Load Group 2 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 3 | 301791 | 04 |  | Load Group 2 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 4 | 301791 | 04 |  | Load Group 2 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 5 | 301791 | 04 |  | Load Group 2 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 6 | 301791 | 04 |  | Load Group 2 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 7 | 301791 | 04 |  | Load Group 2 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 8 | 301791 | 04 |  | Load Group 2 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 9 | 301791 | 04 |  | Load Group 2 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 10 | 301791 | 04 |  | Load Group 2 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 11 | 301791 | 04 |  | Load Group 2 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 12 | 301791 | 04 |  | Load Group 2 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 13 | 301791 | 04 |  | Load Group 2 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 14 | 301791 | 04 |  | Load Group 2 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 15 | 301791 | 04 |  | Load Group 2 Enabled - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 0 | 301792 | 04 |  | Load Group 3 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 1 | 301792 | 04 |  | Load Group 3 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 2 | 301792 | 04 |  | Load Group 3 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 3 | 301792 | 04 |  | Load Group 3 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 4 | 301792 | 04 |  | Load Group 3 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 5 | 301792 | 04 |  | Load Group 3 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 6 | 301792 | 04 |  | Load Group 3 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 7 | 301792 | 04 |  | Load Group 3 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 8 | 301792 | 04 |  | Load Group 3 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 9 | 301792 | 04 |  | Load Group 3 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 10 | 301792 | 04 |  | Load Group 3 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 11 | 301792 | 04 |  | Load Group 3 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 12 | 301792 | 04 |  | Load Group 3 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 13 | 301792 | 04 |  | Load Group 3 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 14 | 301792 | 04 |  | Load Group 3 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 15 | 301792 | 04 |  | Load Group 3 Enabled - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 0 | 301793 | 04 |  | Load Group 4 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 1 | 301793 | 04 |  | Load Group 4 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 2 | 301793 | 04 |  | Load Group 4 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 3 | 301793 | 04 |  | Load Group 4 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 4 | 301793 | 04 |  | Load Group 4 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 5 | 301793 | 04 |  | Load Group 4 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 6 | 301793 | 04 |  | Load Group 4 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 7 | 301793 | 04 |  | Load Group 4 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 8 | 301793 | 04 |  | Load Group 4 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 9 | 301793 | 04 |  | Load Group 4 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 10 | 301793 | 04 |  | Load Group 4 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 11 | 301793 | 04 |  | Load Group 4 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 12 | 301793 | 04 |  | Load Group 4 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 13 | 301793 | 04 |  | Load Group 4 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 14 | 301793 | 04 |  | Load Group 4 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 15 | 301793 | 04 |  | Load Group 4 Enabled - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 0 | 301794 | 04 |  | Load Group 5 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 1 | 301794 | 04 |  | Load Group 5 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 2 | 301794 | 04 |  | Load Group 5 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 3 | 301794 | 04 |  | Load Group 5 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 4 | 301794 | 04 |  | Load Group 5 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 5 | 301794 | 04 |  | Load Group 5 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 6 | 301794 | 04 |  | Load Group 5 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 7 | 301794 | 04 |  | Load Group 5 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 8 | 301794 | 04 |  | Load Group 5 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 9 | 301794 | 04 |  | Load Group 5 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 10 | 301794 | 04 |  | Load Group 5 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 11 | 301794 | 04 |  | Load Group 5 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 12 | 301794 | 04 |  | Load Group 5 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 13 | 301794 | 04 |  | Load Group 5 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 14 | 301794 | 04 |  | Load Group 5 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 15 | 301794 | 04 |  | Load Group 5 Enabled - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 0 | 301795 | 04 |  | Load Group 6 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 1 | 301795 | 04 |  | Load Group 6 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 2 | 301795 | 04 |  | Load Group 6 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 3 | 301795 | 04 |  | Load Group 6 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 4 | 301795 | 04 |  | Load Group 6 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 5 | 301795 | 04 |  | Load Group 6 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 6 | 301795 | 04 |  | Load Group 6 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 7 | 301795 | 04 |  | Load Group 6 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 8 | 301795 | 04 |  | Load Group 6 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 9 | 301795 | 04 |  | Load Group 6 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 10 | 301795 | 04 |  | Load Group 6 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 11 | 301795 | 04 |  | Load Group 6 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 12 | 301795 | 04 |  | Load Group 6 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 13 | 301795 | 04 |  | Load Group 6 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 14 | 301795 | 04 |  | Load Group 6 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 15 | 301795 | 04 |  | Load Group 6 Enabled - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 0 | 301796 | 04 |  | Load Group 7 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 1 | 301796 | 04 |  | Load Group 7 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 2 | 301796 | 04 |  | Load Group 7 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 3 | 301796 | 04 |  | Load Group 7 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 4 | 301796 | 04 |  | Load Group 7 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 5 | 301796 | 04 |  | Load Group 7 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 6 | 301796 | 04 |  | Load Group 7 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 7 | 301796 | 04 |  | Load Group 7 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 8 | 301796 | 04 |  | Load Group 7 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 9 | 301796 | 04 |  | Load Group 7 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 10 | 301796 | 04 |  | Load Group 7 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 11 | 301796 | 04 |  | Load Group 7 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 12 | 301796 | 04 |  | Load Group 7 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 13 | 301796 | 04 |  | Load Group 7 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 14 | 301796 | 04 |  | Load Group 7 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 15 | 301796 | 04 |  | Load Group 7 Enabled - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 0 | 301797 | 04 |  | Load Group 8 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 1 | 301797 | 04 |  | Load Group 8 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 2 | 301797 | 04 |  | Load Group 8 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 3 | 301797 | 04 |  | Load Group 8 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 4 | 301797 | 04 |  | Load Group 8 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 5 | 301797 | 04 |  | Load Group 8 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 6 | 301797 | 04 |  | Load Group 8 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 7 | 301797 | 04 |  | Load Group 8 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 8 | 301797 | 04 |  | Load Group 8 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 9 | 301797 | 04 |  | Load Group 8 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 10 | 301797 | 04 |  | Load Group 8 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 11 | 301797 | 04 |  | Load Group 8 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 12 | 301797 | 04 |  | Load Group 8 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 13 | 301797 | 04 |  | Load Group 8 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 14 | 301797 | 04 |  | Load Group 8 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 15 | 301797 | 04 |  | Load Group 8 Enabled - ID 32 | BOOL |  |  |  | X | X
Counter | 1842 |  | 301843 | 04 |  | BB Export, active energy counter, total | INT32s | ABCD | 0 | kWh | X | X
Counter | 1844 |  | 301845 | 04 |  | BB Export, active energy counter, month | INT32s | ABCD | 0 | kWh | X | X
Counter | 1846 |  | 301847 | 04 |  | BB Export, active energy counter, week | INT32s | ABCD | 0 | kWh | X | X
Counter | 1848 |  | 301849 | 04 |  | BB Export, active energy counter, day | INT32s | ABCD | 0 | kWh | X | X
Counter | 1850 |  | 301851 | 04 |  | BB Export, reactive energy counter, total | INT32s | ABCD | 0 | kvarh | X | X
Counter | 1852 |  | 301853 | 04 |  | BB Export, reactive energy counter, month | INT32s | ABCD | 0 | kvarh | X | X
Counter | 1854 |  | 301855 | 04 |  | BB Export, reactive energy counter, week | INT32s | ABCD | 0 | kvarh | X | X
Counter | 1856 |  | 301857 | 04 |  | BB Export, reactive energy counter, day | INT32s | ABCD | 0 | kvarh | X | X
Counter | 1858 |  | 301859 | 04 |  | BB Import, active energy counter, total | INT32s | ABCD | 0 | kWh | X | X
Counter | 1860 |  | 301861 | 04 |  | BB Import, active energy counter, month | INT32s | ABCD | 0 | kWh | X | X
Counter | 1862 |  | 301863 | 04 |  | BB Import, active energy counter, week | INT32s | ABCD | 0 | kWh | X | X
Counter | 1864 |  | 301865 | 04 |  | BB Import, active energy counter, day | INT32s | ABCD | 0 | kWh | X | X
Counter | 1866 |  | 301867 | 04 |  | BB Import, reactive energy counter, total | INT32s | ABCD | 0 | kvarh | X | X
Counter | 1868 |  | 301869 | 04 |  | BB Import, reactive energy counter, month | INT32s | ABCD | 0 | kvarh | X | X
Counter | 1870 |  | 301871 | 04 |  | BB Import, reactive energy counter, week | INT32s | ABCD | 0 | kvarh | X | X
Counter | 1872 |  | 301873 | 04 |  | BB Import, reactive energy counter, day | INT32s | ABCD | 0 | kvarh | X | X
Counter | 1874 |  | 301875 | 04 |  | ESS, active energy counter, year | INT32s | ABCD | 0 | kWh |  | X
Counter | 1874 |  | 301875 | 04 |  | PV, active energy counter, year | INT32s | ABCD | 0 | kWh | X
Counter | 1876 |  | 301877 | 04 |  | ESS, import active energy counter, year | INT32s | ABCD | 0 | kVArh |  | X
Counter | 1876 |  | 301877 | 04 |  | PV, import active energy counter, year | INT32s | ABCD | 0 | kWh | X
Counter | 1878 |  | 301879 | 04 |  | ESS, reactive energy counter, year | INT32s | ABCD | 0 | kVArh |  | X
Counter | 1878 |  | 301879 | 04 |  | PV, reactive energy counter, year | INT32s | ABCD | 0 | kWh | X
Counter | 1880 |  | 301881 | 04 |  | ESS, import reactive energy counter, year | INT32s | ABCD | 0 | kVArh |  | X
Counter | 1880 |  | 301881 | 04 |  | PV, import reactive energy counter, year | INT32s | ABCD | 0 | kWh | X
Counter | 1905 |  | 301906 | 04 |  | Hotel load energy counter, Total | INT32u | ABCD | 0 | kWh | X | X
Counter | 1907 |  | 301908 | 04 |  | Hotel load energy counter, Year | INT32u | ABCD | 0 | kWh |  | X
Counter | 1907 |  | 301908 | 04 |  | PV, Hotel load energy counter, Year | INT32u | ABCD | 0 | kWh | X
Counter | 1909 |  | 301910 | 04 |  | Hotel load energy counter, Month | INT32u | ABCD | 0 | kWh |  | X
Counter | 1909 |  | 301910 | 04 |  | PV, Hotel load energy counter, Month | INT32u | ABCD | 0 | kWh | X
Counter | 1912 |  | 301913 | 04 |  | Hotel load energy counter, Week | INT32u | ABCD | 0 | kWh |  | X
Counter | 1912 |  | 301913 | 04 |  | PV, Hotel load energy counter, Week | INT32u | ABCD | 0 | kWh | X
Counter | 1914 |  | 301915 | 04 |  | Hotel load energy counter, Day | INT32u | ABCD | 0 | kWh |  | X
Counter | 1914 |  | 301915 | 04 |  | PV, Hotel load energy counter, Day | INT32u | ABCD | 0 | kWh | X
Plant config | 36000 |  | 336001 | 04 |  | Plant option - Plant type | INT16s | AB | 0 |  | X | X
Plant config | 36001 |  | 336002 | 04 |  | Plant option - PMS CAN | INT16s | AB | 0 |  | X | X
Plant config | 36002 |  | 336003 | 04 |  | Plant source ID 1 | INT16s | AB | 0 |  | X | X
Plant config | 36003 |  | 336004 | 04 |  | Plant source ID 2 | INT16s | AB | 0 |  | X | X
Plant config | 36004 |  | 336005 | 04 |  | Plant source ID 3 | INT16s | AB | 0 |  | X | X
Plant config | 36005 |  | 336006 | 04 |  | Plant source ID 4 | INT16s | AB | 0 |  | X | X
Plant config | 36006 |  | 336007 | 04 |  | Plant source ID 5 | INT16s | AB | 0 |  | X | X
Plant config | 36007 |  | 336008 | 04 |  | Plant source ID 6 | INT16s | AB | 0 |  | X | X
Plant config | 36008 |  | 336009 | 04 |  | Plant source ID 7 | INT16s | AB | 0 |  | X | X
Plant config | 36009 |  | 336010 | 04 |  | Plant source ID 8 | INT16s | AB | 0 |  | X | X
Plant config | 36010 |  | 336011 | 04 |  | Plant source ID 9 | INT16s | AB | 0 |  | X | X
Plant config | 36011 |  | 336012 | 04 |  | Plant source ID 10 | INT16s | AB | 0 |  | X | X
Plant config | 36012 |  | 336013 | 04 |  | Plant source ID 11 | INT16s | AB | 0 |  | X | X
Plant config | 36013 |  | 336014 | 04 |  | Plant source ID 12 | INT16s | AB | 0 |  | X | X
Plant config | 36014 |  | 336015 | 04 |  | Plant source ID 13 | INT16s | AB | 0 |  | X | X
Plant config | 36015 |  | 336016 | 04 |  | Plant source ID 14 | INT16s | AB | 0 |  | X | X
Plant config | 36016 |  | 336017 | 04 |  | Plant source ID 15 | INT16s | AB | 0 |  | X | X
Plant config | 36017 |  | 336018 | 04 |  | Plant source ID 16 | INT16s | AB | 0 |  | X | X
Plant config | 36018 |  | 336019 | 04 |  | Plant source ID 17 | INT16s | AB | 0 |  | X | X
Plant config | 36019 |  | 336020 | 04 |  | Plant source ID 18 | INT16s | AB | 0 |  | X | X
Plant config | 36020 |  | 336021 | 04 |  | Plant source ID 19 | INT16s | AB | 0 |  | X | X
Plant config | 36021 |  | 336022 | 04 |  | Plant source ID 20 | INT16s | AB | 0 |  | X | X
Plant config | 36022 |  | 336023 | 04 |  | Plant source ID 21 | INT16s | AB | 0 |  | X | X
Plant config | 36023 |  | 336024 | 04 |  | Plant source ID 22 | INT16s | AB | 0 |  | X | X
Plant config | 36024 |  | 336025 | 04 |  | Plant source ID 23 | INT16s | AB | 0 |  | X | X
Plant config | 36025 |  | 336026 | 04 |  | Plant source ID 24 | INT16s | AB | 0 |  | X | X
Plant config | 36026 |  | 336027 | 04 |  | Plant source ID 25 | INT16s | AB | 0 |  | X | X
Plant config | 36027 |  | 336028 | 04 |  | Plant source ID 26 | INT16s | AB | 0 |  | X | X
Plant config | 36028 |  | 336029 | 04 |  | Plant source ID 27 | INT16s | AB | 0 |  | X | X
Plant config | 36029 |  | 336030 | 04 |  | Plant source ID 28 | INT16s | AB | 0 |  | X | X
Plant config | 36030 |  | 336031 | 04 |  | Plant source ID 29 | INT16s | AB | 0 |  | X | X
Plant config | 36031 |  | 336032 | 04 |  | Plant source ID 30 | INT16s | AB | 0 |  | X | X
Plant config | 36032 |  | 336033 | 04 |  | Plant source ID 31 | INT16s | AB | 0 |  | X | X
Plant config | 36033 |  | 336034 | 04 |  | Plant source ID 32 | INT16s | AB | 0 |  | X | X
Plant config | 36034 |  | 336035 | 04 |  | Plant source ID 33 | INT16s | AB | 0 |  | X | X
Plant config | 36035 |  | 336036 | 04 |  | Plant source ID 34 | INT16s | AB | 0 |  | X | X
Plant config | 36036 |  | 336037 | 04 |  | Plant source ID 35 | INT16s | AB | 0 |  | X | X
Plant config | 36037 |  | 336038 | 04 |  | Plant source ID 36 | INT16s | AB | 0 |  | X | X
Plant config | 36038 |  | 336039 | 04 |  | Plant source ID 37 | INT16s | AB | 0 |  | X | X
Plant config | 36039 |  | 336040 | 04 |  | Plant source ID 38 | INT16s | AB | 0 |  | X | X
Plant config | 36040 |  | 336041 | 04 |  | Plant source ID 39 | INT16s | AB | 0 |  | X | X
Plant config | 36041 |  | 336042 | 04 |  | Plant source ID 40 | INT16s | AB | 0 |  | X | X
PV monitoring area | 40000 |  | 340001 | 04 |  | DC voltage string 05 | INT16u | AB | 1 | V | X
PV monitoring area | 40001 |  | 340002 | 04 |  | DC power string 05 | INT16s | AB | 1 | kW | X
PV monitoring area | 40002 |  | 340003 | 04 |  | DC voltage string 06 | INT16u | AB | 1 | V | X
PV monitoring area | 40003 |  | 340004 | 04 |  | DC power string 06 | INT16s | AB | 1 | kW | X
PV monitoring area | 40004 |  | 340005 | 04 |  | DC voltage string 07 | INT16u | AB | 1 | V | X
PV monitoring area | 40005 |  | 340006 | 04 |  | DC power string 07 | INT16s | AB | 1 | kW | X
PV monitoring area | 40006 |  | 340007 | 04 |  | DC voltage string 08 | INT16u | AB | 1 | V | X
PV monitoring area | 40007 |  | 340008 | 04 |  | DC power string 08 | INT16s | AB | 1 | kW | X
PV monitoring area | 40008 |  | 340009 | 04 |  | DC voltage string 09 | INT16u | AB | 1 | V | X
PV monitoring area | 40009 |  | 340010 | 04 |  | DC power string 09 | INT16s | AB | 1 | kW | X
PV monitoring area | 40010 |  | 340011 | 04 |  | DC voltage string 10 | INT16u | AB | 1 | V | X
PV monitoring area | 40011 |  | 340012 | 04 |  | DC power string 10 | INT16s | AB | 1 | kW | X
PV monitoring area | 40012 |  | 340013 | 04 |  | DC voltage string 11 | INT16u | AB | 1 | V | X
PV monitoring area | 40013 |  | 340014 | 04 |  | DC power string 11 | INT16s | AB | 1 | kW | X
PV monitoring area | 40014 |  | 340015 | 04 |  | DC voltage string 12 | INT16u | AB | 1 | V | X
PV monitoring area | 40015 |  | 340016 | 04 |  | DC power string 12 | INT16s | AB | 1 | kW | X
PV monitoring area | 40016 |  | 340017 | 04 |  | DC current string 01 | INT16u | AB | 1 | A | X
PV monitoring area | 40017 |  | 340018 | 04 |  | DC current string 02 | INT16u | AB | 1 | A | X
PV monitoring area | 40018 |  | 340019 | 04 |  | DC current string 03 | INT16u | AB | 1 | A | X
PV monitoring area | 40019 |  | 340020 | 04 |  | DC current string 04 | INT16u | AB | 1 | A | X
PV monitoring area | 40020 |  | 340021 | 04 |  | DC current string 05 | INT16u | AB | 1 | A | X
PV monitoring area | 40021 |  | 340022 | 04 |  | DC current string 06 | INT16u | AB | 1 | A | X
PV monitoring area | 40022 |  | 340023 | 04 |  | DC current string 07 | INT16u | AB | 1 | A | X
PV monitoring area | 40023 |  | 340024 | 04 |  | DC current string 08 | INT16u | AB | 1 | A | X
PV monitoring area | 40024 |  | 340025 | 04 |  | DC current string 09 | INT16u | AB | 1 | A | X
PV monitoring area | 40025 |  | 340026 | 04 |  | DC current string 10 | INT16u | AB | 1 | A | X
PV monitoring area | 40026 |  | 340027 | 04 |  | DC current string 11 | INT16u | AB | 1 | A | X
PV monitoring area | 40027 |  | 340028 | 04 |  | DC current string 12 | INT16u | AB | 1 | A | X
PV monitoring area | 40028 |  | 340029 | 04 |  | DC current string 13 | INT16u | AB | 1 | A | X
PV monitoring area | 40029 |  | 340030 | 04 |  | DC current string 14 | INT16u | AB | 1 | A | X
PV monitoring area | 40030 |  | 340031 | 04 |  | DC current string 15 | INT16u | AB | 1 | A | X
PV monitoring area | 40031 |  | 340032 | 04 |  | DC current string 16 | INT16u | AB | 1 | A | X
PV monitoring area | 40032 |  | 340033 | 04 |  | DC current string 17 | INT16u | AB | 1 | A | X
PV monitoring area | 40033 |  | 340034 | 04 |  | DC current string 18 | INT16u | AB | 1 | A | X
PV monitoring area | 40034 |  | 340035 | 04 |  | DC current string 19 | INT16u | AB | 1 | A | X
PV monitoring area | 40035 |  | 340036 | 04 |  | DC current string 20 | INT16u | AB | 1 | A | X
PV monitoring area | 40036 |  | 340037 | 04 |  | DC current string 21 | INT16u | AB | 1 | A | X
PV monitoring area | 40037 |  | 340038 | 04 |  | DC current string 22 | INT16u | AB | 1 | A | X
PV monitoring area | 40038 |  | 340039 | 04 |  | DC current string 23 | INT16u | AB | 1 | A | X
PV monitoring area | 40039 |  | 340040 | 04 |  | DC current string 24 | INT16u | AB | 1 | A | X
Power meter area 1 | 46000 |  | 346001 | 04 |  | DG 01 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46001 |  | 346002 | 04 |  | DG 02 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46002 |  | 346003 | 04 |  | DG 03 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46003 |  | 346004 | 04 |  | DG 04 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46004 |  | 346005 | 04 |  | DG 05 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46005 |  | 346006 | 04 |  | DG 06 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46006 |  | 346007 | 04 |  | DG 07 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46007 |  | 346008 | 04 |  | DG 08 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46008 |  | 346009 | 04 |  | DG 09 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46009 |  | 346010 | 04 |  | DG 10 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46010 |  | 346011 | 04 |  | DG 11 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46011 |  | 346012 | 04 |  | DG 12 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46012 |  | 346013 | 04 |  | DG 13 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46013 |  | 346014 | 04 |  | DG 14 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46014 |  | 346015 | 04 |  | DG 15 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46015 |  | 346016 | 04 |  | DG 16 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46016 |  | 346017 | 04 |  | DG 01 actual Q measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46017 |  | 346018 | 04 |  | DG 02 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46018 |  | 346019 | 04 |  | DG 03 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46019 |  | 346020 | 04 |  | DG 04 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46020 |  | 346021 | 04 |  | DG 05 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46021 |  | 346022 | 04 |  | DG 06 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46022 |  | 346023 | 04 |  | DG 07 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46023 |  | 346024 | 04 |  | DG 08 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46024 |  | 346025 | 04 |  | DG 09 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46025 |  | 346026 | 04 |  | DG 10 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46026 |  | 346027 | 04 |  | DG 11 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46027 |  | 346028 | 04 |  | DG 12 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46028 |  | 346029 | 04 |  | DG 13 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46029 |  | 346030 | 04 |  | DG 14 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46030 |  | 346031 | 04 |  | DG 15 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46031 |  | 346032 | 04 |  | DG 16 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46032 |  | 346033 | 04 |  | DG 01 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46033 |  | 346034 | 04 |  | DG 02 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46034 |  | 346035 | 04 |  | DG 03 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46035 |  | 346036 | 04 |  | DG 04 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46036 |  | 346037 | 04 |  | DG 05 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46037 |  | 346038 | 04 |  | DG 06 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46038 |  | 346039 | 04 |  | DG 07 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46039 |  | 346040 | 04 |  | DG 08 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46040 |  | 346041 | 04 |  | DG 09 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46041 |  | 346042 | 04 |  | DG 10 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46042 |  | 346043 | 04 |  | DG 11 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46043 |  | 346044 | 04 |  | DG 12 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46044 |  | 346045 | 04 |  | DG 13 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46045 |  | 346046 | 04 |  | DG 14 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46046 |  | 346047 | 04 |  | DG 15 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46047 |  | 346048 | 04 |  | DG 16 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46048 |  | 346049 | 04 |  | Is the communication to DG 01 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46049 |  | 346050 | 04 |  | Is the communication to DG 02 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46050 |  | 346051 | 04 |  | Is the communication to DG 03 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46051 |  | 346052 | 04 |  | Is the communication to DG 04 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46052 |  | 346053 | 04 |  | Is the communication to DG 05 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46053 |  | 346054 | 04 |  | Is the communication to DG 06 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46054 |  | 346055 | 04 |  | Is the communication to DG 07 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46055 |  | 346056 | 04 |  | Is the communication to DG 08 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46056 |  | 346057 | 04 |  | Is the communication to DG 09 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46057 |  | 346058 | 04 |  | Is the communication to DG 10 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46058 |  | 346059 | 04 |  | Is the communication to DG 11 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46059 |  | 346060 | 04 |  | Is the communication to DG 12 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46060 |  | 346061 | 04 |  | Is the communication to DG 13 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46061 |  | 346062 | 04 |  | Is the communication to DG 14 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46062 |  | 346063 | 04 |  | Is the communication to DG 15 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46063 |  | 346064 | 04 |  | Is the communication to DG 16 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46064 |  | 346065 | 04 |  | PV/ESS 01 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46065 |  | 346066 | 04 |  | PV/ESS 02 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46066 |  | 346067 | 04 |  | PV/ESS 03 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46067 |  | 346068 | 04 |  | PV/ESS 04 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46068 |  | 346069 | 04 |  | PV/ESS 05 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46069 |  | 346070 | 04 |  | PV/ESS 06 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46070 |  | 346071 | 04 |  | PV/ESS 07 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46071 |  | 346072 | 04 |  | PV/ESS 08 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46072 |  | 346073 | 04 |  | PV/ESS 09 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46073 |  | 346074 | 04 |  | PV/ESS 10 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46074 |  | 346075 | 04 |  | PV/ESS 11 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46075 |  | 346076 | 04 |  | PV/ESS 12 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46076 |  | 346077 | 04 |  | PV/ESS 13 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46077 |  | 346078 | 04 |  | PV/ESS 14 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46078 |  | 346079 | 04 |  | PV/ESS 15 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46079 |  | 346080 | 04 |  | PV/ESS 16 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46080 |  | 346081 | 04 |  | PV/ESS 01 actual Q measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46081 |  | 346082 | 04 |  | PV/ESS 02 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46082 |  | 346083 | 04 |  | PV/ESS 03 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46083 |  | 346084 | 04 |  | PV/ESS 04 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46084 |  | 346085 | 04 |  | PV/ESS 05 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46085 |  | 346086 | 04 |  | PV/ESS 06 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46086 |  | 346087 | 04 |  | PV/ESS 07 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46087 |  | 346088 | 04 |  | PV/ESS 08 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46088 |  | 346089 | 04 |  | PV/ESS 09 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46089 |  | 346090 | 04 |  | PV/ESS 10 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46090 |  | 346091 | 04 |  | PV/ESS 11 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46091 |  | 346092 | 04 |  | PV/ESS 12 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46092 |  | 346093 | 04 |  | PV/ESS 13 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46093 |  | 346094 | 04 |  | PV/ESS 14 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46094 |  | 346095 | 04 |  | PV/ESS 15 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46095 |  | 346096 | 04 |  | PV/ESS 16 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46096 |  | 346097 | 04 |  | PV/ESS 01 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46097 |  | 346098 | 04 |  | PV/ESS 02 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46098 |  | 346099 | 04 |  | PV/ESS 03 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46099 |  | 346100 | 04 |  | PV/ESS 04 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46100 |  | 346101 | 04 |  | PV/ESS 05 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46101 |  | 346102 | 04 |  | PV/ESS 06 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46102 |  | 346103 | 04 |  | PV/ESS 07 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46103 |  | 346104 | 04 |  | PV/ESS 08 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46104 |  | 346105 | 04 |  | PV/ESS 09 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46105 |  | 346106 | 04 |  | PV/ESS 10 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46106 |  | 346107 | 04 |  | PV/ESS 11 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46107 |  | 346108 | 04 |  | PV/ESS 12 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46108 |  | 346109 | 04 |  | PV/ESS 13 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46109 |  | 346110 | 04 |  | PV/ESS 14 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46110 |  | 346111 | 04 |  | PV/ESS 15 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46111 |  | 346112 | 04 |  | PV/ESS 16 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46112 |  | 346113 | 04 |  | Is the communication to PV/ESS 01 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46113 |  | 346114 | 04 |  | Is the communication to PV/ESS 02 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46114 |  | 346115 | 04 |  | Is the communication to PV/ESS 03 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46115 |  | 346116 | 04 |  | Is the communication to PV/ESS 04 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46116 |  | 346117 | 04 |  | Is the communication to PV/ESS 05 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46117 |  | 346118 | 04 |  | Is the communication to PV/ESS 06 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46118 |  | 346119 | 04 |  | Is the communication to PV/ESS 07 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46119 |  | 346120 | 04 |  | Is the communication to PV/ESS 08 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46120 |  | 346121 | 04 |  | Is the communication to PV/ESS 09 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46121 |  | 346122 | 04 |  | Is the communication to PV/ESS 10 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46122 |  | 346123 | 04 |  | Is the communication to PV/ESS 11 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46123 |  | 346124 | 04 |  | Is the communication to PV/ESS 12 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46124 |  | 346125 | 04 |  | Is the communication to PV/ESS 13 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46125 |  | 346126 | 04 |  | Is the communication to PV/ESS 14 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46126 |  | 346127 | 04 |  | Is the communication to PV/ESS 15 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46127 |  | 346128 | 04 |  | Is the communication to PV/ESS 16 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46128 |  | 346129 | 04 |  | Mains actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46129 |  | 346130 | 04 |  | Mains actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46130 |  | 346131 | 04 |  | Mains power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46131 |  | 346132 | 04 |  | Is the communication to the mains power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
PV monitoring area | 47000 |  | 347001 | 04 |  | Inverter serial number 01-02 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47001 |  | 347002 | 04 |  | Inverter serial number 03-04 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47002 |  | 347003 | 04 |  | Inverter serial number 05-06 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47003 |  | 347004 | 04 |  | Inverter serial number 07-08 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47004 |  | 347005 | 04 |  | Inverter serial number 09-10 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47005 |  | 347006 | 04 |  | Inverter serial number 11-12 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47006 |  | 347007 | 04 |  | Inverter serial number 13-14 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47007 |  | 347008 | 04 |  | Inverter serial number 15-16 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47008 |  | 347009 | 04 |  | Inverter serial number 17-18 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47009 |  | 347010 | 04 |  | Inverter serial number 19-20 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47010 |  | 347011 | 04 |  | Inverter serial number 21-22 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47011 |  | 347012 | 04 |  | Inverter serial number 23-24 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47012 |  | 347013 | 04 |  | Inverter serial number 25-26 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47013 |  | 347014 | 04 |  | Inverter serial number 27-28 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47014 |  | 347015 | 04 |  | Inverter serial number 19-30 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47015 |  | 347016 | 04 |  | Inverter serial number 31-32 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47016 |  | 347017 | 04 |  | Inverter model 01-02 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47017 |  | 347018 | 04 |  | Inverter model 03-04 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47018 |  | 347019 | 04 |  | Inverter model 05-06 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47019 |  | 347020 | 04 |  | Inverter model 07-08 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47020 |  | 347021 | 04 |  | Inverter model 09-10 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47021 |  | 347022 | 04 |  | Inverter model 11-12 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47022 |  | 347023 | 04 |  | Inverter model 13-14 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47023 |  | 347024 | 04 |  | Inverter model 15-16 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47024 |  | 347025 | 04 |  | Inverter model 17-18 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47025 |  | 347026 | 04 |  | Inverter model 19-20 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47026 |  | 347027 | 04 |  | Inverter model 21-22 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47027 |  | 347028 | 04 |  | Inverter model 23-24 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47028 |  | 347029 | 04 |  | Inverter model 25-26 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47029 |  | 347030 | 04 |  | Inverter model 27-28 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47030 |  | 347031 | 04 |  | Inverter model 19-30 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47031 |  | 347032 | 04 |  | Inverter model 31-32 (format maker-dependent) | string | AB | 0 |  | X
PV monitoring area | 47032 |  | 347033 | 04 |  | Rated active power size | INT16u | AB | 1 | kW | X
PV monitoring area | 47033 |  | 347034 | 04 |  | Rated reactive power size | INT16u | AB | 1 | kVAr | X
PV monitoring area | 47034 |  | 347035 | 04 |  | Country code (format maker-dependent) | INT16u | AB | 0 |  | X
PV monitoring area | 47035 |  | 347036 | 04 |  | DC voltage string 01 | INT16u | AB | 1 | V | X
PV monitoring area | 47036 |  | 347037 | 04 |  | DC power string 01 | INT16s | AB | 1 | kW | X
PV monitoring area | 47037 |  | 347038 | 04 |  | DC voltage string 02 | INT16u | AB | 1 | V | X
PV monitoring area | 47038 |  | 347039 | 04 |  | DC power string 02 | INT16s | AB | 1 | kW | X
PV monitoring area | 47039 |  | 347040 | 04 |  | DC voltage string 03 | INT16u | AB | 1 | V | X
PV monitoring area | 47040 |  | 347041 | 04 |  | DC power string 03 | INT16s | AB | 1 | kW | X
PV monitoring area | 47041 |  | 347042 | 04 |  | DC voltage string 04 | INT16u | AB | 1 | V | X
PV monitoring area | 47042 |  | 347043 | 04 |  | DC power string 04 | INT16s | AB | 1 | kW | X
PV monitoring area | 47043 |  | 347044 | 04 |  | AC active power | INT16s | AB | 1 | kW | X
PV monitoring area | 47044 |  | 347045 | 04 |  | AC reactive power | INT16s | AB | 1 | kVAr | X
PV monitoring area | 47045 |  | 347046 | 04 |  | AC apparent power | INT16s | AB | 1 | kVA | X
PV monitoring area | 47046 |  | 347047 | 04 |  | Energy produced | INT32u | ABCD | 0 | kWh | X
PV monitoring area | 47048 |  | 347049 | 04 |  | Energy produced today | INT32u | ABCD | 1 | kWh | X
PV monitoring area | 47050 |  | 347051 | 04 |  | Operating hours | INT32u | ABCD | 0 | hour | X
PV monitoring area | 47052 |  | 347053 | 04 |  | Operating minutes today | INT16u | AB | 0 | minute | X
PV monitoring area | 47053 |  | 347054 | 04 |  | Cabinet temperature | INT16s | AB | 1 | Deg C | X
PV monitoring area | 47054 |  | 347055 | 04 |  | Phase1 to neutral PV voltage | INT16u | AB | 1 | V | X
PV monitoring area | 47055 |  | 347056 | 04 |  | Phase2 to neutral PV voltage | INT16u | AB | 1 | V | X
PV monitoring area | 47056 |  | 347057 | 04 |  | Phase3 to neutral PV voltage | INT16u | AB | 1 | V | X
PV monitoring area | 47057 |  | 347058 | 04 |  | Phase1 to phase2 PV voltage | INT16u | AB | 1 | V | X
PV monitoring area | 47058 |  | 347059 | 04 |  | Phase2 to phase3 PV voltage | INT16u | AB | 1 | V | X
PV monitoring area | 47059 |  | 347060 | 04 |  | Phase3 to phase1 PV voltage | INT16u | AB | 1 | V | X
PV monitoring area | 47060 |  | 347061 | 04 |  | Grid frequency | INT16u | AB | 1 | Hz | X
PV monitoring area | 47061 |  | 347062 | 04 |  | Active power reference (format maker-dependent) | INT16s | AB | 0 |  | X
PV monitoring area | 47062 |  | 347063 | 04 |  | Reactive power reference (format maker-dependent) | INT16s | AB | 0 |  | X
PV monitoring area | 47063 |  | 347064 | 04 |  | Inverter state (format maker-dependent) | INT16u | AB | 0 |  | X
PV monitoring area | 47064 |  | 347065 | 04 |  | Fault code (format maker-dependent) | INT16u | AB | 0 |  | X
PV monitoring area | 47069 |  | 347070 | 04 |  | 0: Inverter not alive on communication link. 1: Inverter alive on communication link. | INT16s | AB | 0 |  | X
PV monitoring area | 49940 |  | 349941 | 04 |  | PV monitoring version | INT16u | AB | 0 |  | X | X
PV monitoring area | 49941 |  | 349942 | 04 |  | PV protocol selection | INT16u | AB | 0 |  | X | X
PV monitoring area | 49942 |  | 349943 | 04 |  | PV protocol selection 01-02 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49943 |  | 349944 | 04 |  | PV protocol selection 03-04 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49944 |  | 349945 | 04 |  | PV protocol selection 05-06 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49945 |  | 349946 | 04 |  | PV protocol selection 07-08 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49946 |  | 349947 | 04 |  | PV protocol selection 09-10 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49947 |  | 349948 | 04 |  | PV protocol selection 11-12 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49948 |  | 349949 | 04 |  | PV protocol selection 13-14 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49949 |  | 349950 | 04 |  | PV protocol selection 15-16 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49950 |  | 349951 | 04 |  | PV protocol selection 17-18 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49951 |  | 349952 | 04 |  | PV protocol selection 19-20 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49952 |  | 349953 | 04 |  | Monitoring enabled: 0: Disabled. 1: Enabled | INT16u | AB | 0 |  | X | X
PV monitoring area | 49953 |  | 349954 | 04 |  | Number of inverter to monitor | INT16u | AB | 0 |  | X | X
PV monitoring area | 49954 |  | 349955 | 04 |  | Number of inverters missing | INT16u | AB | 0 |  | X | X
PV monitoring area | 49955 |  | 349956 | 04 |  | Lowest inverter ID missing | INT16u | AB | 0 |  | X | X
PV monitoring area | 49956 |  | 349957 | 04 |  | Highest inverter ID missing | INT16u | AB | 0 |  | X | X
PV monitoring area | 49957 |  | 349958 | 04 |  | P ref type: 0: Percentage. 1: kW | INT16u | AB | 0 |  | X | X
PV monitoring area | 49958 |  | 349959 | 04 |  | Q ref type: 0: Percentage. 1: kW. 2: Cos phi. 3: PF | INT16u | AB | 0 |  | X | X
PV monitoring area | 49959 |  | 349960 | 04 |  | P ref resolution: 0: zero decimals. 1: one decimal. 2: two decimals. 3: three decimals. | INT16u | AB | 0 |  | X | X
PV monitoring area | 49960 |  | 349961 | 04 |  | Q ref resolution: 0: zero decimals. 1: one decimal. 2: two decimals. 3: three decimals. | INT16u | AB | 0 |  | X | X
PV monitoring area | 49961 |  | 349962 | 04 |  | Lowest Modbus ID of the inverters | INT16u | AB | 0 |  | X | X