## Data Range
Turbo Control (TC) Steam ¦ Turbine controller
Input / Output list 4189341461-A
Product: TC Turbo Control - Steam ¦ Turbine
Software-Version: x.0.0.5
Sheet No. | Input Output Type | ID Range
1 | Digital Inputs | 1-217
2 | Analog Inputs | 1-56
3 | Temperatue Inputs | 1-74
4 | Digital Outputs | 1-127
5 | Analog Outputs | 1-21

## Digital Inputs
#VALUE! | Digital Inputs:
ID | Text | Terminal | Polarity | Description
1-120 | Conf. DI 1-120 | N.A. | Configurable | Configurable digital input function Depending on the configuration, the alarm can be tripped with a high or low signal on the terminal For example the alarm text, alarm level and delay times can be configured
121-124 | Conf. counter 1-4 | N.A. | Configurable | Configurable counter The pulse count of configurable counter 1 will increase by 1 at a negative edge of this digital input
125-129 | Reset PID 1-5 | N.A. | HIGH = Reset | Configurable PIDs With a positive edge on the digital input, the configurable PID 1 will be reset The PID output will jump to the start value parameter
130-161 | Alarm inhibit 1-32 | N.A. | HIGH = Inhibit | Configurable alarms If configured, any configurable alarm can be inhibited by this digital input The Alarm is inhibited with a high signal
162 | Emergency stop | 323 | LOW = Alarm | Related alarm: 100005
163 | Watchdog | N.A. | LOW = Alarm | Used to check the watchdog functionality of the STG Must be connected with the watchdog output on the PCM module via relay Related alarm: 100008
164 | Safety chain | N.A. | HIGH = Chain closed | Feedback input from the safety chain Related alarm: 100009, 100010, 100011
165 | Pickup 1 | 330/331 | DC-Signal 0V/24V | Speed input for pickup 1 Max frequency: 20kHz
166 | Pickup 2 | 430/431 | DC-Signal 0V/24V | Speed input for pickup 2 Max frequency: 20kHz
167 | Acknowledge alarms | N.A. | RISING EDGE = Acknowledge | All active alarms will be acknowledged at a positive edge
168 | Clear alarms | N.A. | RISING EDGE = Clear | All acknowledged alarms will be cleared at a positive edge
169 | Ack. / Clear alarms | 326 | RISING EDGE = Reset | All alarms will be acknowledged and cleared at a positive edge
170 | Select hot start | N.A. | HIGH = Hot start | Overwrite of hot and cold start time parameters Every start will be a hot start, as long this function is high
171 | Start preparation finished | N.A. | HIGH = Finished | Feedback of external start preparations Transit condition from START PREPARATION to START PREPARATION FINISHED
172 | Start demand | 324 | HIGH = Start demanded | TODO
173 | Stop demand | 325 | HIGH = Stop demanded | TODO
174 | Stop postrun | N.A. | HIGH = Stop postrun | Overwrite for the post run timer, aborts the postrun
175 | Speed limit idle 1 | 368 | RISING EDGE = Limited to idle speed 1 | Forces the STG to operation level 6 Speed setpoint is limited to idle speed 1 Related alarm: 600001
176 | Speed limit idle 2 | N.A. | RISING EDGE = Limited to idle speed 2 | Forces the STG to operation level 7 Speed setpoint is limited to idle speed 2 Related alarm: 700000
177 | No speed limit | N.A. | RISING EDGE = No speed limit | Resets both, idle speed 1 and 2 limitation Related alarms: 600001 / 700000
178 | Overspeed test | N.A. | HIGH = Test | Future use
179 | GCB opened | N.A. | HIGH = Open | Generator circuit breaker feedback (opened)
180 | GCB closed | 367 | HIGH = Closed | Generator circuit breaker feedback (closed)
181 | MCB opened | N.A. | HIGH = Open | Mains circuit breaker feedback (opened)
182 | MCB closed | N.A. | HIGH = Closed | Mains circuit breaker feedback (closed)
183 | Island parallel | N.A. | HIGH = Island parallel | Used in island mode Defines together with parameter 21000 if speed droop is active Defines together with parameter 21100 if voltage droop is active Related parameters: 21000 / 21100
184 | Busbar is black | N.A. | HIGH = Black | Used if no GPM module is used Must be high, if the busbar has no voltage otherwise closing the generator breaker is not possible Related DI-Functions: 'Wish black closing' / 'Release black closing'
185 | Wish black closing | N.A. | HIGH = Wish | If any other generator wants to connect to the black busbar, this must be high Related DI-Functions: 'Busbar is black' / 'Release black closing'
186 | Release black closing | N.A. | HIGH = Released | Must be high, if the controller is allowed to close the generator breaker Related DI-Functions: 'Busbar is black' / 'Wish black closing'
187 | Enable operation | N.A. | HIGH = Enabled | Input for a switch on the switchboard Will trip the 'Operation blocked on switchboard panel' alarm Related alarm: 200110
188 | Manual mode | N.A. | HIGH = Manual | Does not work in remote control Controller is switched to manual mode at a positive edge
189 | Semi-Auto mode | N.A. | HIGH = Semi-Auto | Does not work in remote control Controller is switched to semi-automatic mode at a positive edge
190 | Automatic mode | N.A. | HIGH = Auto | Does not work in remote control Controller is switched to automatic mode at a positive edge
191 | Local / Remote | N.A. | HIGH = Local | Defines if the controller is in local, remote or full control Low: Remote, High: Local, Not assigned: full control
192 | Demand island operation | N.A. | HIGH = Island operation demanded | Demands the island mode If high, the controller will try to open the mains breaker All alarms, which are not relevant in island mode, will not trip anymore
193 | Shutdown | N.A. | HIGH = Shutdown | Will shutdown the turbine if high Related alarm: 200003
194 | Power control (Load) | N.A. | RISING EDGE = Activate power control as position control in grid parallel operation | Does not work in remote control Controller is switched to power control at a positive edge
195 | Power control (Droop) | N.A. | RISING EDGE = Activate power control as speed control in grid parallel operation | Does not work in remote control Controller is switched to speed control at a positive edge
196 | Activate pressure control | N.A. | HIGH = Increase pressure | Activates / Deactivates the pressure control module Deactivated if not assigned
197 | Remote pressure control | N.A. | HIGH = Activate remote pressure control | Defines if the local or remote pressure setpoint is used Remote and local pressure are function assignments
198 | Speed up | 363 | HIGH = Increase speed | Increases the speed setpoint Only working in the following main states NOMINAL SPEED, SYNCHRONIZING, SYNCHRON CONNECT
199 | Speed down | 364 | HIGH = Decrease speed | Decreases the speed setpoint Only working in the following main states NOMINAL SPEED, SYNCHRONIZING, SYNCHRON CONNECT
200 | Power up | 365 | HIGH = Increase power | Increases the power setpoint The longer the input is high, the faster the power setpoint will change
201 | Power down | 366 | HIGH = Decrease power | Decreases the power setpoint The longer the input is high, the faster the power setpoint will change
202 | Voltage up | N.A. | HIGH = Increase voltage | Increases the speed setpoint Only working in voltage droop mode or in the following main states NOMINAL SPEED, SYNCHRONIZING, SYNCHRON CONNECT
203 | Voltage down | N.A. | HIGH = Decrease voltage | Decreases the speed setpoint Only working in voltage droop mode or in the following main states NOMINAL SPEED, SYNCHRONIZING, SYNCHRON CONNECT
204 | Pressure up | N.A. | HIGH = Increase pressure | Increases the pressure setpoint in case of pressure control
205 | Pressure down | N.A. | HIGH = Decrease pressure | Decreases the pressure setpoint in case of pressure control
206 | Modbus write access | N.A. | HIGH = Write access | Defines if the defined modbus values are used or not Related parameters: 43200 / 43300
207 | Trending scope on | N.A. | RISING EDGE = Scope on | The high and normal resolution scopes are started at a positive edge
208 | Trending scope off | N.A. | RISING EDGE = Scope off | The high and normal resolution scopes are stopped at a positive edge
209 | Valve limiter open | N.A. | HIGH = Open | Increases the maximum allowed opening position of the steam valve
210 | Valve limiter close | N.A. | HIGH = Close | Decreases the maximum allowed opening position of the steam valve
211 | Clock synchronization | N.A. | RISING EDGE = Synchronize | A rising edge on this input will set the system time to 4.00 am
212 | Bearing lubrication | N.A. | RISING EDGE = Toggle | A rising edge on this input will toggle the corresponding DO if permitted by control Only if turbine is not running DI is not evaluated in TEST Related DO-Function: 'Bearing lubrication'
213 | Clear power limitation | N.A. | RISING EDGE = Clear | A rising edge on this input will clear an alarm to release power regulation From 'Limited Load' to target power setpoint Related alarm: 1100000
214 | LP valve limiter open | N.A. | limiter open 1% | (Line 1) (Line 2) (Line 3) (Line 4) (Line 5)
215 | LP valve limiter close | N.A. | limiter close 1% | (Line 1) (Line 2) (Line 3) (Line 4) (Line 5)
216 | Extraction demand up | N.A. | HIGH= demand up | (Line 1) (Line 2) (Line 3) (Line 4) (Line 5)
217 | Extraction demand down | N.A. | HIGH= demand down | (Line 1) (Line 2) (Line 3) (Line 4) (Line 5)

## Analog Inputs
#VALUE! | Analog Inputs:
ID | Text | Terminal | Scaling | Description
1 - 48 | Conf. AI 1 - 48 | N.A. | Configurable | Configurable analog input function Depending on the configuration, the alarm can be tripped if the input value is below or above a configurable limit For example the alarm text, alarm level and delay times can be configured
49 | Limit switch input (1) | N.A. | -20...20mA | The input value of the configurable limit switch 1
50 | Limit switch input (2) | N.A. | -20...20mA | The input value of the configurable limit switch 2
51 | Generator power | N.A. | 4...20mA <=> 0...125% Pnom | This input is needed, if no GPM module is used
52 | Demanded power | N.A. | 4...20mA <=> 0...100% of Pnom
53 | Power limitation | N.A. | 4...20mA <=> 0...100% of Pnom | The power setpoint will not go above this value
54 | Speed adjustment | N.A. | -20...+20mA <=> Min...Max | +/- 20mA Minus => Lower speed Plus => Raise speed
55 | Extraction pressure | N.A. | 4...20mA <=> 0..parameter value of Ext
56 | Demand extraction pressure | N.A. | 4...20mA <=> min..max parameter

## Temperature Inputs
#VALUE! | Temperature Inputs:
ID | Text | Terminal | Sensor | Description
1-72 | Conf. TMP 1-72 | N.A. | Configurable | Configurable temperature input function Depending on the configuration, the alarm can be tripped if the temperature is below or above a configurable limit For example the alarm text, alarm level and delay times can be configured
73 | Cold-junction A | N.A. | PT100
74 | Cold-junction B | N.A. | PT100

## Digital Outputs
#VALUE! | Digital Outputs:
ID | Text | Terminal | Polarity | [5 empty] | Description
1-32 | Alarm DO 1-32 | N.A. | HIGH = Alarm active | Configurable alarms | Any configurable alarm can be configured so that this digital output is set in case the alarm is active |  |  |  | Configurable alarms Any configurable alarm can be configured so that this digital output is set in case the alarm is active
33-42 | Alarm number DO 1-10 | N.A. | HIGH = Alarm active | COnfigurable Alarm digital output | The alarm output can be configured with any alarm number | If the specific alarm trips, the digital output will switch to a high signal |  |  | COnfigurable Alarm digital output The alarm output can be configured with any alarm number If the specific alarm trips, the digital output will switch to a high signal
43-52 | ON 1-10 | N.A. | Always ON | Configurable alarms | The digital output will always be high, if no configurable alarm blocks this digital output function |  |  |  | Configurable alarms The digital output will always be high, if no configurable alarm blocks this digital output function
53-54 | Limit DO 1-2 | N.A. | HIGH = Limit violated | Configurable limit switch | According the limit and logic level configuration of the limit switch, | this output will either be high or low dependent on the input signal |  |  | Configurable limit switch According the limit and logic level configuration of the limit switch, this output will either be high or low dependent on the input signal
55 | Load Stage 1-5 | N.A. | LOW = stage 1 active | Blocked - Future use |  |  |  |  | Blocked - Future use
60 | Rearm safety chain | N.A. | HIGH = Rearm chain | High pulse if the controller tries to close the safety chain |  |  |  |  | High pulse if the controller tries to close the safety chain
61 | Trip safety chain | N.A. | LOW = Trip chain | Must be part of the safety chain loop |  |  |  |  | Must be part of the safety chain loop
62 | Reset ext. alarms | N.A. | HIGH = Reset | High pulse, if something tries to clear all alarms |  |  |  |  | High pulse, if something tries to clear all alarms
63 | AGC4: Reset grid protection | N.A. | HIGH = Reset | If a AGC-4 is used for grid protection, this needs to be connected to it | Controller wants to clear all grid protection alarms on the AGC 4 |  |  |  | If a AGC-4 is used for grid protection, this needs to be connected to it Controller wants to clear all grid protection alarms on the AGC 4
64 | Green lamp | N.A. | HIGH = Green lamp on | High, if no alarm triggers the yellow or red lamp |  |  |  |  | High, if no alarm triggers the yellow or red lamp
65 | Yellow lamp | N.A. | HIGH = Yellow lamp on | High if any alarm with the 'yellow lamp' bit is tripped |  |  |  |  | High if any alarm with the 'yellow lamp' bit is tripped
66 | Red lamp | N.A. | HIGH = Red lamp on | High if any alarm with the 'red lamp' bit is tripped |  |  |  |  | High if any alarm with the 'red lamp' bit is tripped
67 | Manual mode | N.A. | HIGH = Manual mode
68 | Semi-Auto mode | N.A. | HIGH = Semi-Auto mode
69 | Automatic mode | N.A. | HIGH = Automatic mode
70 | State 'Available' | N.A. | HIGH = Available | Main state is equal to AVAILABLE |  |  |  |  | Main state is equal to AVAILABLE
71 | State 'Ready to start' | N.A. | HIGH = Ready to start | Main state is equal to READY TO START |  |  |  |  | Main state is equal to READY TO START
72 | State 'Idle speed 1' | N.A. | HIGH = Idle speed 1 | Main state is equal to IDLE SPEED 1 |  |  |  |  | Main state is equal to IDLE SPEED 1
73 | State 'Idle speed 2' | N.A. | HIGH = Idle speed 2 | Main state is equal to IDLE SPEED 2 |  |  |  |  | Main state is equal to IDLE SPEED 2
74 | State 'Nominal speed' | N.A. | HIGH = Nominal speed | Main state is equal to NOMINAL SPEED |  |  |  |  | Main state is equal to NOMINAL SPEED
75 | State 'Compressor' | N.A. | HIGH = Compressor | Future use |  |  |  |  | Future use
76 | State 'Synchronizing' | N.A. | HIGH = Synchronizing | Main state is equal to SYNCHRONIZING |  |  |  |  | Main state is equal to SYNCHRONIZING
77 | State 'Synchron connect' | N.A. | HIGH = Synchron connect | Main state is equal to SYNCHRON CONNECT |  |  |  |  | Main state is equal to SYNCHRON CONNECT
78 | State 'Island' | N.A. | HIGH = Island | Main state is equal to ISLAND but not in island parallel |  |  |  |  | Main state is equal to ISLAND but not in island parallel
79 | State 'Island parallel' | N.A. | HIGH = Island parallel | Main state is equal to ISLAND and in island parallel |  |  |  |  | Main state is equal to ISLAND and in island parallel
80 | State 'Grid parallel' | N.A. | HIGH = Grid parallel | Main state is equal to GIRD PARALLEL |  |  |  |  | Main state is equal to GIRD PARALLEL
81 | Turbine running | N.A. | HIGH = Turbine is running | High if the turbine speed is greater than the turbine speed defined in the 'Turbine running' parameter | Related parameter: 14008 |  |  |  | High if the turbine speed is greater than the turbine speed defined in the 'Turbine running' parameter Related parameter: 14008
82 | Speed control active | N.A. | HIGH = Speed control is active
83 | Frequency control active | N.A. | HIGH = Frequency control is active
84 | Position control active | N.A. | HIGH = Position control is active
85 | Power control active | N.A. | HIGH = Power control is active
86 | Live steam p control active | N.A. | HIGH = Live steam pressure control is active
87 | Exh. steam p control active | N.A. | HIGH = Exhaust steam pressure control is active
88 | GCB On | N.A. | HIGH = Close breaker | Pulse | High until GCB is closed, but no longer than 500ms |  |  |  | Pulse High until GCB is closed, but no longer than 500ms
89 | GCB Off | N.A. | HIGH = Open breaker | Pulse | High until GCB is open, but no longer than 3s |  |  |  | Pulse High until GCB is open, but no longer than 3s
90 | GCB Trip | N.A. | LOW = Trip breaker | Steady signal | GCB is tripped if any active alarm has 'BIT1: Trip GCB' configured |  |  |  | Steady signal GCB is tripped if any active alarm has 'BIT1: Trip GCB' configured
91 | GCB Release | N.A. | HIGH = GCB released | Steady signal | GCB is released if not tripped by any alarm and closing is requested by control | On a low signal the GCB has to disconnected immediately if not already open |  |  | Steady signal GCB is released if not tripped by any alarm and closing is requested by control On a low signal the GCB has to disconnected immediately if not already open
92 | GCB Backup | N.A. | HIGH = Open breaker | Steady signal | Switched on 5s after trip, if GCB does not disconnect | Switched off if all alarms with 'BIT1: Trip GCB' configured are cleared |  |  | Steady signal Switched on 5s after trip, if GCB does not disconnect Switched off if all alarms with 'BIT1: Trip GCB' configured are cleared
93 | MCB Trip | N.A. | HIGH = Trip breaker | Steady signal | MCB is tripped if any active alarm has 'BIT2: Trip MCB' configured |  |  |  | Steady signal MCB is tripped if any active alarm has 'BIT2: Trip MCB' configured
94 | MCB Release | N.A. | HIGH = MCB released | Steady signal | MCB is released if not tripped by any alarm and closing is requested by control | On a low signal the MCB has to disconnected immediately if not already open |  |  | Steady signal MCB is released if not tripped by any alarm and closing is requested by control On a low signal the MCB has to disconnected immediately if not already open
95 | Release AVR | N.A. | HIGH = AVR released | Steady signal | Switched on if requested by control and activation speed exceeded | Switched off after GCB has disconnected or when turbine is stopping depending on parameter setting | Related parameters: 20035 / 20036 |  | Steady signal Switched on if requested by control and activation speed exceeded Switched off after GCB has disconnected or when turbine is stopping depending on parameter setting Related parameters: 20035 / 20036
96 | Release U=U | N.A. | HIGH = U=U released | Steady signal | Switched on during synchronization |  |  |  | Steady signal Switched on during synchronization
97 | Release CosPhi control | N.A. | HIGH = CosPhi control released | Steady signal | Switched on in grid parallel operation | Only if voltage droop is not activated by parameter | Related parameter: 21100 |  | Steady signal Switched on in grid parallel operation Only if voltage droop is not activated by parameter Related parameter: 21100
98 | U/f Busbar is ok | N.A. | HIGH = U/f is ok | Steady signal | Switched on if voltage and frequency on busbar are within limits | Limits are depending on MCB position | MCB open: Limits from generator protection | MCB closed: Limits from grid protection | Steady signal Switched on if voltage and frequency on busbar are within limits Limits are depending on MCB position MCB open: Limits from generator protection MCB closed: Limits from grid protection
99 | Overspeed tripped | N.A. | HIGH = Overspeed tripped | Steady signal | Switched on if an overspeed alarm is active | Related alarms: 200113 / 200114 |  |  | Steady signal Switched on if an overspeed alarm is active Related alarms: 200113 / 200114
100 | Island demand | N.A. | HIGH = Island demanded | Steady signal | Switched on if island operation is demanded by control | Demand can be set by modbus or digital input | Control of MCB has to be realized externally | Related DI-Function: 'Demand island operation' | Steady signal Switched on if island operation is demanded by control Demand can be set by modbus or digital input Control of MCB has to be realized externally Related DI-Function: 'Demand island operation'
101 | Wish black closing | N.A. | HIGH = Wish for black closing | Steady signal | Switched on if the controller wants to close GCB to black busbar | Related DI-Functions: 'Release black closing' / 'Wish black closing' | Related DO-Function: 'Release black closing' |  | Steady signal Switched on if the controller wants to close GCB to black busbar Related DI-Functions: 'Release black closing' / 'Wish black closing' Related DO-Function: 'Release black closing'
102 | Release black closing | N.A. | HIGH = Release black closing | Steady signal | Switched on if the controller gives the release for black closing to other generators | Related DI-Functions: 'Release black closing' / 'Wish black closing' | Related DO-Function: 'Wish black closing' |  | Steady signal Switched on if the controller gives the release for black closing to other generators Related DI-Functions: 'Release black closing' / 'Wish black closing' Related DO-Function: 'Wish black closing'
103 | Startprepare demand | N.A. | HIGH = Startprepare demanded | Steady signal | Switched on in main states START PREPARATION and READY TO START | In START PREPARTION additional auxiliaries should be activated | In READY TO START additional auxiliaries should stay activated until start |  | Steady signal Switched on in main states START PREPARATION and READY TO START In START PREPARTION additional auxiliaries should be activated In READY TO START additional auxiliaries should stay activated until start
104 | kWh pulse | N.A. | 200ms-Pulse each kWh | 100ms pulse | One pulse after each kWh |  |  |  | 100ms pulse One pulse after each kWh
105 | Time switch | N.A. | HIGH = Start demand | Steady signal | Switched on/off depending on day and time settings | Related parameters: 65100 ... 65471 |  |  | Steady signal Switched on/off depending on day and time settings Related parameters: 65100 ... 65471
106 | Limit switch speed < | N.A. | HIGH = Value < Limit | Steady signal | Switched on if measured primary speed is below limit | Switched off if measured primary speed is above limit + hysteresis | Related parameters: 48000 / 48001 |  | Steady signal Switched on if measured primary speed is below limit Switched off if measured primary speed is above limit + hysteresis Related parameters: 48000 / 48001
107 | Limit switch speed > | N.A. | HIGH = Value > Limit | Steady signal | Switched on if measured primary speed is above limit | Switched off if measured primary speed is below limit - hysteresis | Related parameters: 48010 / 48011 |  | Steady signal Switched on if measured primary speed is above limit Switched off if measured primary speed is below limit - hysteresis Related parameters: 48010 / 48011
108 | Limit switch power > | N.A. | HIGH = Value > Limit | Steady signal | Switched on if electrical power is above limit | Switched off if electrical power is below limit - hysteresis | Related parameters: 48030 / 48031 |  | Steady signal Switched on if electrical power is above limit Switched off if electrical power is below limit - hysteresis Related parameters: 48030 / 48031
109 | Limit switch p live steam > | N.A. | HIGH = Value > Limit | Steady signal | Switched on if (local) live steam pressure is above limit | Switched off if (local) live steam pressure is below limit - hysteresis | Related parameters: 48040 / 48041 |  | Steady signal Switched on if (local) live steam pressure is above limit Switched off if (local) live steam pressure is below limit - hysteresis Related parameters: 48040 / 48041
110 | Limit switch p exh. steam > | N.A. | HIGH = Value > Limit | Steady signal | Switched on if (local) exhaust pressure is above limit | Switched off if (local) exhaust pressure is below limit - hysteresis | Related parameters: 48050 / 48051 |  | Steady signal Switched on if (local) exhaust pressure is above limit Switched off if (local) exhaust pressure is below limit - hysteresis Related parameters: 48050 / 48051
111 | Limit switch actuator output > | N.A. | HIGH = Value > Limit | Steady signal | Switched on if governor output is above limit | Switched off if governor output is below limit - hysteresis | Related parameters: 48060 / 48061 |  | Steady signal Switched on if governor output is above limit Switched off if governor output is below limit - hysteresis Related parameters: 48060 / 48061
112 | Limit switch speed setpoint > | N.A. | HIGH = Value > Limit | Steady signal | Switched on if internal speed setpoint is above limit | Switched off if internal speed setpoint is below limit - hysteresis | Related parameters: 48020 / 48021 |  | Steady signal Switched on if internal speed setpoint is above limit Switched off if internal speed setpoint is below limit - hysteresis Related parameters: 48020 / 48021
113 | Cold start | N.A. | HIGH = Cold start | Steady signal | Switched on if next turbine start is a cold start | Related parameters: 17380 / 17381 |  |  | Steady signal Switched on if next turbine start is a cold start Related parameters: 17380 / 17381
114 | Hot start | N.A. | HIGH = Hot start | Steady signal | Switched on if next turbine start is a hot start | Related parameters: 17380 / 17381 |  |  | Steady signal Switched on if next turbine start is a hot start Related parameters: 17380 / 17381
115 | Warm start | N.A. | HIGH = Warm start | Steady signal | Switched on if next turbine start is a warm start | Related parameters: 17380 / 17381 |  |  | Steady signal Switched on if next turbine start is a warm start Related parameters: 17380 / 17381
116 | Bearing lubrication | N.A. | HIGH = Bearing lubrication on | Steady signal | Switched on/off by digital input | Always switched off if primary speed is above half of turbine running speed | Related parameter: 14008 | Related DI-Function: 'Bearing lubrication' | Steady signal Switched on/off by digital input Always switched off if primary speed is above half of turbine running speed Related parameter: 14008 Related DI-Function: 'Bearing lubrication'
117 | operation level > 1 | 375 | HIGH = operation level more than 1 | (Line 1) | (Line 2) | (Line 3) | (Line 4) | (Line 5)
118 | turbine trip | 376 | HIGH = operation level more than 2 | (Line 1) | (Line 2) | (Line 3) | (Line 4) | (Line 5)
119 | speed output 1 | N.A. | HIGH = speed is between parameter range | (Line 1) | (Line 2) | (Line 3) | (Line 4) | (Line 5)
120 | speed output 2 | N.A. | HIGH = speed is between parameter range | (Line 1) | (Line 2) | (Line 3) | (Line 4) | (Line 5)
121 | speed output 3 | N.A. | HIGH = speed is between parameter range | (Line 1) | (Line 2) | (Line 3) | (Line 4) | (Line 5)
122 | speed output 4 | N.A. | HIGH = speed is between parameter range | (Line 1) | (Line 2) | (Line 3) | (Line 4) | (Line 5)
123 | Extraction is allowed | N.A. | HIGH = Extraction is allowed | (Line 1) | (Line 2) | (Line 3) | (Line 4) | (Line 5)
124 | Extraction is active | N.A. | Extraction operation on | (Line 1) | (Line 2) | (Line 3) | (Line 4) | (Line 5)
125 | Extraction under regulation | N.A. | PID regulation is on | (Line 1) | (Line 2) | (Line 3) | (Line 4) | (Line 5)
126 | Extraction demand is analogue | N.A. | analogue input is selected as demand | (Line 1) | (Line 2) | (Line 3) | (Line 4) | (Line 5)
127 | Ext. demand analogue is healthy | N.A. | Demand analogue input is healthy | (Line 1) | (Line 2) | (Line 3) | (Line 4) | (Line 5)

## Analog Outputs
#VALUE! | Analog Outputs:
ID | Text | Terminal | Scaling | Description
1 | PID output 1 | N.A. | 4...20mA | Configurable PID The output for the configurable PID 1
2 | PID output 2 | N.A. | 4...20mA | Configurable PID The output for the configurable PID 2
3 | PID output 3 | N.A. | 4...20mA | Configurable PID The output for the configurable PID 3
4 | PID output 4 | N.A. | 4...20mA | Configurable PID The output for the configurable PID 4
5 | PID output 5 | N.A. | 4...20mA | Configurable PID The output for the configurable PID 5
6 | Steam valve | 319/320 | 4...20mA <=> 0...100% | The governor output Must be connected to the regulation valve
7 | Voltage regulator | N.A. | (-20...0...16)...(-16...20...20)mA <=> min...max | The voltage regulator output In case the generator voltage / reactive power shall regulated with the STG, this must be connected to the AVR The AVR must be in voltage regulation mode in any case
8 | V instrument | N.A. | 4...20mA <=> See parameter values | The actual generator voltage GPM needed Related parameters: 17220 / 17221
9 | kvar instrument | N.A. | 4...20mA <=> See parameter values | The actual reactive power GPM needed Related parameters: 17210 / 17211
10 | kW instrument | N.A. | 4...20mA <=> See parameter values | The actual real power Related parameters: 17200 / 17201
11 | Maximum allowed load | N.A. | 4...20mA <=> 0...100% | The actual allowed load of the turbine
12 | Power setpoint | N.A. | 4...20mA <=> 0...100% | The actual power setpoint of the turbine
13 | Speed | N.A. | 0...20mA <=> 0...125% | The actual turbine speed
14 | Speed setpoint | N.A. | 0...20mA <=> 0...125% | The actual speed setpoint of the turbine
15 | Live steam pressure | N.A. | 0...20mA <=> 0...60bar | The actual live steam pressure
16 | Live steam press. setp. | N.A. | 0...20mA <=> 0...60bar | The actual live steam pressure setpoint
17 | Exhaust steam pressure | N.A. | 0...20mA <=> 0...60bar | The actual exhaust steam pressure
18 | Exh. steam press. setp. | N.A. | 0...20mA <=> 0...60bar | The actual exhaust steam pressure setpoint
19 | LP valve | N.A. | 4...20mA <=> 0...100%
20 | LP valve (scale) | N.A. | LP scale output
21 | Steam valve(scale) | N.A. | Steam valve(scale)