Counter | 18218 |  | 318219 | Counters - Custom counters - Custom counter 66 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18220 |  | 318221 | Counters - Custom counters - Custom counter 67 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18222 |  | 318223 | Counters - Custom counters - Custom counter 68 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18224 |  | 318225 | Counters - Custom counters - Custom counter 69 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18226 |  | 318227 | Counters - Custom counters - Custom counter 70 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18228 |  | 318229 | Counters - Custom counters - Custom counter 71 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18230 |  | 318231 | Counters - Custom counters - Custom counter 72 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18232 |  | 318233 | Counters - Custom counters - Custom counter 73 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18234 |  | 318235 | Counters - Custom counters - Custom counter 74 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18236 |  | 318237 | Counters - Custom counters - Custom counter 75 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18238 |  | 318239 | Counters - Custom counters - Custom counter 76 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18240 |  | 318241 | Counters - Custom counters - Custom counter 77 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18242 |  | 318243 | Counters - Custom counters - Custom counter 78 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18244 |  | 318245 | Counters - Custom counters - Custom counter 79 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18246 |  | 318247 | Counters - Custom counters - Custom counter 80 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18248 |  | 318249 | Counters - Custom counters - Custom counter 81 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18250 |  | 318251 | Counters - Custom counters - Custom counter 82 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18252 |  | 318253 | Counters - Custom counters - Custom counter 83 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18254 |  | 318255 | Counters - Custom counters - Custom counter 84 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18256 |  | 318257 | Counters - Custom counters - Custom counter 85 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18258 |  | 318259 | Counters - Custom counters - Custom counter 86 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18260 |  | 318261 | Counters - Custom counters - Custom counter 87 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18262 |  | 318263 | Counters - Custom counters - Custom counter 88 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18264 |  | 318265 | Counters - Custom counters - Custom counter 89 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18266 |  | 318267 | Counters - Custom counters - Custom counter 90 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18268 |  | 318269 | Counters - Custom counters - Custom counter 91 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18270 |  | 318271 | Counters - Custom counters - Custom counter 92 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18272 |  | 318273 | Counters - Custom counters - Custom counter 93 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18274 |  | 318275 | Counters - Custom counters - Custom counter 94 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18276 |  | 318277 | Counters - Custom counters - Custom counter 95 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18278 |  | 318279 | Counters - Custom counters - Custom counter 96 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18280 |  | 318281 | Counters - Custom counters - Custom counter 97 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18282 |  | 318283 | Counters - Custom counters - Custom counter 98 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18284 |  | 318285 | Counters - Custom counters - Custom counter 99 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18286 |  | 318287 | Counters - Engine - Operation time - Running hours load profiled | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18288 |  | 318289 | Counters - Engine - Operation time - Running days since reset 1 | INT32 | X * 1 | X * 1 | d | X |  | X | X | X
Counter | 18290 |  | 318291 | Counters - Engine - Operation time - Running days since reset 2 | INT32 | X * 1 | X * 1 | d | X |  | X | X | X
Counter | 18292 |  | 318293 | Counters - Engine - Operation time - Running days since reset 3 | INT32 | X * 1 | X * 1 | d | X |  | X | X | X
Counter | 18294 |  | 318295 | Counters - Engine - Operation time - Running days since reset 4 | INT32 | X * 1 | X * 1 | d | X |  | X | X | X
Counter | 18296 |  | 318297 | Counters - Engine - Operation time - Running hours relative | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18298 |  | 318299 | Counters - Engine - Operation time - Automatic priority swap hours | INT32 | X * 1 | X * 1 | h | X | X | X | X | X | X | X
Counter | 18300 |  | 318301 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Active energy export (transducer 1) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18302 |  | 318303 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy export (transducer 1) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18304 |  | 318305 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Active energy import (transducer 1) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18306 |  | 318307 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy import (transducer 1) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18308 |  | 318309 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Active energy difference (transducer 1) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18310 |  | 318311 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy difference (transducer 1) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18312 |  | 318313 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Active energy export (transducer 2) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18314 |  | 318315 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy export (transducer 2) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18316 |  | 318317 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Active energy import (transducer 2) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18318 |  | 318319 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy import (transducer 2) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18320 |  | 318321 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Active energy difference (transducer 2) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18322 |  | 318323 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy difference (transducer 2) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18324 |  | 318325 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Active energy export (transducer 3) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18326 |  | 318327 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy export (transducer 3) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18328 |  | 318329 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Active energy import (transducer 3) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18330 |  | 318331 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy import (transducer 3) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18332 |  | 318333 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Active energy difference (transducer 3) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18334 |  | 318335 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy difference (transducer 3) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18336 |  | 318337 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Active energy export (transducer 4) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18338 |  | 318339 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy export (transducer 4) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18340 |  | 318341 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Active energy import (transducer 4) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18342 |  | 318343 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy import (transducer 4) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18344 |  | 318345 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Active energy difference (transducer 4) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18346 |  | 318347 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy difference (transducer 4) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Alarm status: Operating value | 20000 |  | 320001 | Application initialisation error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20001 |  | 320002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20002 |  | 320003 | Preliminary software | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20003 |  | 320004 | Parameters - Engine - Stop sequence - Stop failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20004 |  | 320005 | Parameters - Engine - Start sequence - Start failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20005 |  | 320006 | Parameters - Engine - Start sequence - Crank failure - Information | INT16 | X * 10 | X * 0.1 | RPM | X |  | X | X | X
Alarm status: Operating value | 20006 |  | 320007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20007 |  | 320008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20008 |  | 320009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20009 |  | 320010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20010 |  | 320011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Magnetic pickup wire break alarm | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20011 |  | 320012 | Parameters - Engine - Stop sequence - Externally stopped - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20013 |  | 320014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information | INT16 | X * 10 | X * 0.1 | bar | X |  | X | X | X
Alarm status: Operating value | 20014 |  | 320015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information | INT16 | X * 10 | X * 0.1 | bar | X |  | X | X | X
Alarm status: Operating value | 20015 |  | 320016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm status: Operating value | 20016 |  | 320017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm status: Operating value | 20017 |  | 320018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm status: Operating value | 20018 |  | 320019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm status: Operating value | 20019 |  | 320020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm status: Operating value | 20020 |  | 320021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20021 |  | 320022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20022 |  | 320023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20027 |  | 320028 | Parameters - Engine - Running detection - Primary running feedback failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20041 |  | 320042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - GB closing failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20041 |  | 320042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - BTB closing failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20041 |  | 320042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - MB closing failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20042 |  | 320043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - GB opening failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20042 |  | 320043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - BTB opening failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20042 |  | 320043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - MB opening failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20043 |  | 320044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - GB position failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20043 |  | 320044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - BTB position failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20043 |  | 320044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - MB position failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20044 |  | 320045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - GB configuration failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20044 |  | 320045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - BTB configuration failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20044 |  | 320045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - MB configuration failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20045 |  | 320046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - GB synchronisation failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20045 |  | 320046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - BTB synchronisation failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20045 |  | 320046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - MB synchronisation failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20046 |  | 320047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - GB de-load failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20046 |  | 320047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - BTB de-load failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20046 |  | 320047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - MB de-load failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20047 |  | 320048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - GB tripped (external) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20047 |  | 320048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - BTB tripped (external) | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20047 |  | 320048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - MB tripped (external) | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20048 |  | 320049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - GB short circuit | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20048 |  | 320049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - BTB short circuit | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20048 |  | 320049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - MB short circuit | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20049 |  | 320050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - MB closing failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20049 |  | 320050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - TB closing failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20050 |  | 320051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - MB opening failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20050 |  | 320051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - TB opening failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20051 |  | 320052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - MB position failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20051 |  | 320052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - TB position failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20052 |  | 320053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - MB configuration failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20052 |  | 320053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - TB configuration failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20053 |  | 320054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - MB synchronisation failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20053 |  | 320054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - TB synchronisation failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20054 |  | 320055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - MB de-load failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20054 |  | 320055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - TB de-load failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20055 |  | 320056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - MB tripped (external) | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20055 |  | 320056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - TB tripped (external) | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20056 |  | 320057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - MB short circuit | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20056 |  | 320057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - TB short circuit | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20060 |  | 320061 | Parameters - Mains - AC setup - Phase sequence error - Information - Mains phase sequence error | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Operating value | 20060 |  | 320061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Busbar phase sequence error | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Operating value | 20060 |  | 320061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Busbar B phase sequence error | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20061 |  | 320062 | Parameters - Generator - AC setup - Phase sequence error - Information - Generator phase sequence error | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20061 |  | 320062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Busbar A phase sequence error | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20061 |  | 320062 | Parameters - Mains - AC setup - Phase sequence error - Information - Mains phase sequence error | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20062 |  | 320063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20103 |  | 320104 | Parameters - Mains - Additional protections - ROCOF - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Operating value | 20103 |  | 320104 | Parameters - Busbar - Additional protections - ROCOF - Information | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Operating value | 20103 |  | 320104 | Parameters - Busbar B - Additional protections - ROCOF - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20104 |  | 320105 | Parameters - Mains - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 | ° |  |  | X | X
Alarm status: Operating value | 20104 |  | 320105 | Parameters - Busbar - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 | ° | X |  |  |  | X | X | X
Alarm status: Operating value | 20104 |  | 320105 | Parameters - Busbar B - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 | ° |  | X
Alarm status: Operating value | 20105 |  | 320106 | Parameters - Generator - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20105 |  | 320106 | Parameters - Busbar A - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20105 |  | 320106 | Parameters - Mains - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20106 |  | 320107 | Parameters - Local - 4th current input - Earth inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20107 |  | 320108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20108 |  | 320109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20108 |  | 320109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20108 |  | 320109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20109 |  | 320110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20109 |  | 320110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20109 |  | 320110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20110 |  | 320111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20110 |  | 320111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20110 |  | 320111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20111 |  | 320112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20111 |  | 320112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20111 |  | 320112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20115 |  | 320116 | Protection set point out of range | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20116 |  | 320117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Stabilised differential | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20117 |  | 320118 | Parameters - Generator - Current protections - High set differential current - Information - High set differential | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
Alarm status: Operating value | 20118 |  | 320119 | Protection set point out of range (differential current) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20119 |  | 320120 | Parameters - Local - Mode - Not under remote control - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20121 |  | 320122 | Parameters - Local - Monitoring - System not OK - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20122 |  | 320123 | Configuration update delayed | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20123 |  | 320124 | Critical process error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20124 |  | 320125 | Restore error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20125 |  | 320126 | SD-card format error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20126 |  | 320127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20127 |  | 320128 | Fieldbus configuration exceeded maximum I/O configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20128 |  | 320129 | Parameters - Custom alarms - Custom alarm 0 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20129 |  | 320130 | Parameters - Custom alarms - Custom alarm 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20130 |  | 320131 | Parameters - Custom alarms - Custom alarm 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20131 |  | 320132 | Parameters - Custom alarms - Custom alarm 3 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20132 |  | 320133 | Parameters - Custom alarms - Custom alarm 4 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20133 |  | 320134 | Parameters - Custom alarms - Custom alarm 5 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20134 |  | 320135 | Parameters - Custom alarms - Custom alarm 6 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20135 |  | 320136 | Parameters - Custom alarms - Custom alarm 7 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20136 |  | 320137 | Parameters - Custom alarms - Custom alarm 8 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20137 |  | 320138 | Parameters - Custom alarms - Custom alarm 9 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20138 |  | 320139 | Parameters - Custom alarms - Custom alarm 10 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20139 |  | 320140 | Parameters - Custom alarms - Custom alarm 11 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20140 |  | 320141 | Parameters - Custom alarms - Custom alarm 12 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20141 |  | 320142 | Parameters - Custom alarms - Custom alarm 13 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20142 |  | 320143 | Parameters - Custom alarms - Custom alarm 14 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20143 |  | 320144 | Parameters - Custom alarms - Custom alarm 15 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20144 |  | 320145 | Parameters - Custom alarms - Custom alarm 16 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20145 |  | 320146 | Parameters - Custom alarms - Custom alarm 17 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20146 |  | 320147 | Parameters - Custom alarms - Custom alarm 18 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20147 |  | 320148 | Parameters - Custom alarms - Custom alarm 19 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20148 |  | 320149 | Parameters - Custom alarms - Custom alarm 20 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20149 |  | 320150 | Parameters - Custom alarms - Custom alarm 21 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20150 |  | 320151 | Parameters - Custom alarms - Custom alarm 22 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20151 |  | 320152 | Parameters - Custom alarms - Custom alarm 23 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20152 |  | 320153 | Parameters - Custom alarms - Custom alarm 24 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20153 |  | 320154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - GOV regulation error | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20154 |  | 320155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - AVR regulation error | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20163 |  | 320164 | Required hardware card(s) not found | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20164 |  | 320165 | Software mismatch on hardware module(s) | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20165 |  | 320166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Mains L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Operating value | 20165 |  | 320166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Busbar L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Operating value | 20165 |  | 320166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Busbar B L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20166 |  | 320167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Generator L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Operating value | 20166 |  | 320167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Busbar A L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20166 |  | 320167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Mains L1-L2-L3 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Operating value | 20167 |  | 320168 | Parameters - Mains - AC setup - L1 wire break - Information - Mains L1 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Operating value | 20167 |  | 320168 | Parameters - Busbar - AC setup - L1 wire break - Information - Busbar L1 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Operating value | 20167 |  | 320168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Busbar B L1 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20168 |  | 320169 | Parameters - Mains - AC setup - L2 wire break - Information - Mains L2 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Operating value | 20168 |  | 320169 | Parameters - Busbar - AC setup - L2 wire break - Information - Busbar L2 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Operating value | 20168 |  | 320169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Busbar B L2 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20169 |  | 320170 | Parameters - Mains - AC setup - L3 wire break - Information - Mains L3 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Operating value | 20169 |  | 320170 | Parameters - Busbar - AC setup - L3 wire break - Information - Busbar L3 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Operating value | 20169 |  | 320170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Busbar B L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20170 |  | 320171 | Parameters - Generator - AC setup - L1 wire break - Information - Generator L1 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Operating value | 20170 |  | 320171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Busbar A L1 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20170 |  | 320171 | Parameters - Mains - AC setup - L1 wire break - Information - Mains L1 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Operating value | 20171 |  | 320172 | Parameters - Generator - AC setup - L2 wire break - Information - Generator L2 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Operating value | 20171 |  | 320172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Busbar A L2 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20171 |  | 320172 | Parameters - Mains - AC setup - L2 wire break - Information - Mains L2 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Operating value | 20172 |  | 320173 | Parameters - Generator - AC setup - L3 wire break - Information - Generator L3 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Operating value | 20172 |  | 320173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Busbar A L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20172 |  | 320173 | Parameters - Mains - AC setup - L3 wire break - Information - Mains L3 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Operating value | 20178 |  | 320179 | Parameters - Mains - AC setup - Supervision alarm - Information - Mains supervision alarm | INT16 | X * 1 | X * 1 |  |  |  | X | X |  | X | X
Alarm status: Operating value | 20179 |  | 320180 | Parameters - Engine - Emergency stop - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20179 |  | 320180 | Parameters - Busbar A - Emergency stop - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20179 |  | 320180 | Parameters - Mains - Emergency stop - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20180 |  | 320181 | Clock battery failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20181 |  | 320182 | Controller temperature too high | INT16 | X * 1 | X * 1 | °C | X | X | X | X | X | X | X
Alarm status: Operating value | 20182 |  | 320183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - PSM3.1 1 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20183 |  | 320184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - PSM3.1 1 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20184 |  | 320185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - PSM3.2 1 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20185 |  | 320186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - PSM3.2 1 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20186 |  | 320187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - PSM3.2 2 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20187 |  | 320188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - PSM3.2 2 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20188 |  | 320189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - PSM3.2 3 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20189 |  | 320190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - PSM3.2 3 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20190 |  | 320191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - EIM3.1 1 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20191 |  | 320192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - EIM3.1 1 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20192 |  | 320193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - EIM3.1 2 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20193 |  | 320194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - EIM3.1 2 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20194 |  | 320195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - EIM3.1 3 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20195 |  | 320196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - EIM3.1 3 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20196 |  | 320197 | EIM3.1 4 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20197 |  | 320198 | EIM3.1 4 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20198 |  | 320199 | EIM3.1 5 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20199 |  | 320200 | EIM3.1 5 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20200 |  | 320201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - EIM3.1 1 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20201 |  | 320202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - EIM3.1 2 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20202 |  | 320203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - EIM3.1 3 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20203 |  | 320204 | EIM3.1 4 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20204 |  | 320205 | EIM3.1 5 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20205 |  | 320206 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20206 |  | 320207 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20207 |  | 320208 | AC protections not running (differential current) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20208 |  | 320209 | AC data is missing (differential current) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20209 |  | 320210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - GAM3.2 1 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20210 |  | 320211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - GAM3.2 1 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20211 |  | 320212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - GAM3.2 2 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20212 |  | 320213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - GAM3.2 2 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20213 |  | 320214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - GAM3.2 3 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20214 |  | 320215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - GAM3.2 3 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20215 |  | 320216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - PSM3.2 4 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20216 |  | 320217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - PSM3.2 4 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20217 |  | 320218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - PSM3.2 5 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20218 |  | 320219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - PSM3.2 5 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20219 |  | 320220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - PSM3.2 6 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20220 |  | 320221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - PSM3.2 6 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20221 |  | 320222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - PSM3.2 7 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20222 |  | 320223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - PSM3.2 7 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20223 |  | 320224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - PSM3.2 8 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20224 |  | 320225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - PSM3.2 8 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20225 |  | 320226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - PSM3.2 9 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20226 |  | 320227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - PSM3.2 9 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20228 |  | 320229 | Parameters - System - Monitoring - Duplicate controller ID - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20229 |  | 320230 | Parameters - System - Monitoring - Missing all controllers - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20231 |  | 320232 | Controller ID not configured | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20236 |  | 320237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20237 |  | 320238 | Blackout detection mismatch | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20240 |  | 320241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - NTP server 1 could not connect | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20241 |  | 320242 | Parameters - Communication - NTP - NTP server 1 not responding - Information - NTP server 1 is not responding | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20242 |  | 320243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - NTP server 2 could not connect | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20243 |  | 320244 | Parameters - Communication - NTP - NTP server 2 not responding - Information - NTP server 2 is not responding | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20244 |  | 320245 | Parameters - Communication - NTP - No NTP server time synchronisation - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20245 |  | 320246 | Parameters - Communication - NTP - No NTP server(s) connected - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20246 |  | 320247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20247 |  | 320248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20296 |  | 320297 | Controller not part of system | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20297 |  | 320298 | Different single-line configurations | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20298 |  | 320299 | Single-line missing/none active | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20299 |  | 320300 | Parameters - Communication - Modbus - Modbus communication timeout - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20300 |  | 320301 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - CODESYS configuration conflict | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20301 |  | 320302 | Parameters - CODESYS - Monitoring - Application not OK - Information - CODESYS application not OK | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20302 |  | 320303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20303 |  | 320304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20304 |  | 320305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20305 |  | 320306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20306 |  | 320307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20307 |  | 320308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20308 |  | 320309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20309 |  | 320310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20310 |  | 320311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20311 |  | 320312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20312 |  | 320313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20315 |  | 320316 | Parameters - Local - CustomLogic - Configuration invalid - Information - CustomLogic configuration invalid | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20316 |  | 320317 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Digital AVR communication error | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20317 |  | 320318 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20318 |  | 320319 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20319 |  | 320320 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20320 |  | 320321 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20321 |  | 320322 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20322 |  | 320323 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20323 |  | 320324 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20324 |  | 320325 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20325 |  | 320326 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20326 |  | 320327 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20327 |  | 320328 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20328 |  | 320329 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20329 |  | 320330 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20330 |  | 320331 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20331 |  | 320332 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20332 |  | 320333 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20333 |  | 320334 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20334 |  | 320335 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20335 |  | 320336 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20336 |  | 320337 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20337 |  | 320338 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20338 |  | 320339 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20339 |  | 320340 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20340 |  | 320341 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20341 |  | 320342 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20342 |  | 320343 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20343 |  | 320344 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20344 |  | 320345 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20345 |  | 320346 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20346 |  | 320347 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20347 |  | 320348 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20348 |  | 320349 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20349 |  | 320350 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20350 |  | 320351 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20351 |  | 320352 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20352 |  | 320353 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20353 |  | 320354 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20354 |  | 320355 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20355 |  | 320356 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20356 |  | 320357 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20357 |  | 320358 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20358 |  | 320359 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20359 |  | 320360 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20360 |  | 320361 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20361 |  | 320362 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20362 |  | 320363 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20363 |  | 320364 | DAVR unsupported AC configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20364 |  | 320365 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Illegal DAVR configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20365 |  | 320366 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Generator under-voltage 1 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20365 |  | 320366 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Busbar A under-voltage 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20365 |  | 320366 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Mains under-voltage 1 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20366 |  | 320367 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Generator under-voltage 2 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20366 |  | 320367 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Busbar A under-voltage 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20366 |  | 320367 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Mains under-voltage 2 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20367 |  | 320368 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Generator under-voltage 3 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20367 |  | 320368 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Busbar A under-voltage 3 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20367 |  | 320368 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Mains under-voltage 3 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20368 |  | 320369 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Generator over-voltage 1 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20368 |  | 320369 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Busbar A over-voltage 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20368 |  | 320369 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Mains over-voltage 1 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20369 |  | 320370 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Generator over-voltage 2 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20369 |  | 320370 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Busbar A over-voltage 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20369 |  | 320370 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Mains over-voltage 2 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20370 |  | 320371 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Generator voltage unbalance | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20370 |  | 320371 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Busbar A voltage unbalance | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20370 |  | 320371 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Mains voltage unbalance | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20371 |  | 320372 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Generator negative sequence voltage | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20371 |  | 320372 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Busbar A negative sequence voltage | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20371 |  | 320372 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Mains negative sequence voltage | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20372 |  | 320373 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Generator zero sequence voltage | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20372 |  | 320373 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Busbar A zero sequence voltage | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20372 |  | 320373 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Mains zero sequence voltage | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20373 |  | 320374 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Generator positive sequence under-voltage | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20373 |  | 320374 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Busbar A positive sequence under-voltage | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20373 |  | 320374 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Mains positive sequence under-voltage | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20374 |  | 320375 | Parameters - Generator - Current protections - Over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20374 |  | 320375 | Parameters - Busbar A - Current protections - Over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20374 |  | 320375 | Parameters - Mains - Current protections - Over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20375 |  | 320376 | Parameters - Generator - Current protections - Over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20375 |  | 320376 | Parameters - Busbar A - Current protections - Over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20375 |  | 320376 | Parameters - Mains - Current protections - Over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20376 |  | 320377 | Parameters - Generator - Current protections - Over-current 3 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20376 |  | 320377 | Parameters - Busbar A - Current protections - Over-current 3 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20376 |  | 320377 | Parameters - Mains - Current protections - Over-current 3 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20377 |  | 320378 | Parameters - Generator - Current protections - Over-current 4 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20377 |  | 320378 | Parameters - Busbar A - Current protections - Over-current 4 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20377 |  | 320378 | Parameters - Mains - Current protections - Over-current 4 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20378 |  | 320379 | Parameters - Generator - Current protections - Fast over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20378 |  | 320379 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20378 |  | 320379 | Parameters - Mains - Current protections - Fast over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20379 |  | 320380 | Parameters - Generator - Current protections - Fast over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20379 |  | 320380 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20379 |  | 320380 | Parameters - Mains - Current protections - Fast over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20380 |  | 320381 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20380 |  | 320381 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20380 |  | 320381 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20381 |  | 320382 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20381 |  | 320382 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20381 |  | 320382 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20382 |  | 320383 | Parameters - Generator - Current protections - Directional over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20382 |  | 320383 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20382 |  | 320383 | Parameters - Mains - Current protections - Directional over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20383 |  | 320384 | Parameters - Generator - Current protections - Directional over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20383 |  | 320384 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20383 |  | 320384 | Parameters - Mains - Current protections - Directional over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20384 |  | 320385 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20385 |  | 320386 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20386 |  | 320387 | Parameters - Generator - Current protections - Negative sequence current - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20386 |  | 320387 | Parameters - Busbar A - Current protections - Negative sequence current - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20386 |  | 320387 | Parameters - Mains - Current protections - Negative sequence current - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20387 |  | 320388 | Parameters - Generator - Current protections - Zero sequence current - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20387 |  | 320388 | Parameters - Busbar A - Current protections - Zero sequence current - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20387 |  | 320388 | Parameters - Mains - Current protections - Zero sequence current - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20388 |  | 320389 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Generator over-frequency 1 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20388 |  | 320389 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Busbar A over-frequency 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20388 |  | 320389 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Mains over-frequency 1 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20389 |  | 320390 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Generator over-frequency 2 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20389 |  | 320390 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Busbar A over-frequency 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20389 |  | 320390 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Mains over-frequency 2 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20390 |  | 320391 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Generator over-frequency 3 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20390 |  | 320391 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Busbar A over-frequency 3 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20390 |  | 320391 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Mains over-frequency 3 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20391 |  | 320392 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Generator under-frequency 1 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20391 |  | 320392 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Busbar A under-frequency 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20391 |  | 320392 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Mains under-frequency 1 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20392 |  | 320393 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Generator under-frequency 2 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20392 |  | 320393 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Busbar A under-frequency 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20392 |  | 320393 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Mains under-frequency 2 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20393 |  | 320394 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Generator under-frequency 3 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20393 |  | 320394 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Busbar A under-frequency 3 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20393 |  | 320394 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Mains under-frequency 3 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20394 |  | 320395 | Parameters - Generator - Power protections - Overload 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20394 |  | 320395 | Parameters - Busbar A - Power protections - Power export 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20394 |  | 320395 | Parameters - Mains - Power protections - Overload 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20395 |  | 320396 | Parameters - Generator - Power protections - Overload 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20395 |  | 320396 | Parameters - Busbar A - Power protections - Power export 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20395 |  | 320396 | Parameters - Mains - Power protections - Overload 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20396 |  | 320397 | Parameters - Generator - Power protections - Overload 3 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20396 |  | 320397 | Parameters - Busbar A - Power protections - Power export 3 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20396 |  | 320397 | Parameters - Mains - Power protections - Overload 3 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20397 |  | 320398 | Parameters - Generator - Power protections - Overload 4 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20397 |  | 320398 | Parameters - Busbar A - Power protections - Power export 4 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20397 |  | 320398 | Parameters - Mains - Power protections - Overload 4 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20398 |  | 320399 | Parameters - Generator - Power protections - Overload 5 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20398 |  | 320399 | Parameters - Busbar A - Power protections - Power export 5 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20398 |  | 320399 | Parameters - Mains - Power protections - Overload 5 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20399 |  | 320400 | Parameters - Generator - Power protections - Reverse power 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20399 |  | 320400 | Parameters - Busbar A - Power protections - Power import 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20399 |  | 320400 | Parameters - Mains - Power protections - Reverse power 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20400 |  | 320401 | Parameters - Generator - Power protections - Reverse power 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20400 |  | 320401 | Parameters - Busbar A - Power protections - Power import 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20400 |  | 320401 | Parameters - Mains - Power protections - Reverse power 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20401 |  | 320402 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20401 |  | 320402 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20401 |  | 320402 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20402 |  | 320403 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20402 |  | 320403 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20402 |  | 320403 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20403 |  | 320404 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20403 |  | 320404 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20403 |  | 320404 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20404 |  | 320405 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20404 |  | 320405 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20404 |  | 320405 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20405 |  | 320406 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Mains over-voltage 1 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20405 |  | 320406 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Busbar over-voltage 1 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20405 |  | 320406 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Busbar B over-voltage 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20406 |  | 320407 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Mains over-voltage 2 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20406 |  | 320407 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Busbar over-voltage 2 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20406 |  | 320407 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Busbar B over-voltage 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20407 |  | 320408 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Mains over-voltage 3 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20407 |  | 320408 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Busbar over-voltage 3 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20407 |  | 320408 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Busbar B over-voltage 3 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20408 |  | 320409 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Mains under-voltage 1 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20408 |  | 320409 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Busbar under-voltage 1 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20408 |  | 320409 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Busbar B under-voltage 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20409 |  | 320410 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Mains under-voltage 2 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20409 |  | 320410 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Busbar under-voltage 2 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20409 |  | 320410 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Busbar B under-voltage 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20410 |  | 320411 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Mains under-voltage 3 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20410 |  | 320411 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Busbar under-voltage 3 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20410 |  | 320411 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Busbar B under-voltage 3 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20411 |  | 320412 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Mains under-voltage 4 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20411 |  | 320412 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Busbar under-voltage 4 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20411 |  | 320412 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Busbar B under-voltage 4 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20412 |  | 320413 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Mains voltage unbalance | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20412 |  | 320413 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Busbar voltage unbalance | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20412 |  | 320413 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Busbar B voltage unbalance | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20413 |  | 320414 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Mains over-frequency 1 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20413 |  | 320414 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Busbar over-frequency 1 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20413 |  | 320414 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Busbar B over-frequency 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20414 |  | 320415 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Mains over-frequency 2 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20414 |  | 320415 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Busbar over-frequency 2 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20414 |  | 320415 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Busbar B over-frequency 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20415 |  | 320416 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Mains over-frequency 3 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20415 |  | 320416 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Busbar over-frequency 3 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20415 |  | 320416 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Busbar B over-frequency 3 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20416 |  | 320417 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Mains under-frequency 1 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20416 |  | 320417 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Busbar under-frequency 1 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20416 |  | 320417 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Busbar B under-frequency 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20417 |  | 320418 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Mains under-frequency 2 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20417 |  | 320418 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Busbar under-frequency 2 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20417 |  | 320418 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Busbar B under-frequency 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20418 |  | 320419 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Mains under-frequency 3 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20418 |  | 320419 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Busbar under-frequency 3 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20418 |  | 320419 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Busbar B under-frequency 3 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20419 |  | 320420 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Mains under-frequency 4 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20419 |  | 320420 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Busbar under-frequency 4 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20419 |  | 320420 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Busbar B under-frequency 4 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20420 |  | 320421 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Busbar negative sequence voltage | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20420 |  | 320421 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Busbar negative sequence voltage | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20420 |  | 320421 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Busbar B negative sequence voltage | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20421 |  | 320422 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Busbar zero sequence voltage | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20421 |  | 320422 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Busbar zero sequence voltage | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20421 |  | 320422 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Busbar B zero sequence voltage | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20422 |  | 320423 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Busbar positive sequence under-voltage | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20422 |  | 320423 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Busbar positive sequence under-voltage | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20422 |  | 320423 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Busbar B positive sequence under-voltage | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20467 |  | 320468 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20468 |  | 320469 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20469 |  | 320470 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 3 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20470 |  | 320471 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 4 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20471 |  | 320472 | External MB open failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20472 |  | 320473 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20473 |  | 320474 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20474 |  | 320475 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20475 |  | 320476 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20476 |  | 320477 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20477 |  | 320478 | Parameters - Breakers - Close before excitation - CBE failure - Information - Close before excitation failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20478 |  | 320479 | Load too high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20479 |  | 320480 | ID to run configuration failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20481 |  | 320482 | Parameters - System - Monitoring - Missing any genset controller - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20482 |  | 320483 | Parameters - System - Monitoring - Missing any mains controller - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20483 |  | 320484 | Parameters - System - Monitoring - Missing any bus tie controller - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20484 |  | 320485 | Can ID not available | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20485 |  | 320486 | Duplicated CAN IDs | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20486 |  | 320487 | Parameters - Local power management - Alarms - Busbar blocked - Information - Busbar blocked due to position failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Operating value | 20487 |  | 320488 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Busbar A blocked due to position failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20488 |  | 320489 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Busbar B blocked due to position failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20489 |  | 320490 | Parameters - System - Monitoring - BTB 33 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20490 |  | 320491 | Parameters - System - Monitoring - BTB 34 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20491 |  | 320492 | Parameters - System - Monitoring - BTB 35 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20492 |  | 320493 | Parameters - System - Monitoring - BTB 36 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20493 |  | 320494 | Parameters - System - Monitoring - BTB 37 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20494 |  | 320495 | Parameters - System - Monitoring - BTB 38 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20495 |  | 320496 | Parameters - System - Monitoring - BTB 39 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20496 |  | 320497 | Parameters - System - Monitoring - BTB 40 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20497 |  | 320498 | Primary CAN missing ID 1 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20498 |  | 320499 | Primary CAN missing ID 2 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20499 |  | 320500 | Primary CAN missing ID 3 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20500 |  | 320501 | Primary CAN missing ID 4 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20501 |  | 320502 | Primary CAN missing ID 5 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20502 |  | 320503 | Primary CAN missing ID 6 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20503 |  | 320504 | Primary CAN missing ID 7 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20504 |  | 320505 | Primary CAN missing ID 8 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20505 |  | 320506 | Primary CAN missing ID 9 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20506 |  | 320507 | Primary CAN missing ID 10 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20507 |  | 320508 | Primary CAN missing ID 11 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20508 |  | 320509 | Primary CAN missing ID 12 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20509 |  | 320510 | Primary CAN missing ID 13 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20510 |  | 320511 | Primary CAN missing ID 14 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20511 |  | 320512 | Primary CAN missing ID 15 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20512 |  | 320513 | Primary CAN missing ID 16 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20513 |  | 320514 | Primary CAN missing ID 17 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20514 |  | 320515 | Primary CAN missing ID 18 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20515 |  | 320516 | Primary CAN missing ID 19 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20516 |  | 320517 | Primary CAN missing ID 20 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20517 |  | 320518 | Primary CAN missing ID 21 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20518 |  | 320519 | Primary CAN missing ID 22 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20519 |  | 320520 | Primary CAN missing ID 23 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20520 |  | 320521 | Primary CAN missing ID 24 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20521 |  | 320522 | Primary CAN missing ID 25 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20522 |  | 320523 | Primary CAN missing ID 26 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20523 |  | 320524 | Primary CAN missing ID 27 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20524 |  | 320525 | Primary CAN missing ID 28 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20525 |  | 320526 | Primary CAN missing ID 29 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20526 |  | 320527 | Primary CAN missing ID 30 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20527 |  | 320528 | Primary CAN missing ID 31 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20528 |  | 320529 | Primary CAN missing ID 32 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20529 |  | 320530 | Primary CAN missing ID 33 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20530 |  | 320531 | Primary CAN missing ID 34 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20531 |  | 320532 | Primary CAN missing ID 35 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20532 |  | 320533 | Primary CAN missing ID 36 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20533 |  | 320534 | Primary CAN missing ID 37 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20534 |  | 320535 | Primary CAN missing ID 38 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20535 |  | 320536 | Primary CAN missing ID 39 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20536 |  | 320537 | Primary CAN missing ID 40 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20537 |  | 320538 | Secondary CAN missing ID 1 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20538 |  | 320539 | Secondary CAN missing ID 2 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20539 |  | 320540 | Secondary CAN missing ID 3 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20540 |  | 320541 | Secondary CAN missing ID 4 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20541 |  | 320542 | Secondary CAN missing ID 5 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20542 |  | 320543 | Secondary CAN missing ID 6 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20543 |  | 320544 | Secondary CAN missing ID 7 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20544 |  | 320545 | Secondary CAN missing ID 8 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20545 |  | 320546 | Secondary CAN missing ID 9 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20546 |  | 320547 | Secondary CAN missing ID 10 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20547 |  | 320548 | Secondary CAN missing ID 11 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20548 |  | 320549 | Secondary CAN missing ID 12 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20549 |  | 320550 | Secondary CAN missing ID 13 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20550 |  | 320551 | Secondary CAN missing ID 14 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20551 |  | 320552 | Secondary CAN missing ID 15 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20552 |  | 320553 | Secondary CAN missing ID 16 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20553 |  | 320554 | Secondary CAN missing ID 17 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20554 |  | 320555 | Secondary CAN missing ID 18 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20555 |  | 320556 | Secondary CAN missing ID 19 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20556 |  | 320557 | Secondary CAN missing ID 20 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20557 |  | 320558 | Secondary CAN missing ID 21 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20558 |  | 320559 | Secondary CAN missing ID 22 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20559 |  | 320560 | Secondary CAN missing ID 23 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20560 |  | 320561 | Secondary CAN missing ID 24 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20561 |  | 320562 | Secondary CAN missing ID 25 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20562 |  | 320563 | Secondary CAN missing ID 26 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20563 |  | 320564 | Secondary CAN missing ID 27 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20564 |  | 320565 | Secondary CAN missing ID 28 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20565 |  | 320566 | Secondary CAN missing ID 29 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20566 |  | 320567 | Secondary CAN missing ID 30 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20567 |  | 320568 | Secondary CAN missing ID 31 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20568 |  | 320569 | Secondary CAN missing ID 32 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20569 |  | 320570 | Secondary CAN missing ID 33 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20570 |  | 320571 | Secondary CAN missing ID 34 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20571 |  | 320572 | Secondary CAN missing ID 35 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20572 |  | 320573 | Secondary CAN missing ID 36 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20573 |  | 320574 | Secondary CAN missing ID 37 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20574 |  | 320575 | Secondary CAN missing ID 38 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20575 |  | 320576 | Secondary CAN missing ID 39 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20576 |  | 320577 | Secondary CAN missing ID 40 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20577 |  | 320578 | Priority error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20578 |  | 320579 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - NEL 1 over-current | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20579 |  | 320580 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - NEL 1 under-frequency | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20580 |  | 320581 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - NEL 1 overload 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20581 |  | 320582 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - NEL 1 overload 2 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20582 |  | 320583 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - NEL 1 reactive overload | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20583 |  | 320584 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - NEL 2 over-current | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20584 |  | 320585 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - NEL 2 under-frequency | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20585 |  | 320586 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - NEL 2 overload 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20586 |  | 320587 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - NEL 2 overload 2 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20587 |  | 320588 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - NEL 2 reactive overload | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20588 |  | 320589 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - NEL 3 over-current | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20589 |  | 320590 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - NEL 3 under-frequency | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20590 |  | 320591 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - NEL 3 overload 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20591 |  | 320592 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - NEL 3 overload 2 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20592 |  | 320593 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - NEL 3 reactive overload | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20593 |  | 320594 | Parameters - System - Monitoring - Single-line hazard - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20594 |  | 320595 | ID not present | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20595 |  | 320596 | Unsupported application | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20596 |  | 320597 | Application internal CAN protocol conflict | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20597 |  | 320598 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Section P> | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20598 |  | 320599 | Dry mode: Voltage level unexpected | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20599 |  | 320600 | Invalid DAVR configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20600 |  | 320601 | Parameters - Communication - DEIF network - DEIF network fork detected - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20602 |  | 320603 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20604 |  | 320605 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | ° | X |  | X | X | X
Alarm status: Operating value | 20604 |  | 320605 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | ° |  | X
Alarm status: Operating value | 20604 |  | 320605 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | ° | [5 empty] | X | X
Alarm status: Operating value | 20605 |  | 320606 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | ° |  |  |  | X
Alarm status: Operating value | 20605 |  | 320606 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | ° | [6 empty] | X
Alarm status: Operating value | 20607 |  | 320608 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
Alarm status: Operating value | 20608 |  | 320609 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
Alarm status: Operating value | 20609 |  | 320610 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
Alarm status: Operating value | 20610 |  | 320611 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
Alarm status: Operating value | 20611 |  | 320612 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20612 |  | 320613 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20613 |  | 320614 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20614 |  | 320615 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20615 |  | 320616 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20616 |  | 320617 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20617 |  | 320618 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20618 |  | 320619 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20619 |  | 320620 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20620 |  | 320621 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20621 |  | 320622 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20622 |  | 320623 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20623 |  | 320624 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20624 |  | 320625 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20625 |  | 320626 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20626 |  | 320627 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20627 |  | 320628 | Live voltage detected | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20628 |  | 320629 | Internal issue detected. A restart is required soon! | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Alarm status: Operating value | 20629 |  | 320630 | Parameters - System - Monitoring - Missing controllers - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20630 |  | 320631 | Card issue detected | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20631 |  | 320632 | Card configuration failed | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20632 |  | 320633 | Unknown traffic on DEIF network | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20633 |  | 320634 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20634 |  | 320635 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20635 |  | 320636 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20636 |  | 320637 | Local I/O service error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20637 |  | 320638 | App logging failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20638 |  | 320639 | Event logging failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20639 |  | 320640 | Licence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20640 |  | 320641 | Brightness is dimmed according to temperature | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20641 |  | 320642 | Parameters - Grid code - Mains sync inhibit - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Operating value | 20642 |  | 320643 | Parameters - Grid code - Capability curve - Protections - Import protection - Information - Power import capability curve protection | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Operating value | 20643 |  | 320644 | Parameters - Grid code - Capability curve - Protections - Export protection - Information - Power export capability curve protection | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Operating value | 20644 |  | 320645 | Hardware is not compatible based on module versions | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20645 |  | 320646 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 1 - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Operating value | 20646 |  | 320647 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 2 - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Operating value | 20647 |  | 320648 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 3 - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Operating value | 20680 |  | 320681 | Configuration not supported by licence | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21500 |  | 321501 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21501 |  | 321502 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21502 |  | 321503 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21503 |  | 321504 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21504 |  | 321505 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21505 |  | 321506 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21506 |  | 321507 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21507 |  | 321508 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21508 |  | 321509 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21509 |  | 321510 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21510 |  | 321511 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21511 |  | 321512 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21512 |  | 321513 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21513 |  | 321514 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21514 |  | 321515 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21515 |  | 321516 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21516 |  | 321517 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21517 |  | 321518 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21518 |  | 321519 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21519 |  | 321520 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21520 |  | 321521 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21521 |  | 321522 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21522 |  | 321523 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21523 |  | 321524 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21524 |  | 321525 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21525 |  | 321526 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21526 |  | 321527 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21527 |  | 321528 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21528 |  | 321529 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21529 |  | 321530 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21530 |  | 321531 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21531 |  | 321532 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21532 |  | 321533 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21533 |  | 321534 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21534 |  | 321535 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21535 |  | 321536 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21536 |  | 321537 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21537 |  | 321538 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21538 |  | 321539 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21539 |  | 321540 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21540 |  | 321541 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21541 |  | 321542 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21542 |  | 321543 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21543 |  | 321544 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21544 |  | 321545 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21545 |  | 321546 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21546 |  | 321547 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21547 |  | 321548 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21548 |  | 321549 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21549 |  | 321550 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21600 |  | 321601 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21601 |  | 321602 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21602 |  | 321603 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21603 |  | 321604 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21604 |  | 321605 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21605 |  | 321606 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21606 |  | 321607 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21607 |  | 321608 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21608 |  | 321609 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21609 |  | 321610 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21610 |  | 321611 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21611 |  | 321612 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21612 |  | 321613 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21613 |  | 321614 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21614 |  | 321615 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21615 |  | 321616 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21616 |  | 321617 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21617 |  | 321618 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21618 |  | 321619 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21619 |  | 321620 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21620 |  | 321621 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21621 |  | 321622 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21622 |  | 321623 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21623 |  | 321624 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21624 |  | 321625 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21625 |  | 321626 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21626 |  | 321627 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21627 |  | 321628 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21628 |  | 321629 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21629 |  | 321630 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21630 |  | 321631 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21631 |  | 321632 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21632 |  | 321633 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21633 |  | 321634 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21634 |  | 321635 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21635 |  | 321636 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21636 |  | 321637 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21637 |  | 321638 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21638 |  | 321639 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21639 |  | 321640 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21640 |  | 321641 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21641 |  | 321642 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21642 |  | 321643 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21643 |  | 321644 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21644 |  | 321645 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21645 |  | 321646 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21646 |  | 321647 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21647 |  | 321648 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21648 |  | 321649 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21649 |  | 321650 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21650 |  | 321651 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21651 |  | 321652 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21652 |  | 321653 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21653 |  | 321654 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21654 |  | 321655 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21655 |  | 321656 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21656 |  | 321657 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21657 |  | 321658 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21658 |  | 321659 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21659 |  | 321660 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21660 |  | 321661 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21661 |  | 321662 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21662 |  | 321663 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21663 |  | 321664 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21664 |  | 321665 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21665 |  | 321666 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21666 |  | 321667 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21667 |  | 321668 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21668 |  | 321669 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21669 |  | 321670 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21670 |  | 321671 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21671 |  | 321672 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21672 |  | 321673 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21673 |  | 321674 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21674 |  | 321675 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21675 |  | 321676 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21676 |  | 321677 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21677 |  | 321678 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21678 |  | 321679 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21679 |  | 321680 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21680 |  | 321681 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21681 |  | 321682 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21682 |  | 321683 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21683 |  | 321684 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21684 |  | 321685 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21685 |  | 321686 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21686 |  | 321687 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21687 |  | 321688 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21688 |  | 321689 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21689 |  | 321690 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21690 |  | 321691 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21691 |  | 321692 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21692 |  | 321693 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21693 |  | 321694 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21694 |  | 321695 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21695 |  | 321696 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21696 |  | 321697 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21697 |  | 321698 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21698 |  | 321699 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21699 |  | 321700 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21700 |  | 321701 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21701 |  | 321702 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21702 |  | 321703 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21703 |  | 321704 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21704 |  | 321705 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21705 |  | 321706 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21706 |  | 321707 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21707 |  | 321708 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21708 |  | 321709 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21709 |  | 321710 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21710 |  | 321711 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21711 |  | 321712 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21712 |  | 321713 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21713 |  | 321714 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21714 |  | 321715 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21715 |  | 321716 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21716 |  | 321717 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21717 |  | 321718 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21718 |  | 321719 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21719 |  | 321720 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21720 |  | 321721 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21721 |  | 321722 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21722 |  | 321723 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21723 |  | 321724 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21724 |  | 321725 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21725 |  | 321726 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21726 |  | 321727 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21727 |  | 321728 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21728 |  | 321729 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21729 |  | 321730 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21730 |  | 321731 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21731 |  | 321732 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21732 |  | 321733 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21733 |  | 321734 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21734 |  | 321735 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21735 |  | 321736 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21736 |  | 321737 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21737 |  | 321738 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21738 |  | 321739 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21739 |  | 321740 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21740 |  | 321741 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21741 |  | 321742 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21742 |  | 321743 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21743 |  | 321744 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21744 |  | 321745 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21745 |  | 321746 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21746 |  | 321747 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21747 |  | 321748 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21748 |  | 321749 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21749 |  | 321750 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21750 |  | 321751 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21751 |  | 321752 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21752 |  | 321753 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21753 |  | 321754 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21754 |  | 321755 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21755 |  | 321756 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21756 |  | 321757 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21757 |  | 321758 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21758 |  | 321759 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21759 |  | 321760 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21760 |  | 321761 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21761 |  | 321762 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21762 |  | 321763 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21763 |  | 321764 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21764 |  | 321765 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21765 |  | 321766 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21766 |  | 321767 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21767 |  | 321768 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21768 |  | 321769 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21769 |  | 321770 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21770 |  | 321771 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21771 |  | 321772 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21772 |  | 321773 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21773 |  | 321774 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21774 |  | 321775 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21775 |  | 321776 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21776 |  | 321777 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21777 |  | 321778 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21778 |  | 321779 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21779 |  | 321780 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21780 |  | 321781 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21781 |  | 321782 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21782 |  | 321783 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21783 |  | 321784 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21784 |  | 321785 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21785 |  | 321786 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21786 |  | 321787 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21787 |  | 321788 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21788 |  | 321789 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21789 |  | 321790 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21790 |  | 321791 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21791 |  | 321792 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21792 |  | 321793 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21793 |  | 321794 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21794 |  | 321795 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21795 |  | 321796 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21796 |  | 321797 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21797 |  | 321798 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21798 |  | 321799 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21799 |  | 321800 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22003 |  | 322004 | Parameters - Engine - Stop sequence - Stop failure - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22005 |  | 322006 | Parameters - Engine - Start sequence - Crank failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22006 |  | 322007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22007 |  | 322008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22008 |  | 322009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22009 |  | 322010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22010 |  | 322011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22013 |  | 322014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22014 |  | 322015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22015 |  | 322016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22016 |  | 322017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22017 |  | 322018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22018 |  | 322019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22019 |  | 322020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22020 |  | 322021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22021 |  | 322022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22022 |  | 322023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22027 |  | 322028 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22041 |  | 322042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22041 |  | 322042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22041 |  | 322042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22042 |  | 322043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22042 |  | 322043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22042 |  | 322043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22043 |  | 322044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22043 |  | 322044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22043 |  | 322044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22044 |  | 322045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22044 |  | 322045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22044 |  | 322045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22045 |  | 322046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22045 |  | 322046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22045 |  | 322046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22046 |  | 322047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22046 |  | 322047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22046 |  | 322047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22049 |  | 322050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer elapsed time | 22049 |  | 322050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer elapsed time | 22050 |  | 322051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer elapsed time | 22050 |  | 322051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer elapsed time | 22051 |  | 322052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer elapsed time | 22051 |  | 322052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer elapsed time | 22052 |  | 322053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer elapsed time | 22052 |  | 322053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer elapsed time | 22053 |  | 322054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer elapsed time | 22053 |  | 322054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer elapsed time | 22054 |  | 322055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer elapsed time | 22054 |  | 322055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer elapsed time | 22060 |  | 322061 | Parameters - Mains - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22060 |  | 322061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22060 |  | 322061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22061 |  | 322062 | Parameters - Generator - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22061 |  | 322062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22061 |  | 322062 | Parameters - Mains - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22062 |  | 322063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22103 |  | 322104 | Parameters - Mains - Additional protections - ROCOF - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22103 |  | 322104 | Parameters - Busbar - Additional protections - ROCOF - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22103 |  | 322104 | Parameters - Busbar B - Additional protections - ROCOF - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22108 |  | 322109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22108 |  | 322109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22108 |  | 322109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22109 |  | 322110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22109 |  | 322110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22109 |  | 322110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22110 |  | 322111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22110 |  | 322111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22110 |  | 322111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22111 |  | 322112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22111 |  | 322112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22111 |  | 322112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22116 |  | 322117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22117 |  | 322118 | Parameters - Generator - Current protections - High set differential current - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22119 |  | 322120 | Parameters - Local - Mode - Not under remote control - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22128 |  | 322129 | Parameters - Custom alarms - Custom alarm 0 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22129 |  | 322130 | Parameters - Custom alarms - Custom alarm 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22130 |  | 322131 | Parameters - Custom alarms - Custom alarm 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22131 |  | 322132 | Parameters - Custom alarms - Custom alarm 3 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22132 |  | 322133 | Parameters - Custom alarms - Custom alarm 4 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22133 |  | 322134 | Parameters - Custom alarms - Custom alarm 5 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22134 |  | 322135 | Parameters - Custom alarms - Custom alarm 6 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22135 |  | 322136 | Parameters - Custom alarms - Custom alarm 7 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22136 |  | 322137 | Parameters - Custom alarms - Custom alarm 8 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22137 |  | 322138 | Parameters - Custom alarms - Custom alarm 9 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22138 |  | 322139 | Parameters - Custom alarms - Custom alarm 10 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22139 |  | 322140 | Parameters - Custom alarms - Custom alarm 11 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22140 |  | 322141 | Parameters - Custom alarms - Custom alarm 12 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22141 |  | 322142 | Parameters - Custom alarms - Custom alarm 13 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22142 |  | 322143 | Parameters - Custom alarms - Custom alarm 14 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22143 |  | 322144 | Parameters - Custom alarms - Custom alarm 15 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22144 |  | 322145 | Parameters - Custom alarms - Custom alarm 16 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22145 |  | 322146 | Parameters - Custom alarms - Custom alarm 17 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22146 |  | 322147 | Parameters - Custom alarms - Custom alarm 18 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22147 |  | 322148 | Parameters - Custom alarms - Custom alarm 19 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22148 |  | 322149 | Parameters - Custom alarms - Custom alarm 20 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22149 |  | 322150 | Parameters - Custom alarms - Custom alarm 21 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22150 |  | 322151 | Parameters - Custom alarms - Custom alarm 22 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22151 |  | 322152 | Parameters - Custom alarms - Custom alarm 23 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22152 |  | 322153 | Parameters - Custom alarms - Custom alarm 24 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22153 |  | 322154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22154 |  | 322155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22163 |  | 322164 | Required hardware card(s) not found - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22164 |  | 322165 | Software mismatch on hardware module(s) - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22165 |  | 322166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  | X
Alarm status: Delay timer elapsed time | 22165 |  | 322166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X
Alarm status: Delay timer elapsed time | 22165 |  | 322166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22166 |  | 322167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X |  | X
Alarm status: Delay timer elapsed time | 22166 |  | 322167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22166 |  | 322167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
Alarm status: Delay timer elapsed time | 22167 |  | 322168 | Parameters - Mains - AC setup - L1 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  | X
Alarm status: Delay timer elapsed time | 22167 |  | 322168 | Parameters - Busbar - AC setup - L1 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X
Alarm status: Delay timer elapsed time | 22167 |  | 322168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22168 |  | 322169 | Parameters - Mains - AC setup - L2 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  | X
Alarm status: Delay timer elapsed time | 22168 |  | 322169 | Parameters - Busbar - AC setup - L2 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X
Alarm status: Delay timer elapsed time | 22168 |  | 322169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22169 |  | 322170 | Parameters - Mains - AC setup - L3 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  | X
Alarm status: Delay timer elapsed time | 22169 |  | 322170 | Parameters - Busbar - AC setup - L3 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X
Alarm status: Delay timer elapsed time | 22169 |  | 322170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22170 |  | 322171 | Parameters - Generator - AC setup - L1 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X |  | X
Alarm status: Delay timer elapsed time | 22170 |  | 322171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22170 |  | 322171 | Parameters - Mains - AC setup - L1 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
Alarm status: Delay timer elapsed time | 22171 |  | 322172 | Parameters - Generator - AC setup - L2 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X |  | X
Alarm status: Delay timer elapsed time | 22171 |  | 322172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22171 |  | 322172 | Parameters - Mains - AC setup - L2 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
Alarm status: Delay timer elapsed time | 22172 |  | 322173 | Parameters - Generator - AC setup - L3 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X |  | X
Alarm status: Delay timer elapsed time | 22172 |  | 322173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22172 |  | 322173 | Parameters - Mains - AC setup - L3 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
Alarm status: Delay timer elapsed time | 22179 |  | 322180 | Parameters - Engine - Emergency stop - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22179 |  | 322180 | Parameters - Busbar A - Emergency stop - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22179 |  | 322180 | Parameters - Mains - Emergency stop - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22180 |  | 322181 | Clock battery failure - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22181 |  | 322182 | Controller temperature too high - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22182 |  | 322183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22183 |  | 322184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22184 |  | 322185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22185 |  | 322186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22186 |  | 322187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22187 |  | 322188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22188 |  | 322189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22189 |  | 322190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22190 |  | 322191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22191 |  | 322192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22192 |  | 322193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22193 |  | 322194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22194 |  | 322195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22195 |  | 322196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22196 |  | 322197 | EIM3.1 4 supply voltage high - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22197 |  | 322198 | EIM3.1 4 supply voltage low or missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22198 |  | 322199 | EIM3.1 5 supply voltage high - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22199 |  | 322200 | EIM3.1 5 supply voltage low or missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22200 |  | 322201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22201 |  | 322202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22202 |  | 322203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22203 |  | 322204 | EIM3.1 4 relay 4 wire break - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22204 |  | 322205 | EIM3.1 5 relay 4 wire break - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22205 |  | 322206 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22206 |  | 322207 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22207 |  | 322208 | AC protections not running (differential current) - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22208 |  | 322209 | AC data is missing (differential current) - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22209 |  | 322210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22210 |  | 322211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22211 |  | 322212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22212 |  | 322213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22213 |  | 322214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22214 |  | 322215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22215 |  | 322216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22216 |  | 322217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22217 |  | 322218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22218 |  | 322219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22219 |  | 322220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22220 |  | 322221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22221 |  | 322222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22222 |  | 322223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22223 |  | 322224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22224 |  | 322225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22225 |  | 322226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22226 |  | 322227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22237 |  | 322238 | Blackout detection mismatch - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22240 |  | 322241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22241 |  | 322242 | Parameters - Communication - NTP - NTP server 1 not responding - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22242 |  | 322243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22243 |  | 322244 | Parameters - Communication - NTP - NTP server 2 not responding - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22244 |  | 322245 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22245 |  | 322246 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22297 |  | 322298 | Different single-line configurations - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22299 |  | 322300 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22301 |  | 322302 | Parameters - CODESYS - Monitoring - Application not OK - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22306 |  | 322307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22316 |  | 322317 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22364 |  | 322365 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22365 |  | 322366 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22365 |  | 322366 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22365 |  | 322366 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22366 |  | 322367 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22366 |  | 322367 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22366 |  | 322367 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22367 |  | 322368 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22367 |  | 322368 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22367 |  | 322368 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22368 |  | 322369 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22368 |  | 322369 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22368 |  | 322369 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22369 |  | 322370 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22369 |  | 322370 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22369 |  | 322370 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22370 |  | 322371 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22370 |  | 322371 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22370 |  | 322371 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22371 |  | 322372 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22371 |  | 322372 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22371 |  | 322372 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22372 |  | 322373 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22372 |  | 322373 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22372 |  | 322373 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22373 |  | 322374 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22373 |  | 322374 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22373 |  | 322374 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22374 |  | 322375 | Parameters - Generator - Current protections - Over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22374 |  | 322375 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22374 |  | 322375 | Parameters - Mains - Current protections - Over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22375 |  | 322376 | Parameters - Generator - Current protections - Over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22375 |  | 322376 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22375 |  | 322376 | Parameters - Mains - Current protections - Over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22376 |  | 322377 | Parameters - Generator - Current protections - Over-current 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22376 |  | 322377 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22376 |  | 322377 | Parameters - Mains - Current protections - Over-current 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22377 |  | 322378 | Parameters - Generator - Current protections - Over-current 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22377 |  | 322378 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22377 |  | 322378 | Parameters - Mains - Current protections - Over-current 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22378 |  | 322379 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22378 |  | 322379 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22378 |  | 322379 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22379 |  | 322380 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22379 |  | 322380 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22379 |  | 322380 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22380 |  | 322381 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22380 |  | 322381 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22380 |  | 322381 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22381 |  | 322382 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22381 |  | 322382 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22381 |  | 322382 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22382 |  | 322383 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22382 |  | 322383 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22382 |  | 322383 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22383 |  | 322384 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22383 |  | 322384 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22383 |  | 322384 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22384 |  | 322385 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22385 |  | 322386 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22386 |  | 322387 | Parameters - Generator - Current protections - Negative sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22386 |  | 322387 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22386 |  | 322387 | Parameters - Mains - Current protections - Negative sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22387 |  | 322388 | Parameters - Generator - Current protections - Zero sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22387 |  | 322388 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22387 |  | 322388 | Parameters - Mains - Current protections - Zero sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22388 |  | 322389 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22388 |  | 322389 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22388 |  | 322389 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22389 |  | 322390 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22389 |  | 322390 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22389 |  | 322390 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22390 |  | 322391 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22390 |  | 322391 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22390 |  | 322391 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22391 |  | 322392 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22391 |  | 322392 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22391 |  | 322392 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22392 |  | 322393 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22392 |  | 322393 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22392 |  | 322393 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22393 |  | 322394 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22393 |  | 322394 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22393 |  | 322394 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22394 |  | 322395 | Parameters - Generator - Power protections - Overload 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22394 |  | 322395 | Parameters - Busbar A - Power protections - Power export 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22394 |  | 322395 | Parameters - Mains - Power protections - Overload 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22395 |  | 322396 | Parameters - Generator - Power protections - Overload 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22395 |  | 322396 | Parameters - Busbar A - Power protections - Power export 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22395 |  | 322396 | Parameters - Mains - Power protections - Overload 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22396 |  | 322397 | Parameters - Generator - Power protections - Overload 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22396 |  | 322397 | Parameters - Busbar A - Power protections - Power export 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22396 |  | 322397 | Parameters - Mains - Power protections - Overload 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22397 |  | 322398 | Parameters - Generator - Power protections - Overload 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22397 |  | 322398 | Parameters - Busbar A - Power protections - Power export 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22397 |  | 322398 | Parameters - Mains - Power protections - Overload 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22398 |  | 322399 | Parameters - Generator - Power protections - Overload 5 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22398 |  | 322399 | Parameters - Busbar A - Power protections - Power export 5 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22398 |  | 322399 | Parameters - Mains - Power protections - Overload 5 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22399 |  | 322400 | Parameters - Generator - Power protections - Reverse power 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22399 |  | 322400 | Parameters - Busbar A - Power protections - Power import 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22399 |  | 322400 | Parameters - Mains - Power protections - Reverse power 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22400 |  | 322401 | Parameters - Generator - Power protections - Reverse power 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22400 |  | 322401 | Parameters - Busbar A - Power protections - Power import 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22400 |  | 322401 | Parameters - Mains - Power protections - Reverse power 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22401 |  | 322402 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22401 |  | 322402 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22401 |  | 322402 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22402 |  | 322403 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22402 |  | 322403 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22402 |  | 322403 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22403 |  | 322404 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22403 |  | 322404 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22403 |  | 322404 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22404 |  | 322405 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22404 |  | 322405 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22404 |  | 322405 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22405 |  | 322406 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22405 |  | 322406 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22405 |  | 322406 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22406 |  | 322407 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22406 |  | 322407 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22406 |  | 322407 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22407 |  | 322408 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22407 |  | 322408 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22407 |  | 322408 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22408 |  | 322409 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22408 |  | 322409 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22408 |  | 322409 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22409 |  | 322410 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22409 |  | 322410 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22409 |  | 322410 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22410 |  | 322411 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22410 |  | 322411 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22410 |  | 322411 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22411 |  | 322412 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22411 |  | 322412 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22411 |  | 322412 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22412 |  | 322413 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22412 |  | 322413 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22412 |  | 322413 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22413 |  | 322414 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22413 |  | 322414 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22413 |  | 322414 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22414 |  | 322415 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22414 |  | 322415 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22414 |  | 322415 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22415 |  | 322416 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22415 |  | 322416 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22415 |  | 322416 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22416 |  | 322417 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22416 |  | 322417 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22416 |  | 322417 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22417 |  | 322418 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22417 |  | 322418 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22417 |  | 322418 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22418 |  | 322419 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22418 |  | 322419 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22418 |  | 322419 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22419 |  | 322420 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22419 |  | 322420 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22419 |  | 322420 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22420 |  | 322421 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22420 |  | 322421 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22420 |  | 322421 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22421 |  | 322422 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22421 |  | 322422 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22421 |  | 322422 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22422 |  | 322423 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22422 |  | 322423 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22422 |  | 322423 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22471 |  | 322472 | External MB open failure - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22472 |  | 322473 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22473 |  | 322474 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22474 |  | 322475 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22475 |  | 322476 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22476 |  | 322477 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22477 |  | 322478 | Parameters - Breakers - Close before excitation - CBE failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22478 |  | 322479 | Load too high - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22479 |  | 322480 | ID to run configuration failure - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22484 |  | 322485 | Can ID not available - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22485 |  | 322486 | Duplicated CAN IDs - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22486 |  | 322487 | Parameters - Local power management - Alarms - Busbar blocked - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22487 |  | 322488 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22488 |  | 322489 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22489 |  | 322490 | Parameters - System - Monitoring - BTB 33 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22490 |  | 322491 | Parameters - System - Monitoring - BTB 34 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22491 |  | 322492 | Parameters - System - Monitoring - BTB 35 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22492 |  | 322493 | Parameters - System - Monitoring - BTB 36 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22493 |  | 322494 | Parameters - System - Monitoring - BTB 37 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22494 |  | 322495 | Parameters - System - Monitoring - BTB 38 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22495 |  | 322496 | Parameters - System - Monitoring - BTB 39 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22496 |  | 322497 | Parameters - System - Monitoring - BTB 40 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22578 |  | 322579 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22579 |  | 322580 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22580 |  | 322581 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22581 |  | 322582 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22582 |  | 322583 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22583 |  | 322584 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22584 |  | 322585 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22585 |  | 322586 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22586 |  | 322587 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22587 |  | 322588 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22588 |  | 322589 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22589 |  | 322590 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22590 |  | 322591 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22591 |  | 322592 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22592 |  | 322593 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22593 |  | 322594 | Parameters - System - Monitoring - Single-line hazard - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22594 |  | 322595 | ID not present - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22595 |  | 322596 | Unsupported application - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22596 |  | 322597 | Application internal CAN protocol conflict - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22597 |  | 322598 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22598 |  | 322599 | Dry mode: Voltage level unexpected - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22604 |  | 322605 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22604 |  | 322605 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22604 |  | 322605 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22605 |  | 322606 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer elapsed time | 22605 |  | 322606 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer elapsed time | 22607 |  | 322608 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22608 |  | 322609 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22609 |  | 322610 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22610 |  | 322611 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22611 |  | 322612 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22612 |  | 322613 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22613 |  | 322614 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22614 |  | 322615 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22615 |  | 322616 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22616 |  | 322617 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22617 |  | 322618 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22618 |  | 322619 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22619 |  | 322620 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22620 |  | 322621 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22621 |  | 322622 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22622 |  | 322623 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22623 |  | 322624 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22624 |  | 322625 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22625 |  | 322626 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22626 |  | 322627 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22627 |  | 322628 | Live voltage detected - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22631 |  | 322632 | Card configuration failed - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22633 |  | 322634 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22634 |  | 322635 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22635 |  | 322636 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22639 |  | 322640 | Licence error - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22642 |  | 322643 | Parameters - Grid code - Capability curve - Protections - Import protection - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22643 |  | 322644 | Parameters - Grid code - Capability curve - Protections - Export protection - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22644 |  | 322645 | Hardware is not compatible based on module versions - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23500 |  | 323501 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23501 |  | 323502 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23502 |  | 323503 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23503 |  | 323504 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23504 |  | 323505 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23505 |  | 323506 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23506 |  | 323507 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23507 |  | 323508 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23508 |  | 323509 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23509 |  | 323510 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23510 |  | 323511 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23511 |  | 323512 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23512 |  | 323513 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23513 |  | 323514 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23514 |  | 323515 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23515 |  | 323516 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23516 |  | 323517 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23517 |  | 323518 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23518 |  | 323519 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23519 |  | 323520 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23520 |  | 323521 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23521 |  | 323522 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23522 |  | 323523 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23523 |  | 323524 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23524 |  | 323525 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23525 |  | 323526 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23526 |  | 323527 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23527 |  | 323528 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23528 |  | 323529 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23529 |  | 323530 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23530 |  | 323531 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23531 |  | 323532 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23532 |  | 323533 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23533 |  | 323534 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23534 |  | 323535 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23535 |  | 323536 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23536 |  | 323537 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23537 |  | 323538 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23538 |  | 323539 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23539 |  | 323540 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23540 |  | 323541 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23541 |  | 323542 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23542 |  | 323543 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23543 |  | 323544 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23544 |  | 323545 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23545 |  | 323546 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23546 |  | 323547 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23547 |  | 323548 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23548 |  | 323549 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23549 |  | 323550 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23600 |  | 323601 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23601 |  | 323602 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23602 |  | 323603 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23603 |  | 323604 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23604 |  | 323605 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23605 |  | 323606 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23606 |  | 323607 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23607 |  | 323608 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23608 |  | 323609 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23609 |  | 323610 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23610 |  | 323611 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23611 |  | 323612 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23612 |  | 323613 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23613 |  | 323614 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23614 |  | 323615 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23615 |  | 323616 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23616 |  | 323617 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23617 |  | 323618 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23618 |  | 323619 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23619 |  | 323620 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23620 |  | 323621 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23621 |  | 323622 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23622 |  | 323623 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23623 |  | 323624 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23624 |  | 323625 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23625 |  | 323626 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23626 |  | 323627 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23627 |  | 323628 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23628 |  | 323629 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23629 |  | 323630 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23630 |  | 323631 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23631 |  | 323632 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23632 |  | 323633 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23633 |  | 323634 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23634 |  | 323635 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23635 |  | 323636 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23636 |  | 323637 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23637 |  | 323638 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23638 |  | 323639 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23639 |  | 323640 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23640 |  | 323641 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23641 |  | 323642 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23642 |  | 323643 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23643 |  | 323644 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23644 |  | 323645 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23645 |  | 323646 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23646 |  | 323647 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23647 |  | 323648 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23648 |  | 323649 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23649 |  | 323650 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23650 |  | 323651 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23651 |  | 323652 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23652 |  | 323653 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23653 |  | 323654 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23654 |  | 323655 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23655 |  | 323656 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23656 |  | 323657 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23657 |  | 323658 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23658 |  | 323659 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23659 |  | 323660 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23660 |  | 323661 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23661 |  | 323662 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23662 |  | 323663 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23663 |  | 323664 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23664 |  | 323665 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23665 |  | 323666 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23666 |  | 323667 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23667 |  | 323668 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23668 |  | 323669 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23669 |  | 323670 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23670 |  | 323671 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23671 |  | 323672 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23672 |  | 323673 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23673 |  | 323674 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23674 |  | 323675 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23675 |  | 323676 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23676 |  | 323677 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23677 |  | 323678 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23678 |  | 323679 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23679 |  | 323680 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23680 |  | 323681 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23681 |  | 323682 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23682 |  | 323683 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23683 |  | 323684 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23684 |  | 323685 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23685 |  | 323686 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23686 |  | 323687 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23687 |  | 323688 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23688 |  | 323689 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23689 |  | 323690 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23690 |  | 323691 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23691 |  | 323692 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23692 |  | 323693 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23693 |  | 323694 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23694 |  | 323695 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23695 |  | 323696 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23696 |  | 323697 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23697 |  | 323698 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23698 |  | 323699 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23699 |  | 323700 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23700 |  | 323701 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23701 |  | 323702 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23702 |  | 323703 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23703 |  | 323704 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23704 |  | 323705 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23705 |  | 323706 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23706 |  | 323707 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23707 |  | 323708 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23708 |  | 323709 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23709 |  | 323710 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23710 |  | 323711 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23711 |  | 323712 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23712 |  | 323713 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23713 |  | 323714 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23714 |  | 323715 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23715 |  | 323716 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23716 |  | 323717 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23717 |  | 323718 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23718 |  | 323719 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23719 |  | 323720 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23720 |  | 323721 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23721 |  | 323722 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23722 |  | 323723 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23723 |  | 323724 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23724 |  | 323725 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23725 |  | 323726 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23726 |  | 323727 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23727 |  | 323728 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23728 |  | 323729 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23729 |  | 323730 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23730 |  | 323731 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23731 |  | 323732 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23732 |  | 323733 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23733 |  | 323734 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23734 |  | 323735 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23735 |  | 323736 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23736 |  | 323737 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23737 |  | 323738 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23738 |  | 323739 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23739 |  | 323740 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23740 |  | 323741 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23741 |  | 323742 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23742 |  | 323743 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23743 |  | 323744 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23744 |  | 323745 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23745 |  | 323746 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23746 |  | 323747 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23747 |  | 323748 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23748 |  | 323749 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23749 |  | 323750 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23750 |  | 323751 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23751 |  | 323752 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23752 |  | 323753 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23753 |  | 323754 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23754 |  | 323755 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23755 |  | 323756 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23756 |  | 323757 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23757 |  | 323758 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23758 |  | 323759 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23759 |  | 323760 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23760 |  | 323761 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23761 |  | 323762 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23762 |  | 323763 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23763 |  | 323764 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23764 |  | 323765 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23765 |  | 323766 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23766 |  | 323767 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23767 |  | 323768 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23768 |  | 323769 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23769 |  | 323770 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23770 |  | 323771 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23771 |  | 323772 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23772 |  | 323773 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23773 |  | 323774 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23774 |  | 323775 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23775 |  | 323776 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23776 |  | 323777 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23777 |  | 323778 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23778 |  | 323779 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23779 |  | 323780 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23780 |  | 323781 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23781 |  | 323782 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23782 |  | 323783 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23783 |  | 323784 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23784 |  | 323785 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23785 |  | 323786 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23786 |  | 323787 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23787 |  | 323788 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23788 |  | 323789 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23789 |  | 323790 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23790 |  | 323791 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23791 |  | 323792 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23792 |  | 323793 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23793 |  | 323794 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23794 |  | 323795 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23795 |  | 323796 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23796 |  | 323797 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23797 |  | 323798 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23798 |  | 323799 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 23799 |  | 323800 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24003 |  | 324004 | Parameters - Engine - Stop sequence - Stop failure - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24005 |  | 324006 | Parameters - Engine - Start sequence - Crank failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24006 |  | 324007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24007 |  | 324008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24008 |  | 324009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24009 |  | 324010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24010 |  | 324011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24013 |  | 324014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24014 |  | 324015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24015 |  | 324016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24016 |  | 324017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24017 |  | 324018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24018 |  | 324019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24019 |  | 324020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24020 |  | 324021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24021 |  | 324022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24022 |  | 324023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24027 |  | 324028 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24041 |  | 324042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24041 |  | 324042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24041 |  | 324042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24042 |  | 324043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24042 |  | 324043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24042 |  | 324043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24043 |  | 324044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24043 |  | 324044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24043 |  | 324044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24044 |  | 324045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24044 |  | 324045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24044 |  | 324045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24045 |  | 324046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24045 |  | 324046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24045 |  | 324046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24046 |  | 324047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24046 |  | 324047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24046 |  | 324047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24049 |  | 324050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24049 |  | 324050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer remaining time | 24050 |  | 324051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24050 |  | 324051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer remaining time | 24051 |  | 324052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24051 |  | 324052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer remaining time | 24052 |  | 324053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24052 |  | 324053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer remaining time | 24053 |  | 324054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24053 |  | 324054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer remaining time | 24054 |  | 324055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24054 |  | 324055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer remaining time | 24060 |  | 324061 | Parameters - Mains - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24060 |  | 324061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24060 |  | 324061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24061 |  | 324062 | Parameters - Generator - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24061 |  | 324062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24061 |  | 324062 | Parameters - Mains - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24062 |  | 324063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24103 |  | 324104 | Parameters - Mains - Additional protections - ROCOF - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24103 |  | 324104 | Parameters - Busbar - Additional protections - ROCOF - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24103 |  | 324104 | Parameters - Busbar B - Additional protections - ROCOF - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24108 |  | 324109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24108 |  | 324109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24108 |  | 324109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24109 |  | 324110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24109 |  | 324110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24109 |  | 324110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24110 |  | 324111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24110 |  | 324111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24110 |  | 324111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24111 |  | 324112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24111 |  | 324112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24111 |  | 324112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24116 |  | 324117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24117 |  | 324118 | Parameters - Generator - Current protections - High set differential current - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24119 |  | 324120 | Parameters - Local - Mode - Not under remote control - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24128 |  | 324129 | Parameters - Custom alarms - Custom alarm 0 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24129 |  | 324130 | Parameters - Custom alarms - Custom alarm 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24130 |  | 324131 | Parameters - Custom alarms - Custom alarm 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24131 |  | 324132 | Parameters - Custom alarms - Custom alarm 3 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24132 |  | 324133 | Parameters - Custom alarms - Custom alarm 4 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24133 |  | 324134 | Parameters - Custom alarms - Custom alarm 5 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24134 |  | 324135 | Parameters - Custom alarms - Custom alarm 6 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24135 |  | 324136 | Parameters - Custom alarms - Custom alarm 7 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24136 |  | 324137 | Parameters - Custom alarms - Custom alarm 8 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24137 |  | 324138 | Parameters - Custom alarms - Custom alarm 9 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24138 |  | 324139 | Parameters - Custom alarms - Custom alarm 10 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24139 |  | 324140 | Parameters - Custom alarms - Custom alarm 11 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24140 |  | 324141 | Parameters - Custom alarms - Custom alarm 12 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24141 |  | 324142 | Parameters - Custom alarms - Custom alarm 13 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24142 |  | 324143 | Parameters - Custom alarms - Custom alarm 14 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24143 |  | 324144 | Parameters - Custom alarms - Custom alarm 15 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24144 |  | 324145 | Parameters - Custom alarms - Custom alarm 16 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24145 |  | 324146 | Parameters - Custom alarms - Custom alarm 17 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24146 |  | 324147 | Parameters - Custom alarms - Custom alarm 18 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24147 |  | 324148 | Parameters - Custom alarms - Custom alarm 19 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24148 |  | 324149 | Parameters - Custom alarms - Custom alarm 20 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24149 |  | 324150 | Parameters - Custom alarms - Custom alarm 21 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24150 |  | 324151 | Parameters - Custom alarms - Custom alarm 22 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24151 |  | 324152 | Parameters - Custom alarms - Custom alarm 23 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24152 |  | 324153 | Parameters - Custom alarms - Custom alarm 24 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24153 |  | 324154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24154 |  | 324155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24163 |  | 324164 | Required hardware card(s) not found - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24164 |  | 324165 | Software mismatch on hardware module(s) - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24165 |  | 324166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  | X
Alarm status: Delay timer remaining time | 24165 |  | 324166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X
Alarm status: Delay timer remaining time | 24165 |  | 324166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24166 |  | 324167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X |  | X
Alarm status: Delay timer remaining time | 24166 |  | 324167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24166 |  | 324167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
Alarm status: Delay timer remaining time | 24167 |  | 324168 | Parameters - Mains - AC setup - L1 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  | X
Alarm status: Delay timer remaining time | 24167 |  | 324168 | Parameters - Busbar - AC setup - L1 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X
Alarm status: Delay timer remaining time | 24167 |  | 324168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24168 |  | 324169 | Parameters - Mains - AC setup - L2 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  | X
Alarm status: Delay timer remaining time | 24168 |  | 324169 | Parameters - Busbar - AC setup - L2 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X
Alarm status: Delay timer remaining time | 24168 |  | 324169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24169 |  | 324170 | Parameters - Mains - AC setup - L3 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  | X
Alarm status: Delay timer remaining time | 24169 |  | 324170 | Parameters - Busbar - AC setup - L3 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X
Alarm status: Delay timer remaining time | 24169 |  | 324170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24170 |  | 324171 | Parameters - Generator - AC setup - L1 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X |  | X
Alarm status: Delay timer remaining time | 24170 |  | 324171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24170 |  | 324171 | Parameters - Mains - AC setup - L1 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
Alarm status: Delay timer remaining time | 24171 |  | 324172 | Parameters - Generator - AC setup - L2 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X |  | X
Alarm status: Delay timer remaining time | 24171 |  | 324172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24171 |  | 324172 | Parameters - Mains - AC setup - L2 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
Alarm status: Delay timer remaining time | 24172 |  | 324173 | Parameters - Generator - AC setup - L3 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X |  | X
Alarm status: Delay timer remaining time | 24172 |  | 324173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24172 |  | 324173 | Parameters - Mains - AC setup - L3 wire break - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
Alarm status: Delay timer remaining time | 24179 |  | 324180 | Parameters - Engine - Emergency stop - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24179 |  | 324180 | Parameters - Busbar A - Emergency stop - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24179 |  | 324180 | Parameters - Mains - Emergency stop - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24180 |  | 324181 | Clock battery failure - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24181 |  | 324182 | Controller temperature too high - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24182 |  | 324183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24183 |  | 324184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24184 |  | 324185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24185 |  | 324186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24186 |  | 324187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24187 |  | 324188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24188 |  | 324189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24189 |  | 324190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24190 |  | 324191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24191 |  | 324192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24192 |  | 324193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24193 |  | 324194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24194 |  | 324195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24195 |  | 324196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24196 |  | 324197 | EIM3.1 4 supply voltage high - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24197 |  | 324198 | EIM3.1 4 supply voltage low or missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24198 |  | 324199 | EIM3.1 5 supply voltage high - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24199 |  | 324200 | EIM3.1 5 supply voltage low or missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24200 |  | 324201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24201 |  | 324202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24202 |  | 324203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24203 |  | 324204 | EIM3.1 4 relay 4 wire break - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24204 |  | 324205 | EIM3.1 5 relay 4 wire break - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24205 |  | 324206 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24206 |  | 324207 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24207 |  | 324208 | AC protections not running (differential current) - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24208 |  | 324209 | AC data is missing (differential current) - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24209 |  | 324210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24210 |  | 324211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24211 |  | 324212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24212 |  | 324213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24213 |  | 324214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24214 |  | 324215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24215 |  | 324216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24216 |  | 324217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24217 |  | 324218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24218 |  | 324219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24219 |  | 324220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24220 |  | 324221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24221 |  | 324222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24222 |  | 324223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24223 |  | 324224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24224 |  | 324225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24225 |  | 324226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24226 |  | 324227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24237 |  | 324238 | Blackout detection mismatch - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24240 |  | 324241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24241 |  | 324242 | Parameters - Communication - NTP - NTP server 1 not responding - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24242 |  | 324243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24243 |  | 324244 | Parameters - Communication - NTP - NTP server 2 not responding - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24244 |  | 324245 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24245 |  | 324246 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24297 |  | 324298 | Different single-line configurations - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24299 |  | 324300 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24301 |  | 324302 | Parameters - CODESYS - Monitoring - Application not OK - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24306 |  | 324307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24316 |  | 324317 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24364 |  | 324365 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24365 |  | 324366 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24365 |  | 324366 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24365 |  | 324366 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24366 |  | 324367 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24366 |  | 324367 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24366 |  | 324367 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24367 |  | 324368 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24367 |  | 324368 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24367 |  | 324368 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24368 |  | 324369 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24368 |  | 324369 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24368 |  | 324369 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24369 |  | 324370 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24369 |  | 324370 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24369 |  | 324370 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24370 |  | 324371 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24370 |  | 324371 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24370 |  | 324371 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24371 |  | 324372 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24371 |  | 324372 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24371 |  | 324372 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24372 |  | 324373 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24372 |  | 324373 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24372 |  | 324373 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24373 |  | 324374 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24373 |  | 324374 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24373 |  | 324374 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24374 |  | 324375 | Parameters - Generator - Current protections - Over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24374 |  | 324375 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24374 |  | 324375 | Parameters - Mains - Current protections - Over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24375 |  | 324376 | Parameters - Generator - Current protections - Over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24375 |  | 324376 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24375 |  | 324376 | Parameters - Mains - Current protections - Over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24376 |  | 324377 | Parameters - Generator - Current protections - Over-current 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24376 |  | 324377 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24376 |  | 324377 | Parameters - Mains - Current protections - Over-current 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24377 |  | 324378 | Parameters - Generator - Current protections - Over-current 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24377 |  | 324378 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24377 |  | 324378 | Parameters - Mains - Current protections - Over-current 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24378 |  | 324379 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24378 |  | 324379 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24378 |  | 324379 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24379 |  | 324380 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24379 |  | 324380 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24379 |  | 324380 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24380 |  | 324381 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24380 |  | 324381 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24380 |  | 324381 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24381 |  | 324382 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24381 |  | 324382 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24381 |  | 324382 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24382 |  | 324383 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24382 |  | 324383 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24382 |  | 324383 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24383 |  | 324384 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24383 |  | 324384 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24383 |  | 324384 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24384 |  | 324385 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24385 |  | 324386 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24386 |  | 324387 | Parameters - Generator - Current protections - Negative sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24386 |  | 324387 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24386 |  | 324387 | Parameters - Mains - Current protections - Negative sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24387 |  | 324388 | Parameters - Generator - Current protections - Zero sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24387 |  | 324388 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24387 |  | 324388 | Parameters - Mains - Current protections - Zero sequence current - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24388 |  | 324389 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24388 |  | 324389 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24388 |  | 324389 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24389 |  | 324390 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24389 |  | 324390 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24389 |  | 324390 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24390 |  | 324391 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24390 |  | 324391 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24390 |  | 324391 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24391 |  | 324392 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24391 |  | 324392 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24391 |  | 324392 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24392 |  | 324393 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24392 |  | 324393 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24392 |  | 324393 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24393 |  | 324394 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24393 |  | 324394 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24393 |  | 324394 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24394 |  | 324395 | Parameters - Generator - Power protections - Overload 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24394 |  | 324395 | Parameters - Busbar A - Power protections - Power export 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24394 |  | 324395 | Parameters - Mains - Power protections - Overload 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24395 |  | 324396 | Parameters - Generator - Power protections - Overload 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24395 |  | 324396 | Parameters - Busbar A - Power protections - Power export 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24395 |  | 324396 | Parameters - Mains - Power protections - Overload 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24396 |  | 324397 | Parameters - Generator - Power protections - Overload 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24396 |  | 324397 | Parameters - Busbar A - Power protections - Power export 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24396 |  | 324397 | Parameters - Mains - Power protections - Overload 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24397 |  | 324398 | Parameters - Generator - Power protections - Overload 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24397 |  | 324398 | Parameters - Busbar A - Power protections - Power export 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24397 |  | 324398 | Parameters - Mains - Power protections - Overload 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24398 |  | 324399 | Parameters - Generator - Power protections - Overload 5 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24398 |  | 324399 | Parameters - Busbar A - Power protections - Power export 5 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24398 |  | 324399 | Parameters - Mains - Power protections - Overload 5 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24399 |  | 324400 | Parameters - Generator - Power protections - Reverse power 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24399 |  | 324400 | Parameters - Busbar A - Power protections - Power import 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24399 |  | 324400 | Parameters - Mains - Power protections - Reverse power 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24400 |  | 324401 | Parameters - Generator - Power protections - Reverse power 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24400 |  | 324401 | Parameters - Busbar A - Power protections - Power import 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24400 |  | 324401 | Parameters - Mains - Power protections - Reverse power 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24401 |  | 324402 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24401 |  | 324402 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24401 |  | 324402 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24402 |  | 324403 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24402 |  | 324403 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24402 |  | 324403 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24403 |  | 324404 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24403 |  | 324404 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24403 |  | 324404 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24404 |  | 324405 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24404 |  | 324405 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24404 |  | 324405 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24405 |  | 324406 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24405 |  | 324406 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24405 |  | 324406 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24406 |  | 324407 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24406 |  | 324407 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24406 |  | 324407 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24407 |  | 324408 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24407 |  | 324408 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24407 |  | 324408 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24408 |  | 324409 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24408 |  | 324409 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24408 |  | 324409 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24409 |  | 324410 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24409 |  | 324410 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24409 |  | 324410 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24410 |  | 324411 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24410 |  | 324411 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24410 |  | 324411 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24411 |  | 324412 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24411 |  | 324412 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24411 |  | 324412 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24412 |  | 324413 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24412 |  | 324413 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24412 |  | 324413 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24413 |  | 324414 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24413 |  | 324414 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24413 |  | 324414 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24414 |  | 324415 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24414 |  | 324415 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24414 |  | 324415 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24415 |  | 324416 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24415 |  | 324416 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24415 |  | 324416 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24416 |  | 324417 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24416 |  | 324417 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24416 |  | 324417 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24417 |  | 324418 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24417 |  | 324418 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24417 |  | 324418 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24418 |  | 324419 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24418 |  | 324419 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24418 |  | 324419 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24419 |  | 324420 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24419 |  | 324420 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24419 |  | 324420 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24420 |  | 324421 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24420 |  | 324421 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24420 |  | 324421 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24421 |  | 324422 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24421 |  | 324422 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24421 |  | 324422 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24422 |  | 324423 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24422 |  | 324423 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer remaining time | 24422 |  | 324423 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer remaining time | 24471 |  | 324472 | External MB open failure - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24472 |  | 324473 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24473 |  | 324474 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24474 |  | 324475 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24475 |  | 324476 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24476 |  | 324477 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24477 |  | 324478 | Parameters - Breakers - Close before excitation - CBE failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24478 |  | 324479 | Load too high - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24479 |  | 324480 | ID to run configuration failure - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24484 |  | 324485 | Can ID not available - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24485 |  | 324486 | Duplicated CAN IDs - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24486 |  | 324487 | Parameters - Local power management - Alarms - Busbar blocked - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24487 |  | 324488 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24488 |  | 324489 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24489 |  | 324490 | Parameters - System - Monitoring - BTB 33 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24490 |  | 324491 | Parameters - System - Monitoring - BTB 34 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24491 |  | 324492 | Parameters - System - Monitoring - BTB 35 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24492 |  | 324493 | Parameters - System - Monitoring - BTB 36 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24493 |  | 324494 | Parameters - System - Monitoring - BTB 37 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24494 |  | 324495 | Parameters - System - Monitoring - BTB 38 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24495 |  | 324496 | Parameters - System - Monitoring - BTB 39 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24496 |  | 324497 | Parameters - System - Monitoring - BTB 40 position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24578 |  | 324579 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24579 |  | 324580 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24580 |  | 324581 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24581 |  | 324582 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24582 |  | 324583 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24583 |  | 324584 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24584 |  | 324585 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24585 |  | 324586 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24586 |  | 324587 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24587 |  | 324588 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24588 |  | 324589 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24589 |  | 324590 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24590 |  | 324591 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24591 |  | 324592 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24592 |  | 324593 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm status: Delay timer remaining time | 24593 |  | 324594 | Parameters - System - Monitoring - Single-line hazard - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24594 |  | 324595 | ID not present - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24595 |  | 324596 | Unsupported application - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24596 |  | 324597 | Application internal CAN protocol conflict - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24597 |  | 324598 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24598 |  | 324599 | Dry mode: Voltage level unexpected - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24604 |  | 324605 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24604 |  | 324605 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer remaining time | 24604 |  | 324605 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer remaining time | 24605 |  | 324606 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer remaining time | 24605 |  | 324606 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer remaining time | 24607 |  | 324608 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24608 |  | 324609 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24609 |  | 324610 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24610 |  | 324611 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24611 |  | 324612 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24612 |  | 324613 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24613 |  | 324614 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24614 |  | 324615 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24615 |  | 324616 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24616 |  | 324617 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24617 |  | 324618 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24618 |  | 324619 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24619 |  | 324620 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24620 |  | 324621 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24621 |  | 324622 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24622 |  | 324623 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24623 |  | 324624 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24624 |  | 324625 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24625 |  | 324626 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24626 |  | 324627 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24627 |  | 324628 | Live voltage detected - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24631 |  | 324632 | Card configuration failed - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24633 |  | 324634 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24634 |  | 324635 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24635 |  | 324636 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer remaining time | 24639 |  | 324640 | Licence error - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 24642 |  | 324643 | Parameters - Grid code - Capability curve - Protections - Import protection - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24643 |  | 324644 | Parameters - Grid code - Capability curve - Protections - Export protection - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer remaining time | 24644 |  | 324645 | Hardware is not compatible based on module versions - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25500 |  | 325501 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25501 |  | 325502 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25502 |  | 325503 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25503 |  | 325504 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25504 |  | 325505 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25505 |  | 325506 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25506 |  | 325507 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25507 |  | 325508 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25508 |  | 325509 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25509 |  | 325510 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25510 |  | 325511 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25511 |  | 325512 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25512 |  | 325513 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25513 |  | 325514 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25514 |  | 325515 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25515 |  | 325516 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25516 |  | 325517 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25517 |  | 325518 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25518 |  | 325519 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25519 |  | 325520 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25520 |  | 325521 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25521 |  | 325522 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25522 |  | 325523 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25523 |  | 325524 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25524 |  | 325525 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25525 |  | 325526 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25526 |  | 325527 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25527 |  | 325528 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25528 |  | 325529 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25529 |  | 325530 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25530 |  | 325531 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25531 |  | 325532 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25532 |  | 325533 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25533 |  | 325534 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25534 |  | 325535 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25535 |  | 325536 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25536 |  | 325537 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25537 |  | 325538 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25538 |  | 325539 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25539 |  | 325540 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25540 |  | 325541 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25541 |  | 325542 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25542 |  | 325543 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25543 |  | 325544 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25544 |  | 325545 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25545 |  | 325546 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25546 |  | 325547 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25547 |  | 325548 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25548 |  | 325549 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25549 |  | 325550 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25600 |  | 325601 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25601 |  | 325602 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25602 |  | 325603 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25603 |  | 325604 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25604 |  | 325605 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25605 |  | 325606 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25606 |  | 325607 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25607 |  | 325608 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25608 |  | 325609 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25609 |  | 325610 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25610 |  | 325611 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25611 |  | 325612 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25612 |  | 325613 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25613 |  | 325614 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25614 |  | 325615 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25615 |  | 325616 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25616 |  | 325617 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25617 |  | 325618 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25618 |  | 325619 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25619 |  | 325620 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25620 |  | 325621 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25621 |  | 325622 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25622 |  | 325623 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25623 |  | 325624 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25624 |  | 325625 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25625 |  | 325626 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25626 |  | 325627 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25627 |  | 325628 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25628 |  | 325629 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25629 |  | 325630 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25630 |  | 325631 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25631 |  | 325632 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25632 |  | 325633 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25633 |  | 325634 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25634 |  | 325635 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25635 |  | 325636 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25636 |  | 325637 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25637 |  | 325638 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25638 |  | 325639 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25639 |  | 325640 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25640 |  | 325641 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25641 |  | 325642 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25642 |  | 325643 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25643 |  | 325644 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25644 |  | 325645 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25645 |  | 325646 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25646 |  | 325647 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25647 |  | 325648 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25648 |  | 325649 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25649 |  | 325650 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25650 |  | 325651 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25651 |  | 325652 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25652 |  | 325653 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25653 |  | 325654 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25654 |  | 325655 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25655 |  | 325656 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25656 |  | 325657 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25657 |  | 325658 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25658 |  | 325659 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25659 |  | 325660 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25660 |  | 325661 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25661 |  | 325662 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25662 |  | 325663 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25663 |  | 325664 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25664 |  | 325665 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25665 |  | 325666 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25666 |  | 325667 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25667 |  | 325668 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25668 |  | 325669 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25669 |  | 325670 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25670 |  | 325671 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25671 |  | 325672 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25672 |  | 325673 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25673 |  | 325674 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25674 |  | 325675 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25675 |  | 325676 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25676 |  | 325677 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25677 |  | 325678 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25678 |  | 325679 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25679 |  | 325680 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25680 |  | 325681 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25681 |  | 325682 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25682 |  | 325683 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25683 |  | 325684 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25684 |  | 325685 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25685 |  | 325686 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25686 |  | 325687 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25687 |  | 325688 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25688 |  | 325689 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25689 |  | 325690 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25690 |  | 325691 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25691 |  | 325692 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25692 |  | 325693 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25693 |  | 325694 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25694 |  | 325695 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25695 |  | 325696 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25696 |  | 325697 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25697 |  | 325698 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25698 |  | 325699 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25699 |  | 325700 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25700 |  | 325701 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25701 |  | 325702 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25702 |  | 325703 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25703 |  | 325704 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25704 |  | 325705 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25705 |  | 325706 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25706 |  | 325707 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25707 |  | 325708 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25708 |  | 325709 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25709 |  | 325710 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25710 |  | 325711 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25711 |  | 325712 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25712 |  | 325713 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25713 |  | 325714 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25714 |  | 325715 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25715 |  | 325716 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25716 |  | 325717 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25717 |  | 325718 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25718 |  | 325719 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25719 |  | 325720 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25720 |  | 325721 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25721 |  | 325722 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25722 |  | 325723 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25723 |  | 325724 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25724 |  | 325725 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25725 |  | 325726 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25726 |  | 325727 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25727 |  | 325728 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25728 |  | 325729 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25729 |  | 325730 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25730 |  | 325731 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25731 |  | 325732 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25732 |  | 325733 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25733 |  | 325734 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25734 |  | 325735 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25735 |  | 325736 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25736 |  | 325737 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25737 |  | 325738 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25738 |  | 325739 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25739 |  | 325740 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25740 |  | 325741 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25741 |  | 325742 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25742 |  | 325743 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25743 |  | 325744 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25744 |  | 325745 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25745 |  | 325746 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25746 |  | 325747 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25747 |  | 325748 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25748 |  | 325749 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25749 |  | 325750 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25750 |  | 325751 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25751 |  | 325752 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25752 |  | 325753 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25753 |  | 325754 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25754 |  | 325755 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25755 |  | 325756 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25756 |  | 325757 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25757 |  | 325758 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25758 |  | 325759 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25759 |  | 325760 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25760 |  | 325761 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25761 |  | 325762 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25762 |  | 325763 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25763 |  | 325764 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25764 |  | 325765 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25765 |  | 325766 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25766 |  | 325767 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25767 |  | 325768 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25768 |  | 325769 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25769 |  | 325770 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25770 |  | 325771 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25771 |  | 325772 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25772 |  | 325773 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25773 |  | 325774 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25774 |  | 325775 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25775 |  | 325776 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25776 |  | 325777 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25777 |  | 325778 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25778 |  | 325779 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25779 |  | 325780 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25780 |  | 325781 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25781 |  | 325782 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25782 |  | 325783 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25783 |  | 325784 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25784 |  | 325785 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25785 |  | 325786 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25786 |  | 325787 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25787 |  | 325788 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25788 |  | 325789 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25789 |  | 325790 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25790 |  | 325791 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25791 |  | 325792 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25792 |  | 325793 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25793 |  | 325794 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25794 |  | 325795 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25795 |  | 325796 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25796 |  | 325797 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25797 |  | 325798 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25798 |  | 325799 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Delay timer remaining time | 25799 |  | 325800 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm status: Alarm state | 26000 |  | 326001 | Application initialisation error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26001 |  | 326002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26002 |  | 326003 | Preliminary software | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26003 |  | 326004 | Parameters - Engine - Stop sequence - Stop failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26004 |  | 326005 | Parameters - Engine - Start sequence - Start failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26005 |  | 326006 | Parameters - Engine - Start sequence - Crank failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26006 |  | 326007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26007 |  | 326008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26008 |  | 326009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26009 |  | 326010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26010 |  | 326011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Magnetic pickup wire break alarm | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26011 |  | 326012 | Parameters - Engine - Stop sequence - Externally stopped - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26013 |  | 326014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26014 |  | 326015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26015 |  | 326016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26016 |  | 326017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26017 |  | 326018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26018 |  | 326019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26019 |  | 326020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26020 |  | 326021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26021 |  | 326022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26022 |  | 326023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26027 |  | 326028 | Parameters - Engine - Running detection - Primary running feedback failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26041 |  | 326042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - GB closing failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26041 |  | 326042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - BTB closing failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26041 |  | 326042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - MB closing failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26042 |  | 326043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - GB opening failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26042 |  | 326043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - BTB opening failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26042 |  | 326043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - MB opening failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26043 |  | 326044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - GB position failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26043 |  | 326044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - BTB position failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26043 |  | 326044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - MB position failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26044 |  | 326045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - GB configuration failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26044 |  | 326045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - BTB configuration failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26044 |  | 326045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - MB configuration failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26045 |  | 326046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - GB synchronisation failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26045 |  | 326046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - BTB synchronisation failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26045 |  | 326046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - MB synchronisation failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26046 |  | 326047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - GB de-load failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26046 |  | 326047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - BTB de-load failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26046 |  | 326047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - MB de-load failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26047 |  | 326048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - GB tripped (external) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26047 |  | 326048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - BTB tripped (external) | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26047 |  | 326048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - MB tripped (external) | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26048 |  | 326049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - GB short circuit | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26048 |  | 326049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - BTB short circuit | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26048 |  | 326049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - MB short circuit | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26049 |  | 326050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - MB closing failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26049 |  | 326050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - TB closing failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm state | 26050 |  | 326051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - MB opening failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26050 |  | 326051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - TB opening failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm state | 26051 |  | 326052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - MB position failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26051 |  | 326052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - TB position failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm state | 26052 |  | 326053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - MB configuration failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26052 |  | 326053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - TB configuration failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm state | 26053 |  | 326054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - MB synchronisation failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26053 |  | 326054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - TB synchronisation failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm state | 26054 |  | 326055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - MB de-load failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26054 |  | 326055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - TB de-load failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm state | 26055 |  | 326056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - MB tripped (external) | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26055 |  | 326056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - TB tripped (external) | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm state | 26056 |  | 326057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - MB short circuit | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26056 |  | 326057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - TB short circuit | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm state | 26060 |  | 326061 | Parameters - Mains - AC setup - Phase sequence error - Information - Mains phase sequence error | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26060 |  | 326061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Busbar phase sequence error | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26060 |  | 326061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Busbar B phase sequence error | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26061 |  | 326062 | Parameters - Generator - AC setup - Phase sequence error - Information - Generator phase sequence error | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26061 |  | 326062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Busbar A phase sequence error | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26061 |  | 326062 | Parameters - Mains - AC setup - Phase sequence error - Information - Mains phase sequence error | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26062 |  | 326063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26103 |  | 326104 | Parameters - Mains - Additional protections - ROCOF - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26103 |  | 326104 | Parameters - Busbar - Additional protections - ROCOF - Information | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26103 |  | 326104 | Parameters - Busbar B - Additional protections - ROCOF - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26104 |  | 326105 | Parameters - Mains - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26104 |  | 326105 | Parameters - Busbar - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26104 |  | 326105 | Parameters - Busbar B - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26105 |  | 326106 | Parameters - Generator - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26105 |  | 326106 | Parameters - Busbar A - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26105 |  | 326106 | Parameters - Mains - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26106 |  | 326107 | Parameters - Local - 4th current input - Earth inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26107 |  | 326108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26108 |  | 326109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26108 |  | 326109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26108 |  | 326109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26109 |  | 326110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26109 |  | 326110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26109 |  | 326110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26110 |  | 326111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26110 |  | 326111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26110 |  | 326111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26111 |  | 326112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26111 |  | 326112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26111 |  | 326112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26115 |  | 326116 | Protection set point out of range | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26116 |  | 326117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Stabilised differential | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26117 |  | 326118 | Parameters - Generator - Current protections - High set differential current - Information - High set differential | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26118 |  | 326119 | Protection set point out of range (differential current) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26119 |  | 326120 | Parameters - Local - Mode - Not under remote control - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26121 |  | 326122 | Parameters - Local - Monitoring - System not OK - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26122 |  | 326123 | Configuration update delayed | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26123 |  | 326124 | Critical process error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26124 |  | 326125 | Restore error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26125 |  | 326126 | SD-card format error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26126 |  | 326127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26127 |  | 326128 | Fieldbus configuration exceeded maximum I/O configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26128 |  | 326129 | Parameters - Custom alarms - Custom alarm 0 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26129 |  | 326130 | Parameters - Custom alarms - Custom alarm 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26130 |  | 326131 | Parameters - Custom alarms - Custom alarm 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26131 |  | 326132 | Parameters - Custom alarms - Custom alarm 3 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26132 |  | 326133 | Parameters - Custom alarms - Custom alarm 4 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26133 |  | 326134 | Parameters - Custom alarms - Custom alarm 5 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26134 |  | 326135 | Parameters - Custom alarms - Custom alarm 6 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26135 |  | 326136 | Parameters - Custom alarms - Custom alarm 7 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26136 |  | 326137 | Parameters - Custom alarms - Custom alarm 8 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26137 |  | 326138 | Parameters - Custom alarms - Custom alarm 9 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26138 |  | 326139 | Parameters - Custom alarms - Custom alarm 10 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26139 |  | 326140 | Parameters - Custom alarms - Custom alarm 11 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26140 |  | 326141 | Parameters - Custom alarms - Custom alarm 12 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26141 |  | 326142 | Parameters - Custom alarms - Custom alarm 13 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26142 |  | 326143 | Parameters - Custom alarms - Custom alarm 14 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26143 |  | 326144 | Parameters - Custom alarms - Custom alarm 15 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26144 |  | 326145 | Parameters - Custom alarms - Custom alarm 16 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26145 |  | 326146 | Parameters - Custom alarms - Custom alarm 17 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26146 |  | 326147 | Parameters - Custom alarms - Custom alarm 18 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26147 |  | 326148 | Parameters - Custom alarms - Custom alarm 19 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26148 |  | 326149 | Parameters - Custom alarms - Custom alarm 20 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26149 |  | 326150 | Parameters - Custom alarms - Custom alarm 21 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26150 |  | 326151 | Parameters - Custom alarms - Custom alarm 22 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26151 |  | 326152 | Parameters - Custom alarms - Custom alarm 23 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26152 |  | 326153 | Parameters - Custom alarms - Custom alarm 24 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26153 |  | 326154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - GOV regulation error | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26154 |  | 326155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - AVR regulation error | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26163 |  | 326164 | Required hardware card(s) not found | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26164 |  | 326165 | Software mismatch on hardware module(s) | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26165 |  | 326166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Mains L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm state | 26165 |  | 326166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Busbar L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm state | 26165 |  | 326166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Busbar B L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26166 |  | 326167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Generator L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm state | 26166 |  | 326167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Busbar A L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26166 |  | 326167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Mains L1-L2-L3 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26167 |  | 326168 | Parameters - Mains - AC setup - L1 wire break - Information - Mains L1 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm state | 26167 |  | 326168 | Parameters - Busbar - AC setup - L1 wire break - Information - Busbar L1 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm state | 26167 |  | 326168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Busbar B L1 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26168 |  | 326169 | Parameters - Mains - AC setup - L2 wire break - Information - Mains L2 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm state | 26168 |  | 326169 | Parameters - Busbar - AC setup - L2 wire break - Information - Busbar L2 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm state | 26168 |  | 326169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Busbar B L2 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26169 |  | 326170 | Parameters - Mains - AC setup - L3 wire break - Information - Mains L3 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm state | 26169 |  | 326170 | Parameters - Busbar - AC setup - L3 wire break - Information - Busbar L3 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm state | 26169 |  | 326170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Busbar B L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26170 |  | 326171 | Parameters - Generator - AC setup - L1 wire break - Information - Generator L1 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm state | 26170 |  | 326171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Busbar A L1 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26170 |  | 326171 | Parameters - Mains - AC setup - L1 wire break - Information - Mains L1 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26171 |  | 326172 | Parameters - Generator - AC setup - L2 wire break - Information - Generator L2 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm state | 26171 |  | 326172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Busbar A L2 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26171 |  | 326172 | Parameters - Mains - AC setup - L2 wire break - Information - Mains L2 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26172 |  | 326173 | Parameters - Generator - AC setup - L3 wire break - Information - Generator L3 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm state | 26172 |  | 326173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Busbar A L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26172 |  | 326173 | Parameters - Mains - AC setup - L3 wire break - Information - Mains L3 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm state | 26178 |  | 326179 | Parameters - Mains - AC setup - Supervision alarm - Information - Mains supervision alarm | INT16 | X * 1 | X * 1 |  |  |  | X | X |  | X | X
Alarm status: Alarm state | 26179 |  | 326180 | Parameters - Engine - Emergency stop - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26179 |  | 326180 | Parameters - Busbar A - Emergency stop - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26179 |  | 326180 | Parameters - Mains - Emergency stop - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26180 |  | 326181 | Clock battery failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26181 |  | 326182 | Controller temperature too high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26182 |  | 326183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - PSM3.1 1 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26183 |  | 326184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - PSM3.1 1 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26184 |  | 326185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - PSM3.2 1 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26185 |  | 326186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - PSM3.2 1 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26186 |  | 326187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - PSM3.2 2 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26187 |  | 326188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - PSM3.2 2 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26188 |  | 326189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - PSM3.2 3 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26189 |  | 326190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - PSM3.2 3 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26190 |  | 326191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - EIM3.1 1 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26191 |  | 326192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - EIM3.1 1 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26192 |  | 326193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - EIM3.1 2 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26193 |  | 326194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - EIM3.1 2 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26194 |  | 326195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - EIM3.1 3 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26195 |  | 326196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - EIM3.1 3 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26196 |  | 326197 | EIM3.1 4 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26197 |  | 326198 | EIM3.1 4 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26198 |  | 326199 | EIM3.1 5 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26199 |  | 326200 | EIM3.1 5 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26200 |  | 326201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - EIM3.1 1 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26201 |  | 326202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - EIM3.1 2 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26202 |  | 326203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - EIM3.1 3 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26203 |  | 326204 | EIM3.1 4 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26204 |  | 326205 | EIM3.1 5 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26205 |  | 326206 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26206 |  | 326207 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26207 |  | 326208 | AC protections not running (differential current) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26208 |  | 326209 | AC data is missing (differential current) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26209 |  | 326210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - GAM3.2 1 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26210 |  | 326211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - GAM3.2 1 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26211 |  | 326212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - GAM3.2 2 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26212 |  | 326213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - GAM3.2 2 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26213 |  | 326214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - GAM3.2 3 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26214 |  | 326215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - GAM3.2 3 supply voltage low or missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26215 |  | 326216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - PSM3.2 4 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26216 |  | 326217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - PSM3.2 4 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26217 |  | 326218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - PSM3.2 5 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26218 |  | 326219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - PSM3.2 5 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26219 |  | 326220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - PSM3.2 6 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26220 |  | 326221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - PSM3.2 6 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26221 |  | 326222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - PSM3.2 7 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26222 |  | 326223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - PSM3.2 7 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26223 |  | 326224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - PSM3.2 8 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26224 |  | 326225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - PSM3.2 8 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26225 |  | 326226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - PSM3.2 9 supply voltage high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26226 |  | 326227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - PSM3.2 9 supply voltage low | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26228 |  | 326229 | Parameters - System - Monitoring - Duplicate controller ID - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26229 |  | 326230 | Parameters - System - Monitoring - Missing all controllers - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26231 |  | 326232 | Controller ID not configured | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26236 |  | 326237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26237 |  | 326238 | Blackout detection mismatch | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26240 |  | 326241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - NTP server 1 could not connect | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26241 |  | 326242 | Parameters - Communication - NTP - NTP server 1 not responding - Information - NTP server 1 is not responding | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26242 |  | 326243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - NTP server 2 could not connect | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26243 |  | 326244 | Parameters - Communication - NTP - NTP server 2 not responding - Information - NTP server 2 is not responding | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26244 |  | 326245 | Parameters - Communication - NTP - No NTP server time synchronisation - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26245 |  | 326246 | Parameters - Communication - NTP - No NTP server(s) connected - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26246 |  | 326247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26247 |  | 326248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26296 |  | 326297 | Controller not part of system | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26297 |  | 326298 | Different single-line configurations | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26298 |  | 326299 | Single-line missing/none active | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26299 |  | 326300 | Parameters - Communication - Modbus - Modbus communication timeout - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26300 |  | 326301 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - CODESYS configuration conflict | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26301 |  | 326302 | Parameters - CODESYS - Monitoring - Application not OK - Information - CODESYS application not OK | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26302 |  | 326303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26303 |  | 326304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26304 |  | 326305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26305 |  | 326306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26306 |  | 326307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26307 |  | 326308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26308 |  | 326309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26309 |  | 326310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26310 |  | 326311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26311 |  | 326312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26312 |  | 326313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26315 |  | 326316 | Parameters - Local - CustomLogic - Configuration invalid - Information - CustomLogic configuration invalid | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26316 |  | 326317 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Digital AVR communication error | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26317 |  | 326318 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26318 |  | 326319 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26319 |  | 326320 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26320 |  | 326321 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26321 |  | 326322 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26322 |  | 326323 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26323 |  | 326324 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26324 |  | 326325 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26325 |  | 326326 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26326 |  | 326327 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26327 |  | 326328 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26328 |  | 326329 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26329 |  | 326330 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26330 |  | 326331 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26331 |  | 326332 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26332 |  | 326333 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26333 |  | 326334 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26334 |  | 326335 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26335 |  | 326336 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26336 |  | 326337 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26337 |  | 326338 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26338 |  | 326339 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26339 |  | 326340 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26340 |  | 326341 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26341 |  | 326342 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26342 |  | 326343 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26343 |  | 326344 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26344 |  | 326345 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26345 |  | 326346 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26346 |  | 326347 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26347 |  | 326348 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26348 |  | 326349 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26349 |  | 326350 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26350 |  | 326351 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26351 |  | 326352 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26352 |  | 326353 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26353 |  | 326354 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26354 |  | 326355 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26355 |  | 326356 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26356 |  | 326357 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26357 |  | 326358 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26358 |  | 326359 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26359 |  | 326360 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26360 |  | 326361 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26361 |  | 326362 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26362 |  | 326363 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26363 |  | 326364 | DAVR unsupported AC configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26364 |  | 326365 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Illegal DAVR configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26365 |  | 326366 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Generator under-voltage 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26365 |  | 326366 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Busbar A under-voltage 1 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26365 |  | 326366 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Mains under-voltage 1 | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26366 |  | 326367 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Generator under-voltage 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26366 |  | 326367 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Busbar A under-voltage 2 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26366 |  | 326367 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Mains under-voltage 2 | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26367 |  | 326368 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Generator under-voltage 3 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26367 |  | 326368 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Busbar A under-voltage 3 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26367 |  | 326368 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Mains under-voltage 3 | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26368 |  | 326369 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Generator over-voltage 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26368 |  | 326369 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Busbar A over-voltage 1 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26368 |  | 326369 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Mains over-voltage 1 | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26369 |  | 326370 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Generator over-voltage 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26369 |  | 326370 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Busbar A over-voltage 2 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26369 |  | 326370 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Mains over-voltage 2 | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26370 |  | 326371 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Generator voltage unbalance | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26370 |  | 326371 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Busbar A voltage unbalance | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26370 |  | 326371 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Mains voltage unbalance | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26371 |  | 326372 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Generator negative sequence voltage | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26371 |  | 326372 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Busbar A negative sequence voltage | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26371 |  | 326372 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Mains negative sequence voltage | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26372 |  | 326373 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Generator zero sequence voltage | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26372 |  | 326373 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Busbar A zero sequence voltage | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26372 |  | 326373 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Mains zero sequence voltage | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26373 |  | 326374 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Generator positive sequence under-voltage | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26373 |  | 326374 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Busbar A positive sequence under-voltage | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26373 |  | 326374 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Mains positive sequence under-voltage | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26374 |  | 326375 | Parameters - Generator - Current protections - Over-current 1 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26374 |  | 326375 | Parameters - Busbar A - Current protections - Over-current 1 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26374 |  | 326375 | Parameters - Mains - Current protections - Over-current 1 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26375 |  | 326376 | Parameters - Generator - Current protections - Over-current 2 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26375 |  | 326376 | Parameters - Busbar A - Current protections - Over-current 2 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26375 |  | 326376 | Parameters - Mains - Current protections - Over-current 2 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26376 |  | 326377 | Parameters - Generator - Current protections - Over-current 3 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26376 |  | 326377 | Parameters - Busbar A - Current protections - Over-current 3 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26376 |  | 326377 | Parameters - Mains - Current protections - Over-current 3 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26377 |  | 326378 | Parameters - Generator - Current protections - Over-current 4 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26377 |  | 326378 | Parameters - Busbar A - Current protections - Over-current 4 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26377 |  | 326378 | Parameters - Mains - Current protections - Over-current 4 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26378 |  | 326379 | Parameters - Generator - Current protections - Fast over-current 1 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26378 |  | 326379 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26378 |  | 326379 | Parameters - Mains - Current protections - Fast over-current 1 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26379 |  | 326380 | Parameters - Generator - Current protections - Fast over-current 2 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26379 |  | 326380 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26379 |  | 326380 | Parameters - Mains - Current protections - Fast over-current 2 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26380 |  | 326381 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26380 |  | 326381 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26380 |  | 326381 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26381 |  | 326382 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26381 |  | 326382 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26381 |  | 326382 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26382 |  | 326383 | Parameters - Generator - Current protections - Directional over-current 1 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26382 |  | 326383 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26382 |  | 326383 | Parameters - Mains - Current protections - Directional over-current 1 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26383 |  | 326384 | Parameters - Generator - Current protections - Directional over-current 2 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26383 |  | 326384 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26383 |  | 326384 | Parameters - Mains - Current protections - Directional over-current 2 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26384 |  | 326385 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26385 |  | 326386 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26386 |  | 326387 | Parameters - Generator - Current protections - Negative sequence current - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26386 |  | 326387 | Parameters - Busbar A - Current protections - Negative sequence current - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26386 |  | 326387 | Parameters - Mains - Current protections - Negative sequence current - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26387 |  | 326388 | Parameters - Generator - Current protections - Zero sequence current - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26387 |  | 326388 | Parameters - Busbar A - Current protections - Zero sequence current - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26387 |  | 326388 | Parameters - Mains - Current protections - Zero sequence current - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26388 |  | 326389 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Generator over-frequency 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26388 |  | 326389 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Busbar A over-frequency 1 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26388 |  | 326389 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Mains over-frequency 1 | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26389 |  | 326390 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Generator over-frequency 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26389 |  | 326390 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Busbar A over-frequency 2 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26389 |  | 326390 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Mains over-frequency 2 | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26390 |  | 326391 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Generator over-frequency 3 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26390 |  | 326391 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Busbar A over-frequency 3 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26390 |  | 326391 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Mains over-frequency 3 | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26391 |  | 326392 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Generator under-frequency 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26391 |  | 326392 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Busbar A under-frequency 1 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26391 |  | 326392 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Mains under-frequency 1 | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26392 |  | 326393 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Generator under-frequency 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26392 |  | 326393 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Busbar A under-frequency 2 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26392 |  | 326393 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Mains under-frequency 2 | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26393 |  | 326394 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Generator under-frequency 3 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26393 |  | 326394 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Busbar A under-frequency 3 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26393 |  | 326394 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Mains under-frequency 3 | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26394 |  | 326395 | Parameters - Generator - Power protections - Overload 1 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26394 |  | 326395 | Parameters - Busbar A - Power protections - Power export 1 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26394 |  | 326395 | Parameters - Mains - Power protections - Overload 1 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26395 |  | 326396 | Parameters - Generator - Power protections - Overload 2 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26395 |  | 326396 | Parameters - Busbar A - Power protections - Power export 2 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26395 |  | 326396 | Parameters - Mains - Power protections - Overload 2 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26396 |  | 326397 | Parameters - Generator - Power protections - Overload 3 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26396 |  | 326397 | Parameters - Busbar A - Power protections - Power export 3 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26396 |  | 326397 | Parameters - Mains - Power protections - Overload 3 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26397 |  | 326398 | Parameters - Generator - Power protections - Overload 4 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26397 |  | 326398 | Parameters - Busbar A - Power protections - Power export 4 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26397 |  | 326398 | Parameters - Mains - Power protections - Overload 4 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26398 |  | 326399 | Parameters - Generator - Power protections - Overload 5 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26398 |  | 326399 | Parameters - Busbar A - Power protections - Power export 5 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26398 |  | 326399 | Parameters - Mains - Power protections - Overload 5 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26399 |  | 326400 | Parameters - Generator - Power protections - Reverse power 1 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26399 |  | 326400 | Parameters - Busbar A - Power protections - Power import 1 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26399 |  | 326400 | Parameters - Mains - Power protections - Reverse power 1 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26400 |  | 326401 | Parameters - Generator - Power protections - Reverse power 2 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26400 |  | 326401 | Parameters - Busbar A - Power protections - Power import 2 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26400 |  | 326401 | Parameters - Mains - Power protections - Reverse power 2 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26401 |  | 326402 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26401 |  | 326402 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26401 |  | 326402 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26402 |  | 326403 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26402 |  | 326403 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26402 |  | 326403 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26403 |  | 326404 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26403 |  | 326404 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26403 |  | 326404 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26404 |  | 326405 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26404 |  | 326405 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26404 |  | 326405 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26405 |  | 326406 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Mains over-voltage 1 | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26405 |  | 326406 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Busbar over-voltage 1 | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26405 |  | 326406 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Busbar B over-voltage 1 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26406 |  | 326407 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Mains over-voltage 2 | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26406 |  | 326407 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Busbar over-voltage 2 | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26406 |  | 326407 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Busbar B over-voltage 2 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26407 |  | 326408 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Mains over-voltage 3 | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26407 |  | 326408 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Busbar over-voltage 3 | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26407 |  | 326408 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Busbar B over-voltage 3 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26408 |  | 326409 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Mains under-voltage 1 | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26408 |  | 326409 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Busbar under-voltage 1 | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26408 |  | 326409 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Busbar B under-voltage 1 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26409 |  | 326410 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Mains under-voltage 2 | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26409 |  | 326410 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Busbar under-voltage 2 | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26409 |  | 326410 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Busbar B under-voltage 2 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26410 |  | 326411 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Mains under-voltage 3 | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26410 |  | 326411 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Busbar under-voltage 3 | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26410 |  | 326411 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Busbar B under-voltage 3 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26411 |  | 326412 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Mains under-voltage 4 | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26411 |  | 326412 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Busbar under-voltage 4 | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26411 |  | 326412 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Busbar B under-voltage 4 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26412 |  | 326413 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Mains voltage unbalance | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26412 |  | 326413 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Busbar voltage unbalance | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26412 |  | 326413 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Busbar B voltage unbalance | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26413 |  | 326414 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Mains over-frequency 1 | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26413 |  | 326414 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Busbar over-frequency 1 | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26413 |  | 326414 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Busbar B over-frequency 1 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26414 |  | 326415 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Mains over-frequency 2 | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26414 |  | 326415 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Busbar over-frequency 2 | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26414 |  | 326415 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Busbar B over-frequency 2 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26415 |  | 326416 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Mains over-frequency 3 | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26415 |  | 326416 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Busbar over-frequency 3 | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26415 |  | 326416 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Busbar B over-frequency 3 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26416 |  | 326417 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Mains under-frequency 1 | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26416 |  | 326417 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Busbar under-frequency 1 | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26416 |  | 326417 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Busbar B under-frequency 1 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26417 |  | 326418 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Mains under-frequency 2 | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26417 |  | 326418 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Busbar under-frequency 2 | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26417 |  | 326418 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Busbar B under-frequency 2 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26418 |  | 326419 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Mains under-frequency 3 | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26418 |  | 326419 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Busbar under-frequency 3 | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26418 |  | 326419 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Busbar B under-frequency 3 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26419 |  | 326420 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Mains under-frequency 4 | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26419 |  | 326420 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Busbar under-frequency 4 | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26419 |  | 326420 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Busbar B under-frequency 4 | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26420 |  | 326421 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Busbar negative sequence voltage | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26420 |  | 326421 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Busbar negative sequence voltage | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26420 |  | 326421 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Busbar B negative sequence voltage | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26421 |  | 326422 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Busbar zero sequence voltage | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26421 |  | 326422 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Busbar zero sequence voltage | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26421 |  | 326422 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Busbar B zero sequence voltage | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26422 |  | 326423 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Busbar positive sequence under-voltage | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26422 |  | 326423 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Busbar positive sequence under-voltage | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm state | 26422 |  | 326423 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Busbar B positive sequence under-voltage | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26467 |  | 326468 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26468 |  | 326469 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26469 |  | 326470 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 3 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26470 |  | 326471 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 4 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26471 |  | 326472 | External MB open failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26472 |  | 326473 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26473 |  | 326474 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26474 |  | 326475 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26475 |  | 326476 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26476 |  | 326477 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26477 |  | 326478 | Parameters - Breakers - Close before excitation - CBE failure - Information - Close before excitation failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26478 |  | 326479 | Load too high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26479 |  | 326480 | ID to run configuration failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26481 |  | 326482 | Parameters - System - Monitoring - Missing any genset controller - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26482 |  | 326483 | Parameters - System - Monitoring - Missing any mains controller - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26483 |  | 326484 | Parameters - System - Monitoring - Missing any bus tie controller - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26484 |  | 326485 | Can ID not available | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26485 |  | 326486 | Duplicated CAN IDs | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26486 |  | 326487 | Parameters - Local power management - Alarms - Busbar blocked - Information - Busbar blocked due to position failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26487 |  | 326488 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Busbar A blocked due to position failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26488 |  | 326489 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Busbar B blocked due to position failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26489 |  | 326490 | Parameters - System - Monitoring - BTB 33 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26490 |  | 326491 | Parameters - System - Monitoring - BTB 34 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26491 |  | 326492 | Parameters - System - Monitoring - BTB 35 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26492 |  | 326493 | Parameters - System - Monitoring - BTB 36 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26493 |  | 326494 | Parameters - System - Monitoring - BTB 37 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26494 |  | 326495 | Parameters - System - Monitoring - BTB 38 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26495 |  | 326496 | Parameters - System - Monitoring - BTB 39 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26496 |  | 326497 | Parameters - System - Monitoring - BTB 40 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26497 |  | 326498 | Primary CAN missing ID 1 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26498 |  | 326499 | Primary CAN missing ID 2 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26499 |  | 326500 | Primary CAN missing ID 3 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26500 |  | 326501 | Primary CAN missing ID 4 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26501 |  | 326502 | Primary CAN missing ID 5 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26502 |  | 326503 | Primary CAN missing ID 6 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26503 |  | 326504 | Primary CAN missing ID 7 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26504 |  | 326505 | Primary CAN missing ID 8 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26505 |  | 326506 | Primary CAN missing ID 9 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26506 |  | 326507 | Primary CAN missing ID 10 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26507 |  | 326508 | Primary CAN missing ID 11 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26508 |  | 326509 | Primary CAN missing ID 12 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26509 |  | 326510 | Primary CAN missing ID 13 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26510 |  | 326511 | Primary CAN missing ID 14 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26511 |  | 326512 | Primary CAN missing ID 15 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26512 |  | 326513 | Primary CAN missing ID 16 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26513 |  | 326514 | Primary CAN missing ID 17 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26514 |  | 326515 | Primary CAN missing ID 18 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26515 |  | 326516 | Primary CAN missing ID 19 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26516 |  | 326517 | Primary CAN missing ID 20 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26517 |  | 326518 | Primary CAN missing ID 21 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26518 |  | 326519 | Primary CAN missing ID 22 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26519 |  | 326520 | Primary CAN missing ID 23 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26520 |  | 326521 | Primary CAN missing ID 24 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26521 |  | 326522 | Primary CAN missing ID 25 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26522 |  | 326523 | Primary CAN missing ID 26 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26523 |  | 326524 | Primary CAN missing ID 27 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26524 |  | 326525 | Primary CAN missing ID 28 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26525 |  | 326526 | Primary CAN missing ID 29 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26526 |  | 326527 | Primary CAN missing ID 30 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26527 |  | 326528 | Primary CAN missing ID 31 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26528 |  | 326529 | Primary CAN missing ID 32 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26529 |  | 326530 | Primary CAN missing ID 33 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26530 |  | 326531 | Primary CAN missing ID 34 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26531 |  | 326532 | Primary CAN missing ID 35 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26532 |  | 326533 | Primary CAN missing ID 36 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26533 |  | 326534 | Primary CAN missing ID 37 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26534 |  | 326535 | Primary CAN missing ID 38 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26535 |  | 326536 | Primary CAN missing ID 39 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26536 |  | 326537 | Primary CAN missing ID 40 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26537 |  | 326538 | Secondary CAN missing ID 1 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26538 |  | 326539 | Secondary CAN missing ID 2 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26539 |  | 326540 | Secondary CAN missing ID 3 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26540 |  | 326541 | Secondary CAN missing ID 4 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26541 |  | 326542 | Secondary CAN missing ID 5 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26542 |  | 326543 | Secondary CAN missing ID 6 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26543 |  | 326544 | Secondary CAN missing ID 7 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26544 |  | 326545 | Secondary CAN missing ID 8 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26545 |  | 326546 | Secondary CAN missing ID 9 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26546 |  | 326547 | Secondary CAN missing ID 10 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26547 |  | 326548 | Secondary CAN missing ID 11 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26548 |  | 326549 | Secondary CAN missing ID 12 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26549 |  | 326550 | Secondary CAN missing ID 13 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26550 |  | 326551 | Secondary CAN missing ID 14 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26551 |  | 326552 | Secondary CAN missing ID 15 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26552 |  | 326553 | Secondary CAN missing ID 16 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26553 |  | 326554 | Secondary CAN missing ID 17 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26554 |  | 326555 | Secondary CAN missing ID 18 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26555 |  | 326556 | Secondary CAN missing ID 19 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26556 |  | 326557 | Secondary CAN missing ID 20 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26557 |  | 326558 | Secondary CAN missing ID 21 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26558 |  | 326559 | Secondary CAN missing ID 22 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26559 |  | 326560 | Secondary CAN missing ID 23 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26560 |  | 326561 | Secondary CAN missing ID 24 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26561 |  | 326562 | Secondary CAN missing ID 25 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26562 |  | 326563 | Secondary CAN missing ID 26 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26563 |  | 326564 | Secondary CAN missing ID 27 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26564 |  | 326565 | Secondary CAN missing ID 28 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26565 |  | 326566 | Secondary CAN missing ID 29 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26566 |  | 326567 | Secondary CAN missing ID 30 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26567 |  | 326568 | Secondary CAN missing ID 31 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26568 |  | 326569 | Secondary CAN missing ID 32 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26569 |  | 326570 | Secondary CAN missing ID 33 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26570 |  | 326571 | Secondary CAN missing ID 34 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26571 |  | 326572 | Secondary CAN missing ID 35 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26572 |  | 326573 | Secondary CAN missing ID 36 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26573 |  | 326574 | Secondary CAN missing ID 37 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26574 |  | 326575 | Secondary CAN missing ID 38 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26575 |  | 326576 | Secondary CAN missing ID 39 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26576 |  | 326577 | Secondary CAN missing ID 40 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26577 |  | 326578 | Priority error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26578 |  | 326579 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - NEL 1 over-current | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26579 |  | 326580 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - NEL 1 under-frequency | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26580 |  | 326581 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - NEL 1 overload 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26581 |  | 326582 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - NEL 1 overload 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26582 |  | 326583 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - NEL 1 reactive overload | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26583 |  | 326584 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - NEL 2 over-current | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26584 |  | 326585 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - NEL 2 under-frequency | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26585 |  | 326586 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - NEL 2 overload 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26586 |  | 326587 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - NEL 2 overload 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26587 |  | 326588 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - NEL 2 reactive overload | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26588 |  | 326589 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - NEL 3 over-current | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26589 |  | 326590 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - NEL 3 under-frequency | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26590 |  | 326591 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - NEL 3 overload 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26591 |  | 326592 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - NEL 3 overload 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26592 |  | 326593 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - NEL 3 reactive overload | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm state | 26593 |  | 326594 | Parameters - System - Monitoring - Single-line hazard - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26594 |  | 326595 | ID not present | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26595 |  | 326596 | Unsupported application | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26596 |  | 326597 | Application internal CAN protocol conflict | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26597 |  | 326598 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Section P> | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26598 |  | 326599 | Dry mode: Voltage level unexpected | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26599 |  | 326600 | Invalid DAVR configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26600 |  | 326601 | Parameters - Communication - DEIF network - DEIF network fork detected - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26602 |  | 326603 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26604 |  | 326605 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26604 |  | 326605 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Alarm state | 26604 |  | 326605 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm state | 26605 |  | 326606 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm state | 26605 |  | 326606 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm state | 26607 |  | 326608 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26608 |  | 326609 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26609 |  | 326610 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26610 |  | 326611 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26611 |  | 326612 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26612 |  | 326613 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26613 |  | 326614 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26614 |  | 326615 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26615 |  | 326616 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26616 |  | 326617 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26617 |  | 326618 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26618 |  | 326619 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26619 |  | 326620 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26620 |  | 326621 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26621 |  | 326622 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26622 |  | 326623 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26623 |  | 326624 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26624 |  | 326625 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26625 |  | 326626 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26626 |  | 326627 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26627 |  | 326628 | Live voltage detected | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26628 |  | 326629 | Internal issue detected. A restart is required soon! | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26629 |  | 326630 | Parameters - System - Monitoring - Missing controllers - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26630 |  | 326631 | Card issue detected | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26631 |  | 326632 | Card configuration failed | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26632 |  | 326633 | Unknown traffic on DEIF network | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26633 |  | 326634 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26634 |  | 326635 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26635 |  | 326636 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm state | 26636 |  | 326637 | Local I/O service error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26637 |  | 326638 | App logging failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26638 |  | 326639 | Event logging failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26639 |  | 326640 | Licence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26640 |  | 326641 | Brightness is dimmed according to temperature | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26641 |  | 326642 | Parameters - Grid code - Mains sync inhibit - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26642 |  | 326643 | Parameters - Grid code - Capability curve - Protections - Import protection - Information - Power import capability curve protection | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26643 |  | 326644 | Parameters - Grid code - Capability curve - Protections - Export protection - Information - Power export capability curve protection | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26644 |  | 326645 | Hardware is not compatible based on module versions | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 26645 |  | 326646 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 1 - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26646 |  | 326647 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 2 - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26647 |  | 326648 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 3 - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm state | 26680 |  | 326681 | Configuration not supported by licence | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27500 |  | 327501 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27501 |  | 327502 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27502 |  | 327503 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27503 |  | 327504 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27504 |  | 327505 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27505 |  | 327506 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27506 |  | 327507 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27507 |  | 327508 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27508 |  | 327509 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27509 |  | 327510 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27510 |  | 327511 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27511 |  | 327512 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27512 |  | 327513 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27513 |  | 327514 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27514 |  | 327515 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27515 |  | 327516 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27516 |  | 327517 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27517 |  | 327518 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27518 |  | 327519 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27519 |  | 327520 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27520 |  | 327521 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27521 |  | 327522 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27522 |  | 327523 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27523 |  | 327524 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27524 |  | 327525 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27525 |  | 327526 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27526 |  | 327527 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27527 |  | 327528 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27528 |  | 327529 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27529 |  | 327530 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27530 |  | 327531 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27531 |  | 327532 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27532 |  | 327533 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27533 |  | 327534 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27534 |  | 327535 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27535 |  | 327536 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27536 |  | 327537 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27537 |  | 327538 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27538 |  | 327539 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27539 |  | 327540 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27540 |  | 327541 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27541 |  | 327542 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27542 |  | 327543 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27543 |  | 327544 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27544 |  | 327545 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27545 |  | 327546 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27546 |  | 327547 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27547 |  | 327548 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27548 |  | 327549 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27549 |  | 327550 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27600 |  | 327601 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27601 |  | 327602 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27602 |  | 327603 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27603 |  | 327604 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27604 |  | 327605 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27605 |  | 327606 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27606 |  | 327607 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27607 |  | 327608 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27608 |  | 327609 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27609 |  | 327610 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27610 |  | 327611 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27611 |  | 327612 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27612 |  | 327613 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27613 |  | 327614 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27614 |  | 327615 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27615 |  | 327616 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27616 |  | 327617 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27617 |  | 327618 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27618 |  | 327619 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27619 |  | 327620 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27620 |  | 327621 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27621 |  | 327622 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27622 |  | 327623 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27623 |  | 327624 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27624 |  | 327625 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27625 |  | 327626 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27626 |  | 327627 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27627 |  | 327628 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27628 |  | 327629 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27629 |  | 327630 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27630 |  | 327631 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27631 |  | 327632 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27632 |  | 327633 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27633 |  | 327634 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27634 |  | 327635 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27635 |  | 327636 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27636 |  | 327637 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27637 |  | 327638 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27638 |  | 327639 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27639 |  | 327640 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27640 |  | 327641 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27641 |  | 327642 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27642 |  | 327643 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27643 |  | 327644 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27644 |  | 327645 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27645 |  | 327646 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27646 |  | 327647 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27647 |  | 327648 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27648 |  | 327649 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27649 |  | 327650 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27650 |  | 327651 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27651 |  | 327652 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27652 |  | 327653 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27653 |  | 327654 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27654 |  | 327655 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27655 |  | 327656 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27656 |  | 327657 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27657 |  | 327658 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27658 |  | 327659 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27659 |  | 327660 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27660 |  | 327661 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27661 |  | 327662 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27662 |  | 327663 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27663 |  | 327664 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27664 |  | 327665 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27665 |  | 327666 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27666 |  | 327667 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27667 |  | 327668 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27668 |  | 327669 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27669 |  | 327670 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27670 |  | 327671 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27671 |  | 327672 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27672 |  | 327673 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27673 |  | 327674 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27674 |  | 327675 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27675 |  | 327676 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27676 |  | 327677 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27677 |  | 327678 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27678 |  | 327679 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27679 |  | 327680 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27680 |  | 327681 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27681 |  | 327682 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27682 |  | 327683 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27683 |  | 327684 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27684 |  | 327685 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27685 |  | 327686 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27686 |  | 327687 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27687 |  | 327688 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27688 |  | 327689 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27689 |  | 327690 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27690 |  | 327691 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27691 |  | 327692 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27692 |  | 327693 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27693 |  | 327694 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27694 |  | 327695 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27695 |  | 327696 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27696 |  | 327697 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27697 |  | 327698 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27698 |  | 327699 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27699 |  | 327700 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27700 |  | 327701 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27701 |  | 327702 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27702 |  | 327703 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27703 |  | 327704 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27704 |  | 327705 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27705 |  | 327706 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27706 |  | 327707 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27707 |  | 327708 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27708 |  | 327709 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27709 |  | 327710 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27710 |  | 327711 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27711 |  | 327712 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27712 |  | 327713 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27713 |  | 327714 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27714 |  | 327715 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27715 |  | 327716 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27716 |  | 327717 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27717 |  | 327718 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27718 |  | 327719 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27719 |  | 327720 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27720 |  | 327721 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27721 |  | 327722 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27722 |  | 327723 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27723 |  | 327724 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27724 |  | 327725 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27725 |  | 327726 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27726 |  | 327727 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27727 |  | 327728 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27728 |  | 327729 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27729 |  | 327730 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27730 |  | 327731 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27731 |  | 327732 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27732 |  | 327733 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27733 |  | 327734 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27734 |  | 327735 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27735 |  | 327736 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27736 |  | 327737 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27737 |  | 327738 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27738 |  | 327739 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27739 |  | 327740 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27740 |  | 327741 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27741 |  | 327742 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27742 |  | 327743 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27743 |  | 327744 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27744 |  | 327745 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27745 |  | 327746 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27746 |  | 327747 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27747 |  | 327748 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27748 |  | 327749 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27749 |  | 327750 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27750 |  | 327751 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27751 |  | 327752 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27752 |  | 327753 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27753 |  | 327754 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27754 |  | 327755 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27755 |  | 327756 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27756 |  | 327757 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27757 |  | 327758 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27758 |  | 327759 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27759 |  | 327760 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27760 |  | 327761 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27761 |  | 327762 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27762 |  | 327763 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27763 |  | 327764 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27764 |  | 327765 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27765 |  | 327766 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27766 |  | 327767 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27767 |  | 327768 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27768 |  | 327769 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27769 |  | 327770 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27770 |  | 327771 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27771 |  | 327772 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27772 |  | 327773 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27773 |  | 327774 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27774 |  | 327775 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27775 |  | 327776 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27776 |  | 327777 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27777 |  | 327778 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27778 |  | 327779 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27779 |  | 327780 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27780 |  | 327781 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27781 |  | 327782 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27782 |  | 327783 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27783 |  | 327784 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27784 |  | 327785 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27785 |  | 327786 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27786 |  | 327787 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27787 |  | 327788 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27788 |  | 327789 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27789 |  | 327790 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27790 |  | 327791 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27791 |  | 327792 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27792 |  | 327793 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27793 |  | 327794 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27794 |  | 327795 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27795 |  | 327796 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27796 |  | 327797 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27797 |  | 327798 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27798 |  | 327799 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm state | 27799 |  | 327800 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28000 | 0 | 328001 | Application initialisation error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28000 | 1 | 328001 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28000 | 2 | 328001 | Preliminary software | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28000 | 3 | 328001 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28000 | 4 | 328001 | Parameters - Engine - Start sequence - Start failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28000 | 5 | 328001 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28000 | 6 | 328001 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28000 | 7 | 328001 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28000 | 8 | 328001 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28000 | 9 | 328001 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28000 | 10 | 328001 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28000 | 11 | 328001 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28000 | 13 | 328001 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28000 | 14 | 328001 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28000 | 15 | 328001 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28001 | 0 | 328002 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28001 | 1 | 328002 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28001 | 2 | 328002 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28001 | 3 | 328002 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28001 | 4 | 328002 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28001 | 5 | 328002 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28001 | 6 | 328002 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28001 | 11 | 328002 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28002 | 9 | 328003 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28002 | 9 | 328003 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28002 | 9 | 328003 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28002 | 10 | 328003 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28002 | 10 | 328003 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28002 | 10 | 328003 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28002 | 11 | 328003 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28002 | 11 | 328003 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28002 | 11 | 328003 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28002 | 12 | 328003 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28002 | 12 | 328003 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28002 | 12 | 328003 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28002 | 13 | 328003 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28002 | 13 | 328003 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28002 | 13 | 328003 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28002 | 14 | 328003 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28002 | 14 | 328003 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28002 | 14 | 328003 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28002 | 15 | 328003 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28002 | 15 | 328003 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28002 | 15 | 328003 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28003 | 0 | 328004 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28003 | 0 | 328004 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28003 | 0 | 328004 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28003 | 1 | 328004 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28003 | 1 | 328004 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm active | 28003 | 2 | 328004 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28003 | 2 | 328004 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm active | 28003 | 3 | 328004 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28003 | 3 | 328004 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm active | 28003 | 4 | 328004 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28003 | 4 | 328004 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm active | 28003 | 5 | 328004 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28003 | 5 | 328004 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm active | 28003 | 6 | 328004 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28003 | 6 | 328004 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm active | 28003 | 7 | 328004 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28003 | 7 | 328004 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm active | 28003 | 8 | 328004 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28003 | 8 | 328004 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm active | 28003 | 12 | 328004 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28003 | 12 | 328004 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28003 | 12 | 328004 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28003 | 13 | 328004 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28003 | 13 | 328004 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28003 | 13 | 328004 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28003 | 14 | 328004 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28006 | 7 | 328007 | Parameters - Mains - Additional protections - ROCOF - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28006 | 7 | 328007 | Parameters - Busbar - Additional protections - ROCOF - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28006 | 7 | 328007 | Parameters - Busbar B - Additional protections - ROCOF - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28006 | 8 | 328007 | Parameters - Mains - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28006 | 8 | 328007 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28006 | 8 | 328007 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28006 | 9 | 328007 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28006 | 9 | 328007 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28006 | 9 | 328007 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28006 | 10 | 328007 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28006 | 11 | 328007 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28006 | 12 | 328007 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28006 | 12 | 328007 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28006 | 12 | 328007 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28006 | 13 | 328007 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28006 | 13 | 328007 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28006 | 13 | 328007 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28006 | 14 | 328007 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28006 | 14 | 328007 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28006 | 14 | 328007 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28006 | 15 | 328007 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28006 | 15 | 328007 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28006 | 15 | 328007 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28007 | 3 | 328008 | Protection set point out of range | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 4 | 328008 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28007 | 5 | 328008 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28007 | 6 | 328008 | Protection set point out of range (differential current) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28007 | 7 | 328008 | Parameters - Local - Mode - Not under remote control - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 9 | 328008 | Parameters - Local - Monitoring - System not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 10 | 328008 | Configuration update delayed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 11 | 328008 | Critical process error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 12 | 328008 | Restore error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 13 | 328008 | SD-card format error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 14 | 328008 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28007 | 15 | 328008 | Fieldbus configuration exceeded maximum I/O configuration | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 0 | 328009 | Parameters - Custom alarms - Custom alarm 0 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 1 | 328009 | Parameters - Custom alarms - Custom alarm 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 2 | 328009 | Parameters - Custom alarms - Custom alarm 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 3 | 328009 | Parameters - Custom alarms - Custom alarm 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 4 | 328009 | Parameters - Custom alarms - Custom alarm 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 5 | 328009 | Parameters - Custom alarms - Custom alarm 5 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 6 | 328009 | Parameters - Custom alarms - Custom alarm 6 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 7 | 328009 | Parameters - Custom alarms - Custom alarm 7 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 8 | 328009 | Parameters - Custom alarms - Custom alarm 8 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 9 | 328009 | Parameters - Custom alarms - Custom alarm 9 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 10 | 328009 | Parameters - Custom alarms - Custom alarm 10 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 11 | 328009 | Parameters - Custom alarms - Custom alarm 11 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 12 | 328009 | Parameters - Custom alarms - Custom alarm 12 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 13 | 328009 | Parameters - Custom alarms - Custom alarm 13 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 14 | 328009 | Parameters - Custom alarms - Custom alarm 14 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28008 | 15 | 328009 | Parameters - Custom alarms - Custom alarm 15 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 0 | 328010 | Parameters - Custom alarms - Custom alarm 16 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 1 | 328010 | Parameters - Custom alarms - Custom alarm 17 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 2 | 328010 | Parameters - Custom alarms - Custom alarm 18 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 3 | 328010 | Parameters - Custom alarms - Custom alarm 19 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 4 | 328010 | Parameters - Custom alarms - Custom alarm 20 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 5 | 328010 | Parameters - Custom alarms - Custom alarm 21 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 6 | 328010 | Parameters - Custom alarms - Custom alarm 22 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 7 | 328010 | Parameters - Custom alarms - Custom alarm 23 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 8 | 328010 | Parameters - Custom alarms - Custom alarm 24 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28009 | 9 | 328010 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28009 | 10 | 328010 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28010 | 3 | 328011 | Required hardware card(s) not found | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28010 | 4 | 328011 | Software mismatch on hardware module(s) | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28010 | 5 | 328011 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm active | 28010 | 5 | 328011 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm active | 28010 | 5 | 328011 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28010 | 6 | 328011 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm active | 28010 | 6 | 328011 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28010 | 6 | 328011 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28010 | 7 | 328011 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm active | 28010 | 7 | 328011 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm active | 28010 | 7 | 328011 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28010 | 8 | 328011 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm active | 28010 | 8 | 328011 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm active | 28010 | 8 | 328011 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28010 | 9 | 328011 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm active | 28010 | 9 | 328011 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm active | 28010 | 9 | 328011 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28010 | 10 | 328011 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm active | 28010 | 10 | 328011 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28010 | 10 | 328011 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28010 | 11 | 328011 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm active | 28010 | 11 | 328011 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28010 | 11 | 328011 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28010 | 12 | 328011 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm active | 28010 | 12 | 328011 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28010 | 12 | 328011 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm active | 28011 | 2 | 328012 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm | BOOL | X * 1 | X * 1 |  |  |  | X | X |  | X | X
Alarm status: Alarm active | 28011 | 3 | 328012 | Parameters - Engine - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28011 | 3 | 328012 | Parameters - Busbar A - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28011 | 3 | 328012 | Parameters - Mains - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28011 | 4 | 328012 | Clock battery failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 5 | 328012 | Controller temperature too high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 6 | 328012 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 7 | 328012 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 8 | 328012 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 9 | 328012 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 10 | 328012 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 11 | 328012 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 12 | 328012 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 13 | 328012 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 14 | 328012 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28011 | 15 | 328012 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 0 | 328013 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 1 | 328013 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 2 | 328013 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 3 | 328013 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 4 | 328013 | EIM3.1 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 5 | 328013 | EIM3.1 4 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 6 | 328013 | EIM3.1 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 7 | 328013 | EIM3.1 5 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 8 | 328013 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 9 | 328013 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 10 | 328013 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 11 | 328013 | EIM3.1 4 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 12 | 328013 | EIM3.1 5 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 13 | 328013 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 14 | 328013 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28012 | 15 | 328013 | AC protections not running (differential current) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28013 | 0 | 328014 | AC data is missing (differential current) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28013 | 1 | 328014 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 2 | 328014 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 3 | 328014 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 4 | 328014 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 5 | 328014 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 6 | 328014 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 7 | 328014 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 8 | 328014 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 9 | 328014 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 10 | 328014 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 11 | 328014 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 12 | 328014 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 13 | 328014 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 14 | 328014 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28013 | 15 | 328014 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 0 | 328015 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 1 | 328015 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 2 | 328015 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 4 | 328015 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 5 | 328015 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 7 | 328015 | Controller ID not configured | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 12 | 328015 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28014 | 13 | 328015 | Blackout detection mismatch | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28015 | 0 | 328016 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28015 | 1 | 328016 | Parameters - Communication - NTP - NTP server 1 not responding - Information - Flags - NTP server 1 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28015 | 2 | 328016 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28015 | 3 | 328016 | Parameters - Communication - NTP - NTP server 2 not responding - Information - Flags - NTP server 2 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28015 | 4 | 328016 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28015 | 5 | 328016 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28015 | 6 | 328016 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28015 | 7 | 328016 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28018 | 8 | 328019 | Controller not part of system | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28018 | 9 | 328019 | Different single-line configurations | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28018 | 10 | 328019 | Single-line missing/none active | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28018 | 11 | 328019 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28018 | 12 | 328019 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28018 | 13 | 328019 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28018 | 14 | 328019 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28018 | 15 | 328019 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28019 | 0 | 328020 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28019 | 1 | 328020 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28019 | 2 | 328020 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28019 | 3 | 328020 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28019 | 4 | 328020 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28019 | 5 | 328020 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28019 | 6 | 328020 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28019 | 7 | 328020 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28019 | 8 | 328020 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28019 | 11 | 328020 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28019 | 12 | 328020 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28019 | 13 | 328020 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28019 | 14 | 328020 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28019 | 15 | 328020 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 0 | 328021 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 1 | 328021 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 2 | 328021 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 3 | 328021 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 4 | 328021 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 5 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 6 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 7 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 8 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 9 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 10 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 11 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 12 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 13 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 14 | 328021 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28020 | 15 | 328021 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 0 | 328022 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 1 | 328022 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 2 | 328022 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 3 | 328022 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 4 | 328022 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 5 | 328022 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 6 | 328022 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 7 | 328022 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 8 | 328022 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 9 | 328022 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 10 | 328022 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 11 | 328022 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 12 | 328022 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 13 | 328022 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 14 | 328022 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28021 | 15 | 328022 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 0 | 328023 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 1 | 328023 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 2 | 328023 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 3 | 328023 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 4 | 328023 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 5 | 328023 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 6 | 328023 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 7 | 328023 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 8 | 328023 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 9 | 328023 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 10 | 328023 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 11 | 328023 | DAVR unsupported AC configuration | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 12 | 328023 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 13 | 328023 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 13 | 328023 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28022 | 13 | 328023 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28022 | 14 | 328023 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 14 | 328023 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28022 | 14 | 328023 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28022 | 15 | 328023 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28022 | 15 | 328023 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28022 | 15 | 328023 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 0 | 328024 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 0 | 328024 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 0 | 328024 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 1 | 328024 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 1 | 328024 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 1 | 328024 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 2 | 328024 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 2 | 328024 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 2 | 328024 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 3 | 328024 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 3 | 328024 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 3 | 328024 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 4 | 328024 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 4 | 328024 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 4 | 328024 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 5 | 328024 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 5 | 328024 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 5 | 328024 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 6 | 328024 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 6 | 328024 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 6 | 328024 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 7 | 328024 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 7 | 328024 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 7 | 328024 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 8 | 328024 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 8 | 328024 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 8 | 328024 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 9 | 328024 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 9 | 328024 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 9 | 328024 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 10 | 328024 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 10 | 328024 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 10 | 328024 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 11 | 328024 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 11 | 328024 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 11 | 328024 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 12 | 328024 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 12 | 328024 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 12 | 328024 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 13 | 328024 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 13 | 328024 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 13 | 328024 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 14 | 328024 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 14 | 328024 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 14 | 328024 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28023 | 15 | 328024 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28023 | 15 | 328024 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28023 | 15 | 328024 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28024 | 0 | 328025 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 1 | 328025 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 2 | 328025 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28024 | 2 | 328025 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 2 | 328025 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28024 | 3 | 328025 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28024 | 3 | 328025 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 3 | 328025 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28024 | 4 | 328025 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28024 | 4 | 328025 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 4 | 328025 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28024 | 5 | 328025 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28024 | 5 | 328025 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 5 | 328025 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28024 | 6 | 328025 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28024 | 6 | 328025 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 6 | 328025 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28024 | 7 | 328025 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28024 | 7 | 328025 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 7 | 328025 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28024 | 8 | 328025 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28024 | 8 | 328025 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 8 | 328025 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28024 | 9 | 328025 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28024 | 9 | 328025 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 9 | 328025 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28024 | 10 | 328025 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28024 | 10 | 328025 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 10 | 328025 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28024 | 11 | 328025 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28024 | 11 | 328025 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 11 | 328025 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28024 | 12 | 328025 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28024 | 12 | 328025 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 12 | 328025 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28024 | 13 | 328025 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28024 | 13 | 328025 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 13 | 328025 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28024 | 14 | 328025 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28024 | 14 | 328025 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 14 | 328025 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28024 | 15 | 328025 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28024 | 15 | 328025 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28024 | 15 | 328025 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28025 | 0 | 328026 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28025 | 0 | 328026 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28025 | 0 | 328026 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28025 | 1 | 328026 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28025 | 1 | 328026 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28025 | 1 | 328026 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28025 | 2 | 328026 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28025 | 2 | 328026 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28025 | 2 | 328026 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28025 | 3 | 328026 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28025 | 3 | 328026 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28025 | 3 | 328026 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28025 | 4 | 328026 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28025 | 4 | 328026 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28025 | 4 | 328026 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28025 | 5 | 328026 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28025 | 5 | 328026 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28025 | 5 | 328026 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28025 | 6 | 328026 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28025 | 6 | 328026 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28025 | 6 | 328026 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28025 | 7 | 328026 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28025 | 7 | 328026 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28025 | 7 | 328026 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28025 | 8 | 328026 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28025 | 8 | 328026 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28025 | 8 | 328026 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28025 | 9 | 328026 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28025 | 9 | 328026 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28025 | 9 | 328026 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28025 | 10 | 328026 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28025 | 10 | 328026 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28025 | 10 | 328026 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28025 | 11 | 328026 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28025 | 11 | 328026 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28025 | 11 | 328026 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28025 | 12 | 328026 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28025 | 12 | 328026 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28025 | 12 | 328026 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28025 | 13 | 328026 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28025 | 13 | 328026 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28025 | 13 | 328026 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28025 | 14 | 328026 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28025 | 14 | 328026 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28025 | 14 | 328026 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28025 | 15 | 328026 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28025 | 15 | 328026 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28025 | 15 | 328026 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28026 | 0 | 328027 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28026 | 0 | 328027 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28026 | 0 | 328027 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28026 | 1 | 328027 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28026 | 1 | 328027 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28026 | 1 | 328027 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28026 | 2 | 328027 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28026 | 2 | 328027 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28026 | 2 | 328027 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28026 | 3 | 328027 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28026 | 3 | 328027 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28026 | 3 | 328027 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28026 | 4 | 328027 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28026 | 4 | 328027 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28026 | 4 | 328027 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28026 | 5 | 328027 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28026 | 5 | 328027 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28026 | 5 | 328027 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28026 | 6 | 328027 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28026 | 6 | 328027 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm active | 28026 | 6 | 328027 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28029 | 3 | 328030 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28029 | 4 | 328030 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28029 | 5 | 328030 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28029 | 6 | 328030 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 4 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28029 | 7 | 328030 | External MB open failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28029 | 8 | 328030 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28029 | 9 | 328030 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28029 | 10 | 328030 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28029 | 11 | 328030 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28029 | 12 | 328030 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28029 | 13 | 328030 | Parameters - Breakers - Close before excitation - CBE failure - Information - Flags - Close before excitation failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28029 | 14 | 328030 | Load too high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28029 | 15 | 328030 | ID to run configuration failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28030 | 1 | 328031 | Parameters - System - Monitoring - Missing any genset controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28030 | 2 | 328031 | Parameters - System - Monitoring - Missing any mains controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28030 | 3 | 328031 | Parameters - System - Monitoring - Missing any bus tie controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28030 | 4 | 328031 | Can ID not available | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28030 | 5 | 328031 | Duplicated CAN IDs | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28030 | 6 | 328031 | Parameters - Local power management - Alarms - Busbar blocked - Information - Flags - Busbar blocked due to position failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28030 | 7 | 328031 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Flags - Busbar A blocked due to position failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28030 | 8 | 328031 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Flags - Busbar B blocked due to position failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28030 | 9 | 328031 | Parameters - System - Monitoring - BTB 33 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28030 | 10 | 328031 | Parameters - System - Monitoring - BTB 34 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28030 | 11 | 328031 | Parameters - System - Monitoring - BTB 35 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28030 | 12 | 328031 | Parameters - System - Monitoring - BTB 36 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28030 | 13 | 328031 | Parameters - System - Monitoring - BTB 37 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28030 | 14 | 328031 | Parameters - System - Monitoring - BTB 38 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28030 | 15 | 328031 | Parameters - System - Monitoring - BTB 39 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 0 | 328032 | Parameters - System - Monitoring - BTB 40 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 1 | 328032 | Primary CAN missing ID 1 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 2 | 328032 | Primary CAN missing ID 2 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 3 | 328032 | Primary CAN missing ID 3 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 4 | 328032 | Primary CAN missing ID 4 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 5 | 328032 | Primary CAN missing ID 5 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 6 | 328032 | Primary CAN missing ID 6 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 7 | 328032 | Primary CAN missing ID 7 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 8 | 328032 | Primary CAN missing ID 8 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 9 | 328032 | Primary CAN missing ID 9 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 10 | 328032 | Primary CAN missing ID 10 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 11 | 328032 | Primary CAN missing ID 11 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 12 | 328032 | Primary CAN missing ID 12 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 13 | 328032 | Primary CAN missing ID 13 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 14 | 328032 | Primary CAN missing ID 14 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28031 | 15 | 328032 | Primary CAN missing ID 15 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 0 | 328033 | Primary CAN missing ID 16 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 1 | 328033 | Primary CAN missing ID 17 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 2 | 328033 | Primary CAN missing ID 18 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 3 | 328033 | Primary CAN missing ID 19 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 4 | 328033 | Primary CAN missing ID 20 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 5 | 328033 | Primary CAN missing ID 21 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 6 | 328033 | Primary CAN missing ID 22 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 7 | 328033 | Primary CAN missing ID 23 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 8 | 328033 | Primary CAN missing ID 24 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 9 | 328033 | Primary CAN missing ID 25 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 10 | 328033 | Primary CAN missing ID 26 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 11 | 328033 | Primary CAN missing ID 27 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 12 | 328033 | Primary CAN missing ID 28 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 13 | 328033 | Primary CAN missing ID 29 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 14 | 328033 | Primary CAN missing ID 30 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28032 | 15 | 328033 | Primary CAN missing ID 31 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 0 | 328034 | Primary CAN missing ID 32 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 1 | 328034 | Primary CAN missing ID 33 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 2 | 328034 | Primary CAN missing ID 34 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 3 | 328034 | Primary CAN missing ID 35 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 4 | 328034 | Primary CAN missing ID 36 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 5 | 328034 | Primary CAN missing ID 37 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 6 | 328034 | Primary CAN missing ID 38 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 7 | 328034 | Primary CAN missing ID 39 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 8 | 328034 | Primary CAN missing ID 40 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 9 | 328034 | Secondary CAN missing ID 1 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 10 | 328034 | Secondary CAN missing ID 2 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 11 | 328034 | Secondary CAN missing ID 3 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 12 | 328034 | Secondary CAN missing ID 4 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 13 | 328034 | Secondary CAN missing ID 5 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 14 | 328034 | Secondary CAN missing ID 6 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28033 | 15 | 328034 | Secondary CAN missing ID 7 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 0 | 328035 | Secondary CAN missing ID 8 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 1 | 328035 | Secondary CAN missing ID 9 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 2 | 328035 | Secondary CAN missing ID 10 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 3 | 328035 | Secondary CAN missing ID 11 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 4 | 328035 | Secondary CAN missing ID 12 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 5 | 328035 | Secondary CAN missing ID 13 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 6 | 328035 | Secondary CAN missing ID 14 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 7 | 328035 | Secondary CAN missing ID 15 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 8 | 328035 | Secondary CAN missing ID 16 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 9 | 328035 | Secondary CAN missing ID 17 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 10 | 328035 | Secondary CAN missing ID 18 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 11 | 328035 | Secondary CAN missing ID 19 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 12 | 328035 | Secondary CAN missing ID 20 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 13 | 328035 | Secondary CAN missing ID 21 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 14 | 328035 | Secondary CAN missing ID 22 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28034 | 15 | 328035 | Secondary CAN missing ID 23 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 0 | 328036 | Secondary CAN missing ID 24 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 1 | 328036 | Secondary CAN missing ID 25 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 2 | 328036 | Secondary CAN missing ID 26 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 3 | 328036 | Secondary CAN missing ID 27 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 4 | 328036 | Secondary CAN missing ID 28 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 5 | 328036 | Secondary CAN missing ID 29 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 6 | 328036 | Secondary CAN missing ID 30 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 7 | 328036 | Secondary CAN missing ID 31 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 8 | 328036 | Secondary CAN missing ID 32 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 9 | 328036 | Secondary CAN missing ID 33 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 10 | 328036 | Secondary CAN missing ID 34 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 11 | 328036 | Secondary CAN missing ID 35 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 12 | 328036 | Secondary CAN missing ID 36 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 13 | 328036 | Secondary CAN missing ID 37 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 14 | 328036 | Secondary CAN missing ID 38 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28035 | 15 | 328036 | Secondary CAN missing ID 39 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28036 | 0 | 328037 | Secondary CAN missing ID 40 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28036 | 1 | 328037 | Priority error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28036 | 2 | 328037 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - Flags - NEL 1 over-current | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28036 | 3 | 328037 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - Flags - NEL 1 under-frequency | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28036 | 4 | 328037 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - Flags - NEL 1 overload 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28036 | 5 | 328037 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - Flags - NEL 1 overload 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28036 | 6 | 328037 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - Flags - NEL 1 reactive overload | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28036 | 7 | 328037 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - Flags - NEL 2 over-current | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28036 | 8 | 328037 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - Flags - NEL 2 under-frequency | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28036 | 9 | 328037 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - Flags - NEL 2 overload 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28036 | 10 | 328037 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - Flags - NEL 2 overload 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28036 | 11 | 328037 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - Flags - NEL 2 reactive overload | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28036 | 12 | 328037 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - Flags - NEL 3 over-current | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28036 | 13 | 328037 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - Flags - NEL 3 under-frequency | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28036 | 14 | 328037 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - Flags - NEL 3 overload 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28036 | 15 | 328037 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - Flags - NEL 3 overload 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28037 | 0 | 328038 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - Flags - NEL 3 reactive overload | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm active | 28037 | 1 | 328038 | Parameters - System - Monitoring - Single-line hazard - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28037 | 2 | 328038 | ID not present | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28037 | 3 | 328038 | Unsupported application | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28037 | 4 | 328038 | Application internal CAN protocol conflict | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28037 | 5 | 328038 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Flags - Section P> | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28037 | 6 | 328038 | Dry mode: Voltage level unexpected | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28037 | 7 | 328038 | Invalid DAVR configuration | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28037 | 8 | 328038 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28037 | 10 | 328038 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28037 | 12 | 328038 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28037 | 12 | 328038 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm active | 28037 | 12 | 328038 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm active | 28037 | 13 | 328038 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm active | 28037 | 13 | 328038 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm active | 28037 | 15 | 328038 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 0 | 328039 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 1 | 328039 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 2 | 328039 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 3 | 328039 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 4 | 328039 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 5 | 328039 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 6 | 328039 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 7 | 328039 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 8 | 328039 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 9 | 328039 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 10 | 328039 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 11 | 328039 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 12 | 328039 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 13 | 328039 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 14 | 328039 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28038 | 15 | 328039 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 0 | 328040 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 1 | 328040 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 2 | 328040 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 3 | 328040 | Live voltage detected | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 4 | 328040 | Internal issue detected. A restart is required soon! | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 5 | 328040 | Parameters - System - Monitoring - Missing controllers - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 6 | 328040 | Card issue detected | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 7 | 328040 | Card configuration failed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 8 | 328040 | Unknown traffic on DEIF network | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 9 | 328040 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28039 | 10 | 328040 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28039 | 11 | 328040 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm active | 28039 | 12 | 328040 | Local I/O service error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 13 | 328040 | App logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 14 | 328040 | Event logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28039 | 15 | 328040 | Licence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28040 | 0 | 328041 | Brightness is dimmed according to temperature | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28040 | 1 | 328041 | Parameters - Grid code - Mains sync inhibit - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28040 | 2 | 328041 | Parameters - Grid code - Capability curve - Protections - Import protection - Information - Flags - Power import capability curve protection | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28040 | 3 | 328041 | Parameters - Grid code - Capability curve - Protections - Export protection - Information - Flags - Power export capability curve protection | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28040 | 4 | 328041 | Hardware is not compatible based on module versions | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28040 | 5 | 328041 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28040 | 6 | 328041 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28040 | 7 | 328041 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm active | 28042 | 8 | 328043 | Configuration not supported by licence | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28093 | 12 | 328094 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28093 | 13 | 328094 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28093 | 14 | 328094 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28093 | 15 | 328094 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 0 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 1 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 2 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 3 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 4 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 5 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 6 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 7 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 8 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 9 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 10 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 11 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 12 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 13 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 14 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28094 | 15 | 328095 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 0 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 1 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 2 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 3 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 4 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 5 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 6 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 7 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 8 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 9 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 10 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 11 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 12 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 13 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 14 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28095 | 15 | 328096 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 0 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 1 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 2 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 3 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 4 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 5 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 6 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 7 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 8 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 9 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 10 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 11 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 12 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28096 | 13 | 328097 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 0 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 1 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 2 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 3 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 4 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 5 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 6 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 7 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 8 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 9 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 10 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 11 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 12 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 13 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 14 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28100 | 15 | 328101 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 0 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 1 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 2 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 3 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 4 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 5 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 6 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 7 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 8 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 9 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 10 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 11 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 12 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 13 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 14 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28101 | 15 | 328102 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 0 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 1 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 2 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 3 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 4 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 5 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 6 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 7 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 8 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 9 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 10 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 11 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 12 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 13 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 14 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28102 | 15 | 328103 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 0 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 1 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 2 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 3 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 4 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 5 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 6 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 7 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 8 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 9 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 10 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 11 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 12 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 13 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 14 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28103 | 15 | 328104 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 0 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 1 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 2 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 3 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 4 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 5 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 6 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 7 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 8 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 9 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 10 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 11 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 12 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 13 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 14 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28104 | 15 | 328105 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 0 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 1 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 2 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 3 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 4 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 5 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 6 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 7 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 8 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 9 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 10 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 11 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 12 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 13 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 14 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28105 | 15 | 328106 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 0 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 1 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 2 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 3 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 4 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 5 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 6 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 7 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 8 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 9 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 10 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 11 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 12 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 13 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 14 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28106 | 15 | 328107 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 0 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 1 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 2 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 3 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 4 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 5 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 6 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 7 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 8 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 9 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 10 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 11 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 12 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 13 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 14 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28107 | 15 | 328108 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 0 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 1 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 2 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 3 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 4 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 5 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 6 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 7 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 8 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 9 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 10 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 11 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 12 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 13 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 14 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28108 | 15 | 328109 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 0 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 1 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 2 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 3 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 4 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 5 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 6 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 7 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 8 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 9 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 10 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 11 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 12 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 13 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 14 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28109 | 15 | 328110 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 0 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 1 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 2 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 3 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 4 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 5 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 6 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 7 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 8 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 9 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 10 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 11 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 12 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 13 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 14 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28110 | 15 | 328111 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 0 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 1 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 2 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 3 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 4 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 5 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 6 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 7 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 8 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 9 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 10 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 11 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 12 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 13 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 14 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28111 | 15 | 328112 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 0 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 1 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 2 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 3 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 4 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 5 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 6 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm active | 28112 | 7 | 328113 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28125 | 0 | 328126 | Application initialisation error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28125 | 1 | 328126 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28125 | 2 | 328126 | Preliminary software | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28125 | 3 | 328126 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 4 | 328126 | Parameters - Engine - Start sequence - Start failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 5 | 328126 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 6 | 328126 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 7 | 328126 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 8 | 328126 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 9 | 328126 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 10 | 328126 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 11 | 328126 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 13 | 328126 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 14 | 328126 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28125 | 15 | 328126 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 0 | 328127 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 1 | 328127 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 2 | 328127 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 3 | 328127 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 4 | 328127 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 5 | 328127 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 6 | 328127 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28126 | 11 | 328127 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 9 | 328128 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 9 | 328128 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28127 | 9 | 328128 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28127 | 10 | 328128 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 10 | 328128 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28127 | 10 | 328128 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28127 | 11 | 328128 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 11 | 328128 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28127 | 11 | 328128 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28127 | 12 | 328128 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 12 | 328128 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28127 | 12 | 328128 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28127 | 13 | 328128 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 13 | 328128 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28127 | 13 | 328128 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28127 | 14 | 328128 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 14 | 328128 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28127 | 14 | 328128 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28127 | 15 | 328128 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28127 | 15 | 328128 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28127 | 15 | 328128 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28128 | 0 | 328129 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28128 | 0 | 328129 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28128 | 0 | 328129 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28128 | 1 | 328129 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28128 | 1 | 328129 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm acknowledged | 28128 | 2 | 328129 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28128 | 2 | 328129 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm acknowledged | 28128 | 3 | 328129 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28128 | 3 | 328129 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm acknowledged | 28128 | 4 | 328129 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28128 | 4 | 328129 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm acknowledged | 28128 | 5 | 328129 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28128 | 5 | 328129 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm acknowledged | 28128 | 6 | 328129 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28128 | 6 | 328129 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm acknowledged | 28128 | 7 | 328129 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28128 | 7 | 328129 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm acknowledged | 28128 | 8 | 328129 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28128 | 8 | 328129 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm acknowledged | 28128 | 12 | 328129 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28128 | 12 | 328129 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28128 | 12 | 328129 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28128 | 13 | 328129 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28128 | 13 | 328129 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28128 | 13 | 328129 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28128 | 14 | 328129 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28131 | 7 | 328132 | Parameters - Mains - Additional protections - ROCOF - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28131 | 7 | 328132 | Parameters - Busbar - Additional protections - ROCOF - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28131 | 7 | 328132 | Parameters - Busbar B - Additional protections - ROCOF - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28131 | 8 | 328132 | Parameters - Mains - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28131 | 8 | 328132 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28131 | 8 | 328132 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28131 | 9 | 328132 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28131 | 9 | 328132 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28131 | 9 | 328132 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28131 | 10 | 328132 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28131 | 11 | 328132 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28131 | 12 | 328132 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28131 | 12 | 328132 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28131 | 12 | 328132 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28131 | 13 | 328132 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28131 | 13 | 328132 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28131 | 13 | 328132 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28131 | 14 | 328132 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28131 | 14 | 328132 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28131 | 14 | 328132 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28131 | 15 | 328132 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28131 | 15 | 328132 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28131 | 15 | 328132 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28132 | 3 | 328133 | Protection set point out of range | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 4 | 328133 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28132 | 5 | 328133 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28132 | 6 | 328133 | Protection set point out of range (differential current) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28132 | 7 | 328133 | Parameters - Local - Mode - Not under remote control - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 9 | 328133 | Parameters - Local - Monitoring - System not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 10 | 328133 | Configuration update delayed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 11 | 328133 | Critical process error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 12 | 328133 | Restore error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 13 | 328133 | SD-card format error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 14 | 328133 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28132 | 15 | 328133 | Fieldbus configuration exceeded maximum I/O configuration | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 0 | 328134 | Parameters - Custom alarms - Custom alarm 0 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 1 | 328134 | Parameters - Custom alarms - Custom alarm 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 2 | 328134 | Parameters - Custom alarms - Custom alarm 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 3 | 328134 | Parameters - Custom alarms - Custom alarm 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 4 | 328134 | Parameters - Custom alarms - Custom alarm 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 5 | 328134 | Parameters - Custom alarms - Custom alarm 5 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 6 | 328134 | Parameters - Custom alarms - Custom alarm 6 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 7 | 328134 | Parameters - Custom alarms - Custom alarm 7 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 8 | 328134 | Parameters - Custom alarms - Custom alarm 8 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 9 | 328134 | Parameters - Custom alarms - Custom alarm 9 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 10 | 328134 | Parameters - Custom alarms - Custom alarm 10 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 11 | 328134 | Parameters - Custom alarms - Custom alarm 11 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 12 | 328134 | Parameters - Custom alarms - Custom alarm 12 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 13 | 328134 | Parameters - Custom alarms - Custom alarm 13 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 14 | 328134 | Parameters - Custom alarms - Custom alarm 14 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28133 | 15 | 328134 | Parameters - Custom alarms - Custom alarm 15 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 0 | 328135 | Parameters - Custom alarms - Custom alarm 16 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 1 | 328135 | Parameters - Custom alarms - Custom alarm 17 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 2 | 328135 | Parameters - Custom alarms - Custom alarm 18 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 3 | 328135 | Parameters - Custom alarms - Custom alarm 19 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 4 | 328135 | Parameters - Custom alarms - Custom alarm 20 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 5 | 328135 | Parameters - Custom alarms - Custom alarm 21 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 6 | 328135 | Parameters - Custom alarms - Custom alarm 22 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 7 | 328135 | Parameters - Custom alarms - Custom alarm 23 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 8 | 328135 | Parameters - Custom alarms - Custom alarm 24 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28134 | 9 | 328135 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28134 | 10 | 328135 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28135 | 3 | 328136 | Required hardware card(s) not found | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28135 | 4 | 328136 | Software mismatch on hardware module(s) | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28135 | 5 | 328136 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm acknowledged | 28135 | 5 | 328136 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm acknowledged | 28135 | 5 | 328136 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28135 | 6 | 328136 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm acknowledged | 28135 | 6 | 328136 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28135 | 6 | 328136 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28135 | 7 | 328136 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm acknowledged | 28135 | 7 | 328136 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm acknowledged | 28135 | 7 | 328136 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28135 | 8 | 328136 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm acknowledged | 28135 | 8 | 328136 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm acknowledged | 28135 | 8 | 328136 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28135 | 9 | 328136 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm acknowledged | 28135 | 9 | 328136 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm acknowledged | 28135 | 9 | 328136 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28135 | 10 | 328136 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm acknowledged | 28135 | 10 | 328136 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28135 | 10 | 328136 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28135 | 11 | 328136 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm acknowledged | 28135 | 11 | 328136 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28135 | 11 | 328136 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28135 | 12 | 328136 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm acknowledged | 28135 | 12 | 328136 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28135 | 12 | 328136 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm acknowledged | 28136 | 2 | 328137 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm | BOOL | X * 1 | X * 1 |  |  |  | X | X |  | X | X
Alarm status: Alarm acknowledged | 28136 | 3 | 328137 | Parameters - Engine - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28136 | 3 | 328137 | Parameters - Busbar A - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28136 | 3 | 328137 | Parameters - Mains - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28136 | 4 | 328137 | Clock battery failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 5 | 328137 | Controller temperature too high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 6 | 328137 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 7 | 328137 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 8 | 328137 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 9 | 328137 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 10 | 328137 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 11 | 328137 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 12 | 328137 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 13 | 328137 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 14 | 328137 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28136 | 15 | 328137 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 0 | 328138 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 1 | 328138 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 2 | 328138 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 3 | 328138 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 4 | 328138 | EIM3.1 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 5 | 328138 | EIM3.1 4 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 6 | 328138 | EIM3.1 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 7 | 328138 | EIM3.1 5 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 8 | 328138 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 9 | 328138 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 10 | 328138 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 11 | 328138 | EIM3.1 4 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 12 | 328138 | EIM3.1 5 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 13 | 328138 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 14 | 328138 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28137 | 15 | 328138 | AC protections not running (differential current) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28138 | 0 | 328139 | AC data is missing (differential current) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28138 | 1 | 328139 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 2 | 328139 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 3 | 328139 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 4 | 328139 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 5 | 328139 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 6 | 328139 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 7 | 328139 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 8 | 328139 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 9 | 328139 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 10 | 328139 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 11 | 328139 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 12 | 328139 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 13 | 328139 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 14 | 328139 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28138 | 15 | 328139 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 0 | 328140 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 1 | 328140 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 2 | 328140 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 4 | 328140 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 5 | 328140 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 7 | 328140 | Controller ID not configured | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 12 | 328140 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28139 | 13 | 328140 | Blackout detection mismatch | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28140 | 0 | 328141 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 1 | 328141 | Parameters - Communication - NTP - NTP server 1 not responding - Information - Flags - NTP server 1 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 2 | 328141 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 3 | 328141 | Parameters - Communication - NTP - NTP server 2 not responding - Information - Flags - NTP server 2 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 4 | 328141 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 5 | 328141 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 6 | 328141 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28140 | 7 | 328141 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28143 | 8 | 328144 | Controller not part of system | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28143 | 9 | 328144 | Different single-line configurations | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28143 | 10 | 328144 | Single-line missing/none active | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28143 | 11 | 328144 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28143 | 12 | 328144 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28143 | 13 | 328144 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28143 | 14 | 328144 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28143 | 15 | 328144 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 0 | 328145 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 1 | 328145 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 2 | 328145 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 3 | 328145 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 4 | 328145 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 5 | 328145 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 6 | 328145 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 7 | 328145 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28144 | 8 | 328145 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28144 | 11 | 328145 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28144 | 12 | 328145 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 13 | 328145 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 14 | 328145 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28144 | 15 | 328145 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 0 | 328146 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 1 | 328146 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 2 | 328146 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 3 | 328146 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 4 | 328146 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 5 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 6 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 7 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 8 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 9 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 10 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 11 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 12 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 13 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 14 | 328146 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28145 | 15 | 328146 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 0 | 328147 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 1 | 328147 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 2 | 328147 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 3 | 328147 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 4 | 328147 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 5 | 328147 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 6 | 328147 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 7 | 328147 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 8 | 328147 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 9 | 328147 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 10 | 328147 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 11 | 328147 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 12 | 328147 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 13 | 328147 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 14 | 328147 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28146 | 15 | 328147 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 0 | 328148 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 1 | 328148 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 2 | 328148 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 3 | 328148 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 4 | 328148 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 5 | 328148 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 6 | 328148 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 7 | 328148 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 8 | 328148 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 9 | 328148 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 10 | 328148 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 11 | 328148 | DAVR unsupported AC configuration | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 12 | 328148 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 13 | 328148 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 13 | 328148 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28147 | 13 | 328148 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28147 | 14 | 328148 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 14 | 328148 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28147 | 14 | 328148 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28147 | 15 | 328148 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28147 | 15 | 328148 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28147 | 15 | 328148 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 0 | 328149 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 0 | 328149 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 0 | 328149 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 1 | 328149 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 1 | 328149 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 1 | 328149 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 2 | 328149 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 2 | 328149 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 2 | 328149 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 3 | 328149 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 3 | 328149 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 3 | 328149 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 4 | 328149 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 4 | 328149 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 4 | 328149 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 5 | 328149 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 5 | 328149 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 5 | 328149 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 6 | 328149 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 6 | 328149 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 6 | 328149 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 7 | 328149 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 7 | 328149 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 7 | 328149 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 8 | 328149 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 8 | 328149 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 8 | 328149 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 9 | 328149 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 9 | 328149 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 9 | 328149 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 10 | 328149 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 10 | 328149 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 10 | 328149 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 11 | 328149 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 11 | 328149 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 11 | 328149 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 12 | 328149 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 12 | 328149 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 12 | 328149 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 13 | 328149 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 13 | 328149 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 13 | 328149 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 14 | 328149 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 14 | 328149 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 14 | 328149 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28148 | 15 | 328149 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28148 | 15 | 328149 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28148 | 15 | 328149 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 0 | 328150 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 1 | 328150 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 2 | 328150 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 2 | 328150 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 2 | 328150 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 3 | 328150 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 3 | 328150 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 3 | 328150 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 4 | 328150 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 4 | 328150 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 4 | 328150 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 5 | 328150 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 5 | 328150 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 5 | 328150 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 6 | 328150 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 6 | 328150 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 6 | 328150 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 7 | 328150 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 7 | 328150 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 7 | 328150 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 8 | 328150 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 8 | 328150 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 8 | 328150 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 9 | 328150 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 9 | 328150 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 9 | 328150 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 10 | 328150 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 10 | 328150 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 10 | 328150 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 11 | 328150 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 11 | 328150 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 11 | 328150 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 12 | 328150 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 12 | 328150 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 12 | 328150 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 13 | 328150 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 13 | 328150 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 13 | 328150 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 14 | 328150 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 14 | 328150 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 14 | 328150 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28149 | 15 | 328150 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28149 | 15 | 328150 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28149 | 15 | 328150 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28150 | 0 | 328151 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 0 | 328151 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28150 | 0 | 328151 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28150 | 1 | 328151 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 1 | 328151 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28150 | 1 | 328151 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28150 | 2 | 328151 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 2 | 328151 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28150 | 2 | 328151 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28150 | 3 | 328151 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 3 | 328151 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28150 | 3 | 328151 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28150 | 4 | 328151 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 4 | 328151 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28150 | 4 | 328151 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28150 | 5 | 328151 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28150 | 5 | 328151 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 5 | 328151 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28150 | 6 | 328151 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28150 | 6 | 328151 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 6 | 328151 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28150 | 7 | 328151 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28150 | 7 | 328151 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 7 | 328151 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28150 | 8 | 328151 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28150 | 8 | 328151 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 8 | 328151 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28150 | 9 | 328151 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28150 | 9 | 328151 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 9 | 328151 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28150 | 10 | 328151 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28150 | 10 | 328151 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 10 | 328151 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28150 | 11 | 328151 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28150 | 11 | 328151 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 11 | 328151 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28150 | 12 | 328151 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28150 | 12 | 328151 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 12 | 328151 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28150 | 13 | 328151 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28150 | 13 | 328151 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 13 | 328151 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28150 | 14 | 328151 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28150 | 14 | 328151 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 14 | 328151 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28150 | 15 | 328151 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28150 | 15 | 328151 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28150 | 15 | 328151 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28151 | 0 | 328152 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28151 | 0 | 328152 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28151 | 0 | 328152 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28151 | 1 | 328152 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28151 | 1 | 328152 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28151 | 1 | 328152 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28151 | 2 | 328152 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28151 | 2 | 328152 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28151 | 2 | 328152 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28151 | 3 | 328152 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28151 | 3 | 328152 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28151 | 3 | 328152 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28151 | 4 | 328152 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28151 | 4 | 328152 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28151 | 4 | 328152 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28151 | 5 | 328152 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28151 | 5 | 328152 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28151 | 5 | 328152 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28151 | 6 | 328152 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28151 | 6 | 328152 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm acknowledged | 28151 | 6 | 328152 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28154 | 3 | 328155 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28154 | 4 | 328155 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28154 | 5 | 328155 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28154 | 6 | 328155 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 4 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28154 | 7 | 328155 | External MB open failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28154 | 8 | 328155 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28154 | 9 | 328155 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28154 | 10 | 328155 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28154 | 11 | 328155 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28154 | 12 | 328155 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28154 | 13 | 328155 | Parameters - Breakers - Close before excitation - CBE failure - Information - Flags - Close before excitation failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28154 | 14 | 328155 | Load too high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28154 | 15 | 328155 | ID to run configuration failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28155 | 1 | 328156 | Parameters - System - Monitoring - Missing any genset controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28155 | 2 | 328156 | Parameters - System - Monitoring - Missing any mains controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28155 | 3 | 328156 | Parameters - System - Monitoring - Missing any bus tie controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28155 | 4 | 328156 | Can ID not available | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28155 | 5 | 328156 | Duplicated CAN IDs | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28155 | 6 | 328156 | Parameters - Local power management - Alarms - Busbar blocked - Information - Flags - Busbar blocked due to position failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28155 | 7 | 328156 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Flags - Busbar A blocked due to position failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28155 | 8 | 328156 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Flags - Busbar B blocked due to position failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28155 | 9 | 328156 | Parameters - System - Monitoring - BTB 33 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28155 | 10 | 328156 | Parameters - System - Monitoring - BTB 34 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28155 | 11 | 328156 | Parameters - System - Monitoring - BTB 35 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28155 | 12 | 328156 | Parameters - System - Monitoring - BTB 36 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28155 | 13 | 328156 | Parameters - System - Monitoring - BTB 37 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28155 | 14 | 328156 | Parameters - System - Monitoring - BTB 38 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28155 | 15 | 328156 | Parameters - System - Monitoring - BTB 39 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 0 | 328157 | Parameters - System - Monitoring - BTB 40 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 1 | 328157 | Primary CAN missing ID 1 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 2 | 328157 | Primary CAN missing ID 2 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 3 | 328157 | Primary CAN missing ID 3 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 4 | 328157 | Primary CAN missing ID 4 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 5 | 328157 | Primary CAN missing ID 5 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 6 | 328157 | Primary CAN missing ID 6 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 7 | 328157 | Primary CAN missing ID 7 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 8 | 328157 | Primary CAN missing ID 8 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 9 | 328157 | Primary CAN missing ID 9 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 10 | 328157 | Primary CAN missing ID 10 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 11 | 328157 | Primary CAN missing ID 11 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 12 | 328157 | Primary CAN missing ID 12 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 13 | 328157 | Primary CAN missing ID 13 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 14 | 328157 | Primary CAN missing ID 14 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28156 | 15 | 328157 | Primary CAN missing ID 15 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 0 | 328158 | Primary CAN missing ID 16 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 1 | 328158 | Primary CAN missing ID 17 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 2 | 328158 | Primary CAN missing ID 18 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 3 | 328158 | Primary CAN missing ID 19 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 4 | 328158 | Primary CAN missing ID 20 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 5 | 328158 | Primary CAN missing ID 21 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 6 | 328158 | Primary CAN missing ID 22 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 7 | 328158 | Primary CAN missing ID 23 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 8 | 328158 | Primary CAN missing ID 24 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 9 | 328158 | Primary CAN missing ID 25 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 10 | 328158 | Primary CAN missing ID 26 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 11 | 328158 | Primary CAN missing ID 27 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 12 | 328158 | Primary CAN missing ID 28 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 13 | 328158 | Primary CAN missing ID 29 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 14 | 328158 | Primary CAN missing ID 30 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28157 | 15 | 328158 | Primary CAN missing ID 31 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 0 | 328159 | Primary CAN missing ID 32 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 1 | 328159 | Primary CAN missing ID 33 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 2 | 328159 | Primary CAN missing ID 34 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 3 | 328159 | Primary CAN missing ID 35 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 4 | 328159 | Primary CAN missing ID 36 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 5 | 328159 | Primary CAN missing ID 37 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 6 | 328159 | Primary CAN missing ID 38 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 7 | 328159 | Primary CAN missing ID 39 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 8 | 328159 | Primary CAN missing ID 40 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 9 | 328159 | Secondary CAN missing ID 1 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 10 | 328159 | Secondary CAN missing ID 2 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 11 | 328159 | Secondary CAN missing ID 3 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 12 | 328159 | Secondary CAN missing ID 4 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 13 | 328159 | Secondary CAN missing ID 5 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 14 | 328159 | Secondary CAN missing ID 6 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28158 | 15 | 328159 | Secondary CAN missing ID 7 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 0 | 328160 | Secondary CAN missing ID 8 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 1 | 328160 | Secondary CAN missing ID 9 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 2 | 328160 | Secondary CAN missing ID 10 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 3 | 328160 | Secondary CAN missing ID 11 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 4 | 328160 | Secondary CAN missing ID 12 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 5 | 328160 | Secondary CAN missing ID 13 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 6 | 328160 | Secondary CAN missing ID 14 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 7 | 328160 | Secondary CAN missing ID 15 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 8 | 328160 | Secondary CAN missing ID 16 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 9 | 328160 | Secondary CAN missing ID 17 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 10 | 328160 | Secondary CAN missing ID 18 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 11 | 328160 | Secondary CAN missing ID 19 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 12 | 328160 | Secondary CAN missing ID 20 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 13 | 328160 | Secondary CAN missing ID 21 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 14 | 328160 | Secondary CAN missing ID 22 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28159 | 15 | 328160 | Secondary CAN missing ID 23 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 0 | 328161 | Secondary CAN missing ID 24 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 1 | 328161 | Secondary CAN missing ID 25 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 2 | 328161 | Secondary CAN missing ID 26 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 3 | 328161 | Secondary CAN missing ID 27 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 4 | 328161 | Secondary CAN missing ID 28 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 5 | 328161 | Secondary CAN missing ID 29 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 6 | 328161 | Secondary CAN missing ID 30 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 7 | 328161 | Secondary CAN missing ID 31 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 8 | 328161 | Secondary CAN missing ID 32 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 9 | 328161 | Secondary CAN missing ID 33 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 10 | 328161 | Secondary CAN missing ID 34 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 11 | 328161 | Secondary CAN missing ID 35 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 12 | 328161 | Secondary CAN missing ID 36 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 13 | 328161 | Secondary CAN missing ID 37 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 14 | 328161 | Secondary CAN missing ID 38 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28160 | 15 | 328161 | Secondary CAN missing ID 39 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 0 | 328162 | Secondary CAN missing ID 40 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 1 | 328162 | Priority error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 2 | 328162 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - Flags - NEL 1 over-current | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 3 | 328162 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - Flags - NEL 1 under-frequency | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 4 | 328162 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - Flags - NEL 1 overload 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 5 | 328162 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - Flags - NEL 1 overload 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 6 | 328162 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - Flags - NEL 1 reactive overload | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 7 | 328162 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - Flags - NEL 2 over-current | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 8 | 328162 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - Flags - NEL 2 under-frequency | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 9 | 328162 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - Flags - NEL 2 overload 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 10 | 328162 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - Flags - NEL 2 overload 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 11 | 328162 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - Flags - NEL 2 reactive overload | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 12 | 328162 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - Flags - NEL 3 over-current | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 13 | 328162 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - Flags - NEL 3 under-frequency | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 14 | 328162 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - Flags - NEL 3 overload 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28161 | 15 | 328162 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - Flags - NEL 3 overload 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28162 | 0 | 328163 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - Flags - NEL 3 reactive overload | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm acknowledged | 28162 | 1 | 328163 | Parameters - System - Monitoring - Single-line hazard - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28162 | 2 | 328163 | ID not present | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28162 | 3 | 328163 | Unsupported application | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28162 | 4 | 328163 | Application internal CAN protocol conflict | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28162 | 5 | 328163 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Flags - Section P> | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28162 | 6 | 328163 | Dry mode: Voltage level unexpected | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28162 | 7 | 328163 | Invalid DAVR configuration | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28162 | 8 | 328163 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28162 | 10 | 328163 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28162 | 12 | 328163 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28162 | 12 | 328163 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm acknowledged | 28162 | 12 | 328163 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm acknowledged | 28162 | 13 | 328163 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm acknowledged | 28162 | 13 | 328163 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm acknowledged | 28162 | 15 | 328163 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 0 | 328164 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 1 | 328164 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 2 | 328164 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 3 | 328164 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 4 | 328164 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 5 | 328164 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 6 | 328164 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 7 | 328164 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 8 | 328164 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 9 | 328164 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 10 | 328164 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 11 | 328164 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 12 | 328164 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 13 | 328164 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 14 | 328164 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28163 | 15 | 328164 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 0 | 328165 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 1 | 328165 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 2 | 328165 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 3 | 328165 | Live voltage detected | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 4 | 328165 | Internal issue detected. A restart is required soon! | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 5 | 328165 | Parameters - System - Monitoring - Missing controllers - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 6 | 328165 | Card issue detected | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 7 | 328165 | Card configuration failed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 8 | 328165 | Unknown traffic on DEIF network | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 9 | 328165 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28164 | 10 | 328165 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28164 | 11 | 328165 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm acknowledged | 28164 | 12 | 328165 | Local I/O service error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 13 | 328165 | App logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 14 | 328165 | Event logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28164 | 15 | 328165 | Licence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28165 | 0 | 328166 | Brightness is dimmed according to temperature | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28165 | 1 | 328166 | Parameters - Grid code - Mains sync inhibit - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28165 | 2 | 328166 | Parameters - Grid code - Capability curve - Protections - Import protection - Information - Flags - Power import capability curve protection | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28165 | 3 | 328166 | Parameters - Grid code - Capability curve - Protections - Export protection - Information - Flags - Power export capability curve protection | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28165 | 4 | 328166 | Hardware is not compatible based on module versions | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28165 | 5 | 328166 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28165 | 6 | 328166 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28165 | 7 | 328166 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm acknowledged | 28167 | 8 | 328168 | Configuration not supported by licence | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28218 | 12 | 328219 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28218 | 13 | 328219 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28218 | 14 | 328219 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28218 | 15 | 328219 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 0 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 1 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 2 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 3 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 4 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 5 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 6 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 7 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 8 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 9 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 10 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 11 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 12 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 13 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 14 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28219 | 15 | 328220 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 0 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 1 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 2 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 3 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 4 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 5 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 6 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 7 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 8 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 9 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 10 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 11 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 12 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 13 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 14 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28220 | 15 | 328221 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 0 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 1 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 2 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 3 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 4 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 5 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 6 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 7 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 8 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 9 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 10 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 11 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 12 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28221 | 13 | 328222 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 0 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 1 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 2 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 3 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 4 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 5 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 6 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 7 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 8 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 9 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 10 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 11 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 12 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 13 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 14 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28225 | 15 | 328226 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 0 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 1 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 2 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 3 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 4 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 5 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 6 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 7 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 8 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 9 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 10 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 11 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 12 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 13 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 14 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28226 | 15 | 328227 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 0 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 1 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 2 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 3 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 4 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 5 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 6 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 7 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 8 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 9 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 10 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 11 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 12 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 13 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 14 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28227 | 15 | 328228 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 0 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 1 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 2 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 3 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 4 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 5 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 6 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 7 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 8 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 9 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 10 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 11 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 12 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 13 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 14 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28228 | 15 | 328229 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 0 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 1 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 2 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 3 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 4 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 5 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 6 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 7 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 8 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 9 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 10 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 11 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 12 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 13 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 14 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28229 | 15 | 328230 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 0 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 1 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 2 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 3 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 4 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 5 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 6 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 7 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 8 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 9 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 10 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 11 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 12 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 13 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 14 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28230 | 15 | 328231 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 0 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 1 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 2 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 3 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 4 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 5 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 6 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 7 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 8 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 9 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 10 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 11 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 12 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 13 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 14 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28231 | 15 | 328232 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 0 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 1 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 2 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 3 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 4 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 5 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 6 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 7 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 8 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 9 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 10 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 11 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 12 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 13 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 14 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28232 | 15 | 328233 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 0 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 1 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 2 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 3 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 4 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 5 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 6 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 7 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 8 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 9 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 10 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 11 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 12 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 13 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 14 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28233 | 15 | 328234 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 0 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 1 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 2 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 3 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 4 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 5 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 6 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 7 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 8 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 9 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 10 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 11 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 12 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 13 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 14 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28234 | 15 | 328235 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 0 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 1 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 2 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 3 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 4 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 5 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 6 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 7 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 8 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 9 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 10 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 11 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 12 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 13 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 14 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28235 | 15 | 328236 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 0 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 1 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 2 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 3 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 4 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 5 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 6 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 7 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 8 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 9 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 10 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 11 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 12 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 13 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 14 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28236 | 15 | 328237 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 0 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 1 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 2 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 3 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 4 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 5 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 6 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm acknowledged | 28237 | 7 | 328238 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28250 | 0 | 328251 | Application initialisation error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28250 | 1 | 328251 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28250 | 2 | 328251 | Preliminary software | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28250 | 3 | 328251 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28250 | 4 | 328251 | Parameters - Engine - Start sequence - Start failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28250 | 5 | 328251 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28250 | 6 | 328251 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28250 | 7 | 328251 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28250 | 8 | 328251 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28250 | 9 | 328251 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28250 | 10 | 328251 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28250 | 11 | 328251 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28250 | 13 | 328251 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28250 | 14 | 328251 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28250 | 15 | 328251 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28251 | 0 | 328252 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28251 | 1 | 328252 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28251 | 2 | 328252 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28251 | 3 | 328252 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28251 | 4 | 328252 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28251 | 5 | 328252 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28251 | 6 | 328252 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28251 | 11 | 328252 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28252 | 9 | 328253 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28252 | 9 | 328253 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28252 | 9 | 328253 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28252 | 10 | 328253 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28252 | 10 | 328253 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28252 | 10 | 328253 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28252 | 11 | 328253 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28252 | 11 | 328253 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28252 | 11 | 328253 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28252 | 12 | 328253 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28252 | 12 | 328253 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28252 | 12 | 328253 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28252 | 13 | 328253 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28252 | 13 | 328253 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28252 | 13 | 328253 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28252 | 14 | 328253 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28252 | 14 | 328253 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28252 | 14 | 328253 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28252 | 15 | 328253 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28252 | 15 | 328253 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28252 | 15 | 328253 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28253 | 0 | 328254 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28253 | 0 | 328254 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28253 | 0 | 328254 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28253 | 1 | 328254 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28253 | 1 | 328254 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm latched | 28253 | 2 | 328254 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28253 | 2 | 328254 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm latched | 28253 | 3 | 328254 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28253 | 3 | 328254 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm latched | 28253 | 4 | 328254 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28253 | 4 | 328254 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm latched | 28253 | 5 | 328254 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28253 | 5 | 328254 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm latched | 28253 | 6 | 328254 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28253 | 6 | 328254 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm latched | 28253 | 7 | 328254 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28253 | 7 | 328254 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm latched | 28253 | 8 | 328254 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28253 | 8 | 328254 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm latched | 28253 | 12 | 328254 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28253 | 12 | 328254 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28253 | 12 | 328254 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28253 | 13 | 328254 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28253 | 13 | 328254 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28253 | 13 | 328254 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28253 | 14 | 328254 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28256 | 7 | 328257 | Parameters - Mains - Additional protections - ROCOF - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28256 | 7 | 328257 | Parameters - Busbar - Additional protections - ROCOF - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28256 | 7 | 328257 | Parameters - Busbar B - Additional protections - ROCOF - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28256 | 8 | 328257 | Parameters - Mains - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28256 | 8 | 328257 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28256 | 8 | 328257 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28256 | 9 | 328257 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28256 | 9 | 328257 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28256 | 9 | 328257 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28256 | 10 | 328257 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28256 | 11 | 328257 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28256 | 12 | 328257 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28256 | 12 | 328257 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28256 | 12 | 328257 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28256 | 13 | 328257 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28256 | 13 | 328257 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28256 | 13 | 328257 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28256 | 14 | 328257 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28256 | 14 | 328257 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28256 | 14 | 328257 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28256 | 15 | 328257 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28256 | 15 | 328257 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28256 | 15 | 328257 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28257 | 3 | 328258 | Protection set point out of range | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 4 | 328258 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28257 | 5 | 328258 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28257 | 6 | 328258 | Protection set point out of range (differential current) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28257 | 7 | 328258 | Parameters - Local - Mode - Not under remote control - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 9 | 328258 | Parameters - Local - Monitoring - System not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 10 | 328258 | Configuration update delayed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 11 | 328258 | Critical process error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 12 | 328258 | Restore error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 13 | 328258 | SD-card format error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 14 | 328258 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28257 | 15 | 328258 | Fieldbus configuration exceeded maximum I/O configuration | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 0 | 328259 | Parameters - Custom alarms - Custom alarm 0 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 1 | 328259 | Parameters - Custom alarms - Custom alarm 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 2 | 328259 | Parameters - Custom alarms - Custom alarm 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 3 | 328259 | Parameters - Custom alarms - Custom alarm 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 4 | 328259 | Parameters - Custom alarms - Custom alarm 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 5 | 328259 | Parameters - Custom alarms - Custom alarm 5 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 6 | 328259 | Parameters - Custom alarms - Custom alarm 6 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 7 | 328259 | Parameters - Custom alarms - Custom alarm 7 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 8 | 328259 | Parameters - Custom alarms - Custom alarm 8 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 9 | 328259 | Parameters - Custom alarms - Custom alarm 9 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 10 | 328259 | Parameters - Custom alarms - Custom alarm 10 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 11 | 328259 | Parameters - Custom alarms - Custom alarm 11 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 12 | 328259 | Parameters - Custom alarms - Custom alarm 12 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 13 | 328259 | Parameters - Custom alarms - Custom alarm 13 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 14 | 328259 | Parameters - Custom alarms - Custom alarm 14 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28258 | 15 | 328259 | Parameters - Custom alarms - Custom alarm 15 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 0 | 328260 | Parameters - Custom alarms - Custom alarm 16 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 1 | 328260 | Parameters - Custom alarms - Custom alarm 17 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 2 | 328260 | Parameters - Custom alarms - Custom alarm 18 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 3 | 328260 | Parameters - Custom alarms - Custom alarm 19 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 4 | 328260 | Parameters - Custom alarms - Custom alarm 20 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 5 | 328260 | Parameters - Custom alarms - Custom alarm 21 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 6 | 328260 | Parameters - Custom alarms - Custom alarm 22 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 7 | 328260 | Parameters - Custom alarms - Custom alarm 23 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 8 | 328260 | Parameters - Custom alarms - Custom alarm 24 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28259 | 9 | 328260 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28259 | 10 | 328260 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28260 | 3 | 328261 | Required hardware card(s) not found | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28260 | 4 | 328261 | Software mismatch on hardware module(s) | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28260 | 5 | 328261 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm latched | 28260 | 5 | 328261 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm latched | 28260 | 5 | 328261 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28260 | 6 | 328261 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm latched | 28260 | 6 | 328261 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28260 | 6 | 328261 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28260 | 7 | 328261 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm latched | 28260 | 7 | 328261 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm latched | 28260 | 7 | 328261 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28260 | 8 | 328261 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm latched | 28260 | 8 | 328261 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm latched | 28260 | 8 | 328261 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28260 | 9 | 328261 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Alarm latched | 28260 | 9 | 328261 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Alarm latched | 28260 | 9 | 328261 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28260 | 10 | 328261 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm latched | 28260 | 10 | 328261 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28260 | 10 | 328261 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28260 | 11 | 328261 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm latched | 28260 | 11 | 328261 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28260 | 11 | 328261 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28260 | 12 | 328261 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Alarm latched | 28260 | 12 | 328261 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28260 | 12 | 328261 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Alarm latched | 28261 | 2 | 328262 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm | BOOL | X * 1 | X * 1 |  |  |  | X | X |  | X | X
Alarm status: Alarm latched | 28261 | 3 | 328262 | Parameters - Engine - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28261 | 3 | 328262 | Parameters - Busbar A - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28261 | 3 | 328262 | Parameters - Mains - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28261 | 4 | 328262 | Clock battery failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 5 | 328262 | Controller temperature too high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 6 | 328262 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 7 | 328262 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 8 | 328262 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 9 | 328262 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 10 | 328262 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 11 | 328262 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 12 | 328262 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 13 | 328262 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 14 | 328262 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28261 | 15 | 328262 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 0 | 328263 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 1 | 328263 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 2 | 328263 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 3 | 328263 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 4 | 328263 | EIM3.1 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 5 | 328263 | EIM3.1 4 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 6 | 328263 | EIM3.1 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 7 | 328263 | EIM3.1 5 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 8 | 328263 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 9 | 328263 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 10 | 328263 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 11 | 328263 | EIM3.1 4 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 12 | 328263 | EIM3.1 5 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 13 | 328263 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 14 | 328263 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28262 | 15 | 328263 | AC protections not running (differential current) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28263 | 0 | 328264 | AC data is missing (differential current) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28263 | 1 | 328264 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 2 | 328264 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 3 | 328264 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 4 | 328264 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 5 | 328264 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 6 | 328264 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 7 | 328264 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 8 | 328264 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 9 | 328264 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 10 | 328264 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 11 | 328264 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 12 | 328264 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 13 | 328264 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 14 | 328264 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28263 | 15 | 328264 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 0 | 328265 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 1 | 328265 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 2 | 328265 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 4 | 328265 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 5 | 328265 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 7 | 328265 | Controller ID not configured | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 12 | 328265 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28264 | 13 | 328265 | Blackout detection mismatch | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28265 | 0 | 328266 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28265 | 1 | 328266 | Parameters - Communication - NTP - NTP server 1 not responding - Information - Flags - NTP server 1 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28265 | 2 | 328266 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28265 | 3 | 328266 | Parameters - Communication - NTP - NTP server 2 not responding - Information - Flags - NTP server 2 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28265 | 4 | 328266 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28265 | 5 | 328266 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28265 | 6 | 328266 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28265 | 7 | 328266 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28268 | 8 | 328269 | Controller not part of system | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28268 | 9 | 328269 | Different single-line configurations | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28268 | 10 | 328269 | Single-line missing/none active | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28268 | 11 | 328269 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28268 | 12 | 328269 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28268 | 13 | 328269 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28268 | 14 | 328269 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28268 | 15 | 328269 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28269 | 0 | 328270 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28269 | 1 | 328270 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28269 | 2 | 328270 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28269 | 3 | 328270 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28269 | 4 | 328270 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28269 | 5 | 328270 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28269 | 6 | 328270 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28269 | 7 | 328270 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28269 | 8 | 328270 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28269 | 11 | 328270 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28269 | 12 | 328270 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28269 | 13 | 328270 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28269 | 14 | 328270 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28269 | 15 | 328270 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 0 | 328271 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 1 | 328271 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 2 | 328271 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 3 | 328271 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 4 | 328271 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 5 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 6 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 7 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 8 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 9 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 10 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 11 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 12 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 13 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 14 | 328271 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28270 | 15 | 328271 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 0 | 328272 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 1 | 328272 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 2 | 328272 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 3 | 328272 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 4 | 328272 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 5 | 328272 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 6 | 328272 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 7 | 328272 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 8 | 328272 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 9 | 328272 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 10 | 328272 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 11 | 328272 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 12 | 328272 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 13 | 328272 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 14 | 328272 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28271 | 15 | 328272 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 0 | 328273 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 1 | 328273 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 2 | 328273 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 3 | 328273 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 4 | 328273 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 5 | 328273 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 6 | 328273 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 7 | 328273 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 8 | 328273 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 9 | 328273 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 10 | 328273 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 11 | 328273 | DAVR unsupported AC configuration | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 12 | 328273 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 13 | 328273 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 13 | 328273 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28272 | 13 | 328273 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28272 | 14 | 328273 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 14 | 328273 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28272 | 14 | 328273 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28272 | 15 | 328273 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28272 | 15 | 328273 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28272 | 15 | 328273 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 0 | 328274 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 0 | 328274 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 0 | 328274 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 1 | 328274 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 1 | 328274 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 1 | 328274 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 2 | 328274 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 2 | 328274 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 2 | 328274 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 3 | 328274 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 3 | 328274 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 3 | 328274 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 4 | 328274 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 4 | 328274 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 4 | 328274 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 5 | 328274 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 5 | 328274 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 5 | 328274 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 6 | 328274 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 6 | 328274 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 6 | 328274 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 7 | 328274 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 7 | 328274 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 7 | 328274 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 8 | 328274 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 8 | 328274 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 8 | 328274 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 9 | 328274 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 9 | 328274 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 9 | 328274 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 10 | 328274 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 10 | 328274 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 10 | 328274 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 11 | 328274 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 11 | 328274 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 11 | 328274 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 12 | 328274 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 12 | 328274 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 12 | 328274 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 13 | 328274 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 13 | 328274 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 13 | 328274 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 14 | 328274 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 14 | 328274 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 14 | 328274 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28273 | 15 | 328274 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28273 | 15 | 328274 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28273 | 15 | 328274 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28274 | 0 | 328275 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 1 | 328275 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 2 | 328275 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28274 | 2 | 328275 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 2 | 328275 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28274 | 3 | 328275 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28274 | 3 | 328275 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 3 | 328275 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28274 | 4 | 328275 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28274 | 4 | 328275 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 4 | 328275 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28274 | 5 | 328275 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28274 | 5 | 328275 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 5 | 328275 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28274 | 6 | 328275 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28274 | 6 | 328275 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 6 | 328275 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28274 | 7 | 328275 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28274 | 7 | 328275 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 7 | 328275 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28274 | 8 | 328275 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28274 | 8 | 328275 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 8 | 328275 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28274 | 9 | 328275 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28274 | 9 | 328275 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 9 | 328275 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28274 | 10 | 328275 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28274 | 10 | 328275 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 10 | 328275 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28274 | 11 | 328275 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28274 | 11 | 328275 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 11 | 328275 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28274 | 12 | 328275 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28274 | 12 | 328275 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 12 | 328275 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28274 | 13 | 328275 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28274 | 13 | 328275 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 13 | 328275 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28274 | 14 | 328275 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28274 | 14 | 328275 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 14 | 328275 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28274 | 15 | 328275 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28274 | 15 | 328275 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28274 | 15 | 328275 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28275 | 0 | 328276 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28275 | 0 | 328276 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28275 | 0 | 328276 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28275 | 1 | 328276 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28275 | 1 | 328276 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28275 | 1 | 328276 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28275 | 2 | 328276 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28275 | 2 | 328276 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28275 | 2 | 328276 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28275 | 3 | 328276 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28275 | 3 | 328276 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28275 | 3 | 328276 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28275 | 4 | 328276 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28275 | 4 | 328276 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28275 | 4 | 328276 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28275 | 5 | 328276 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28275 | 5 | 328276 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28275 | 5 | 328276 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28275 | 6 | 328276 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28275 | 6 | 328276 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28275 | 6 | 328276 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28275 | 7 | 328276 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28275 | 7 | 328276 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28275 | 7 | 328276 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28275 | 8 | 328276 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28275 | 8 | 328276 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28275 | 8 | 328276 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28275 | 9 | 328276 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28275 | 9 | 328276 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28275 | 9 | 328276 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28275 | 10 | 328276 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28275 | 10 | 328276 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28275 | 10 | 328276 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28275 | 11 | 328276 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28275 | 11 | 328276 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28275 | 11 | 328276 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28275 | 12 | 328276 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28275 | 12 | 328276 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28275 | 12 | 328276 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28275 | 13 | 328276 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28275 | 13 | 328276 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28275 | 13 | 328276 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28275 | 14 | 328276 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28275 | 14 | 328276 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28275 | 14 | 328276 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28275 | 15 | 328276 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28275 | 15 | 328276 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28275 | 15 | 328276 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28276 | 0 | 328277 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28276 | 0 | 328277 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28276 | 0 | 328277 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28276 | 1 | 328277 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28276 | 1 | 328277 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28276 | 1 | 328277 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28276 | 2 | 328277 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28276 | 2 | 328277 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28276 | 2 | 328277 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28276 | 3 | 328277 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28276 | 3 | 328277 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28276 | 3 | 328277 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28276 | 4 | 328277 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28276 | 4 | 328277 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28276 | 4 | 328277 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28276 | 5 | 328277 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28276 | 5 | 328277 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28276 | 5 | 328277 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28276 | 6 | 328277 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28276 | 6 | 328277 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Alarm latched | 28276 | 6 | 328277 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28279 | 3 | 328280 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28279 | 4 | 328280 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28279 | 5 | 328280 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28279 | 6 | 328280 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 4 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28279 | 7 | 328280 | External MB open failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28279 | 8 | 328280 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28279 | 9 | 328280 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28279 | 10 | 328280 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28279 | 11 | 328280 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28279 | 12 | 328280 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28279 | 13 | 328280 | Parameters - Breakers - Close before excitation - CBE failure - Information - Flags - Close before excitation failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28279 | 14 | 328280 | Load too high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28279 | 15 | 328280 | ID to run configuration failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28280 | 1 | 328281 | Parameters - System - Monitoring - Missing any genset controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28280 | 2 | 328281 | Parameters - System - Monitoring - Missing any mains controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28280 | 3 | 328281 | Parameters - System - Monitoring - Missing any bus tie controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28280 | 4 | 328281 | Can ID not available | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28280 | 5 | 328281 | Duplicated CAN IDs | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28280 | 6 | 328281 | Parameters - Local power management - Alarms - Busbar blocked - Information - Flags - Busbar blocked due to position failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28280 | 7 | 328281 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Flags - Busbar A blocked due to position failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28280 | 8 | 328281 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Flags - Busbar B blocked due to position failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28280 | 9 | 328281 | Parameters - System - Monitoring - BTB 33 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28280 | 10 | 328281 | Parameters - System - Monitoring - BTB 34 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28280 | 11 | 328281 | Parameters - System - Monitoring - BTB 35 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28280 | 12 | 328281 | Parameters - System - Monitoring - BTB 36 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28280 | 13 | 328281 | Parameters - System - Monitoring - BTB 37 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28280 | 14 | 328281 | Parameters - System - Monitoring - BTB 38 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28280 | 15 | 328281 | Parameters - System - Monitoring - BTB 39 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 0 | 328282 | Parameters - System - Monitoring - BTB 40 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 1 | 328282 | Primary CAN missing ID 1 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 2 | 328282 | Primary CAN missing ID 2 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 3 | 328282 | Primary CAN missing ID 3 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 4 | 328282 | Primary CAN missing ID 4 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 5 | 328282 | Primary CAN missing ID 5 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 6 | 328282 | Primary CAN missing ID 6 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 7 | 328282 | Primary CAN missing ID 7 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 8 | 328282 | Primary CAN missing ID 8 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 9 | 328282 | Primary CAN missing ID 9 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 10 | 328282 | Primary CAN missing ID 10 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 11 | 328282 | Primary CAN missing ID 11 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 12 | 328282 | Primary CAN missing ID 12 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 13 | 328282 | Primary CAN missing ID 13 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 14 | 328282 | Primary CAN missing ID 14 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28281 | 15 | 328282 | Primary CAN missing ID 15 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 0 | 328283 | Primary CAN missing ID 16 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 1 | 328283 | Primary CAN missing ID 17 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 2 | 328283 | Primary CAN missing ID 18 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 3 | 328283 | Primary CAN missing ID 19 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 4 | 328283 | Primary CAN missing ID 20 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 5 | 328283 | Primary CAN missing ID 21 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 6 | 328283 | Primary CAN missing ID 22 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 7 | 328283 | Primary CAN missing ID 23 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 8 | 328283 | Primary CAN missing ID 24 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 9 | 328283 | Primary CAN missing ID 25 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 10 | 328283 | Primary CAN missing ID 26 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 11 | 328283 | Primary CAN missing ID 27 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 12 | 328283 | Primary CAN missing ID 28 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 13 | 328283 | Primary CAN missing ID 29 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 14 | 328283 | Primary CAN missing ID 30 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28282 | 15 | 328283 | Primary CAN missing ID 31 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 0 | 328284 | Primary CAN missing ID 32 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 1 | 328284 | Primary CAN missing ID 33 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 2 | 328284 | Primary CAN missing ID 34 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 3 | 328284 | Primary CAN missing ID 35 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 4 | 328284 | Primary CAN missing ID 36 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 5 | 328284 | Primary CAN missing ID 37 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 6 | 328284 | Primary CAN missing ID 38 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 7 | 328284 | Primary CAN missing ID 39 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 8 | 328284 | Primary CAN missing ID 40 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 9 | 328284 | Secondary CAN missing ID 1 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 10 | 328284 | Secondary CAN missing ID 2 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 11 | 328284 | Secondary CAN missing ID 3 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 12 | 328284 | Secondary CAN missing ID 4 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 13 | 328284 | Secondary CAN missing ID 5 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 14 | 328284 | Secondary CAN missing ID 6 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28283 | 15 | 328284 | Secondary CAN missing ID 7 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 0 | 328285 | Secondary CAN missing ID 8 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 1 | 328285 | Secondary CAN missing ID 9 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 2 | 328285 | Secondary CAN missing ID 10 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 3 | 328285 | Secondary CAN missing ID 11 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 4 | 328285 | Secondary CAN missing ID 12 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 5 | 328285 | Secondary CAN missing ID 13 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 6 | 328285 | Secondary CAN missing ID 14 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 7 | 328285 | Secondary CAN missing ID 15 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 8 | 328285 | Secondary CAN missing ID 16 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 9 | 328285 | Secondary CAN missing ID 17 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 10 | 328285 | Secondary CAN missing ID 18 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 11 | 328285 | Secondary CAN missing ID 19 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 12 | 328285 | Secondary CAN missing ID 20 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 13 | 328285 | Secondary CAN missing ID 21 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 14 | 328285 | Secondary CAN missing ID 22 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28284 | 15 | 328285 | Secondary CAN missing ID 23 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 0 | 328286 | Secondary CAN missing ID 24 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 1 | 328286 | Secondary CAN missing ID 25 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 2 | 328286 | Secondary CAN missing ID 26 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 3 | 328286 | Secondary CAN missing ID 27 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 4 | 328286 | Secondary CAN missing ID 28 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 5 | 328286 | Secondary CAN missing ID 29 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 6 | 328286 | Secondary CAN missing ID 30 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 7 | 328286 | Secondary CAN missing ID 31 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 8 | 328286 | Secondary CAN missing ID 32 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 9 | 328286 | Secondary CAN missing ID 33 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 10 | 328286 | Secondary CAN missing ID 34 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 11 | 328286 | Secondary CAN missing ID 35 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 12 | 328286 | Secondary CAN missing ID 36 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 13 | 328286 | Secondary CAN missing ID 37 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 14 | 328286 | Secondary CAN missing ID 38 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28285 | 15 | 328286 | Secondary CAN missing ID 39 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 0 | 328287 | Secondary CAN missing ID 40 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 1 | 328287 | Priority error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 2 | 328287 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - Flags - NEL 1 over-current | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 3 | 328287 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - Flags - NEL 1 under-frequency | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 4 | 328287 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - Flags - NEL 1 overload 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 5 | 328287 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - Flags - NEL 1 overload 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 6 | 328287 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - Flags - NEL 1 reactive overload | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 7 | 328287 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - Flags - NEL 2 over-current | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 8 | 328287 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - Flags - NEL 2 under-frequency | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 9 | 328287 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - Flags - NEL 2 overload 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 10 | 328287 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - Flags - NEL 2 overload 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 11 | 328287 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - Flags - NEL 2 reactive overload | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 12 | 328287 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - Flags - NEL 3 over-current | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 13 | 328287 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - Flags - NEL 3 under-frequency | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 14 | 328287 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - Flags - NEL 3 overload 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28286 | 15 | 328287 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - Flags - NEL 3 overload 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28287 | 0 | 328288 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - Flags - NEL 3 reactive overload | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Alarm latched | 28287 | 1 | 328288 | Parameters - System - Monitoring - Single-line hazard - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28287 | 2 | 328288 | ID not present | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28287 | 3 | 328288 | Unsupported application | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28287 | 4 | 328288 | Application internal CAN protocol conflict | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28287 | 5 | 328288 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Flags - Section P> | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28287 | 6 | 328288 | Dry mode: Voltage level unexpected | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28287 | 7 | 328288 | Invalid DAVR configuration | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28287 | 8 | 328288 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28287 | 10 | 328288 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28287 | 12 | 328288 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28287 | 12 | 328288 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Alarm latched | 28287 | 12 | 328288 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Alarm latched | 28287 | 13 | 328288 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Alarm latched | 28287 | 13 | 328288 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Alarm latched | 28287 | 15 | 328288 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 0 | 328289 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 1 | 328289 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 2 | 328289 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 3 | 328289 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 4 | 328289 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 5 | 328289 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 6 | 328289 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 7 | 328289 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 8 | 328289 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 9 | 328289 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 10 | 328289 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 11 | 328289 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 12 | 328289 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 13 | 328289 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 14 | 328289 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28288 | 15 | 328289 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 0 | 328290 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 1 | 328290 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 2 | 328290 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 3 | 328290 | Live voltage detected | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 4 | 328290 | Internal issue detected. A restart is required soon! | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 5 | 328290 | Parameters - System - Monitoring - Missing controllers - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 6 | 328290 | Card issue detected | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 7 | 328290 | Card configuration failed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 8 | 328290 | Unknown traffic on DEIF network | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 9 | 328290 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28289 | 10 | 328290 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28289 | 11 | 328290 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Alarm latched | 28289 | 12 | 328290 | Local I/O service error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 13 | 328290 | App logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 14 | 328290 | Event logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28289 | 15 | 328290 | Licence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28290 | 0 | 328291 | Brightness is dimmed according to temperature | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28290 | 1 | 328291 | Parameters - Grid code - Mains sync inhibit - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28290 | 2 | 328291 | Parameters - Grid code - Capability curve - Protections - Import protection - Information - Flags - Power import capability curve protection | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28290 | 3 | 328291 | Parameters - Grid code - Capability curve - Protections - Export protection - Information - Flags - Power export capability curve protection | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28290 | 4 | 328291 | Hardware is not compatible based on module versions | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28290 | 5 | 328291 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28290 | 6 | 328291 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28290 | 7 | 328291 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Alarm latched | 28292 | 8 | 328293 | Configuration not supported by licence | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28343 | 12 | 328344 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28343 | 13 | 328344 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28343 | 14 | 328344 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28343 | 15 | 328344 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 0 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 1 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 2 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 3 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 4 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 5 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 6 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 7 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 8 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 9 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 10 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 11 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 12 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 13 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 14 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28344 | 15 | 328345 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 0 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 1 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 2 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 3 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 4 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 5 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 6 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 7 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 8 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 9 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 10 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 11 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 12 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 13 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 14 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28345 | 15 | 328346 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 0 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 1 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 2 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 3 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 4 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 5 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 6 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 7 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 8 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 9 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 10 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 11 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 12 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28346 | 13 | 328347 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 0 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 1 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 2 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 3 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 4 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 5 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 6 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 7 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 8 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 9 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 10 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 11 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 12 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 13 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 14 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28350 | 15 | 328351 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 0 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 1 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 2 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 3 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 4 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 5 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 6 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 7 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 8 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 9 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 10 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 11 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 12 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 13 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 14 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28351 | 15 | 328352 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 0 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 1 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 2 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 3 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 4 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 5 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 6 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 7 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 8 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 9 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 10 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 11 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 12 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 13 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 14 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28352 | 15 | 328353 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 0 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 1 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 2 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 3 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 4 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 5 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 6 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 7 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 8 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 9 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 10 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 11 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 12 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 13 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 14 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28353 | 15 | 328354 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 0 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 1 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 2 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 3 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 4 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 5 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 6 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 7 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 8 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 9 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 10 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 11 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 12 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 13 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 14 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28354 | 15 | 328355 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 0 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 1 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 2 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 3 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 4 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 5 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 6 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 7 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 8 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 9 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 10 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 11 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 12 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 13 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 14 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28355 | 15 | 328356 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 0 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 1 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 2 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 3 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 4 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 5 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 6 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 7 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 8 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 9 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 10 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 11 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 12 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 13 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 14 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28356 | 15 | 328357 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 0 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 1 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 2 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 3 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 4 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 5 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 6 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 7 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 8 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 9 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 10 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 11 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 12 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 13 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 14 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28357 | 15 | 328358 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 0 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 1 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 2 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 3 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 4 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 5 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 6 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 7 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 8 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 9 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 10 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 11 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 12 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 13 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 14 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28358 | 15 | 328359 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 0 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 1 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 2 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 3 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 4 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 5 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 6 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 7 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 8 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 9 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 10 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 11 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 12 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 13 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 14 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28359 | 15 | 328360 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 0 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 1 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 2 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 3 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 4 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 5 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 6 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 7 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 8 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 9 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 10 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 11 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 12 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 13 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 14 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28360 | 15 | 328361 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 0 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 1 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 2 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 3 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 4 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 5 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 6 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 7 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 8 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 9 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 10 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 11 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 12 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 13 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 14 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28361 | 15 | 328362 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 0 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 1 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 2 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 3 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 4 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 5 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 6 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Alarm latched | 28362 | 7 | 328363 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28375 | 0 | 328376 | Application initialisation error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28375 | 1 | 328376 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28375 | 2 | 328376 | Preliminary software | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28375 | 3 | 328376 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28375 | 4 | 328376 | Parameters - Engine - Start sequence - Start failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28375 | 5 | 328376 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28375 | 6 | 328376 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28375 | 7 | 328376 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28375 | 8 | 328376 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28375 | 9 | 328376 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28375 | 10 | 328376 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28375 | 11 | 328376 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28375 | 13 | 328376 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28375 | 14 | 328376 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28375 | 15 | 328376 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28376 | 0 | 328377 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28376 | 1 | 328377 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28376 | 2 | 328377 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28376 | 3 | 328377 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28376 | 4 | 328377 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28376 | 5 | 328377 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28376 | 6 | 328377 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28376 | 11 | 328377 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28377 | 9 | 328378 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28377 | 9 | 328378 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28377 | 9 | 328378 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28377 | 10 | 328378 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28377 | 10 | 328378 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28377 | 10 | 328378 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28377 | 11 | 328378 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28377 | 11 | 328378 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28377 | 11 | 328378 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28377 | 12 | 328378 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28377 | 12 | 328378 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28377 | 12 | 328378 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28377 | 13 | 328378 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28377 | 13 | 328378 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28377 | 13 | 328378 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28377 | 14 | 328378 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28377 | 14 | 328378 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28377 | 14 | 328378 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28377 | 15 | 328378 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28377 | 15 | 328378 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28377 | 15 | 328378 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28378 | 0 | 328379 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28378 | 0 | 328379 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28378 | 0 | 328379 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28378 | 1 | 328379 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28378 | 1 | 328379 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Inhibited | 28378 | 2 | 328379 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28378 | 2 | 328379 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Inhibited | 28378 | 3 | 328379 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28378 | 3 | 328379 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Inhibited | 28378 | 4 | 328379 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28378 | 4 | 328379 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Inhibited | 28378 | 5 | 328379 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28378 | 5 | 328379 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Inhibited | 28378 | 6 | 328379 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28378 | 6 | 328379 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Inhibited | 28378 | 7 | 328379 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28378 | 7 | 328379 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Inhibited | 28378 | 8 | 328379 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28378 | 8 | 328379 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Inhibited | 28378 | 12 | 328379 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28378 | 12 | 328379 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28378 | 12 | 328379 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28378 | 13 | 328379 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28378 | 13 | 328379 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28378 | 13 | 328379 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28378 | 14 | 328379 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28381 | 7 | 328382 | Parameters - Mains - Additional protections - ROCOF - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28381 | 7 | 328382 | Parameters - Busbar - Additional protections - ROCOF - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28381 | 7 | 328382 | Parameters - Busbar B - Additional protections - ROCOF - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28381 | 8 | 328382 | Parameters - Mains - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28381 | 8 | 328382 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28381 | 8 | 328382 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28381 | 9 | 328382 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28381 | 9 | 328382 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28381 | 9 | 328382 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28381 | 10 | 328382 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28381 | 11 | 328382 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28381 | 12 | 328382 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28381 | 12 | 328382 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28381 | 12 | 328382 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28381 | 13 | 328382 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28381 | 13 | 328382 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28381 | 13 | 328382 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28381 | 14 | 328382 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28381 | 14 | 328382 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28381 | 14 | 328382 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28381 | 15 | 328382 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28381 | 15 | 328382 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28381 | 15 | 328382 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28382 | 3 | 328383 | Protection set point out of range | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 4 | 328383 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28382 | 5 | 328383 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28382 | 6 | 328383 | Protection set point out of range (differential current) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28382 | 7 | 328383 | Parameters - Local - Mode - Not under remote control - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 9 | 328383 | Parameters - Local - Monitoring - System not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 10 | 328383 | Configuration update delayed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 11 | 328383 | Critical process error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 12 | 328383 | Restore error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 13 | 328383 | SD-card format error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 14 | 328383 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 15 | 328383 | Fieldbus configuration exceeded maximum I/O configuration | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 0 | 328384 | Parameters - Custom alarms - Custom alarm 0 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 1 | 328384 | Parameters - Custom alarms - Custom alarm 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 2 | 328384 | Parameters - Custom alarms - Custom alarm 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 3 | 328384 | Parameters - Custom alarms - Custom alarm 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 4 | 328384 | Parameters - Custom alarms - Custom alarm 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 5 | 328384 | Parameters - Custom alarms - Custom alarm 5 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 6 | 328384 | Parameters - Custom alarms - Custom alarm 6 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 7 | 328384 | Parameters - Custom alarms - Custom alarm 7 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 8 | 328384 | Parameters - Custom alarms - Custom alarm 8 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 9 | 328384 | Parameters - Custom alarms - Custom alarm 9 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 10 | 328384 | Parameters - Custom alarms - Custom alarm 10 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 11 | 328384 | Parameters - Custom alarms - Custom alarm 11 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 12 | 328384 | Parameters - Custom alarms - Custom alarm 12 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 13 | 328384 | Parameters - Custom alarms - Custom alarm 13 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 14 | 328384 | Parameters - Custom alarms - Custom alarm 14 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 15 | 328384 | Parameters - Custom alarms - Custom alarm 15 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 0 | 328385 | Parameters - Custom alarms - Custom alarm 16 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 1 | 328385 | Parameters - Custom alarms - Custom alarm 17 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 2 | 328385 | Parameters - Custom alarms - Custom alarm 18 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 3 | 328385 | Parameters - Custom alarms - Custom alarm 19 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 4 | 328385 | Parameters - Custom alarms - Custom alarm 20 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 5 | 328385 | Parameters - Custom alarms - Custom alarm 21 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 6 | 328385 | Parameters - Custom alarms - Custom alarm 22 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 7 | 328385 | Parameters - Custom alarms - Custom alarm 23 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 8 | 328385 | Parameters - Custom alarms - Custom alarm 24 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 9 | 328385 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28384 | 10 | 328385 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28385 | 3 | 328386 | Required hardware card(s) not found | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28385 | 4 | 328386 | Software mismatch on hardware module(s) | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28385 | 5 | 328386 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Inhibited | 28385 | 5 | 328386 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Inhibited | 28385 | 5 | 328386 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28385 | 6 | 328386 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Inhibited | 28385 | 6 | 328386 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28385 | 6 | 328386 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28385 | 7 | 328386 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Inhibited | 28385 | 7 | 328386 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Inhibited | 28385 | 7 | 328386 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28385 | 8 | 328386 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Inhibited | 28385 | 8 | 328386 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Inhibited | 28385 | 8 | 328386 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28385 | 9 | 328386 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Inhibited | 28385 | 9 | 328386 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Inhibited | 28385 | 9 | 328386 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28385 | 10 | 328386 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Inhibited | 28385 | 10 | 328386 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28385 | 10 | 328386 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28385 | 11 | 328386 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Inhibited | 28385 | 11 | 328386 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28385 | 11 | 328386 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28385 | 12 | 328386 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Inhibited | 28385 | 12 | 328386 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28385 | 12 | 328386 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Inhibited | 28386 | 2 | 328387 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm | BOOL | X * 1 | X * 1 |  |  |  | X | X |  | X | X
Alarm status: Inhibited | 28386 | 3 | 328387 | Parameters - Engine - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28386 | 3 | 328387 | Parameters - Busbar A - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28386 | 3 | 328387 | Parameters - Mains - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28386 | 4 | 328387 | Clock battery failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 5 | 328387 | Controller temperature too high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 6 | 328387 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 7 | 328387 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 8 | 328387 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 9 | 328387 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 10 | 328387 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 11 | 328387 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 12 | 328387 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 13 | 328387 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 14 | 328387 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 15 | 328387 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 0 | 328388 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 1 | 328388 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 2 | 328388 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 3 | 328388 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 4 | 328388 | EIM3.1 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 5 | 328388 | EIM3.1 4 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 6 | 328388 | EIM3.1 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 7 | 328388 | EIM3.1 5 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 8 | 328388 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 9 | 328388 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 10 | 328388 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 11 | 328388 | EIM3.1 4 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 12 | 328388 | EIM3.1 5 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 13 | 328388 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 14 | 328388 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 15 | 328388 | AC protections not running (differential current) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28388 | 0 | 328389 | AC data is missing (differential current) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28388 | 1 | 328389 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 2 | 328389 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 3 | 328389 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 4 | 328389 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 5 | 328389 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 6 | 328389 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 7 | 328389 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 8 | 328389 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 9 | 328389 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 10 | 328389 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 11 | 328389 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 12 | 328389 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 13 | 328389 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 14 | 328389 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 15 | 328389 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 0 | 328390 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 1 | 328390 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 2 | 328390 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 4 | 328390 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 5 | 328390 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 7 | 328390 | Controller ID not configured | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 12 | 328390 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 13 | 328390 | Blackout detection mismatch | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28390 | 0 | 328391 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 1 | 328391 | Parameters - Communication - NTP - NTP server 1 not responding - Information - Flags - NTP server 1 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 2 | 328391 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 3 | 328391 | Parameters - Communication - NTP - NTP server 2 not responding - Information - Flags - NTP server 2 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 4 | 328391 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 5 | 328391 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 6 | 328391 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 7 | 328391 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28393 | 8 | 328394 | Controller not part of system | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28393 | 9 | 328394 | Different single-line configurations | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28393 | 10 | 328394 | Single-line missing/none active | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28393 | 11 | 328394 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28393 | 12 | 328394 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28393 | 13 | 328394 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28393 | 14 | 328394 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28393 | 15 | 328394 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28394 | 0 | 328395 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28394 | 1 | 328395 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28394 | 2 | 328395 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28394 | 3 | 328395 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28394 | 4 | 328395 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28394 | 5 | 328395 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28394 | 6 | 328395 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28394 | 7 | 328395 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28394 | 8 | 328395 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28394 | 11 | 328395 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28394 | 12 | 328395 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28394 | 13 | 328395 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28394 | 14 | 328395 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28394 | 15 | 328395 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 0 | 328396 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 1 | 328396 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 2 | 328396 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 3 | 328396 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 4 | 328396 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 5 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 6 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 7 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 8 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 9 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 10 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 11 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 12 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 13 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 14 | 328396 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28395 | 15 | 328396 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 0 | 328397 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 1 | 328397 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 2 | 328397 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 3 | 328397 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 4 | 328397 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 5 | 328397 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 6 | 328397 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 7 | 328397 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 8 | 328397 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 9 | 328397 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 10 | 328397 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 11 | 328397 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 12 | 328397 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 13 | 328397 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 14 | 328397 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28396 | 15 | 328397 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 0 | 328398 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 1 | 328398 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 2 | 328398 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 3 | 328398 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 4 | 328398 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 5 | 328398 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 6 | 328398 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 7 | 328398 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 8 | 328398 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 9 | 328398 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 10 | 328398 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 11 | 328398 | DAVR unsupported AC configuration | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 12 | 328398 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 13 | 328398 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 13 | 328398 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28397 | 13 | 328398 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28397 | 14 | 328398 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 14 | 328398 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28397 | 14 | 328398 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28397 | 15 | 328398 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28397 | 15 | 328398 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28397 | 15 | 328398 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 0 | 328399 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 0 | 328399 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 0 | 328399 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 1 | 328399 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 1 | 328399 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 1 | 328399 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 2 | 328399 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 2 | 328399 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 2 | 328399 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 3 | 328399 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 3 | 328399 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 3 | 328399 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 4 | 328399 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 4 | 328399 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 4 | 328399 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 5 | 328399 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 5 | 328399 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 5 | 328399 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 6 | 328399 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 6 | 328399 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 6 | 328399 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 7 | 328399 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 7 | 328399 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 7 | 328399 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 8 | 328399 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 8 | 328399 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 8 | 328399 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 9 | 328399 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 9 | 328399 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 9 | 328399 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 10 | 328399 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 10 | 328399 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 10 | 328399 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 11 | 328399 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 11 | 328399 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 11 | 328399 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 12 | 328399 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 12 | 328399 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 12 | 328399 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 13 | 328399 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 13 | 328399 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 13 | 328399 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 14 | 328399 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 14 | 328399 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 14 | 328399 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28398 | 15 | 328399 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28398 | 15 | 328399 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28398 | 15 | 328399 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28399 | 0 | 328400 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 1 | 328400 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 2 | 328400 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28399 | 2 | 328400 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 2 | 328400 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28399 | 3 | 328400 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28399 | 3 | 328400 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 3 | 328400 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28399 | 4 | 328400 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28399 | 4 | 328400 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 4 | 328400 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28399 | 5 | 328400 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28399 | 5 | 328400 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 5 | 328400 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28399 | 6 | 328400 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28399 | 6 | 328400 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 6 | 328400 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28399 | 7 | 328400 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28399 | 7 | 328400 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 7 | 328400 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28399 | 8 | 328400 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28399 | 8 | 328400 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 8 | 328400 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28399 | 9 | 328400 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28399 | 9 | 328400 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 9 | 328400 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28399 | 10 | 328400 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28399 | 10 | 328400 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 10 | 328400 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28399 | 11 | 328400 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28399 | 11 | 328400 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 11 | 328400 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28399 | 12 | 328400 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28399 | 12 | 328400 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 12 | 328400 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28399 | 13 | 328400 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28399 | 13 | 328400 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 13 | 328400 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28399 | 14 | 328400 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28399 | 14 | 328400 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 14 | 328400 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28399 | 15 | 328400 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28399 | 15 | 328400 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28399 | 15 | 328400 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28400 | 0 | 328401 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28400 | 0 | 328401 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28400 | 0 | 328401 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28400 | 1 | 328401 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28400 | 1 | 328401 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28400 | 1 | 328401 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28400 | 2 | 328401 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28400 | 2 | 328401 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28400 | 2 | 328401 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28400 | 3 | 328401 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28400 | 3 | 328401 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28400 | 3 | 328401 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28400 | 4 | 328401 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28400 | 4 | 328401 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28400 | 4 | 328401 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28400 | 5 | 328401 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28400 | 5 | 328401 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28400 | 5 | 328401 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28400 | 6 | 328401 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28400 | 6 | 328401 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28400 | 6 | 328401 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28400 | 7 | 328401 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28400 | 7 | 328401 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28400 | 7 | 328401 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28400 | 8 | 328401 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28400 | 8 | 328401 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28400 | 8 | 328401 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28400 | 9 | 328401 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28400 | 9 | 328401 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28400 | 9 | 328401 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28400 | 10 | 328401 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28400 | 10 | 328401 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28400 | 10 | 328401 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28400 | 11 | 328401 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28400 | 11 | 328401 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28400 | 11 | 328401 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28400 | 12 | 328401 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28400 | 12 | 328401 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28400 | 12 | 328401 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28400 | 13 | 328401 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28400 | 13 | 328401 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28400 | 13 | 328401 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28400 | 14 | 328401 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28400 | 14 | 328401 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28400 | 14 | 328401 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28400 | 15 | 328401 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28400 | 15 | 328401 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28400 | 15 | 328401 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28401 | 0 | 328402 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28401 | 0 | 328402 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28401 | 0 | 328402 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28401 | 1 | 328402 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28401 | 1 | 328402 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28401 | 1 | 328402 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28401 | 2 | 328402 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28401 | 2 | 328402 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28401 | 2 | 328402 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28401 | 3 | 328402 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28401 | 3 | 328402 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28401 | 3 | 328402 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28401 | 4 | 328402 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28401 | 4 | 328402 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28401 | 4 | 328402 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28401 | 5 | 328402 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28401 | 5 | 328402 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28401 | 5 | 328402 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28401 | 6 | 328402 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28401 | 6 | 328402 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Inhibited | 28401 | 6 | 328402 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28404 | 3 | 328405 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28404 | 4 | 328405 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28404 | 5 | 328405 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28404 | 6 | 328405 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 4 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28404 | 7 | 328405 | External MB open failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28404 | 8 | 328405 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28404 | 9 | 328405 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28404 | 10 | 328405 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28404 | 11 | 328405 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28404 | 12 | 328405 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28404 | 13 | 328405 | Parameters - Breakers - Close before excitation - CBE failure - Information - Flags - Close before excitation failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28404 | 14 | 328405 | Load too high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28404 | 15 | 328405 | ID to run configuration failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28405 | 1 | 328406 | Parameters - System - Monitoring - Missing any genset controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28405 | 2 | 328406 | Parameters - System - Monitoring - Missing any mains controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28405 | 3 | 328406 | Parameters - System - Monitoring - Missing any bus tie controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28405 | 4 | 328406 | Can ID not available | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28405 | 5 | 328406 | Duplicated CAN IDs | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28405 | 6 | 328406 | Parameters - Local power management - Alarms - Busbar blocked - Information - Flags - Busbar blocked due to position failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28405 | 7 | 328406 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Flags - Busbar A blocked due to position failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28405 | 8 | 328406 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Flags - Busbar B blocked due to position failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28405 | 9 | 328406 | Parameters - System - Monitoring - BTB 33 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28405 | 10 | 328406 | Parameters - System - Monitoring - BTB 34 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28405 | 11 | 328406 | Parameters - System - Monitoring - BTB 35 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28405 | 12 | 328406 | Parameters - System - Monitoring - BTB 36 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28405 | 13 | 328406 | Parameters - System - Monitoring - BTB 37 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28405 | 14 | 328406 | Parameters - System - Monitoring - BTB 38 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28405 | 15 | 328406 | Parameters - System - Monitoring - BTB 39 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 0 | 328407 | Parameters - System - Monitoring - BTB 40 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 1 | 328407 | Primary CAN missing ID 1 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 2 | 328407 | Primary CAN missing ID 2 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 3 | 328407 | Primary CAN missing ID 3 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 4 | 328407 | Primary CAN missing ID 4 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 5 | 328407 | Primary CAN missing ID 5 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 6 | 328407 | Primary CAN missing ID 6 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 7 | 328407 | Primary CAN missing ID 7 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 8 | 328407 | Primary CAN missing ID 8 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 9 | 328407 | Primary CAN missing ID 9 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 10 | 328407 | Primary CAN missing ID 10 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 11 | 328407 | Primary CAN missing ID 11 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 12 | 328407 | Primary CAN missing ID 12 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 13 | 328407 | Primary CAN missing ID 13 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 14 | 328407 | Primary CAN missing ID 14 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 15 | 328407 | Primary CAN missing ID 15 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 0 | 328408 | Primary CAN missing ID 16 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 1 | 328408 | Primary CAN missing ID 17 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 2 | 328408 | Primary CAN missing ID 18 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 3 | 328408 | Primary CAN missing ID 19 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 4 | 328408 | Primary CAN missing ID 20 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 5 | 328408 | Primary CAN missing ID 21 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 6 | 328408 | Primary CAN missing ID 22 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 7 | 328408 | Primary CAN missing ID 23 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 8 | 328408 | Primary CAN missing ID 24 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 9 | 328408 | Primary CAN missing ID 25 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 10 | 328408 | Primary CAN missing ID 26 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 11 | 328408 | Primary CAN missing ID 27 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 12 | 328408 | Primary CAN missing ID 28 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 13 | 328408 | Primary CAN missing ID 29 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 14 | 328408 | Primary CAN missing ID 30 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 15 | 328408 | Primary CAN missing ID 31 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 0 | 328409 | Primary CAN missing ID 32 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 1 | 328409 | Primary CAN missing ID 33 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 2 | 328409 | Primary CAN missing ID 34 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 3 | 328409 | Primary CAN missing ID 35 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 4 | 328409 | Primary CAN missing ID 36 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 5 | 328409 | Primary CAN missing ID 37 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 6 | 328409 | Primary CAN missing ID 38 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 7 | 328409 | Primary CAN missing ID 39 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 8 | 328409 | Primary CAN missing ID 40 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 9 | 328409 | Secondary CAN missing ID 1 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 10 | 328409 | Secondary CAN missing ID 2 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 11 | 328409 | Secondary CAN missing ID 3 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 12 | 328409 | Secondary CAN missing ID 4 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 13 | 328409 | Secondary CAN missing ID 5 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 14 | 328409 | Secondary CAN missing ID 6 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 15 | 328409 | Secondary CAN missing ID 7 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 0 | 328410 | Secondary CAN missing ID 8 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 1 | 328410 | Secondary CAN missing ID 9 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 2 | 328410 | Secondary CAN missing ID 10 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 3 | 328410 | Secondary CAN missing ID 11 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 4 | 328410 | Secondary CAN missing ID 12 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 5 | 328410 | Secondary CAN missing ID 13 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 6 | 328410 | Secondary CAN missing ID 14 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 7 | 328410 | Secondary CAN missing ID 15 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 8 | 328410 | Secondary CAN missing ID 16 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 9 | 328410 | Secondary CAN missing ID 17 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 10 | 328410 | Secondary CAN missing ID 18 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 11 | 328410 | Secondary CAN missing ID 19 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 12 | 328410 | Secondary CAN missing ID 20 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 13 | 328410 | Secondary CAN missing ID 21 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 14 | 328410 | Secondary CAN missing ID 22 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 15 | 328410 | Secondary CAN missing ID 23 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 0 | 328411 | Secondary CAN missing ID 24 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 1 | 328411 | Secondary CAN missing ID 25 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 2 | 328411 | Secondary CAN missing ID 26 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 3 | 328411 | Secondary CAN missing ID 27 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 4 | 328411 | Secondary CAN missing ID 28 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 5 | 328411 | Secondary CAN missing ID 29 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 6 | 328411 | Secondary CAN missing ID 30 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 7 | 328411 | Secondary CAN missing ID 31 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 8 | 328411 | Secondary CAN missing ID 32 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 9 | 328411 | Secondary CAN missing ID 33 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 10 | 328411 | Secondary CAN missing ID 34 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 11 | 328411 | Secondary CAN missing ID 35 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 12 | 328411 | Secondary CAN missing ID 36 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 13 | 328411 | Secondary CAN missing ID 37 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 14 | 328411 | Secondary CAN missing ID 38 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 15 | 328411 | Secondary CAN missing ID 39 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28411 | 0 | 328412 | Secondary CAN missing ID 40 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28411 | 1 | 328412 | Priority error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28411 | 2 | 328412 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - Flags - NEL 1 over-current | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28411 | 3 | 328412 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - Flags - NEL 1 under-frequency | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28411 | 4 | 328412 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - Flags - NEL 1 overload 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28411 | 5 | 328412 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - Flags - NEL 1 overload 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28411 | 6 | 328412 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - Flags - NEL 1 reactive overload | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28411 | 7 | 328412 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - Flags - NEL 2 over-current | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28411 | 8 | 328412 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - Flags - NEL 2 under-frequency | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28411 | 9 | 328412 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - Flags - NEL 2 overload 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28411 | 10 | 328412 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - Flags - NEL 2 overload 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28411 | 11 | 328412 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - Flags - NEL 2 reactive overload | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28411 | 12 | 328412 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - Flags - NEL 3 over-current | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28411 | 13 | 328412 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - Flags - NEL 3 under-frequency | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28411 | 14 | 328412 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - Flags - NEL 3 overload 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28411 | 15 | 328412 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - Flags - NEL 3 overload 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28412 | 0 | 328413 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - Flags - NEL 3 reactive overload | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Inhibited | 28412 | 1 | 328413 | Parameters - System - Monitoring - Single-line hazard - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28412 | 2 | 328413 | ID not present | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28412 | 3 | 328413 | Unsupported application | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28412 | 4 | 328413 | Application internal CAN protocol conflict | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28412 | 5 | 328413 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Flags - Section P> | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28412 | 6 | 328413 | Dry mode: Voltage level unexpected | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28412 | 7 | 328413 | Invalid DAVR configuration | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28412 | 8 | 328413 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28412 | 10 | 328413 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28412 | 12 | 328413 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28412 | 12 | 328413 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Inhibited | 28412 | 12 | 328413 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Inhibited | 28412 | 13 | 328413 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Inhibited | 28412 | 13 | 328413 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Inhibited | 28412 | 15 | 328413 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 0 | 328414 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 1 | 328414 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 2 | 328414 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 3 | 328414 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 4 | 328414 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 5 | 328414 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 6 | 328414 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 7 | 328414 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 8 | 328414 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 9 | 328414 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 10 | 328414 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 11 | 328414 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 12 | 328414 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 13 | 328414 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 14 | 328414 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 15 | 328414 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 0 | 328415 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 1 | 328415 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 2 | 328415 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 3 | 328415 | Live voltage detected | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 4 | 328415 | Internal issue detected. A restart is required soon! | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 5 | 328415 | Parameters - System - Monitoring - Missing controllers - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 6 | 328415 | Card issue detected | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 7 | 328415 | Card configuration failed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 8 | 328415 | Unknown traffic on DEIF network | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 9 | 328415 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28414 | 10 | 328415 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28414 | 11 | 328415 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Inhibited | 28414 | 12 | 328415 | Local I/O service error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 13 | 328415 | App logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 14 | 328415 | Event logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 15 | 328415 | Licence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28415 | 0 | 328416 | Brightness is dimmed according to temperature | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28415 | 1 | 328416 | Parameters - Grid code - Mains sync inhibit - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28415 | 2 | 328416 | Parameters - Grid code - Capability curve - Protections - Import protection - Information - Flags - Power import capability curve protection | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28415 | 3 | 328416 | Parameters - Grid code - Capability curve - Protections - Export protection - Information - Flags - Power export capability curve protection | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28415 | 4 | 328416 | Hardware is not compatible based on module versions | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28415 | 5 | 328416 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28415 | 6 | 328416 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28415 | 7 | 328416 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Inhibited | 28417 | 8 | 328418 | Configuration not supported by licence | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28468 | 12 | 328469 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28468 | 13 | 328469 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28468 | 14 | 328469 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28468 | 15 | 328469 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 0 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 1 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 2 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 3 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 4 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 5 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 6 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 7 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 8 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 9 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 10 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 11 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 12 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 13 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 14 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 15 | 328470 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 0 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 1 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 2 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 3 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 4 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 5 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 6 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 7 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 8 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 9 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 10 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 11 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 12 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 13 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 14 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 15 | 328471 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 0 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 1 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 2 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 3 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 4 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 5 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 6 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 7 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 8 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 9 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 10 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 11 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 12 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 13 | 328472 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 0 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 1 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 2 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 3 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 4 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 5 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 6 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 7 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 8 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 9 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 10 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 11 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 12 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 13 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 14 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 15 | 328476 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 0 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 1 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 2 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 3 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 4 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 5 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 6 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 7 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 8 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 9 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 10 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 11 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 12 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 13 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 14 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 15 | 328477 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 0 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 1 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 2 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 3 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 4 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 5 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 6 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 7 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 8 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 9 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 10 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 11 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 12 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 13 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 14 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 15 | 328478 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 0 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 1 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 2 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 3 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 4 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 5 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 6 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 7 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 8 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 9 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 10 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 11 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 12 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 13 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 14 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 15 | 328479 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 0 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 1 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 2 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 3 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 4 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 5 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 6 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 7 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 8 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 9 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 10 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 11 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 12 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 13 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 14 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 15 | 328480 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 0 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 1 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 2 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 3 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 4 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 5 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 6 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 7 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 8 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 9 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 10 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 11 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 12 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 13 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 14 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 15 | 328481 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 0 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 1 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 2 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 3 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 4 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 5 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 6 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 7 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 8 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 9 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 10 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 11 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 12 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 13 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 14 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 15 | 328482 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 0 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 1 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 2 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 3 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 4 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 5 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 6 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 7 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 8 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 9 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 10 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 11 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 12 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 13 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 14 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 15 | 328483 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 0 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 1 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 2 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 3 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 4 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 5 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 6 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 7 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 8 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 9 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 10 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 11 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 12 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 13 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 14 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 15 | 328484 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 0 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 1 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 2 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 3 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 4 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 5 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 6 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 7 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 8 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 9 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 10 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 11 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 12 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 13 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 14 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 15 | 328485 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 0 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 1 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 2 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 3 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 4 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 5 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 6 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 7 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 8 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 9 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 10 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 11 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 12 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 13 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 14 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 15 | 328486 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 0 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 1 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 2 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 3 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 4 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 5 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 6 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 7 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 8 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 9 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 10 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 11 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 12 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 13 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 14 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 15 | 328487 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 0 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 1 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 2 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 3 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 4 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 5 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 6 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 7 | 328488 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28500 | 0 | 328501 | Application initialisation error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28500 | 1 | 328501 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28500 | 2 | 328501 | Preliminary software | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28500 | 3 | 328501 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28500 | 4 | 328501 | Parameters - Engine - Start sequence - Start failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28500 | 5 | 328501 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28500 | 6 | 328501 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28500 | 7 | 328501 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28500 | 8 | 328501 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28500 | 9 | 328501 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28500 | 10 | 328501 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28500 | 11 | 328501 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28500 | 13 | 328501 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28500 | 14 | 328501 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28500 | 15 | 328501 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28501 | 0 | 328502 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28501 | 1 | 328502 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28501 | 2 | 328502 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28501 | 3 | 328502 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28501 | 4 | 328502 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28501 | 5 | 328502 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28501 | 6 | 328502 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28501 | 11 | 328502 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28502 | 9 | 328503 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28502 | 9 | 328503 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28502 | 9 | 328503 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28502 | 10 | 328503 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28502 | 10 | 328503 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28502 | 10 | 328503 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28502 | 11 | 328503 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28502 | 11 | 328503 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28502 | 11 | 328503 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28502 | 12 | 328503 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28502 | 12 | 328503 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28502 | 12 | 328503 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28502 | 13 | 328503 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28502 | 13 | 328503 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28502 | 13 | 328503 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28502 | 14 | 328503 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28502 | 14 | 328503 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28502 | 14 | 328503 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28502 | 15 | 328503 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28502 | 15 | 328503 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28502 | 15 | 328503 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28503 | 0 | 328504 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28503 | 0 | 328504 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28503 | 0 | 328504 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28503 | 1 | 328504 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28503 | 1 | 328504 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Out of service | 28503 | 2 | 328504 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28503 | 2 | 328504 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Out of service | 28503 | 3 | 328504 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28503 | 3 | 328504 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Out of service | 28503 | 4 | 328504 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28503 | 4 | 328504 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Out of service | 28503 | 5 | 328504 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28503 | 5 | 328504 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Out of service | 28503 | 6 | 328504 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28503 | 6 | 328504 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Out of service | 28503 | 7 | 328504 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28503 | 7 | 328504 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Out of service | 28503 | 8 | 328504 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28503 | 8 | 328504 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Out of service | 28503 | 12 | 328504 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28503 | 12 | 328504 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28503 | 12 | 328504 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28503 | 13 | 328504 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28503 | 13 | 328504 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28503 | 13 | 328504 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28503 | 14 | 328504 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28506 | 7 | 328507 | Parameters - Mains - Additional protections - ROCOF - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28506 | 7 | 328507 | Parameters - Busbar - Additional protections - ROCOF - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28506 | 7 | 328507 | Parameters - Busbar B - Additional protections - ROCOF - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28506 | 8 | 328507 | Parameters - Mains - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28506 | 8 | 328507 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28506 | 8 | 328507 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28506 | 9 | 328507 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28506 | 9 | 328507 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28506 | 9 | 328507 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28506 | 10 | 328507 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28506 | 11 | 328507 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28506 | 12 | 328507 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28506 | 12 | 328507 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28506 | 12 | 328507 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28506 | 13 | 328507 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28506 | 13 | 328507 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28506 | 13 | 328507 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28506 | 14 | 328507 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28506 | 14 | 328507 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28506 | 14 | 328507 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28506 | 15 | 328507 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28506 | 15 | 328507 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28506 | 15 | 328507 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28507 | 3 | 328508 | Protection set point out of range | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 4 | 328508 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28507 | 5 | 328508 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28507 | 6 | 328508 | Protection set point out of range (differential current) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28507 | 7 | 328508 | Parameters - Local - Mode - Not under remote control - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 9 | 328508 | Parameters - Local - Monitoring - System not OK - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 10 | 328508 | Configuration update delayed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 11 | 328508 | Critical process error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 12 | 328508 | Restore error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 13 | 328508 | SD-card format error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 14 | 328508 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28507 | 15 | 328508 | Fieldbus configuration exceeded maximum I/O configuration | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 0 | 328509 | Parameters - Custom alarms - Custom alarm 0 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 1 | 328509 | Parameters - Custom alarms - Custom alarm 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 2 | 328509 | Parameters - Custom alarms - Custom alarm 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 3 | 328509 | Parameters - Custom alarms - Custom alarm 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 4 | 328509 | Parameters - Custom alarms - Custom alarm 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 5 | 328509 | Parameters - Custom alarms - Custom alarm 5 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 6 | 328509 | Parameters - Custom alarms - Custom alarm 6 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 7 | 328509 | Parameters - Custom alarms - Custom alarm 7 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 8 | 328509 | Parameters - Custom alarms - Custom alarm 8 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 9 | 328509 | Parameters - Custom alarms - Custom alarm 9 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 10 | 328509 | Parameters - Custom alarms - Custom alarm 10 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 11 | 328509 | Parameters - Custom alarms - Custom alarm 11 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 12 | 328509 | Parameters - Custom alarms - Custom alarm 12 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 13 | 328509 | Parameters - Custom alarms - Custom alarm 13 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 14 | 328509 | Parameters - Custom alarms - Custom alarm 14 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28508 | 15 | 328509 | Parameters - Custom alarms - Custom alarm 15 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 0 | 328510 | Parameters - Custom alarms - Custom alarm 16 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 1 | 328510 | Parameters - Custom alarms - Custom alarm 17 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 2 | 328510 | Parameters - Custom alarms - Custom alarm 18 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 3 | 328510 | Parameters - Custom alarms - Custom alarm 19 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 4 | 328510 | Parameters - Custom alarms - Custom alarm 20 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 5 | 328510 | Parameters - Custom alarms - Custom alarm 21 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 6 | 328510 | Parameters - Custom alarms - Custom alarm 22 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 7 | 328510 | Parameters - Custom alarms - Custom alarm 23 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 8 | 328510 | Parameters - Custom alarms - Custom alarm 24 - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28509 | 9 | 328510 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28509 | 10 | 328510 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28510 | 3 | 328511 | Required hardware card(s) not found | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28510 | 4 | 328511 | Software mismatch on hardware module(s) | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28510 | 5 | 328511 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Out of service | 28510 | 5 | 328511 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Out of service | 28510 | 5 | 328511 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28510 | 6 | 328511 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Out of service | 28510 | 6 | 328511 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28510 | 6 | 328511 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28510 | 7 | 328511 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Out of service | 28510 | 7 | 328511 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Out of service | 28510 | 7 | 328511 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28510 | 8 | 328511 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Out of service | 28510 | 8 | 328511 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Out of service | 28510 | 8 | 328511 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28510 | 9 | 328511 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 |  |  |  | X
Alarm status: Out of service | 28510 | 9 | 328511 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Out of service | 28510 | 9 | 328511 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28510 | 10 | 328511 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Out of service | 28510 | 10 | 328511 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28510 | 10 | 328511 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28510 | 11 | 328511 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Out of service | 28510 | 11 | 328511 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28510 | 11 | 328511 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28510 | 12 | 328511 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | BOOL | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Out of service | 28510 | 12 | 328511 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28510 | 12 | 328511 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | BOOL | X * 1 | X * 1 | [6 empty] | X
Alarm status: Out of service | 28511 | 2 | 328512 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm | BOOL | X * 1 | X * 1 |  |  |  | X | X |  | X | X
Alarm status: Out of service | 28511 | 3 | 328512 | Parameters - Engine - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28511 | 3 | 328512 | Parameters - Busbar A - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28511 | 3 | 328512 | Parameters - Mains - Emergency stop - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28511 | 4 | 328512 | Clock battery failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 5 | 328512 | Controller temperature too high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 6 | 328512 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 7 | 328512 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 8 | 328512 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 9 | 328512 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 10 | 328512 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 11 | 328512 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 12 | 328512 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 13 | 328512 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 14 | 328512 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28511 | 15 | 328512 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 0 | 328513 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 1 | 328513 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 2 | 328513 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 3 | 328513 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 4 | 328513 | EIM3.1 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 5 | 328513 | EIM3.1 4 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 6 | 328513 | EIM3.1 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 7 | 328513 | EIM3.1 5 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 8 | 328513 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 9 | 328513 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 10 | 328513 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 11 | 328513 | EIM3.1 4 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 12 | 328513 | EIM3.1 5 relay 4 wire break | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 13 | 328513 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 14 | 328513 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28512 | 15 | 328513 | AC protections not running (differential current) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28513 | 0 | 328514 | AC data is missing (differential current) | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28513 | 1 | 328514 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 2 | 328514 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 3 | 328514 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 4 | 328514 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 5 | 328514 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 6 | 328514 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 7 | 328514 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 8 | 328514 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 9 | 328514 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 10 | 328514 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 11 | 328514 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 12 | 328514 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 13 | 328514 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 14 | 328514 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28513 | 15 | 328514 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 0 | 328515 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 1 | 328515 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 2 | 328515 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 4 | 328515 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 5 | 328515 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 7 | 328515 | Controller ID not configured | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 12 | 328515 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28514 | 13 | 328515 | Blackout detection mismatch | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28515 | 0 | 328516 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28515 | 1 | 328516 | Parameters - Communication - NTP - NTP server 1 not responding - Information - Flags - NTP server 1 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28515 | 2 | 328516 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28515 | 3 | 328516 | Parameters - Communication - NTP - NTP server 2 not responding - Information - Flags - NTP server 2 is not responding | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28515 | 4 | 328516 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28515 | 5 | 328516 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28515 | 6 | 328516 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28515 | 7 | 328516 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28518 | 8 | 328519 | Controller not part of system | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28518 | 9 | 328519 | Different single-line configurations | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28518 | 10 | 328519 | Single-line missing/none active | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28518 | 11 | 328519 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28518 | 12 | 328519 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28518 | 13 | 328519 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28518 | 14 | 328519 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28518 | 15 | 328519 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28519 | 0 | 328520 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28519 | 1 | 328520 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28519 | 2 | 328520 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28519 | 3 | 328520 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28519 | 4 | 328520 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28519 | 5 | 328520 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28519 | 6 | 328520 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28519 | 7 | 328520 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28519 | 8 | 328520 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28519 | 11 | 328520 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28519 | 12 | 328520 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28519 | 13 | 328520 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28519 | 14 | 328520 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28519 | 15 | 328520 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 0 | 328521 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 1 | 328521 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 2 | 328521 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 3 | 328521 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 4 | 328521 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 5 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 6 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 7 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 8 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 9 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 10 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 11 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 12 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 13 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 14 | 328521 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28520 | 15 | 328521 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 0 | 328522 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 1 | 328522 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 2 | 328522 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 3 | 328522 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 4 | 328522 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 5 | 328522 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 6 | 328522 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 7 | 328522 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 8 | 328522 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 9 | 328522 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 10 | 328522 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 11 | 328522 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 12 | 328522 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 13 | 328522 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 14 | 328522 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28521 | 15 | 328522 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 0 | 328523 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 1 | 328523 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 2 | 328523 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 3 | 328523 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 4 | 328523 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 5 | 328523 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 6 | 328523 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 7 | 328523 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 8 | 328523 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 9 | 328523 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 10 | 328523 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 11 | 328523 | DAVR unsupported AC configuration | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 12 | 328523 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 13 | 328523 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 13 | 328523 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28522 | 13 | 328523 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28522 | 14 | 328523 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 14 | 328523 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28522 | 14 | 328523 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28522 | 15 | 328523 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28522 | 15 | 328523 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28522 | 15 | 328523 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 0 | 328524 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 0 | 328524 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 0 | 328524 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 1 | 328524 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 1 | 328524 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 1 | 328524 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 2 | 328524 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 2 | 328524 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 2 | 328524 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 3 | 328524 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 3 | 328524 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 3 | 328524 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 4 | 328524 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 4 | 328524 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 4 | 328524 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 5 | 328524 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 5 | 328524 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 5 | 328524 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 6 | 328524 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 6 | 328524 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 6 | 328524 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 7 | 328524 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 7 | 328524 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 7 | 328524 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 8 | 328524 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 8 | 328524 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 8 | 328524 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 9 | 328524 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 9 | 328524 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 9 | 328524 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 10 | 328524 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 10 | 328524 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 10 | 328524 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 11 | 328524 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 11 | 328524 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 11 | 328524 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 12 | 328524 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 12 | 328524 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 12 | 328524 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 13 | 328524 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 13 | 328524 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 13 | 328524 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 14 | 328524 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 14 | 328524 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 14 | 328524 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28523 | 15 | 328524 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28523 | 15 | 328524 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28523 | 15 | 328524 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28524 | 0 | 328525 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 1 | 328525 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 2 | 328525 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28524 | 2 | 328525 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 2 | 328525 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28524 | 3 | 328525 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28524 | 3 | 328525 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 3 | 328525 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28524 | 4 | 328525 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28524 | 4 | 328525 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 4 | 328525 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28524 | 5 | 328525 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28524 | 5 | 328525 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 5 | 328525 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28524 | 6 | 328525 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28524 | 6 | 328525 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 6 | 328525 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28524 | 7 | 328525 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28524 | 7 | 328525 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 7 | 328525 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28524 | 8 | 328525 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28524 | 8 | 328525 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 8 | 328525 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28524 | 9 | 328525 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28524 | 9 | 328525 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 9 | 328525 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28524 | 10 | 328525 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28524 | 10 | 328525 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 10 | 328525 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28524 | 11 | 328525 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28524 | 11 | 328525 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 11 | 328525 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28524 | 12 | 328525 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28524 | 12 | 328525 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 12 | 328525 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28524 | 13 | 328525 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28524 | 13 | 328525 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 13 | 328525 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28524 | 14 | 328525 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28524 | 14 | 328525 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 14 | 328525 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28524 | 15 | 328525 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28524 | 15 | 328525 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28524 | 15 | 328525 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28525 | 0 | 328526 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28525 | 0 | 328526 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28525 | 0 | 328526 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28525 | 1 | 328526 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28525 | 1 | 328526 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28525 | 1 | 328526 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28525 | 2 | 328526 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28525 | 2 | 328526 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28525 | 2 | 328526 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28525 | 3 | 328526 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28525 | 3 | 328526 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28525 | 3 | 328526 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28525 | 4 | 328526 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28525 | 4 | 328526 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28525 | 4 | 328526 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28525 | 5 | 328526 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28525 | 5 | 328526 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28525 | 5 | 328526 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28525 | 6 | 328526 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28525 | 6 | 328526 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28525 | 6 | 328526 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28525 | 7 | 328526 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28525 | 7 | 328526 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28525 | 7 | 328526 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28525 | 8 | 328526 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28525 | 8 | 328526 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28525 | 8 | 328526 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28525 | 9 | 328526 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28525 | 9 | 328526 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28525 | 9 | 328526 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28525 | 10 | 328526 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28525 | 10 | 328526 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28525 | 10 | 328526 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28525 | 11 | 328526 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28525 | 11 | 328526 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28525 | 11 | 328526 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28525 | 12 | 328526 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28525 | 12 | 328526 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28525 | 12 | 328526 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28525 | 13 | 328526 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28525 | 13 | 328526 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28525 | 13 | 328526 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28525 | 14 | 328526 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28525 | 14 | 328526 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28525 | 14 | 328526 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28525 | 15 | 328526 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28525 | 15 | 328526 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28525 | 15 | 328526 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28526 | 0 | 328527 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28526 | 0 | 328527 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28526 | 0 | 328527 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28526 | 1 | 328527 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28526 | 1 | 328527 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28526 | 1 | 328527 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28526 | 2 | 328527 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28526 | 2 | 328527 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28526 | 2 | 328527 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28526 | 3 | 328527 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28526 | 3 | 328527 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28526 | 3 | 328527 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28526 | 4 | 328527 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28526 | 4 | 328527 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28526 | 4 | 328527 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28526 | 5 | 328527 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28526 | 5 | 328527 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28526 | 5 | 328527 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28526 | 6 | 328527 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28526 | 6 | 328527 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | BOOL | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Out of service | 28526 | 6 | 328527 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28529 | 3 | 328530 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28529 | 4 | 328530 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28529 | 5 | 328530 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 3 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28529 | 6 | 328530 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 4 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28529 | 7 | 328530 | External MB open failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28529 | 8 | 328530 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28529 | 9 | 328530 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28529 | 10 | 328530 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28529 | 11 | 328530 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28529 | 12 | 328530 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28529 | 13 | 328530 | Parameters - Breakers - Close before excitation - CBE failure - Information - Flags - Close before excitation failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28529 | 14 | 328530 | Load too high | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28529 | 15 | 328530 | ID to run configuration failure | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28530 | 1 | 328531 | Parameters - System - Monitoring - Missing any genset controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28530 | 2 | 328531 | Parameters - System - Monitoring - Missing any mains controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28530 | 3 | 328531 | Parameters - System - Monitoring - Missing any bus tie controller - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28530 | 4 | 328531 | Can ID not available | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28530 | 5 | 328531 | Duplicated CAN IDs | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28530 | 6 | 328531 | Parameters - Local power management - Alarms - Busbar blocked - Information - Flags - Busbar blocked due to position failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28530 | 7 | 328531 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Flags - Busbar A blocked due to position failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28530 | 8 | 328531 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Flags - Busbar B blocked due to position failure | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28530 | 9 | 328531 | Parameters - System - Monitoring - BTB 33 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28530 | 10 | 328531 | Parameters - System - Monitoring - BTB 34 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28530 | 11 | 328531 | Parameters - System - Monitoring - BTB 35 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28530 | 12 | 328531 | Parameters - System - Monitoring - BTB 36 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28530 | 13 | 328531 | Parameters - System - Monitoring - BTB 37 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28530 | 14 | 328531 | Parameters - System - Monitoring - BTB 38 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28530 | 15 | 328531 | Parameters - System - Monitoring - BTB 39 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 0 | 328532 | Parameters - System - Monitoring - BTB 40 position failure - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 1 | 328532 | Primary CAN missing ID 1 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 2 | 328532 | Primary CAN missing ID 2 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 3 | 328532 | Primary CAN missing ID 3 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 4 | 328532 | Primary CAN missing ID 4 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 5 | 328532 | Primary CAN missing ID 5 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 6 | 328532 | Primary CAN missing ID 6 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 7 | 328532 | Primary CAN missing ID 7 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 8 | 328532 | Primary CAN missing ID 8 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 9 | 328532 | Primary CAN missing ID 9 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 10 | 328532 | Primary CAN missing ID 10 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 11 | 328532 | Primary CAN missing ID 11 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 12 | 328532 | Primary CAN missing ID 12 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 13 | 328532 | Primary CAN missing ID 13 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 14 | 328532 | Primary CAN missing ID 14 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28531 | 15 | 328532 | Primary CAN missing ID 15 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 0 | 328533 | Primary CAN missing ID 16 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 1 | 328533 | Primary CAN missing ID 17 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 2 | 328533 | Primary CAN missing ID 18 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 3 | 328533 | Primary CAN missing ID 19 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 4 | 328533 | Primary CAN missing ID 20 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 5 | 328533 | Primary CAN missing ID 21 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 6 | 328533 | Primary CAN missing ID 22 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 7 | 328533 | Primary CAN missing ID 23 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 8 | 328533 | Primary CAN missing ID 24 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 9 | 328533 | Primary CAN missing ID 25 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 10 | 328533 | Primary CAN missing ID 26 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 11 | 328533 | Primary CAN missing ID 27 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 12 | 328533 | Primary CAN missing ID 28 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 13 | 328533 | Primary CAN missing ID 29 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 14 | 328533 | Primary CAN missing ID 30 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28532 | 15 | 328533 | Primary CAN missing ID 31 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 0 | 328534 | Primary CAN missing ID 32 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 1 | 328534 | Primary CAN missing ID 33 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 2 | 328534 | Primary CAN missing ID 34 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 3 | 328534 | Primary CAN missing ID 35 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 4 | 328534 | Primary CAN missing ID 36 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 5 | 328534 | Primary CAN missing ID 37 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 6 | 328534 | Primary CAN missing ID 38 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 7 | 328534 | Primary CAN missing ID 39 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 8 | 328534 | Primary CAN missing ID 40 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 9 | 328534 | Secondary CAN missing ID 1 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 10 | 328534 | Secondary CAN missing ID 2 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 11 | 328534 | Secondary CAN missing ID 3 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 12 | 328534 | Secondary CAN missing ID 4 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 13 | 328534 | Secondary CAN missing ID 5 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 14 | 328534 | Secondary CAN missing ID 6 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28533 | 15 | 328534 | Secondary CAN missing ID 7 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 0 | 328535 | Secondary CAN missing ID 8 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 1 | 328535 | Secondary CAN missing ID 9 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 2 | 328535 | Secondary CAN missing ID 10 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 3 | 328535 | Secondary CAN missing ID 11 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 4 | 328535 | Secondary CAN missing ID 12 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 5 | 328535 | Secondary CAN missing ID 13 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 6 | 328535 | Secondary CAN missing ID 14 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 7 | 328535 | Secondary CAN missing ID 15 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 8 | 328535 | Secondary CAN missing ID 16 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 9 | 328535 | Secondary CAN missing ID 17 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 10 | 328535 | Secondary CAN missing ID 18 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 11 | 328535 | Secondary CAN missing ID 19 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 12 | 328535 | Secondary CAN missing ID 20 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 13 | 328535 | Secondary CAN missing ID 21 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 14 | 328535 | Secondary CAN missing ID 22 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28534 | 15 | 328535 | Secondary CAN missing ID 23 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 0 | 328536 | Secondary CAN missing ID 24 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 1 | 328536 | Secondary CAN missing ID 25 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 2 | 328536 | Secondary CAN missing ID 26 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 3 | 328536 | Secondary CAN missing ID 27 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 4 | 328536 | Secondary CAN missing ID 28 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 5 | 328536 | Secondary CAN missing ID 29 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 6 | 328536 | Secondary CAN missing ID 30 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 7 | 328536 | Secondary CAN missing ID 31 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 8 | 328536 | Secondary CAN missing ID 32 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 9 | 328536 | Secondary CAN missing ID 33 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 10 | 328536 | Secondary CAN missing ID 34 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 11 | 328536 | Secondary CAN missing ID 35 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 12 | 328536 | Secondary CAN missing ID 36 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 13 | 328536 | Secondary CAN missing ID 37 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 14 | 328536 | Secondary CAN missing ID 38 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28535 | 15 | 328536 | Secondary CAN missing ID 39 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28536 | 0 | 328537 | Secondary CAN missing ID 40 | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28536 | 1 | 328537 | Priority error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28536 | 2 | 328537 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - Flags - NEL 1 over-current | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28536 | 3 | 328537 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - Flags - NEL 1 under-frequency | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28536 | 4 | 328537 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - Flags - NEL 1 overload 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28536 | 5 | 328537 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - Flags - NEL 1 overload 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28536 | 6 | 328537 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - Flags - NEL 1 reactive overload | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28536 | 7 | 328537 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - Flags - NEL 2 over-current | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28536 | 8 | 328537 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - Flags - NEL 2 under-frequency | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28536 | 9 | 328537 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - Flags - NEL 2 overload 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28536 | 10 | 328537 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - Flags - NEL 2 overload 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28536 | 11 | 328537 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - Flags - NEL 2 reactive overload | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28536 | 12 | 328537 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - Flags - NEL 3 over-current | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28536 | 13 | 328537 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - Flags - NEL 3 under-frequency | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28536 | 14 | 328537 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - Flags - NEL 3 overload 1 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28536 | 15 | 328537 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - Flags - NEL 3 overload 2 | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28537 | 0 | 328538 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - Flags - NEL 3 reactive overload | BOOL | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Out of service | 28537 | 1 | 328538 | Parameters - System - Monitoring - Single-line hazard - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28537 | 2 | 328538 | ID not present | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28537 | 3 | 328538 | Unsupported application | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28537 | 4 | 328538 | Application internal CAN protocol conflict | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28537 | 5 | 328538 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Flags - Section P> | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28537 | 6 | 328538 | Dry mode: Voltage level unexpected | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28537 | 7 | 328538 | Invalid DAVR configuration | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28537 | 8 | 328538 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28537 | 10 | 328538 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28537 | 12 | 328538 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28537 | 12 | 328538 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  |  | X
Alarm status: Out of service | 28537 | 12 | 328538 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Out of service | 28537 | 13 | 328538 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Out of service | 28537 | 13 | 328538 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | BOOL | X * 1 | X * 1 | [7 empty] | X
Alarm status: Out of service | 28537 | 15 | 328538 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 0 | 328539 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 1 | 328539 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 2 | 328539 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 3 | 328539 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 4 | 328539 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 5 | 328539 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 6 | 328539 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 7 | 328539 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 8 | 328539 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 9 | 328539 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 10 | 328539 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 11 | 328539 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 12 | 328539 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 13 | 328539 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 14 | 328539 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28538 | 15 | 328539 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 0 | 328540 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 1 | 328540 | AC protections not running | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 2 | 328540 | AC data is missing | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 3 | 328540 | Live voltage detected | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 4 | 328540 | Internal issue detected. A restart is required soon! | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 5 | 328540 | Parameters - System - Monitoring - Missing controllers - Information - Flags | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 6 | 328540 | Card issue detected | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 7 | 328540 | Card configuration failed | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 8 | 328540 | Unknown traffic on DEIF network | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 9 | 328540 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28539 | 10 | 328540 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28539 | 11 | 328540 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | BOOL | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Out of service | 28539 | 12 | 328540 | Local I/O service error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 13 | 328540 | App logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 14 | 328540 | Event logging failure | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28539 | 15 | 328540 | Licence error | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28540 | 0 | 328541 | Brightness is dimmed according to temperature | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28540 | 1 | 328541 | Parameters - Grid code - Mains sync inhibit - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28540 | 2 | 328541 | Parameters - Grid code - Capability curve - Protections - Import protection - Information - Flags - Power import capability curve protection | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28540 | 3 | 328541 | Parameters - Grid code - Capability curve - Protections - Export protection - Information - Flags - Power export capability curve protection | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28540 | 4 | 328541 | Hardware is not compatible based on module versions | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28540 | 5 | 328541 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 1 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28540 | 6 | 328541 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 2 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28540 | 7 | 328541 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 3 - Information - Flags | BOOL | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Out of service | 28542 | 8 | 328543 | Configuration not supported by licence | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28593 | 12 | 328594 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28593 | 13 | 328594 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28593 | 14 | 328594 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28593 | 15 | 328594 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 0 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 1 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 2 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 3 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 4 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 5 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 6 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 7 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 8 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 9 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 10 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 11 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 12 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 13 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 14 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28594 | 15 | 328595 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 0 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 1 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 2 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 3 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 4 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 5 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 6 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 7 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 8 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 9 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 10 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 11 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 12 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 13 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 14 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28595 | 15 | 328596 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 0 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 1 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 2 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 3 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 4 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 5 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 6 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 7 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 8 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 9 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 10 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 11 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 12 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28596 | 13 | 328597 | Digital custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 0 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 1 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 2 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 3 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 4 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 5 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 6 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 7 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 8 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 9 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 10 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 11 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 12 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 13 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 14 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28600 | 15 | 328601 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 0 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 1 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 2 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 3 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 4 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 5 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 6 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 7 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 8 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 9 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 10 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 11 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 12 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 13 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 14 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28601 | 15 | 328602 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 0 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 1 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 2 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 3 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 4 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 5 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 6 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 7 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 8 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 9 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 10 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 11 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 12 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 13 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 14 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28602 | 15 | 328603 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 0 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 1 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 2 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 3 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 4 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 5 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 6 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 7 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 8 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 9 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 10 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 11 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 12 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 13 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 14 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28603 | 15 | 328604 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 0 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 1 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 2 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 3 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 4 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 5 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 6 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 7 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 8 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 9 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 10 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 11 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 12 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 13 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 14 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28604 | 15 | 328605 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 0 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 1 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 2 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 3 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 4 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 5 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 6 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 7 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 8 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 9 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 10 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 11 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 12 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 13 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 14 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28605 | 15 | 328606 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 0 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 1 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 2 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 3 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 4 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 5 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 6 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 7 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 8 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 9 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 10 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 11 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 12 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 13 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 14 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28606 | 15 | 328607 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 0 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 1 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 2 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 3 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 4 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 5 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 6 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 7 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 8 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 9 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 10 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 11 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 12 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 13 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 14 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28607 | 15 | 328608 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 0 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 1 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 2 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 3 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 4 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 5 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 6 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 7 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 8 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 9 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 10 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 11 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 12 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 13 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 14 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28608 | 15 | 328609 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 0 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 1 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 2 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 3 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 4 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 5 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 6 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 7 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 8 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 9 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 10 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 11 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 12 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 13 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 14 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28609 | 15 | 328610 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 0 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 1 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 2 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 3 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 4 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 5 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 6 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 7 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 8 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 9 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 10 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 11 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 12 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 13 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 14 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28610 | 15 | 328611 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 0 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 1 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 2 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 3 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 4 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 5 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 6 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 7 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 8 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 9 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 10 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 11 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 12 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 13 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 14 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28611 | 15 | 328612 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 0 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 1 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 2 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 3 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 4 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 5 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 6 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Out of service | 28612 | 7 | 328613 | Analogue custom alarm | BOOL | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30000 |  | 330001 | Application initialisation error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30001 |  | 330002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30002 |  | 330003 | Preliminary software | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30003 |  | 330004 | Parameters - Engine - Stop sequence - Stop failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30004 |  | 330005 | Parameters - Engine - Start sequence - Start failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30005 |  | 330006 | Parameters - Engine - Start sequence - Crank failure - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30006 |  | 330007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30007 |  | 330008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30008 |  | 330009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30009 |  | 330010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30010 |  | 330011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Magnetic pickup wire break alarm | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30011 |  | 330012 | Parameters - Engine - Stop sequence - Externally stopped - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30013 |  | 330014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30014 |  | 330015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30015 |  | 330016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30016 |  | 330017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30017 |  | 330018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30018 |  | 330019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30019 |  | 330020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30020 |  | 330021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30021 |  | 330022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30022 |  | 330023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30027 |  | 330028 | Parameters - Engine - Running detection - Primary running feedback failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30041 |  | 330042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - GB closing failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30041 |  | 330042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - BTB closing failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30041 |  | 330042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - MB closing failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Triggered value | 30042 |  | 330043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - GB opening failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30042 |  | 330043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - BTB opening failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30042 |  | 330043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - MB opening failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Triggered value | 30043 |  | 330044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - GB position failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30043 |  | 330044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - BTB position failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30043 |  | 330044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - MB position failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Triggered value | 30044 |  | 330045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - GB configuration failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30044 |  | 330045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - BTB configuration failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30044 |  | 330045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - MB configuration failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Triggered value | 30045 |  | 330046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - GB synchronisation failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30045 |  | 330046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - BTB synchronisation failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30045 |  | 330046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - MB synchronisation failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Triggered value | 30046 |  | 330047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - GB de-load failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30046 |  | 330047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - BTB de-load failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30046 |  | 330047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - MB de-load failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Triggered value | 30047 |  | 330048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - GB tripped (external) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30047 |  | 330048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - BTB tripped (external) | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30047 |  | 330048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - MB tripped (external) | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Triggered value | 30048 |  | 330049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - GB short circuit | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30048 |  | 330049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - BTB short circuit | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30048 |  | 330049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - MB short circuit | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Triggered value | 30049 |  | 330050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - MB closing failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30049 |  | 330050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - TB closing failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Triggered value | 30050 |  | 330051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - MB opening failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30050 |  | 330051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - TB opening failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Triggered value | 30051 |  | 330052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - MB position failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30051 |  | 330052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - TB position failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Triggered value | 30052 |  | 330053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - MB configuration failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30052 |  | 330053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - TB configuration failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Triggered value | 30053 |  | 330054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - MB synchronisation failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30053 |  | 330054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - TB synchronisation failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Triggered value | 30054 |  | 330055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - MB de-load failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30054 |  | 330055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - TB de-load failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Triggered value | 30055 |  | 330056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - MB tripped (external) | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30055 |  | 330056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - TB tripped (external) | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Triggered value | 30056 |  | 330057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - MB short circuit | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30056 |  | 330057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - TB short circuit | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Triggered value | 30060 |  | 330061 | Parameters - Mains - AC setup - Phase sequence error - Information - Mains phase sequence error | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Triggered value | 30060 |  | 330061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Busbar phase sequence error | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30060 |  | 330061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Busbar B phase sequence error | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30061 |  | 330062 | Parameters - Generator - AC setup - Phase sequence error - Information - Generator phase sequence error | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30061 |  | 330062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Busbar A phase sequence error | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30061 |  | 330062 | Parameters - Mains - AC setup - Phase sequence error - Information - Mains phase sequence error | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Triggered value | 30062 |  | 330063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30103 |  | 330104 | Parameters - Mains - Additional protections - ROCOF - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Triggered value | 30103 |  | 330104 | Parameters - Busbar - Additional protections - ROCOF - Information | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30103 |  | 330104 | Parameters - Busbar B - Additional protections - ROCOF - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30104 |  | 330105 | Parameters - Mains - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Triggered value | 30104 |  | 330105 | Parameters - Busbar - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30104 |  | 330105 | Parameters - Busbar B - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30105 |  | 330106 | Parameters - Generator - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30105 |  | 330106 | Parameters - Busbar A - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30105 |  | 330106 | Parameters - Mains - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Triggered value | 30106 |  | 330107 | Parameters - Local - 4th current input - Earth inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30107 |  | 330108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30108 |  | 330109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30108 |  | 330109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30108 |  | 330109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30109 |  | 330110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30109 |  | 330110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30109 |  | 330110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30110 |  | 330111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30110 |  | 330111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30110 |  | 330111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30111 |  | 330112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30111 |  | 330112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30111 |  | 330112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30115 |  | 330116 | Protection set point out of range | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30116 |  | 330117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Stabilised differential | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30117 |  | 330118 | Parameters - Generator - Current protections - High set differential current - Information - High set differential | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30118 |  | 330119 | Protection set point out of range (differential current) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30119 |  | 330120 | Parameters - Local - Mode - Not under remote control - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30121 |  | 330122 | Parameters - Local - Monitoring - System not OK - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30122 |  | 330123 | Configuration update delayed | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30123 |  | 330124 | Critical process error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30124 |  | 330125 | Restore error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30125 |  | 330126 | SD-card format error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30126 |  | 330127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30127 |  | 330128 | Fieldbus configuration exceeded maximum I/O configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30128 |  | 330129 | Parameters - Custom alarms - Custom alarm 0 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30129 |  | 330130 | Parameters - Custom alarms - Custom alarm 1 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30130 |  | 330131 | Parameters - Custom alarms - Custom alarm 2 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30131 |  | 330132 | Parameters - Custom alarms - Custom alarm 3 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30132 |  | 330133 | Parameters - Custom alarms - Custom alarm 4 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30133 |  | 330134 | Parameters - Custom alarms - Custom alarm 5 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30134 |  | 330135 | Parameters - Custom alarms - Custom alarm 6 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30135 |  | 330136 | Parameters - Custom alarms - Custom alarm 7 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30136 |  | 330137 | Parameters - Custom alarms - Custom alarm 8 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30137 |  | 330138 | Parameters - Custom alarms - Custom alarm 9 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30138 |  | 330139 | Parameters - Custom alarms - Custom alarm 10 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30139 |  | 330140 | Parameters - Custom alarms - Custom alarm 11 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30140 |  | 330141 | Parameters - Custom alarms - Custom alarm 12 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30141 |  | 330142 | Parameters - Custom alarms - Custom alarm 13 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30142 |  | 330143 | Parameters - Custom alarms - Custom alarm 14 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30143 |  | 330144 | Parameters - Custom alarms - Custom alarm 15 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30144 |  | 330145 | Parameters - Custom alarms - Custom alarm 16 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30145 |  | 330146 | Parameters - Custom alarms - Custom alarm 17 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30146 |  | 330147 | Parameters - Custom alarms - Custom alarm 18 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30147 |  | 330148 | Parameters - Custom alarms - Custom alarm 19 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30148 |  | 330149 | Parameters - Custom alarms - Custom alarm 20 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30149 |  | 330150 | Parameters - Custom alarms - Custom alarm 21 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30150 |  | 330151 | Parameters - Custom alarms - Custom alarm 22 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30151 |  | 330152 | Parameters - Custom alarms - Custom alarm 23 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30152 |  | 330153 | Parameters - Custom alarms - Custom alarm 24 - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30153 |  | 330154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - GOV regulation error | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30154 |  | 330155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - AVR regulation error | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30163 |  | 330164 | Required hardware card(s) not found | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30164 |  | 330165 | Software mismatch on hardware module(s) | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30165 |  | 330166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Mains L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Triggered value | 30165 |  | 330166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Busbar L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Triggered value | 30165 |  | 330166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Busbar B L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30166 |  | 330167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Generator L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Triggered value | 30166 |  | 330167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Busbar A L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30166 |  | 330167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Mains L1-L2-L3 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30167 |  | 330168 | Parameters - Mains - AC setup - L1 wire break - Information - Mains L1 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Triggered value | 30167 |  | 330168 | Parameters - Busbar - AC setup - L1 wire break - Information - Busbar L1 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Triggered value | 30167 |  | 330168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Busbar B L1 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30168 |  | 330169 | Parameters - Mains - AC setup - L2 wire break - Information - Mains L2 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Triggered value | 30168 |  | 330169 | Parameters - Busbar - AC setup - L2 wire break - Information - Busbar L2 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Triggered value | 30168 |  | 330169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Busbar B L2 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30169 |  | 330170 | Parameters - Mains - AC setup - L3 wire break - Information - Mains L3 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Triggered value | 30169 |  | 330170 | Parameters - Busbar - AC setup - L3 wire break - Information - Busbar L3 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Triggered value | 30169 |  | 330170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Busbar B L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30170 |  | 330171 | Parameters - Generator - AC setup - L1 wire break - Information - Generator L1 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Triggered value | 30170 |  | 330171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Busbar A L1 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30170 |  | 330171 | Parameters - Mains - AC setup - L1 wire break - Information - Mains L1 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30171 |  | 330172 | Parameters - Generator - AC setup - L2 wire break - Information - Generator L2 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Triggered value | 30171 |  | 330172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Busbar A L2 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30171 |  | 330172 | Parameters - Mains - AC setup - L2 wire break - Information - Mains L2 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30172 |  | 330173 | Parameters - Generator - AC setup - L3 wire break - Information - Generator L3 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Triggered value | 30172 |  | 330173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Busbar A L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30172 |  | 330173 | Parameters - Mains - AC setup - L3 wire break - Information - Mains L3 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Triggered value | 30178 |  | 330179 | Parameters - Mains - AC setup - Supervision alarm - Information - Mains supervision alarm | INT16 | X * 1 | X * 1 |  |  |  | X | X |  | X | X
Alarm status: Triggered value | 30179 |  | 330180 | Parameters - Engine - Emergency stop - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30179 |  | 330180 | Parameters - Busbar A - Emergency stop - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30179 |  | 330180 | Parameters - Mains - Emergency stop - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Triggered value | 30180 |  | 330181 | Clock battery failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30181 |  | 330182 | Controller temperature too high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30182 |  | 330183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - PSM3.1 1 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30183 |  | 330184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - PSM3.1 1 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30184 |  | 330185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - PSM3.2 1 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30185 |  | 330186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - PSM3.2 1 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30186 |  | 330187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - PSM3.2 2 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30187 |  | 330188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - PSM3.2 2 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30188 |  | 330189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - PSM3.2 3 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30189 |  | 330190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - PSM3.2 3 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30190 |  | 330191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - EIM3.1 1 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30191 |  | 330192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - EIM3.1 1 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30192 |  | 330193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - EIM3.1 2 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30193 |  | 330194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - EIM3.1 2 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30194 |  | 330195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - EIM3.1 3 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30195 |  | 330196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - EIM3.1 3 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30196 |  | 330197 | EIM3.1 4 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30197 |  | 330198 | EIM3.1 4 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30198 |  | 330199 | EIM3.1 5 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30199 |  | 330200 | EIM3.1 5 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30200 |  | 330201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - EIM3.1 1 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30201 |  | 330202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - EIM3.1 2 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30202 |  | 330203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - EIM3.1 3 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30203 |  | 330204 | EIM3.1 4 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30204 |  | 330205 | EIM3.1 5 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30205 |  | 330206 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30206 |  | 330207 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30207 |  | 330208 | AC protections not running (differential current) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30208 |  | 330209 | AC data is missing (differential current) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30209 |  | 330210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - GAM3.2 1 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30210 |  | 330211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - GAM3.2 1 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30211 |  | 330212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - GAM3.2 2 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30212 |  | 330213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - GAM3.2 2 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30213 |  | 330214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - GAM3.2 3 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30214 |  | 330215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - GAM3.2 3 supply voltage low or missing | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30215 |  | 330216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - PSM3.2 4 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30216 |  | 330217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - PSM3.2 4 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30217 |  | 330218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - PSM3.2 5 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30218 |  | 330219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - PSM3.2 5 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30219 |  | 330220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - PSM3.2 6 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30220 |  | 330221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - PSM3.2 6 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30221 |  | 330222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - PSM3.2 7 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30222 |  | 330223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - PSM3.2 7 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30223 |  | 330224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - PSM3.2 8 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30224 |  | 330225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - PSM3.2 8 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30225 |  | 330226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - PSM3.2 9 supply voltage high | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30226 |  | 330227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - PSM3.2 9 supply voltage low | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30228 |  | 330229 | Parameters - System - Monitoring - Duplicate controller ID - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30229 |  | 330230 | Parameters - System - Monitoring - Missing all controllers - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30231 |  | 330232 | Controller ID not configured | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30236 |  | 330237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30237 |  | 330238 | Blackout detection mismatch | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30240 |  | 330241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - NTP server 1 could not connect | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30241 |  | 330242 | Parameters - Communication - NTP - NTP server 1 not responding - Information - NTP server 1 is not responding | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30242 |  | 330243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - NTP server 2 could not connect | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30243 |  | 330244 | Parameters - Communication - NTP - NTP server 2 not responding - Information - NTP server 2 is not responding | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30244 |  | 330245 | Parameters - Communication - NTP - No NTP server time synchronisation - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30245 |  | 330246 | Parameters - Communication - NTP - No NTP server(s) connected - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30246 |  | 330247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30247 |  | 330248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30296 |  | 330297 | Controller not part of system | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30297 |  | 330298 | Different single-line configurations | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30298 |  | 330299 | Single-line missing/none active | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30299 |  | 330300 | Parameters - Communication - Modbus - Modbus communication timeout - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30300 |  | 330301 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - CODESYS configuration conflict | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30301 |  | 330302 | Parameters - CODESYS - Monitoring - Application not OK - Information - CODESYS application not OK | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30302 |  | 330303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30303 |  | 330304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30304 |  | 330305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30305 |  | 330306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30306 |  | 330307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30307 |  | 330308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30308 |  | 330309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30309 |  | 330310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30310 |  | 330311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30311 |  | 330312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30312 |  | 330313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30315 |  | 330316 | Parameters - Local - CustomLogic - Configuration invalid - Information - CustomLogic configuration invalid | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30316 |  | 330317 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Digital AVR communication error | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30317 |  | 330318 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30318 |  | 330319 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30319 |  | 330320 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30320 |  | 330321 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30321 |  | 330322 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30322 |  | 330323 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30323 |  | 330324 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30324 |  | 330325 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30325 |  | 330326 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30326 |  | 330327 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30327 |  | 330328 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30328 |  | 330329 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30329 |  | 330330 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30330 |  | 330331 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30331 |  | 330332 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30332 |  | 330333 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30333 |  | 330334 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30334 |  | 330335 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30335 |  | 330336 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30336 |  | 330337 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30337 |  | 330338 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30338 |  | 330339 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30339 |  | 330340 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30340 |  | 330341 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30341 |  | 330342 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30342 |  | 330343 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30343 |  | 330344 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30344 |  | 330345 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30345 |  | 330346 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30346 |  | 330347 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30347 |  | 330348 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30348 |  | 330349 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30349 |  | 330350 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30350 |  | 330351 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30351 |  | 330352 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30352 |  | 330353 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30353 |  | 330354 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30354 |  | 330355 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30355 |  | 330356 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30356 |  | 330357 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30357 |  | 330358 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30358 |  | 330359 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30359 |  | 330360 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30360 |  | 330361 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30361 |  | 330362 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30362 |  | 330363 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30363 |  | 330364 | DAVR unsupported AC configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30364 |  | 330365 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Illegal DAVR configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30365 |  | 330366 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Generator under-voltage 1 | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30365 |  | 330366 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Busbar A under-voltage 1 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30365 |  | 330366 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Mains under-voltage 1 | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30366 |  | 330367 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Generator under-voltage 2 | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30366 |  | 330367 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Busbar A under-voltage 2 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30366 |  | 330367 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Mains under-voltage 2 | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30367 |  | 330368 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Generator under-voltage 3 | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30367 |  | 330368 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Busbar A under-voltage 3 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30367 |  | 330368 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Mains under-voltage 3 | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30368 |  | 330369 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Generator over-voltage 1 | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30368 |  | 330369 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Busbar A over-voltage 1 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30368 |  | 330369 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Mains over-voltage 1 | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30369 |  | 330370 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Generator over-voltage 2 | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30369 |  | 330370 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Busbar A over-voltage 2 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30369 |  | 330370 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Mains over-voltage 2 | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30370 |  | 330371 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Generator voltage unbalance | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30370 |  | 330371 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Busbar A voltage unbalance | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30370 |  | 330371 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Mains voltage unbalance | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30371 |  | 330372 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Generator negative sequence voltage | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30371 |  | 330372 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Busbar A negative sequence voltage | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30371 |  | 330372 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Mains negative sequence voltage | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30372 |  | 330373 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Generator zero sequence voltage | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30372 |  | 330373 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Busbar A zero sequence voltage | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30372 |  | 330373 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Mains zero sequence voltage | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30373 |  | 330374 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Generator positive sequence under-voltage | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30373 |  | 330374 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Busbar A positive sequence under-voltage | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30373 |  | 330374 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Mains positive sequence under-voltage | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30374 |  | 330375 | Parameters - Generator - Current protections - Over-current 1 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30374 |  | 330375 | Parameters - Busbar A - Current protections - Over-current 1 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30374 |  | 330375 | Parameters - Mains - Current protections - Over-current 1 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30375 |  | 330376 | Parameters - Generator - Current protections - Over-current 2 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30375 |  | 330376 | Parameters - Busbar A - Current protections - Over-current 2 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30375 |  | 330376 | Parameters - Mains - Current protections - Over-current 2 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30376 |  | 330377 | Parameters - Generator - Current protections - Over-current 3 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30376 |  | 330377 | Parameters - Busbar A - Current protections - Over-current 3 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30376 |  | 330377 | Parameters - Mains - Current protections - Over-current 3 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30377 |  | 330378 | Parameters - Generator - Current protections - Over-current 4 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30377 |  | 330378 | Parameters - Busbar A - Current protections - Over-current 4 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30377 |  | 330378 | Parameters - Mains - Current protections - Over-current 4 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30378 |  | 330379 | Parameters - Generator - Current protections - Fast over-current 1 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30378 |  | 330379 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30378 |  | 330379 | Parameters - Mains - Current protections - Fast over-current 1 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30379 |  | 330380 | Parameters - Generator - Current protections - Fast over-current 2 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30379 |  | 330380 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30379 |  | 330380 | Parameters - Mains - Current protections - Fast over-current 2 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30380 |  | 330381 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30380 |  | 330381 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30380 |  | 330381 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30381 |  | 330382 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30381 |  | 330382 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30381 |  | 330382 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30382 |  | 330383 | Parameters - Generator - Current protections - Directional over-current 1 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30382 |  | 330383 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30382 |  | 330383 | Parameters - Mains - Current protections - Directional over-current 1 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30383 |  | 330384 | Parameters - Generator - Current protections - Directional over-current 2 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30383 |  | 330384 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30383 |  | 330384 | Parameters - Mains - Current protections - Directional over-current 2 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30384 |  | 330385 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30385 |  | 330386 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30386 |  | 330387 | Parameters - Generator - Current protections - Negative sequence current - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30386 |  | 330387 | Parameters - Busbar A - Current protections - Negative sequence current - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30386 |  | 330387 | Parameters - Mains - Current protections - Negative sequence current - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30387 |  | 330388 | Parameters - Generator - Current protections - Zero sequence current - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30387 |  | 330388 | Parameters - Busbar A - Current protections - Zero sequence current - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30387 |  | 330388 | Parameters - Mains - Current protections - Zero sequence current - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30388 |  | 330389 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Generator over-frequency 1 | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30388 |  | 330389 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Busbar A over-frequency 1 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30388 |  | 330389 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Mains over-frequency 1 | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30389 |  | 330390 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Generator over-frequency 2 | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30389 |  | 330390 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Busbar A over-frequency 2 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30389 |  | 330390 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Mains over-frequency 2 | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30390 |  | 330391 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Generator over-frequency 3 | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30390 |  | 330391 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Busbar A over-frequency 3 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30390 |  | 330391 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Mains over-frequency 3 | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30391 |  | 330392 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Generator under-frequency 1 | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30391 |  | 330392 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Busbar A under-frequency 1 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30391 |  | 330392 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Mains under-frequency 1 | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30392 |  | 330393 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Generator under-frequency 2 | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30392 |  | 330393 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Busbar A under-frequency 2 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30392 |  | 330393 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Mains under-frequency 2 | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30393 |  | 330394 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Generator under-frequency 3 | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30393 |  | 330394 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Busbar A under-frequency 3 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30393 |  | 330394 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Mains under-frequency 3 | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30394 |  | 330395 | Parameters - Generator - Power protections - Overload 1 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30394 |  | 330395 | Parameters - Busbar A - Power protections - Power export 1 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30394 |  | 330395 | Parameters - Mains - Power protections - Overload 1 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30395 |  | 330396 | Parameters - Generator - Power protections - Overload 2 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30395 |  | 330396 | Parameters - Busbar A - Power protections - Power export 2 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30395 |  | 330396 | Parameters - Mains - Power protections - Overload 2 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30396 |  | 330397 | Parameters - Generator - Power protections - Overload 3 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30396 |  | 330397 | Parameters - Busbar A - Power protections - Power export 3 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30396 |  | 330397 | Parameters - Mains - Power protections - Overload 3 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30397 |  | 330398 | Parameters - Generator - Power protections - Overload 4 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30397 |  | 330398 | Parameters - Busbar A - Power protections - Power export 4 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30397 |  | 330398 | Parameters - Mains - Power protections - Overload 4 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30398 |  | 330399 | Parameters - Generator - Power protections - Overload 5 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30398 |  | 330399 | Parameters - Busbar A - Power protections - Power export 5 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30398 |  | 330399 | Parameters - Mains - Power protections - Overload 5 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30399 |  | 330400 | Parameters - Generator - Power protections - Reverse power 1 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30399 |  | 330400 | Parameters - Busbar A - Power protections - Power import 1 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30399 |  | 330400 | Parameters - Mains - Power protections - Reverse power 1 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30400 |  | 330401 | Parameters - Generator - Power protections - Reverse power 2 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30400 |  | 330401 | Parameters - Busbar A - Power protections - Power import 2 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30400 |  | 330401 | Parameters - Mains - Power protections - Reverse power 2 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30401 |  | 330402 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30401 |  | 330402 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30401 |  | 330402 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30402 |  | 330403 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30402 |  | 330403 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30402 |  | 330403 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30403 |  | 330404 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30403 |  | 330404 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30403 |  | 330404 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30404 |  | 330405 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
Alarm status: Triggered value | 30404 |  | 330405 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30404 |  | 330405 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 10 | X * 0.1 | [6 empty] | X | X
Alarm status: Triggered value | 30405 |  | 330406 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Mains over-voltage 1 | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30405 |  | 330406 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Busbar over-voltage 1 | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30405 |  | 330406 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Busbar B over-voltage 1 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30406 |  | 330407 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Mains over-voltage 2 | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30406 |  | 330407 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Busbar over-voltage 2 | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30406 |  | 330407 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Busbar B over-voltage 2 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30407 |  | 330408 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Mains over-voltage 3 | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30407 |  | 330408 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Busbar over-voltage 3 | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30407 |  | 330408 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Busbar B over-voltage 3 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30408 |  | 330409 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Mains under-voltage 1 | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30408 |  | 330409 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Busbar under-voltage 1 | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30408 |  | 330409 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Busbar B under-voltage 1 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30409 |  | 330410 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Mains under-voltage 2 | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30409 |  | 330410 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Busbar under-voltage 2 | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30409 |  | 330410 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Busbar B under-voltage 2 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30410 |  | 330411 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Mains under-voltage 3 | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30410 |  | 330411 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Busbar under-voltage 3 | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30410 |  | 330411 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Busbar B under-voltage 3 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30411 |  | 330412 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Mains under-voltage 4 | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30411 |  | 330412 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Busbar under-voltage 4 | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30411 |  | 330412 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Busbar B under-voltage 4 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30412 |  | 330413 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Mains voltage unbalance | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30412 |  | 330413 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Busbar voltage unbalance | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30412 |  | 330413 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Busbar B voltage unbalance | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30413 |  | 330414 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Mains over-frequency 1 | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30413 |  | 330414 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Busbar over-frequency 1 | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30413 |  | 330414 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Busbar B over-frequency 1 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30414 |  | 330415 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Mains over-frequency 2 | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30414 |  | 330415 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Busbar over-frequency 2 | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30414 |  | 330415 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Busbar B over-frequency 2 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30415 |  | 330416 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Mains over-frequency 3 | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30415 |  | 330416 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Busbar over-frequency 3 | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30415 |  | 330416 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Busbar B over-frequency 3 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30416 |  | 330417 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Mains under-frequency 1 | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30416 |  | 330417 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Busbar under-frequency 1 | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30416 |  | 330417 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Busbar B under-frequency 1 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30417 |  | 330418 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Mains under-frequency 2 | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30417 |  | 330418 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Busbar under-frequency 2 | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30417 |  | 330418 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Busbar B under-frequency 2 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30418 |  | 330419 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Mains under-frequency 3 | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30418 |  | 330419 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Busbar under-frequency 3 | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30418 |  | 330419 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Busbar B under-frequency 3 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30419 |  | 330420 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Mains under-frequency 4 | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30419 |  | 330420 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Busbar under-frequency 4 | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30419 |  | 330420 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Busbar B under-frequency 4 | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30420 |  | 330421 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Busbar negative sequence voltage | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30420 |  | 330421 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Busbar negative sequence voltage | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30420 |  | 330421 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Busbar B negative sequence voltage | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30421 |  | 330422 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Busbar zero sequence voltage | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30421 |  | 330422 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Busbar zero sequence voltage | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30421 |  | 330422 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Busbar B zero sequence voltage | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30422 |  | 330423 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Busbar positive sequence under-voltage | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
Alarm status: Triggered value | 30422 |  | 330423 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Busbar positive sequence under-voltage | INT16 | X * 10 | X * 0.1 |  | X |  |  |  | X | X | X
Alarm status: Triggered value | 30422 |  | 330423 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Busbar B positive sequence under-voltage | INT16 | X * 10 | X * 0.1 |  |  | X
Alarm status: Triggered value | 30467 |  | 330468 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30468 |  | 330469 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30469 |  | 330470 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 3 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30470 |  | 330471 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 4 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30471 |  | 330472 | External MB open failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30472 |  | 330473 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30473 |  | 330474 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30474 |  | 330475 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30475 |  | 330476 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30476 |  | 330477 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30477 |  | 330478 | Parameters - Breakers - Close before excitation - CBE failure - Information - Close before excitation failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30478 |  | 330479 | Load too high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30479 |  | 330480 | ID to run configuration failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Triggered value | 30481 |  | 330482 | Parameters - System - Monitoring - Missing any genset controller - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30482 |  | 330483 | Parameters - System - Monitoring - Missing any mains controller - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30483 |  | 330484 | Parameters - System - Monitoring - Missing any bus tie controller - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30484 |  | 330485 | Can ID not available | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30485 |  | 330486 | Duplicated CAN IDs | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30486 |  | 330487 | Parameters - Local power management - Alarms - Busbar blocked - Information - Busbar blocked due to position failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30487 |  | 330488 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Busbar A blocked due to position failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30488 |  | 330489 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Busbar B blocked due to position failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30489 |  | 330490 | Parameters - System - Monitoring - BTB 33 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30490 |  | 330491 | Parameters - System - Monitoring - BTB 34 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30491 |  | 330492 | Parameters - System - Monitoring - BTB 35 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30492 |  | 330493 | Parameters - System - Monitoring - BTB 36 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30493 |  | 330494 | Parameters - System - Monitoring - BTB 37 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30494 |  | 330495 | Parameters - System - Monitoring - BTB 38 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30495 |  | 330496 | Parameters - System - Monitoring - BTB 39 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30496 |  | 330497 | Parameters - System - Monitoring - BTB 40 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30497 |  | 330498 | Primary CAN missing ID 1 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30498 |  | 330499 | Primary CAN missing ID 2 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30499 |  | 330500 | Primary CAN missing ID 3 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30500 |  | 330501 | Primary CAN missing ID 4 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30501 |  | 330502 | Primary CAN missing ID 5 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30502 |  | 330503 | Primary CAN missing ID 6 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30503 |  | 330504 | Primary CAN missing ID 7 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30504 |  | 330505 | Primary CAN missing ID 8 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30505 |  | 330506 | Primary CAN missing ID 9 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30506 |  | 330507 | Primary CAN missing ID 10 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30507 |  | 330508 | Primary CAN missing ID 11 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30508 |  | 330509 | Primary CAN missing ID 12 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30509 |  | 330510 | Primary CAN missing ID 13 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30510 |  | 330511 | Primary CAN missing ID 14 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30511 |  | 330512 | Primary CAN missing ID 15 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30512 |  | 330513 | Primary CAN missing ID 16 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30513 |  | 330514 | Primary CAN missing ID 17 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30514 |  | 330515 | Primary CAN missing ID 18 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30515 |  | 330516 | Primary CAN missing ID 19 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30516 |  | 330517 | Primary CAN missing ID 20 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30517 |  | 330518 | Primary CAN missing ID 21 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30518 |  | 330519 | Primary CAN missing ID 22 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30519 |  | 330520 | Primary CAN missing ID 23 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30520 |  | 330521 | Primary CAN missing ID 24 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30521 |  | 330522 | Primary CAN missing ID 25 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30522 |  | 330523 | Primary CAN missing ID 26 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30523 |  | 330524 | Primary CAN missing ID 27 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30524 |  | 330525 | Primary CAN missing ID 28 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30525 |  | 330526 | Primary CAN missing ID 29 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30526 |  | 330527 | Primary CAN missing ID 30 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30527 |  | 330528 | Primary CAN missing ID 31 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30528 |  | 330529 | Primary CAN missing ID 32 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30529 |  | 330530 | Primary CAN missing ID 33 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30530 |  | 330531 | Primary CAN missing ID 34 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30531 |  | 330532 | Primary CAN missing ID 35 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30532 |  | 330533 | Primary CAN missing ID 36 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30533 |  | 330534 | Primary CAN missing ID 37 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30534 |  | 330535 | Primary CAN missing ID 38 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30535 |  | 330536 | Primary CAN missing ID 39 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30536 |  | 330537 | Primary CAN missing ID 40 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30537 |  | 330538 | Secondary CAN missing ID 1 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30538 |  | 330539 | Secondary CAN missing ID 2 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30539 |  | 330540 | Secondary CAN missing ID 3 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30540 |  | 330541 | Secondary CAN missing ID 4 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30541 |  | 330542 | Secondary CAN missing ID 5 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30542 |  | 330543 | Secondary CAN missing ID 6 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30543 |  | 330544 | Secondary CAN missing ID 7 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30544 |  | 330545 | Secondary CAN missing ID 8 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30545 |  | 330546 | Secondary CAN missing ID 9 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30546 |  | 330547 | Secondary CAN missing ID 10 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30547 |  | 330548 | Secondary CAN missing ID 11 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30548 |  | 330549 | Secondary CAN missing ID 12 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30549 |  | 330550 | Secondary CAN missing ID 13 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30550 |  | 330551 | Secondary CAN missing ID 14 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30551 |  | 330552 | Secondary CAN missing ID 15 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30552 |  | 330553 | Secondary CAN missing ID 16 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30553 |  | 330554 | Secondary CAN missing ID 17 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30554 |  | 330555 | Secondary CAN missing ID 18 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30555 |  | 330556 | Secondary CAN missing ID 19 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30556 |  | 330557 | Secondary CAN missing ID 20 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30557 |  | 330558 | Secondary CAN missing ID 21 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30558 |  | 330559 | Secondary CAN missing ID 22 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30559 |  | 330560 | Secondary CAN missing ID 23 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30560 |  | 330561 | Secondary CAN missing ID 24 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30561 |  | 330562 | Secondary CAN missing ID 25 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30562 |  | 330563 | Secondary CAN missing ID 26 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30563 |  | 330564 | Secondary CAN missing ID 27 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30564 |  | 330565 | Secondary CAN missing ID 28 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30565 |  | 330566 | Secondary CAN missing ID 29 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30566 |  | 330567 | Secondary CAN missing ID 30 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30567 |  | 330568 | Secondary CAN missing ID 31 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30568 |  | 330569 | Secondary CAN missing ID 32 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30569 |  | 330570 | Secondary CAN missing ID 33 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30570 |  | 330571 | Secondary CAN missing ID 34 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30571 |  | 330572 | Secondary CAN missing ID 35 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30572 |  | 330573 | Secondary CAN missing ID 36 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30573 |  | 330574 | Secondary CAN missing ID 37 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30574 |  | 330575 | Secondary CAN missing ID 38 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30575 |  | 330576 | Secondary CAN missing ID 39 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30576 |  | 330577 | Secondary CAN missing ID 40 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30577 |  | 330578 | Priority error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30578 |  | 330579 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - NEL 1 over-current | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30579 |  | 330580 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - NEL 1 under-frequency | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30580 |  | 330581 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - NEL 1 overload 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30581 |  | 330582 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - NEL 1 overload 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30582 |  | 330583 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - NEL 1 reactive overload | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30583 |  | 330584 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - NEL 2 over-current | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30584 |  | 330585 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - NEL 2 under-frequency | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30585 |  | 330586 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - NEL 2 overload 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30586 |  | 330587 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - NEL 2 overload 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30587 |  | 330588 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - NEL 2 reactive overload | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30588 |  | 330589 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - NEL 3 over-current | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30589 |  | 330590 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - NEL 3 under-frequency | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30590 |  | 330591 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - NEL 3 overload 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30591 |  | 330592 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - NEL 3 overload 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30592 |  | 330593 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - NEL 3 reactive overload | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Triggered value | 30593 |  | 330594 | Parameters - System - Monitoring - Single-line hazard - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30594 |  | 330595 | ID not present | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30595 |  | 330596 | Unsupported application | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30596 |  | 330597 | Application internal CAN protocol conflict | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30597 |  | 330598 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Section P> | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30598 |  | 330599 | Dry mode: Voltage level unexpected | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30599 |  | 330600 | Invalid DAVR configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30600 |  | 330601 | Parameters - Communication - DEIF network - DEIF network fork detected - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30602 |  | 330603 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30604 |  | 330605 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30604 |  | 330605 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Triggered value | 30604 |  | 330605 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Triggered value | 30605 |  | 330606 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Triggered value | 30605 |  | 330606 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Triggered value | 30607 |  | 330608 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30608 |  | 330609 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30609 |  | 330610 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30610 |  | 330611 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30611 |  | 330612 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30612 |  | 330613 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30613 |  | 330614 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30614 |  | 330615 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30615 |  | 330616 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30616 |  | 330617 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30617 |  | 330618 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30618 |  | 330619 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30619 |  | 330620 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30620 |  | 330621 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30621 |  | 330622 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30622 |  | 330623 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30623 |  | 330624 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30624 |  | 330625 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30625 |  | 330626 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30626 |  | 330627 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30627 |  | 330628 | Live voltage detected | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30628 |  | 330629 | Internal issue detected. A restart is required soon! | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30629 |  | 330630 | Parameters - System - Monitoring - Missing controllers - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30630 |  | 330631 | Card issue detected | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30631 |  | 330632 | Card configuration failed | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30632 |  | 330633 | Unknown traffic on DEIF network | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30633 |  | 330634 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30634 |  | 330635 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30635 |  | 330636 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Triggered value | 30636 |  | 330637 | Local I/O service error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30637 |  | 330638 | App logging failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30638 |  | 330639 | Event logging failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30639 |  | 330640 | Licence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30640 |  | 330641 | Brightness is dimmed according to temperature | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30641 |  | 330642 | Parameters - Grid code - Mains sync inhibit - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Triggered value | 30642 |  | 330643 | Parameters - Grid code - Capability curve - Protections - Import protection - Information - Power import capability curve protection | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Triggered value | 30643 |  | 330644 | Parameters - Grid code - Capability curve - Protections - Export protection - Information - Power export capability curve protection | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Triggered value | 30644 |  | 330645 | Hardware is not compatible based on module versions | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 30645 |  | 330646 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 1 - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Triggered value | 30646 |  | 330647 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 2 - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Triggered value | 30647 |  | 330648 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 3 - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Triggered value | 30680 |  | 330681 | Configuration not supported by licence | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31500 |  | 331501 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31501 |  | 331502 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31502 |  | 331503 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31503 |  | 331504 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31504 |  | 331505 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31505 |  | 331506 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31506 |  | 331507 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31507 |  | 331508 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31508 |  | 331509 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31509 |  | 331510 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31510 |  | 331511 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31511 |  | 331512 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31512 |  | 331513 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31513 |  | 331514 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31514 |  | 331515 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31515 |  | 331516 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31516 |  | 331517 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31517 |  | 331518 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31518 |  | 331519 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31519 |  | 331520 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31520 |  | 331521 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31521 |  | 331522 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31522 |  | 331523 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31523 |  | 331524 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31524 |  | 331525 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31525 |  | 331526 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31526 |  | 331527 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31527 |  | 331528 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31528 |  | 331529 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31529 |  | 331530 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31530 |  | 331531 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31531 |  | 331532 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31532 |  | 331533 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31533 |  | 331534 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31534 |  | 331535 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31535 |  | 331536 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31536 |  | 331537 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31537 |  | 331538 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31538 |  | 331539 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31539 |  | 331540 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31540 |  | 331541 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31541 |  | 331542 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31542 |  | 331543 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31543 |  | 331544 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31544 |  | 331545 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31545 |  | 331546 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31546 |  | 331547 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31547 |  | 331548 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31548 |  | 331549 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31549 |  | 331550 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31600 |  | 331601 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31601 |  | 331602 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31602 |  | 331603 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31603 |  | 331604 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31604 |  | 331605 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31605 |  | 331606 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31606 |  | 331607 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31607 |  | 331608 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31608 |  | 331609 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31609 |  | 331610 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31610 |  | 331611 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31611 |  | 331612 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31612 |  | 331613 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31613 |  | 331614 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31614 |  | 331615 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31615 |  | 331616 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31616 |  | 331617 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31617 |  | 331618 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31618 |  | 331619 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31619 |  | 331620 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31620 |  | 331621 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31621 |  | 331622 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31622 |  | 331623 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31623 |  | 331624 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31624 |  | 331625 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31625 |  | 331626 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31626 |  | 331627 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31627 |  | 331628 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31628 |  | 331629 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31629 |  | 331630 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31630 |  | 331631 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31631 |  | 331632 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31632 |  | 331633 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31633 |  | 331634 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31634 |  | 331635 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31635 |  | 331636 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31636 |  | 331637 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31637 |  | 331638 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31638 |  | 331639 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31639 |  | 331640 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31640 |  | 331641 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31641 |  | 331642 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31642 |  | 331643 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31643 |  | 331644 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31644 |  | 331645 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31645 |  | 331646 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31646 |  | 331647 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31647 |  | 331648 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31648 |  | 331649 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31649 |  | 331650 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31650 |  | 331651 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31651 |  | 331652 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31652 |  | 331653 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31653 |  | 331654 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31654 |  | 331655 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31655 |  | 331656 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31656 |  | 331657 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31657 |  | 331658 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31658 |  | 331659 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31659 |  | 331660 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31660 |  | 331661 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31661 |  | 331662 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31662 |  | 331663 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31663 |  | 331664 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31664 |  | 331665 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31665 |  | 331666 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31666 |  | 331667 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31667 |  | 331668 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31668 |  | 331669 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31669 |  | 331670 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31670 |  | 331671 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31671 |  | 331672 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31672 |  | 331673 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31673 |  | 331674 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31674 |  | 331675 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31675 |  | 331676 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31676 |  | 331677 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31677 |  | 331678 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31678 |  | 331679 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31679 |  | 331680 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31680 |  | 331681 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31681 |  | 331682 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31682 |  | 331683 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31683 |  | 331684 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31684 |  | 331685 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31685 |  | 331686 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31686 |  | 331687 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31687 |  | 331688 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31688 |  | 331689 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31689 |  | 331690 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31690 |  | 331691 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31691 |  | 331692 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31692 |  | 331693 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31693 |  | 331694 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31694 |  | 331695 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31695 |  | 331696 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31696 |  | 331697 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31697 |  | 331698 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31698 |  | 331699 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31699 |  | 331700 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31700 |  | 331701 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31701 |  | 331702 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31702 |  | 331703 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31703 |  | 331704 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31704 |  | 331705 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31705 |  | 331706 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31706 |  | 331707 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31707 |  | 331708 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31708 |  | 331709 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31709 |  | 331710 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31710 |  | 331711 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31711 |  | 331712 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31712 |  | 331713 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31713 |  | 331714 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31714 |  | 331715 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31715 |  | 331716 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31716 |  | 331717 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31717 |  | 331718 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31718 |  | 331719 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31719 |  | 331720 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31720 |  | 331721 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31721 |  | 331722 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31722 |  | 331723 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31723 |  | 331724 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31724 |  | 331725 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31725 |  | 331726 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31726 |  | 331727 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31727 |  | 331728 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31728 |  | 331729 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31729 |  | 331730 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31730 |  | 331731 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31731 |  | 331732 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31732 |  | 331733 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31733 |  | 331734 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31734 |  | 331735 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31735 |  | 331736 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31736 |  | 331737 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31737 |  | 331738 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31738 |  | 331739 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31739 |  | 331740 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31740 |  | 331741 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31741 |  | 331742 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31742 |  | 331743 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31743 |  | 331744 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31744 |  | 331745 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31745 |  | 331746 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31746 |  | 331747 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31747 |  | 331748 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31748 |  | 331749 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31749 |  | 331750 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31750 |  | 331751 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31751 |  | 331752 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31752 |  | 331753 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31753 |  | 331754 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31754 |  | 331755 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31755 |  | 331756 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31756 |  | 331757 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31757 |  | 331758 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31758 |  | 331759 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31759 |  | 331760 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31760 |  | 331761 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31761 |  | 331762 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31762 |  | 331763 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31763 |  | 331764 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31764 |  | 331765 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31765 |  | 331766 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31766 |  | 331767 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31767 |  | 331768 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31768 |  | 331769 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31769 |  | 331770 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31770 |  | 331771 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31771 |  | 331772 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31772 |  | 331773 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31773 |  | 331774 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31774 |  | 331775 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31775 |  | 331776 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31776 |  | 331777 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31777 |  | 331778 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31778 |  | 331779 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31779 |  | 331780 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31780 |  | 331781 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31781 |  | 331782 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31782 |  | 331783 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31783 |  | 331784 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31784 |  | 331785 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31785 |  | 331786 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31786 |  | 331787 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31787 |  | 331788 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31788 |  | 331789 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31789 |  | 331790 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31790 |  | 331791 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31791 |  | 331792 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31792 |  | 331793 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31793 |  | 331794 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31794 |  | 331795 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31795 |  | 331796 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31796 |  | 331797 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31797 |  | 331798 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31798 |  | 331799 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Triggered value | 31799 |  | 331800 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40000 |  | 340001 | Parameters - Engine - Start sequence - Start prepare - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40001 |  | 340002 | Parameters - Engine - Start sequence - Crank - Crank on - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40002 |  | 340003 | Parameters - Engine - Start sequence - Crank - Crank off - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40003 |  | 340004 | Parameters - Engine - Start sequence - Run coil - Run coil before crank - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40005 |  | 340006 | Parameters - Engine - Start sequence - Start prepare - Extended start prepare - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40006 |  | 340007 | Parameters - Engine - Stop sequence - Cooldown - Cooldown time - Information | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40008 |  | 340009 | Parameters - Engine - Stop sequence - Extended stop - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40018 |  | 340019 | Parameters - Engine - Idle run start - Minimum - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40027 |  | 340028 | Parameters - Engine - Idle run stop - Minimum - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40033 |  | 340034 | Parameters - Engine - Idle run start - Idle run - Extended inhibit - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40038 |  | 340039 | Parameters - Engine - Running detection - Engine ready - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40049 |  | 340050 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump OFF delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40050 |  | 340051 | Pump source select | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
General parameter: Delay timer elapsed time | 40052 |  | 340053 | Parameters - Breakers - Generator breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40052 |  | 340053 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer elapsed time | 40052 |  | 340053 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer elapsed time | 40053 |  | 340054 | Parameters - Breakers - Generator breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40053 |  | 340054 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer elapsed time | 40053 |  | 340054 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer elapsed time | 40054 |  | 340055 | Parameters - Breakers - Generator breaker configuration - Configuration - Spring load time - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40054 |  | 340055 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Spring load time - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer elapsed time | 40054 |  | 340055 | Parameters - Breakers - Mains breaker configuration - Configuration - Spring-load time - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer elapsed time | 40057 |  | 340058 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40057 |  | 340058 | Parameters - Breakers - Tie breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
General parameter: Delay timer elapsed time | 40058 |  | 340059 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40058 |  | 340059 | Parameters - Breakers - Tie breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
General parameter: Delay timer elapsed time | 40059 |  | 340060 | Parameters - Breakers - Mains breaker configuration - Configuration - Spring-load time - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer elapsed time | 40059 |  | 340060 | Parameters - Breakers - Tie breaker configuration - Configuration - Spring-load time - Information | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
General parameter: Delay timer elapsed time | 40200 |  | 340201 | Parameters - Generator - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40200 |  | 340201 | Parameters - Busbar A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer elapsed time | 40200 |  | 340201 | Parameters - Mains - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer elapsed time | 40202 |  | 340203 | Parameters - Generator - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40202 |  | 340203 | Parameters - Busbar A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer elapsed time | 40202 |  | 340203 | Parameters - Mains - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer elapsed time | 40204 |  | 340205 | Parameters - Busbar A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer elapsed time | 40204 |  | 340205 | Parameters - Mains - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer elapsed time | 40206 |  | 340207 | Parameters - Busbar A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer elapsed time | 40206 |  | 340207 | Parameters - Mains - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer elapsed time | 40208 |  | 340209 | Parameters - Busbar A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer elapsed time | 40208 |  | 340209 | Parameters - Mains - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer elapsed time | 40210 |  | 340211 | Parameters - Busbar A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer elapsed time | 40210 |  | 340211 | Parameters - Mains - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer elapsed time | 40225 |  | 340226 | Parameters - Mains - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General parameter: Delay timer elapsed time | 40225 |  | 340226 | Parameters - Busbar - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X | X
General parameter: Delay timer elapsed time | 40225 |  | 340226 | Parameters - Busbar B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer elapsed time | 40233 |  | 340234 | Blackout delay | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General parameter: Delay timer elapsed time | 40233 |  | 340234 | Parameters - Busbar - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X | X
General parameter: Delay timer elapsed time | 40233 |  | 340234 | Parameters - Busbar B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer elapsed time | 40234 |  | 340235 | Parameters - Generator - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40234 |  | 340235 | Parameters - Busbar A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer elapsed time | 40234 |  | 340235 | Parameters - Mains - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer elapsed time | 40242 |  | 340243 | Blackout delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
General parameter: Delay timer elapsed time | 40242 |  | 340243 | Parameters - Busbar A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer elapsed time | 40243 |  | 340244 | Parameters - Generator - AC setup - Voltage and frequency OK (blackout) - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 40641 |  | 340642 | Parameters - Local - Alarm horn - Horn 1 - Minimum down time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40642 |  | 340643 | Parameters - Local - Alarm horn - Horn 1 - Minimum up time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40645 |  | 340646 | Parameters - Local - Alarm horn - Horn 2 - Minimum down time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40646 |  | 340647 | Parameters - Local - Alarm horn - Horn 2 - Minimum up time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40649 |  | 340650 | Parameters - Local - Alarm horn - Horn 3 - Minimum down time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40650 |  | 340651 | Parameters - Local - Alarm horn - Horn 3 - Minimum up time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40652 |  | 340653 | Parameters - Local - Alive - Alive configuration - Period - Information | INT16 | X * 100 | X * 0.01 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 40705 |  | 340706 | Parameters - Regulators - GOV - General configuration - Regulation delay - Regulator delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41041 |  | 341042 | Parameters - Mains - AC setup - Supervision selector - Recovery selector time - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X | X |  | X | X
General parameter: Delay timer elapsed time | 41042 |  | 341043 | Parameters - Mains - AC setup - Supervision selector - Recovery time fast - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X | X |  | X | X
General parameter: Delay timer elapsed time | 41043 |  | 341044 | Parameters - Mains - AC setup - Supervision selector - Recovery time slow - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X | X |  | X | X
General parameter: Delay timer elapsed time | 41070 |  | 341071 | Parameters - Test functions - Lamp test - Duration - Information | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41071 |  | 341072 | Parameters - Test functions - Lamp test - Colour cycle time - Information | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41073 |  | 341074 | Parameters - CODESYS - Monitoring - Application not OK - Startup time - Information | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41076 |  | 341077 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU powerup time - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 41106 |  | 341107 | Parameters - Engine - ECU - Controls - Reset - Power off timer - Information | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 41147 |  | 341148 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Power-up time - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 41206 |  | 341207 | Parameters - Engine - Stop sequence - Externally stopped - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 41209 |  | 341210 | Parameters - Engine - Start sequence - Run detection not reached - Information | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 41210 |  | 341211 | Parameters - Breakers - Generator breaker configuration - Configuration - Delay after Hz/V OK before close - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41211 |  | 341212 | Parameters - Local power management - Mains configuration - Mains breaker configuration - MB close delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
General parameter: Delay timer elapsed time | 41223 |  | 341224 | Parameters - Breakers - Close before excitation - Configuration - Timer crank release to AVR on - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 41225 |  | 341226 | Parameters - Breakers - Close before excitation - Configuration - Soft-start timer - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 41227 |  | 341228 | Parameters - Breakers - Close before excitation - Configuration - Voltage discharge timer for GB close - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 41234 |  | 341235 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Voltage failure delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
General parameter: Delay timer elapsed time | 41235 |  | 341236 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Voltage OK delay - Information | INT16 | X * 1 | X * 1 | s | X |  | X | X | X | X | X
General parameter: Delay timer elapsed time | 41240 |  | 341241 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Frequency failure delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
General parameter: Delay timer elapsed time | 41241 |  | 341242 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Frequency OK delay - Information | INT16 | X * 1 | X * 1 | s | X |  | X | X | X | X | X
General parameter: Delay timer elapsed time | 41305 |  | 341306 | Parameters - Local power management - Mains configuration - Tie breaker configuration - Power capacity overrule delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41358 |  | 341359 | Parameters - Power management rules - Load-dependent start/stop - Start 1 - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41362 |  | 341363 | Parameters - Power management rules - Load-dependent start/stop - Stop 1 - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41811 |  | 341812 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41813 |  | 341814 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41815 |  | 341816 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41817 |  | 341818 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41819 |  | 341820 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41821 |  | 341822 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41823 |  | 341824 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41825 |  | 341826 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41827 |  | 341828 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41829 |  | 341830 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41831 |  | 341832 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41833 |  | 341834 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41835 |  | 341836 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41837 |  | 341838 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41839 |  | 341840 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41841 |  | 341842 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41843 |  | 341844 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41845 |  | 341846 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41847 |  | 341848 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41849 |  | 341850 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41851 |  | 341852 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41853 |  | 341854 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41855 |  | 341856 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41857 |  | 341858 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41890 |  | 341891 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41898 |  | 341899 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41899 |  | 341900 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41907 |  | 341908 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41908 |  | 341909 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41916 |  | 341917 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41917 |  | 341918 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41925 |  | 341926 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41926 |  | 341927 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41934 |  | 341935 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41935 |  | 341936 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41943 |  | 341944 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41944 |  | 341945 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41952 |  | 341953 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41953 |  | 341954 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41961 |  | 341962 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer elapsed time | 41980 |  | 341981 | Parameters - Breakers - Short-time parallel - Configuration - Maximum overlap time - Information | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X | X | X
General parameter: Delay timer elapsed time | 41989 |  | 341990 | Parameters - Local power management - Genset test - Settings - Test time - Information | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 41989 |  | 341990 | Parameters - Power management rules - Mains power - Mains test - Test time - Information | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
General parameter: Delay timer elapsed time | 41990 |  | 341991 | Parameters - Power management rules - Mains power - Peak shaving - Stop delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 41998 |  | 341999 | Parameters - Engine - ECU diagnostic - Time to enable function - Information | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 42000 |  | 342001 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump ON delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 42004 |  | 342005 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump ON delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 42005 |  | 342006 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump OFF delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 42010 |  | 342011 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump ON delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 42011 |  | 342012 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump OFF delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 42211 |  | 342212 | Parameters - Grid code - Mains sync inhibit - Recovery delay select time - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General parameter: Delay timer elapsed time | 42213 |  | 342214 | Parameters - Grid code - Mains sync inhibit - Recovery delay 1 time - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General parameter: Delay timer elapsed time | 42215 |  | 342216 | Parameters - Grid code - Mains sync inhibit - Recovery delay 2 time - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General parameter: Delay timer elapsed time | 42318 |  | 342319 | Parameters - Regulators - GOV - General configuration - Frequency recovery limit - Frequency recovery duration - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer elapsed time | 42324 |  | 342325 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 1 - Delay - Information | INT16 | X * 100 | X * 0.01 | s |  |  | X | X
General parameter: Delay timer elapsed time | 42327 |  | 342328 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 2 - Delay - Information | INT16 | X * 100 | X * 0.01 | s |  |  | X | X
General parameter: Delay timer elapsed time | 42330 |  | 342331 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 3 - Delay - Information | INT16 | X * 100 | X * 0.01 | s |  |  | X | X
General parameter: Delay timer remaining time | 46000 |  | 346001 | Parameters - Engine - Start sequence - Start prepare - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46001 |  | 346002 | Parameters - Engine - Start sequence - Crank - Crank on - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46002 |  | 346003 | Parameters - Engine - Start sequence - Crank - Crank off - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46003 |  | 346004 | Parameters - Engine - Start sequence - Run coil - Run coil before crank - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46005 |  | 346006 | Parameters - Engine - Start sequence - Start prepare - Extended start prepare - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46006 |  | 346007 | Parameters - Engine - Stop sequence - Cooldown - Cooldown time - Information | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46008 |  | 346009 | Parameters - Engine - Stop sequence - Extended stop - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46018 |  | 346019 | Parameters - Engine - Idle run start - Minimum - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46027 |  | 346028 | Parameters - Engine - Idle run stop - Minimum - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46033 |  | 346034 | Parameters - Engine - Idle run start - Idle run - Extended inhibit - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46038 |  | 346039 | Parameters - Engine - Running detection - Engine ready - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46049 |  | 346050 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump OFF delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46050 |  | 346051 | Pump source select | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
General parameter: Delay timer remaining time | 46052 |  | 346053 | Parameters - Breakers - Generator breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46052 |  | 346053 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer remaining time | 46052 |  | 346053 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer remaining time | 46053 |  | 346054 | Parameters - Breakers - Generator breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46053 |  | 346054 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer remaining time | 46053 |  | 346054 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer remaining time | 46054 |  | 346055 | Parameters - Breakers - Generator breaker configuration - Configuration - Spring load time - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46054 |  | 346055 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Spring load time - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer remaining time | 46054 |  | 346055 | Parameters - Breakers - Mains breaker configuration - Configuration - Spring-load time - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer remaining time | 46057 |  | 346058 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46057 |  | 346058 | Parameters - Breakers - Tie breaker configuration - Configuration - Pulse time ON - Information | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
General parameter: Delay timer remaining time | 46058 |  | 346059 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46058 |  | 346059 | Parameters - Breakers - Tie breaker configuration - Configuration - Pulse time OFF - Information | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
General parameter: Delay timer remaining time | 46059 |  | 346060 | Parameters - Breakers - Mains breaker configuration - Configuration - Spring-load time - Information | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General parameter: Delay timer remaining time | 46059 |  | 346060 | Parameters - Breakers - Tie breaker configuration - Configuration - Spring-load time - Information | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
General parameter: Delay timer remaining time | 46200 |  | 346201 | Parameters - Generator - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46200 |  | 346201 | Parameters - Busbar A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer remaining time | 46200 |  | 346201 | Parameters - Mains - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer remaining time | 46202 |  | 346203 | Parameters - Generator - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46202 |  | 346203 | Parameters - Busbar A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer remaining time | 46202 |  | 346203 | Parameters - Mains - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer remaining time | 46204 |  | 346205 | Parameters - Busbar A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer remaining time | 46204 |  | 346205 | Parameters - Mains - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer remaining time | 46206 |  | 346207 | Parameters - Busbar A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer remaining time | 46206 |  | 346207 | Parameters - Mains - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer remaining time | 46208 |  | 346209 | Parameters - Busbar A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer remaining time | 46208 |  | 346209 | Parameters - Mains - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer remaining time | 46210 |  | 346211 | Parameters - Busbar A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer remaining time | 46210 |  | 346211 | Parameters - Mains - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer remaining time | 46225 |  | 346226 | Parameters - Mains - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General parameter: Delay timer remaining time | 46225 |  | 346226 | Parameters - Busbar - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X | X
General parameter: Delay timer remaining time | 46225 |  | 346226 | Parameters - Busbar B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer remaining time | 46233 |  | 346234 | Blackout delay | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General parameter: Delay timer remaining time | 46233 |  | 346234 | Parameters - Busbar - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X | X
General parameter: Delay timer remaining time | 46233 |  | 346234 | Parameters - Busbar B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer remaining time | 46234 |  | 346235 | Parameters - Generator - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46234 |  | 346235 | Parameters - Busbar A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer remaining time | 46234 |  | 346235 | Parameters - Mains - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General parameter: Delay timer remaining time | 46242 |  | 346243 | Blackout delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
General parameter: Delay timer remaining time | 46242 |  | 346243 | Parameters - Busbar A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s |  | X
General parameter: Delay timer remaining time | 46243 |  | 346244 | Parameters - Generator - AC setup - Voltage and frequency OK (blackout) - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 46641 |  | 346642 | Parameters - Local - Alarm horn - Horn 1 - Minimum down time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 46642 |  | 346643 | Parameters - Local - Alarm horn - Horn 1 - Minimum up time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 46645 |  | 346646 | Parameters - Local - Alarm horn - Horn 2 - Minimum down time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 46646 |  | 346647 | Parameters - Local - Alarm horn - Horn 2 - Minimum up time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 46649 |  | 346650 | Parameters - Local - Alarm horn - Horn 3 - Minimum down time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 46650 |  | 346651 | Parameters - Local - Alarm horn - Horn 3 - Minimum up time - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 46652 |  | 346653 | Parameters - Local - Alive - Alive configuration - Period - Information | INT16 | X * 100 | X * 0.01 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 46705 |  | 346706 | Parameters - Regulators - GOV - General configuration - Regulation delay - Regulator delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47041 |  | 347042 | Parameters - Mains - AC setup - Supervision selector - Recovery selector time - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X | X |  | X | X
General parameter: Delay timer remaining time | 47042 |  | 347043 | Parameters - Mains - AC setup - Supervision selector - Recovery time fast - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X | X |  | X | X
General parameter: Delay timer remaining time | 47043 |  | 347044 | Parameters - Mains - AC setup - Supervision selector - Recovery time slow - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X | X |  | X | X
General parameter: Delay timer remaining time | 47070 |  | 347071 | Parameters - Test functions - Lamp test - Duration - Information | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47071 |  | 347072 | Parameters - Test functions - Lamp test - Colour cycle time - Information | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47073 |  | 347074 | Parameters - CODESYS - Monitoring - Application not OK - Startup time - Information | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47076 |  | 347077 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU powerup time - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 47106 |  | 347107 | Parameters - Engine - ECU - Controls - Reset - Power off timer - Information | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 47147 |  | 347148 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Power-up time - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 47206 |  | 347207 | Parameters - Engine - Stop sequence - Externally stopped - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 47209 |  | 347210 | Parameters - Engine - Start sequence - Run detection not reached - Information | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 47210 |  | 347211 | Parameters - Breakers - Generator breaker configuration - Configuration - Delay after Hz/V OK before close - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47211 |  | 347212 | Parameters - Local power management - Mains configuration - Mains breaker configuration - MB close delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
General parameter: Delay timer remaining time | 47223 |  | 347224 | Parameters - Breakers - Close before excitation - Configuration - Timer crank release to AVR on - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 47225 |  | 347226 | Parameters - Breakers - Close before excitation - Configuration - Soft-start timer - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 47227 |  | 347228 | Parameters - Breakers - Close before excitation - Configuration - Voltage discharge timer for GB close - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 47234 |  | 347235 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Voltage failure delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
General parameter: Delay timer remaining time | 47235 |  | 347236 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Voltage OK delay - Information | INT16 | X * 1 | X * 1 | s | X |  | X | X | X | X | X
General parameter: Delay timer remaining time | 47240 |  | 347241 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Frequency failure delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
General parameter: Delay timer remaining time | 47241 |  | 347242 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Frequency OK delay - Information | INT16 | X * 1 | X * 1 | s | X |  | X | X | X | X | X
General parameter: Delay timer remaining time | 47305 |  | 347306 | Parameters - Local power management - Mains configuration - Tie breaker configuration - Power capacity overrule delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47358 |  | 347359 | Parameters - Power management rules - Load-dependent start/stop - Start 1 - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47362 |  | 347363 | Parameters - Power management rules - Load-dependent start/stop - Stop 1 - Delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47811 |  | 347812 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47813 |  | 347814 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47815 |  | 347816 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47817 |  | 347818 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47819 |  | 347820 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47821 |  | 347822 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47823 |  | 347824 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47825 |  | 347826 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47827 |  | 347828 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47829 |  | 347830 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47831 |  | 347832 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47833 |  | 347834 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47835 |  | 347836 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47837 |  | 347838 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47839 |  | 347840 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47841 |  | 347842 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47843 |  | 347844 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47845 |  | 347846 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47847 |  | 347848 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47849 |  | 347850 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy export - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47851 |  | 347852 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47853 |  | 347854 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy import - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47855 |  | 347856 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47857 |  | 347858 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47890 |  | 347891 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47898 |  | 347899 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47899 |  | 347900 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47907 |  | 347908 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47908 |  | 347909 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47916 |  | 347917 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47917 |  | 347918 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47925 |  | 347926 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47926 |  | 347927 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47934 |  | 347935 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47935 |  | 347936 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47943 |  | 347944 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47944 |  | 347945 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47952 |  | 347953 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47953 |  | 347954 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Voltage and frequency OK - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47961 |  | 347962 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Blackout detection - Blackout delay - Information | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General parameter: Delay timer remaining time | 47980 |  | 347981 | Parameters - Breakers - Short-time parallel - Configuration - Maximum overlap time - Information | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X | X | X
General parameter: Delay timer remaining time | 47989 |  | 347990 | Parameters - Local power management - Genset test - Settings - Test time - Information | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 47989 |  | 347990 | Parameters - Power management rules - Mains power - Mains test - Test time - Information | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
General parameter: Delay timer remaining time | 47990 |  | 347991 | Parameters - Power management rules - Mains power - Peak shaving - Stop delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 47998 |  | 347999 | Parameters - Engine - ECU diagnostic - Time to enable function - Information | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 48000 |  | 348001 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump ON delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 48004 |  | 348005 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump ON delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 48005 |  | 348006 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump OFF delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 48010 |  | 348011 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump ON delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 48011 |  | 348012 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump OFF delay - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 48211 |  | 348212 | Parameters - Grid code - Mains sync inhibit - Recovery delay select time - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General parameter: Delay timer remaining time | 48213 |  | 348214 | Parameters - Grid code - Mains sync inhibit - Recovery delay 1 time - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General parameter: Delay timer remaining time | 48215 |  | 348216 | Parameters - Grid code - Mains sync inhibit - Recovery delay 2 time - Information | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General parameter: Delay timer remaining time | 48318 |  | 348319 | Parameters - Regulators - GOV - General configuration - Frequency recovery limit - Frequency recovery duration - Information | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General parameter: Delay timer remaining time | 48324 |  | 348325 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 1 - Delay - Information | INT16 | X * 100 | X * 0.01 | s |  |  | X | X
General parameter: Delay timer remaining time | 48327 |  | 348328 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 2 - Delay - Information | INT16 | X * 100 | X * 0.01 | s |  |  | X | X
General parameter: Delay timer remaining time | 48330 |  | 348331 | Parameters - Grid code - Power feed in management - Protections - Grid contractual alarm 3 - Delay - Information | INT16 | X * 100 | X * 0.01 | s |  |  | X | X
Values for ML2 USW compatibility | 59900 |  | 359901 | ML-2 Product ID | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X

## Controller text
Text associated to Modbus value
Modbus address | Modbus function code | Controller function name | Modbus output (decimal) | Text
8000 | 04 | Engine state | 0 | Engine not ready to start
|  |  | 1 | Engine ready to start
|  |  | 2 | Pre-running engine
|  |  | 3 | Preparing engine
|  |  | 4 | Crank on
|  |  | 5 | Engine start off
|  |  | 6 | Idle run
|  |  | 7 | Engine running
|  |  | 8 | Engine stopping
|  |  | 9 | Engine cooldown
|  |  | 12 | Extended stop active
8002 | 04 | GB state | 0 | Breaker open
|  | BTB state | 1 | Breaker closed
|  | MB state | 2 | Breaker position unknown
|  |  | 3 | Breaker opening directly
|  |  | 4 | Breaker closing directly
|  |  | 5 | Breaker synchronising
|  |  | 6 | Breaker deloading
8003 | 04 | MB state | 0 | Breaker open
|  |  | 1 | Breaker closed
|  |  | 2 | Breaker position unknown
|  |  | 3 | Breaker opening directly
|  |  | 4 | Breaker closing directly
|  |  | 5 | Breaker synchronising
|  |  | 6 | Breaker deloading
8004 | 04 | Virtual busbar status GB side | 0 | Dead busbar
|  |  | 1 | Busbar not dead and not OK
|  |  | 2 | Busbar OK, and not stable
|  |  | 3 | Live busbar
|  |  | 4 | Unknown state
8005 | 04 | Virtual busbar status MB side | 0 | Dead busbar
|  |  | 1 | Busbar not dead and not OK
|  |  | 2 | Busbar OK, and not stable
|  |  | 3 | Live busbar
|  |  | 4 | Unknown state
8006 | 04 | Mains ¦ State | 0 | Dead busbar
|  | Busbar ¦ State | 1 | Busbar not dead and not OK
|  | Busbar B ¦ State | 2 | Busbar OK, and not stable
|  |  | 3 | Live busbar
|  |  | 4 | Unknown state
8007 | 04 | Generator ¦ State | 0 | Dead busbar
|  | Busbar A ¦ State | 1 | Busbar not dead and not OK
|  | Mains ¦ State | 2 | Busbar OK, and not stable
|  |  | 3 | Live busbar
|  |  | 4 | Unknown state
8008 | 04 | Current command mode | 0 | MANUAL mode
|  |  | 1 | LOCAL mode
|  |  | 2 | Remote mode
8015 | 04 | GOV regulator type | 0 | Frequency synchronisation (analogue)
|  |  | 1 | Phase synchronisation (analogue)
|  |  | 2 | Frequency regulation (analogue)
|  |  | 3 | Power load share (analogue)
|  |  | 4 | Power regulation (analogue)
|  |  | 5 | Manual regulation (analogue)
|  |  | 6 | RPM synchronisation (analogue)
|  |  | 7 | RPM regulation (analogue)
|  |  | 8 | Frequency synchronisation (relay)
|  |  | 9 | Phase synchronisation (relay)
|  |  | 10 | Frequency regulation (relay)
|  |  | 11 | Power load share (relay)
|  |  | 12 | Power regulation (relay)
|  |  | 13 | Manual regulation (relay)
|  |  | 14 | RPM synchronisation (relay)
|  |  | 15 | RPM regulation (relay)
|  |  | 16 | No governor regulator configured
8016 | 04 | AVR regulator type | 0 | Voltage regulation (analogue)
|  |  | 1 | Reactive power load share (analogue)
|  |  | 2 | Reactive power regulation (analogue)
|  |  | 3 | Manual regulation (analogue)
|  |  | 4 | Voltage regulation (relay)
|  |  | 5 | Reactive power load share (relay)
|  |  | 6 | Reactive power regulation (relay)
|  |  | 7 | Manual regulation (relay)
|  |  | 8 | No AVR regulator configured
8027 | 04 | External breaker 1 state | 0 | Breaker open
|  |  | 1 | Breaker closed
|  |  | 2 | Breaker position unknown
8028 | 04 | External breaker 1 busbar A state | 4 | Unknown state
8029 | 04 | External breaker 1 busbar B state | 4 | Unknown state
8030 | 04 | External breaker 2 state | 0 | Breaker open
|  |  | 1 | Breaker closed
|  |  | 2 | Breaker position unknown
8031 | 04 | External breaker 2 busbar A state | 4 | Unknown state
8032 | 04 | External breaker 2 busbar B state | 4 | Unknown state
8033 | 04 | External breaker 3 state | 0 | Breaker open
|  |  | 1 | Breaker closed
|  |  | 2 | Breaker position unknown
8034 | 04 | External breaker 3 busbar A state | 4 | Unknown state
8035 | 04 | External breaker 3 busbar B state | 4 | Unknown state
8036 | 04 | External breaker 4 state | 0 | Breaker open
|  |  | 1 | Breaker closed
|  |  | 2 | Breaker position unknown
8037 | 04 | External breaker 4 busbar A state | 4 | Unknown state
8038 | 04 | External breaker 4 busbar B state | 4 | Unknown state
Note on B4: 04 - Read single or multiple
Note on D4: The controller function name shows the path to the parameter in PICUS. If the function is not visible in PICUS, only the function name is displayed.