## Description
iE 250 Premium Modbus descriptions
Software version
The information contained in these tables (revision J) are applicable to software version 2.0.13.x of the iE 250 Premium software.
Row | Hyperlink index
14 | Modbus function codes
25 | Discrete output coil
41 | Discrete input contact
64 | Holding register
90 | Input register
107 | List of alarm states
Back to index | Modbus function codes
| Function code | Description
| 01 | Read a single or multiple discrete output coils.
| 02 | Read a single or multiple discrete input contacts.
| 03 | Read a single or multiple output holding registers.
| 04 | Read a single or multiple input registers.
| 05 | Write a value to a single discrete output coil.
| 06 | Write a value to a single output holding register.
| 15 | Write a value(s) to multiple consecutive discrete output coils.
| 16 | Write a value(s) to multiple consecutive output holding registers.
Back to index | Discrete output coil
| Function code | Effect
| 01 | Read
| 05 or 15 | Write
| Function group | Description
| Command | Activate a command in the controller. Read: The controller always returns 0 (false). Write: The controller executes the command if you write 1 (true).
| Function | Read and write whether a function is activated. Read: The controller returns 0 (false) when the function is not activated and 1 (true) when the function is activated. Write: The controller changes the value of the associated function if a valid value is entered and the function is not assigned in PICUS.
| CustomLogic: Modbus signal | Read or change the state of a CustomLogic Modbus signal. Read: The controller returns 0 (false) when the Modbus signal is inactive and 1 (true) when the Modbus signal is active. Write: The controller changes the state of CustomLogic Modbus signal. A value can only be written to signals that are not assigned to coils, for example a normally open coil.
| Alarm parameter: Enable | Read or change the alarm enable configuration. Read: The controller returns 0 (false) when the alarm is Not enabled and 1 (true) when the alarm is Enabled. Write: The controller changes the alarm configuration. Danger! You can disable critical controller protections. Only disable alarms if you have a thorough understanding of the system, the controller, and the consequences of disabling an alarm.
| Alarm parameter: Latch | Read or change the alarm latch configuration. Read: The controller returns 0 (false) when the latch is Not enabled and 1 (true) when the latch parameter is Enabled. Write: The controller changes the alarm latch configuration. Danger! You can disable critical controller protections, and the built-in controller lockout relay function. Only disable alarm latches if you have a thorough understanding of the system, the controller, and the consequences of disabling an alarm latch.
| Alarm action: Acknowledge alarm | Acknowledge the alarm. Read: The controller always returns 0 (false). Write: If the alarm is active and unacknowledged, and you write 1 (true), the controller acknowledges the alarm.
| Alarm action: Reset latch | Reset the alarm latch. Read: The controller always returns 0 (false). Write: If the alarm is latched, acknowledged and the operating value does not exceed the set point, and you write 1 (true), the controller resets the latch.
| Alarm action: Remove from service | Remove the alarm from service. Read: The controller returns 0 (false) when the alarm is active and 1 (true) when the alarm is out of service. Write: If the alarm is active, and you write 1 (true), the alarm is taken out of service. Danger! You can disable critical controller protections. Only take alarms out of service if you have a thorough understanding of the system, the controller, and the consequences of disabling an alarm.
| General parameter: Enable | Read or change the parameter configuration. Read: The controller returns 0 (false) when the parameter is Not enabled and 1 (true) when the parameter is Enabled. Write: The controller changes the parameter configuration.
Back to index | Discrete input contact
| Function code | Effect
| 02 | Read
| Function group | Description
| Status flag | Read whether a status flag is activated. The controller returns 0 (false) when the status flag is not activated The controller returns 1 (true) when the status flag is activated.
| CustomLogic: Modbus signal | Read whether a Modbus signal has been triggered by CustomLogic. The controller returns 0 (false) when the Modbus signal is inactive. The controller returns 1 (true) when the Modbus signal is active.
| CustomLogic: ICC flag in | Read whether a communication flag has been triggered by CustomLogic from a specific controller and location. Format of function name: ICC > Inputs > # > Inter-controller communication In # The first # indicates the controller ID of the controller sending the data. Inter-controller communication In # indicates where the communication is received from. The controller returns 0 (false) when the inter-controller communication flag is inactive. No data is being received. The controller returns 1 (true) when the inter-controller communication flag is active. Data is being received.
| CustomLogic: ICC flag out | Read whether a communication flag has been triggered by CustomLogic on the connected controller. Format of function name: ICC > Outputs > Inter-controller communication Out # Inter-controller communication Out # indicates where the communication is being sent from. The controller returns 0 (false) when the inter-controller communication flag is inactive. No data is being sent. The controller returns 1 (true) when the inter-controller communication flag is active. Data is being sent.
| Alarm status: Active | Read whether an alarm is activated. The controller returns 0 (false) when the alarm is not activated (state 0, 3, 6 or 7). The controller returns 1 (true) when the alarm is activated (state 1, 2, 4 or 5).
The alarm states are described in row 107.
| Alarm status: Acknowledged | Read whether an alarm is acknowledged. The controller returns 0 (false) when the alarm is not acknowledged (state 0, 1, 3, 4, 6 or 7). The controller returns 1 (true) when the alarm is acknowledged (state 2 or 5).
The alarm states are described in row 107.
| Alarm status: Latched | Read whether an alarm is latched. The controller returns 0 (false) when the alarm has a state other than latched (state 0, 1, 2, 3, 6 or 7). The controller returns 1 (true) when the alarm is latched (state 4 or 5).
The alarm states are described in row 107.
| Alarm status: Shelved | Read whether an alarm is shelved. The controller returns 0 (false) when the alarm is not shelved (state 0, 1, 2, 3, 4, 5 or 7). The controller returns 1 (true) when the alarm is shelved (state 6).
The alarm states are described in row 107.
| Alarm status: Out of service | Read whether an alarm is out of service. The controller returns 0 (false) when the alarm is not taken out of service (state 0, 1, 2, 3, 4, 5 or 6). The controller returns 1 (true) when the alarm is taken out of service (state 7).
The alarm states are described in row 107.
| Alarm status: Delay timer running | Read whether an alarm delay timer is running. The controller returns 0 (false) if the alarm delay timer is not running. The controller returns 1 (true) if the operating value exceeds the alarm set point and the alarm delay timer is running.
| Alarm status: Delay timer expired | Read whether an alarm delay timer is expired. The controller returns 0 (false) when the alarm delay timer has not expired, or if the operating value does not exceed the alarm set point. The controller returns 1 (true) if the operating value exceeds the alarm set point and the alarm delay timer has expired.
| General parameter: Delay timer running | Read whether a function delay timer is running. The controller returns 0 (false) if the function delay timer is not running. The controller returns 1 (true) if the function delay timer is running.
Back to index | Holding register
| Function code | Effect
| 03 | Read
| 06 or 16 | Write
| Function group | Description
| Function | Read and write the function values. Read: The controller returns the function value. Write: The controller changes the value of the associated function if a valid value is entered and the function is not assigned in PICUS.
| Counter | Read and write the counter values. Read: The controller returns the current counter value. Write: The controller changes the counter value if a valid value is entered.
| Alarm parameter: Set point | Read and write the alarm set point. Read: The controller returns the current set point value. Write: The controller changes the set point of the associated alarm if a valid value is entered.
Only values within the minimum and maximum range of the set point are valid inputs. Refer to the Designer's handbook for alarm descriptions. Danger! You can change critical controller protections. Only adjust alarm set points if you have a thorough understanding of the system, the controller, and the consequences of adjusting an alarm set point.
| Alarm parameter: Reset hysteresis | Read and write the reset hysteresis value of the alarm. Read: The controller returns the current reset hysteresis value of the alarm. Write: The controller changes the reset hysteresis value of the alarm if a valid value is entered. Only values within the minimum and maximum range of the associated alarm's reset hysteresis are valid inputs. Refer to the Designer's handbook for alarm descriptions.
| Alarm parameter: Delay | Read and write the delay timer value (in seconds) of the alarm. Read: The controller returns the current delay time of the alarm. Write: The controller changes the delay time of the alarm if a valid value is entered.
Only values within the minimum and maximum range of the alarm's delay time are valid inputs. Refer to the Designer's handbook for alarm descriptions. Danger! You can change critical controller protections. Only adjust a delay if you have a thorough understanding of the system, the controller, and the consequences of adjusting the delay.
| Alarm parameter: Action | Read and write the alarm action. Read: The controller returns the current action value. Write: The controller changes the alarm action if a valid value is entered.
These are the alarm actions (decimal values): 0 Warning 1 Block [Breaker]* 2 Block mains breaker 3 Trip [Breaker]* 4 Trip mains breaker 5 Trip generator and main breakers 7 Trip generator breaker and stop engine 8 Trip generator breaker and shutdown engine
* [Breaker] depends on the controller type. It is generator breaker for a SINGLE genset and GENSET controller, bus tie breaker for a BUS TIE breaker controller, and mains breaker for a MAINS controller. Caution: The alarm actions are not applicable to all controller types. Refer to the Designer's Handbook to see which alarm actions are applicable to a specific controller type.
| Alarm parameter: Configuration | Read and write the alarm configuration. Read: The controller returns a 16-bit number, where each bit corresponds to an alarm configuration parameter. A configuration parameter is enabled when its bit is on, and not enabled when its bit is off. Write: The controller changes the alarm configuration.
These bits are allocated to the configuration specifications: Bit 0 = Enable When the bit is on the alarm parameter is Enabled. When the bit is off, the alarm parameter is Not enabled. Bit 1 = Trigger level When the bit is on the trigger level is High. When the bit is off the trigger level is Low. Note: For many standard alarms the trigger level can not be changed. Bit 2 = Auto acknowledge When the bit is on auto acknowledge is Enabled. When the bit is off auto acknowledge is Not enabled. Bit 3 = Latch When the bit is on the latch is Enabled. When the bit is off the latch is Not enabled.
Bit 4 = Shelve Bit 5 = Out of service When the bit is on the alarm is Removed from service, when the bit is off the alarm is Returned to service. Bit 6 = Suppress action When the bit is on suppress action is Enabled, when the bit is off suppress action is Not enabled.
| Alarm parameter: Inhibit | Read and write the alarm inhibits. The alarm inhibits stop the controller from activating the alarm. Read: The controller returns a 32-bit number, where each bit corresponds to an alarm inhibit. The inhibit is enabled when its bit is 1, and not enabled when its bit is 0. Write: The controller changes the alarm inhibits.
These bits are allocated to the GPC inhibits: Bit 2 = Generator breaker closed Bit 3 = Generator breaker open Bit 6 = Generator voltage present Bit 7 = Generator voltage not present Bit 8 = Generator frequency present Bit 9 = Generator frequency not present Bit 28 = ACM wire break Bit 29 = Inhibit 1 Bit 30 = Inhibit 2 Bit 31 = Inhibit 3
For example, to enable the Generator breaker open and the Generator voltage not present inhibits for an alarm, write the sum of their values. Bit 3 plus Bit 7 corresponds to 8 + 128 = 136. Danger! You can write other values to the controller, and these will not return an error message. Only the valid inhibits are enabled. Only use combinations of the values listed above.
| Alarm status: Unshelve time | Read and write the time when the alarm is Unshelved. Note: The unshelve time is based on the Current controller time. Read: The controller returns the Unshelve time as an Epoch timestamp. Write: The controller changes the Unshelve time if a valid timestamp is entered.
When PICUS is used to shelve an alarm, the timestamp is automatically updated. If the written time by mistake is overdue, the controller by default set the Unshelve time to 10 seconds. NOTE: Updating the timestamp does not shelve an unshelved alarm.
| General parameter: Value | Read and write values for controller parameters. These parameters can include general configuration settings, for example nominal values. These parameters don't include any alarm related settings. Read: The controller returns the value for the setting. Write: The controller changes the value for the setting if a valid value is entered.
Back to index | Input register
| Function code | Effect
| 04 | Read
| Function group | Description
| [Controlled equipment] ACM measurements | Read the operating value of the AC measurement on the generator side of the breaker.
| [Busbar] ACM measurements | Read the operating value of the AC measurement on the busbar side of the breaker.
| 4th current ACM measurements | Read the operating value of the 4th current AC measurement.
| Status value | Read the operating value of the function, or the controller information. See the Controller text sheet for a discription of the text associated to the value for address that are related to controller texts.
| Controller status text | Read the value of the status text currently active on the controller. Download the associated Modbus texts list to look up controller text for the associated Modbus value.
Direct download: https://www.deif.com/rtd/omni/mt
| Popup text | Read the value of the popup text currently active in a specific line on the controller. These texts are displayed in blue boxes with the heading Information on the display unit and in PICUS. Download the associated Modbus texts list to look up controller text for the associated Modbus value.
Direct download: https://www.deif.com/rtd/omni/mt
| Counter | Read the counter values.
| Alarm status: Operating value | Read the measured value of the alarm. An alarm with an ON/OFF status returns 1 or 0. An alarm with an operating value in a specific range returns the measured value.
| Alarm status: Delay timer elapsed time | Read the time (in seconds) since the delay timer of the alarm started. The controller returns 0 if the alarm operating value is below the set point. The controller returns up to the delay time when the alarm is triggered and the operating value still exceeds the set point.
| Alarm status: Delay timer remaining time | Read the time (in seconds) before the alarm is activated. The controller returns the delay time if the alarm operating value does not exceed the set point. The controller returns 0 when the alarm is activated and the operating value is above the set point.
| Alarm status: Alarm state | Read the alarm state of the alarm. These are the alarm states (decimal values): 0 = The alarm state is normal. 1 = The alarm is unacknowledged. 2 = The alarm is acknowledged. 3 = The alarm state is normal and the alarm is unacknowledged. 4 = The alarm is unacknowledged and latched. 5 = The alarm is acknowledged and latched. 6 = The alarm is shelved. 7 = The alarm is removed from service.
| Alarm status: Alarm active | Read one bit to see whether the alarm is activated. The controller returns 0 (false) when the alarm is not activated (state 0, 3, 6 or 7 above). The controller returns 1 (true) when the alarm is activated (state 1, 2, 4 or 5 above).
| Alarm status: Alarm acknowledged | Read one bit to see whether an alarm is acknowledged. The controller returns 0 (false) when the alarm is not acknowledged (state 0, 1, 3, 4, 6 or 7 above). The controller returns 1 (true) when the alarm is acknowledged (state 2 or 5 above).
| Alarm status: Alarm latched | Read one bit to see whether an alarm is latched. The controller returns 0 (false) when the alarm has a state other than latched (state 0, 1, 2, 3, 6 or 7 above). The controller returns 1 (true) when the alarm is latched (state 4 or 5 above).
| General parameter: Delay timer elapsed time | Read the time (in seconds) since the delay timer of the function was activated. The controller returns 0 if the timer is not running, and has been reset. The controller returns the delay time when the timer has run out and is not reset.
| General parameter: Delay timer remaining time | Read the time (in seconds) before the function can be activated. The controller returns the delay time if the timer is not running, and is reset. The controller returns 0 if the timer has run out and is not reset.

## Discrete output coil (01;05;15)
Discrete output coil (01;05;15)
Function group | Modbus address | PLC address | Controller function name | LC_GENSET_GB | LC_BUSTIE_BTB | LC_SINGLE_GENSET_GB | LC_SINGLE_GENSET_GB_MB | LC_SINGLE_GENSET_GB_NO_MAINS | LC_MAINS_MB | LC_MAINS_MB_TB
Command | 1000 | 1001 | Commands - Start/stop - Start engine | X |  | X | X | X
Command | 1000 | 1001 | Commands - Start/stop - Start | [5 empty] | X | X
Command | 1001 | 1002 | Commands - Start/stop - Stop engine | X |  | X | X | X
Command | 1001 | 1002 | Commands - Start/stop - Stop | [5 empty] | X | X
Command | 1004 | 1005 | Commands - Start/stop - Start engine and close generator breaker | X |  | X | X | X
Command | 1005 | 1006 | Commands - Start/stop - Open generator breaker and stop engine | X |  | X | X | X
Command | 1006 | 1007 | Commands - Generator breaker - Generator breaker close | X |  | X | X | X
Command | 1006 | 1007 | Commands - Bus tie breaker - Bus tie breaker close |  | X
Command | 1006 | 1007 | Commands - Mains breaker - Mains breaker close | [5 empty] | X | X
Command | 1007 | 1008 | Commands - Generator breaker - Generator breaker open | X |  | X | X | X
Command | 1007 | 1008 | Commands - Bus tie breaker - Bus tie breaker open |  | X
Command | 1007 | 1008 | Commands - Mains breaker - Mains breaker open | [5 empty] | X | X
Command | 1011 | 1012 | Commands - Mains breaker - Mains breaker close |  |  |  | X
Command | 1011 | 1012 | Commands - Tie breaker - Tie breaker close | [6 empty] | X
Command | 1012 | 1013 | Commands - Mains breaker - Mains breaker open |  |  |  | X
Command | 1012 | 1013 | Commands - Tie breaker - Tie breaker open | [6 empty] | X
Command | 1016 | 1017 | Commands - Generator breaker - Activate static synchronisation | X |  | X | X | X
Command | 1017 | 1018 | Commands - Generator breaker - Deactivate static synchronisation | X |  | X | X | X
Command | 1018 | 1019 | Commands - Generator breaker - Activate dynamic synchronisation | X |  | X | X | X
Command | 1019 | 1020 | Commands - Generator breaker - Deactivate dynamic synchronisation | X |  | X | X | X
Command | 1029 | 1030 | Commands - Alarms - Acknowledge all alarms | X | X | X | X | X | X | X
Command | 1030 | 1031 | Commands - Alarms - Reset all latches | X | X | X | X | X | X | X
Command | 1031 | 1032 | Commands - Alarms - Reset alarm horn | X | X | X | X | X | X | X
Command | 1032 | 1033 | Commands - Lamp test - Start lamp test | X | X | X | X | X | X | X
Command | 1033 | 1034 | Commands - Lamp test - Stop lamp test | X | X | X | X | X | X | X
Command | 1034 | 1035 | Disclaimer accept | X | X | X | X | X | X | X
Command | 1036 | 1037 | Commands - Fieldbus - Fieldbus conflict accepted | X | X | X | X | X | X | X
Command | 1037 | 1038 | Commands - Accept firmware module update | X | X | X | X | X | X | X
Command | 1038 | 1039 | Commands - Postpone firmware module update | X | X | X | X | X | X | X
Command | 1039 | 1040 | Commands - ECU measurement auto discover - Measurement list filter - available | X |  | X | X | X
Command | 1040 | 1041 | Commands - ECU measurement auto discover - Measurement list filter - clear | X |  | X | X | X
Command | 1041 | 1042 | Commands - J1939 Historical diagnostic log - Log request (DM2) | X |  | X | X | X
Command | 1042 | 1043 | Commands - J1939 Historical diagnostic log - Log clear (DM2) | X |  | X | X | X
Command | 1043 | 1044 | Commands - Modes - Local command control | X | X | X | X | X | X | X
Command | 1044 | 1045 | Commands - Modes - Remote command control | X | X | X | X | X | X | X
Command | 1063 | 1064 | Commands - Emulation - Load on | X |  | X | X | X | X | X
Command | 1064 | 1065 | Commands - Emulation - Load off | X |  | X | X | X | X | X
Command | 1068 | 1069 | Commands - Emulation - Breaker off | X | X | X | X | X | X | X
Command | 1080 | 1081 | Commands - Emulation - Breaker off |  |  |  | X |  |  | X
Command | 1085 | 1086 | Commands - Modes - AUTO | X | X | X | X | X | X | X
Command | 1086 | 1087 | Commands - Modes - MANUAL | X | X | X | X | X | X | X
Command | 1087 | 1088 | Commands - Modes - NO REG | X | X | X | X | X | X | X
Command | 1088 | 1089 | Commands - Modes - TEST | X | X | X | X | X | X | X
Command | 1089 | 1090 | Commands - Priority - 1st priority | X |  |  |  | X
Command | 1090 | 1091 | Commands - External set points - Activate external power set point | X |  | X | X |  | X | X
Command | 1091 | 1092 | Commands - External set points - Deactivate external power set point | X |  | X | X |  | X | X
Command | 1110 | 1111 | Preview feature accepted | X | X | X | X | X | X | X
Command | 1113 | 1114 | Commands - Application selector - Confirm application selection | X | X | X | X | X | X | X
Command | 1114 | 1115 | Commands - Application selector - Cancel application selection | X | X | X | X | X | X | X
Command | 1115 | 1116 | Commands - ECU diagnostic - Activate ECU diagnostic | X |  | X | X | X
Command | 1116 | 1117 | Commands - ECU diagnostic - Deactivate ECU diagnostic | X |  | X | X | X
Function | 8004 | 8005 | Functions - Digital input functions - Engine - Feedback - Digital running detection | X |  | X | X | X
Function | 8006 | 8007 | Functions - Digital input functions - Auxiliary - Pump logic - Deactivate pump logic 1 | X |  | X | X | X
Function | 8007 | 8008 | Functions - Analogue input functions - Auxiliary - Pump logic - Custom analogue input 1 | X |  | X | X | X
Function | 8008 | 8009 | Functions - Digital input functions - Engine - Command - Start enable | X |  | X | X | X
Function | 8009 | 8010 | Functions - Digital input functions - Breakers - Generator breaker - Feedback - GB open | X |  | X | X | X
Function | 8009 | 8010 | Functions - Digital input functions - Breakers - Bus tie breaker - Feedback - BTB open |  | X
Function | 8009 | 8010 | Functions - Digital input functions - Breakers - Mains breaker - Feedback - MB open | [5 empty] | X | X
Function | 8010 | 8011 | Functions - Digital input functions - Breakers - Generator breaker - Feedback - GB closed | X |  | X | X | X
Function | 8010 | 8011 | Functions - Digital input functions - Breakers - Bus tie breaker - Feedback - BTB closed |  | X
Function | 8010 | 8011 | Functions - Digital input functions - Breakers - Mains breaker - Feedback - MB closed | [5 empty] | X | X
Function | 8011 | 8012 | Functions - Digital input functions - Breakers - Generator breaker - Feedback - GB is spring loaded | X |  | X | X | X
Function | 8011 | 8012 | Functions - Digital input functions - Breakers - Bus tie breaker - Feedback - BTB is spring loaded |  | X
Function | 8011 | 8012 | Functions - Digital input functions - Breakers - Mains breaker - Feedback - MB is spring loaded | [5 empty] | X | X
Function | 8012 | 8013 | Functions - Digital input functions - Breakers - Generator breaker - Feedback - GB short circuit | X |  | X | X | X
Function | 8012 | 8013 | Functions - Digital input functions - Breakers - Bus tie breaker - Feedback - BTB short circuit |  | X
Function | 8012 | 8013 | Functions - Digital input functions - Breakers - Mains breaker - Feedback - MB short circuit | [5 empty] | X | X
Function | 8013 | 8014 | Functions - Digital input functions - Breakers - Mains breaker - Feedback - MB open |  |  |  | X
Function | 8013 | 8014 | Functions - Digital input functions - Breakers - Tie breaker - Feedback - TB open | [6 empty] | X
Function | 8014 | 8015 | Functions - Digital input functions - Breakers - Mains breaker - Feedback - MB closed |  |  |  | X
Function | 8014 | 8015 | Functions - Digital input functions - Breakers - Tie breaker - Feedback - TB closed | [6 empty] | X
Function | 8015 | 8016 | Functions - Digital input functions - Breakers - Mains breaker - Feedback - MB is spring loaded |  |  |  | X
Function | 8015 | 8016 | Functions - Digital input functions - Breakers - Tie breaker - Feedback - TB is spring loaded | [6 empty] | X
Function | 8016 | 8017 | Functions - Digital input functions - Breakers - Mains breaker - Feedback - MB short circuit |  |  |  | X
Function | 8016 | 8017 | Functions - Digital input functions - Breakers - Tie breaker - Feedback - TB short circuit | [6 empty] | X
Function | 8023 | 8024 | Functions - Digital input functions - Local - Nominal settings - Controller nominal setting - Nominal settings 1 | X | X | X | X | X | X | X
Function | 8024 | 8025 | Functions - Digital input functions - Local - Nominal settings - Controller nominal setting - Nominal settings 2 | X | X | X | X | X | X | X
Function | 8025 | 8026 | Functions - Digital input functions - Local - Nominal settings - Controller nominal setting - Nominal settings 3 | X | X | X | X | X | X | X
Function | 8026 | 8027 | Functions - Digital input functions - Local - Nominal settings - Controller nominal setting - Nominal settings 4 | X | X | X | X | X | X | X
Function | 8027 | 8028 | Functions - Digital input functions - Local - Mode - Local control | X | X | X | X | X | X | X
Function | 8028 | 8029 | Functions - Digital input functions - Local - Mode - Remote control | X | X | X | X | X | X | X
Function | 8029 | 8030 | Functions - Digital input functions - Alarm system - Inhibits - Activate inhibit 1 | X | X | X | X | X | X | X
Function | 8030 | 8031 | Functions - Digital input functions - Alarm system - Inhibits - Activate inhibit 2 | X | X | X | X | X | X | X
Function | 8031 | 8032 | Functions - Digital input functions - Alarm system - Inhibits - Activate inhibit 3 | X | X | X | X | X | X | X
Function | 8032 | 8033 | Functions - Digital input functions - Alarm system - Command - Acknowledge all alarms | X | X | X | X | X | X | X
Function | 8033 | 8034 | Functions - Digital input functions - Alarm system - Command - Reset all latched alarms | X | X | X | X | X | X | X
Function | 8034 | 8035 | Functions - Digital input functions - Alarm system - Additional functions - Suppress alarm action | X | X | X | X | X | X | X
Function | 8035 | 8036 | Functions - Digital input functions - Alarm system - Command - Reset horn | X | X | X | X | X | X | X
Function | 8071 | 8072 | Functions - Digital input functions - Engine - Command - Start engine | X |  | X | X | X
Function | 8071 | 8072 | Functions - Digital input functions - Mains - Command - Start | [5 empty] | X
Function | 8072 | 8073 | Functions - Digital input functions - Engine - Command - Stop engine | X |  | X | X | X
Function | 8072 | 8073 | Functions - Digital input functions - Mains - Command - Stop | [5 empty] | X
Function | 8078 | 8079 | Functions - Digital input functions - Engine - Command - Start engine and close generator breaker | X |  | X | X | X
Function | 8079 | 8080 | Functions - Digital input functions - Engine - Command - Open generator breaker and stop engine | X |  | X | X | X
Function | 8081 | 8082 | Functions - Digital input functions - Regulators - GOV - Manual - Manual GOV increase | X |  | X | X | X
Function | 8082 | 8083 | Functions - Digital input functions - Regulators - GOV - Manual - Manual GOV decrease | X |  | X | X | X
Function | 8083 | 8084 | Functions - Digital input functions - Regulators - AVR - Manual - Manual AVR increase | X |  | X | X | X
Function | 8084 | 8085 | Functions - Digital input functions - Regulators - AVR - Manual - Manual AVR decrease | X |  | X | X | X
Function | 8098 | 8099 | Functions - Digital input functions - Alarm system - Additional functions - Emergency stop | X | X | X | X | X | X | X
Function | 8111 | 8112 | Functions - Digital input functions - Test functions - Lamp test - Start lamp test | X | X | X | X | X | X | X
Function | 8112 | 8113 | Functions - Digital input functions - Test functions - Lamp test - Stop lamp test | X | X | X | X | X | X | X
Function | 8120 | 8121 | Functions - Digital input functions - Engine - Command - Crank delay | X |  | X | X | X
Function | 8121 | 8122 | Functions - Digital input functions - Engine - Command - Warm up delay | X |  | X | X | X
Function | 8122 | 8123 | Functions - Digital input functions - Engine - Command - Cooldown abort | X |  | X | X | X
Function | 8123 | 8124 | Functions - Digital input functions - Engine - Command - De-load genset | X |  | X | X | X
Function | 8124 | 8125 | Functions - Digital input functions - Engine - Idle run - Low speed | X |  | X | X | X
Function | 8125 | 8126 | Functions - Digital input functions - Engine - Idle run - Temperature control | X |  | X | X | X
Function | 8126 | 8127 | Functions - Digital input functions - System power management - Ground relay - Ground relay position feedback A | X |  | X | X
Function | 8127 | 8128 | Functions - Digital input functions - System power management - Ground relay - Ground relay position feedback B | X |  | X | X
Function | 8128 | 8129 | Functions - Digital input functions - Local - Mode - MANUAL | X | X | X | X | X | X | X
Function | 8129 | 8130 | Functions - Digital input functions - Local - Mode - AUTO | X | X | X | X | X | X | X
Function | 8130 | 8131 | Functions - Digital input functions - Local - Mode - Block | X | X | X | X | X | X | X
Function | 8131 | 8132 | Functions - Digital input functions - Local - Mode - Test | X |  | X | X | X | X | X
Function | 8132 | 8133 | Functions - Digital input functions - Local - Mode - No regulation | X |  | X | X | X
Function | 8133 | 8134 | Functions - Digital input functions - System power management - Automatic start - Auto start/stop | X |  | X | X | X | X | X
Function | 8134 | 8135 | Functions - Digital input functions - Mains - Command - Start | [6 empty] | X
Function | 8135 | 8136 | Functions - Digital input functions - Mains - Command - Stop | [6 empty] | X
Function | 8136 | 8137 | Functions - Digital input functions - System power management - Priority - 1st priority | X |  |  |  | X
Function | 8137 | 8138 | Functions - Digital input functions - Mains - Set point offsets - Active power - Active offset 1 | X |  | X | X | X | X | X
Function | 8138 | 8139 | Functions - Digital input functions - Mains - Set point offsets - Active power - Active offset 2 | X |  | X | X | X | X | X
Function | 8139 | 8140 | Functions - Digital input functions - Mains - Set point offsets - Active power - Active offset 3 | X |  | X | X | X | X | X
Function | 8140 | 8141 | Functions - Digital input functions - Mains - Set point offsets - Cos phi - Active offset 1 | X |  | X | X | X | X | X
Function | 8141 | 8142 | Functions - Digital input functions - Mains - Set point offsets - Cos phi - Active offset 2 | X |  | X | X | X | X | X
Function | 8142 | 8143 | Functions - Digital input functions - Mains - Set point offsets - Cos phi - Active offset 3 | X |  | X | X | X | X | X
Function | 8143 | 8144 | Functions - Digital input functions - Mains - External set points - Activate external power set point | X |  | X | X |  | X | X
Function | 8144 | 8145 | Functions - Digital input functions - Mains - External set points - Deactivate external power set point | X |  | X | X |  | X | X
Function | 8145 | 8146 | Functions - Digital input functions - Breakers - Generator breaker - Command - GB close | X |  | X | X | X
Function | 8145 | 8146 | Functions - Digital input functions - Breakers - Bus tie breaker - Command - BTB close |  | X
Function | 8145 | 8146 | Functions - Digital input functions - Breakers - Mains breaker - Command - MB close | [5 empty] | X | X
Function | 8146 | 8147 | Functions - Digital input functions - Breakers - Generator breaker - Command - GB open | X |  | X | X | X
Function | 8146 | 8147 | Functions - Digital input functions - Breakers - Bus tie breaker - Command - BTB open |  | X
Function | 8146 | 8147 | Functions - Digital input functions - Breakers - Mains breaker - Command - MB open | [5 empty] | X | X
Function | 8148 | 8149 | Functions - Digital input functions - Breakers - Generator breaker - Command - Block GB close | X |  | X | X | X
Function | 8148 | 8149 | Functions - Digital input functions - Breakers - Bus tie breaker - Command - Block BTB close |  | X
Function | 8148 | 8149 | Functions - Digital input functions - Breakers - Mains breaker - Command - Block MB close | [5 empty] | X | X
Function | 8149 | 8150 | Functions - Digital input functions - Breakers - Mains breaker - Command - MB close |  |  |  | X
Function | 8149 | 8150 | Functions - Digital input functions - Breakers - Tie breaker - Command - TB close | [6 empty] | X
Function | 8150 | 8151 | Functions - Digital input functions - Breakers - Mains breaker - Command - MB open |  |  |  | X
Function | 8150 | 8151 | Functions - Digital input functions - Breakers - Tie breaker - Command - TB open | [6 empty] | X
Function | 8152 | 8153 | Functions - Digital input functions - Breakers - Mains breaker - Command - Block MB close |  |  |  | X
Function | 8152 | 8153 | Functions - Digital input functions - Breakers - Tie breaker - Command - Block TB close | [6 empty] | X
Function | 8153 | 8154 | Functions - Digital input functions - Local - Nominal settings - Transducer 1 nominal setting - Nominal settings 1 | X | X | X | X | X | X | X
Function | 8154 | 8155 | Functions - Digital input functions - Local - Nominal settings - Transducer 1 nominal setting - Nominal settings 2 | X | X | X | X | X | X | X
Function | 8155 | 8156 | Functions - Digital input functions - Local - Nominal settings - Transducer 1 nominal setting - Nominal settings 3 | X | X | X | X | X | X | X
Function | 8156 | 8157 | Functions - Digital input functions - Local - Nominal settings - Transducer 1 nominal setting - Nominal settings 4 | X | X | X | X | X | X | X
Function | 8157 | 8158 | Functions - Digital input functions - Local - Nominal settings - Transducer 2 nominal setting - Nominal settings 1 | X | X | X | X | X | X | X
Function | 8158 | 8159 | Functions - Digital input functions - Local - Nominal settings - Transducer 2 nominal setting - Nominal settings 2 | X | X | X | X | X | X | X
Function | 8159 | 8160 | Functions - Digital input functions - Local - Nominal settings - Transducer 2 nominal setting - Nominal settings 3 | X | X | X | X | X | X | X
Function | 8160 | 8161 | Functions - Digital input functions - Local - Nominal settings - Transducer 2 nominal setting - Nominal settings 4 | X | X | X | X | X | X | X
Function | 8161 | 8162 | Functions - Digital input functions - Local - Nominal settings - Transducer 3 nominal setting - Nominal settings 1 | X | X | X | X | X | X | X
Function | 8162 | 8163 | Functions - Digital input functions - Local - Nominal settings - Transducer 3 nominal setting - Nominal settings 2 | X | X | X | X | X | X | X
Function | 8163 | 8164 | Functions - Digital input functions - Local - Nominal settings - Transducer 3 nominal setting - Nominal settings 3 | X | X | X | X | X | X | X
Function | 8164 | 8165 | Functions - Digital input functions - Local - Nominal settings - Transducer 3 nominal setting - Nominal settings 4 | X | X | X | X | X | X | X
Function | 8165 | 8166 | Functions - Digital input functions - Local - Nominal settings - Transducer 4 nominal setting - Nominal settings 1 | X | X | X | X | X | X | X
Function | 8166 | 8167 | Functions - Digital input functions - Local - Nominal settings - Transducer 4 nominal setting - Nominal settings 2 | X | X | X | X | X | X | X
Function | 8167 | 8168 | Functions - Digital input functions - Local - Nominal settings - Transducer 4 nominal setting - Nominal settings 3 | X | X | X | X | X | X | X
Function | 8168 | 8169 | Functions - Digital input functions - Local - Nominal settings - Transducer 4 nominal setting - Nominal settings 4 | X | X | X | X | X | X | X
Function | 8174 | 8175 | Functions - Digital input functions - Engine - ECU diagnostic - ECU diagnostic on | X |  | X | X | X
Function | 8175 | 8176 | Functions - Digital input functions - Engine - ECU diagnostic - ECU diagnostic off | X |  | X | X | X
Function | 8176 | 8177 | Functions - Digital input functions - Auxiliary - Pump logic - Activate pump logic 1 | X |  | X | X | X
Function | 8177 | 8178 | Functions - Digital input functions - Auxiliary - Pump logic - Activate pump logic 2 | X |  | X | X | X
Function | 8178 | 8179 | Functions - Digital input functions - Auxiliary - Pump logic - Deactivate pump logic 2 | X |  | X | X | X
Function | 8179 | 8180 | Functions - Digital input functions - Auxiliary - Pump logic - Activate pump logic 3 | X |  | X | X | X
Function | 8180 | 8181 | Functions - Digital input functions - Auxiliary - Pump logic - Deactivate pump logic 3 | X |  | X | X | X
Function | 8181 | 8182 | Activate external f offset |  |  | X | X
Function | 8182 | 8183 | Deactivate external f offset |  |  | X | X
Function | 8187 | 8188 | Functions - Digital input functions - Grid code - RRCR - RRCR input 1 |  |  | X | X
Function | 8188 | 8189 | Functions - Digital input functions - Grid code - RRCR - RRCR input 2 |  |  | X | X
Function | 8189 | 8190 | Functions - Digital input functions - Grid code - RRCR - RRCR input 3 |  |  | X | X
Function | 8190 | 8191 | Functions - Digital input functions - Grid code - RRCR - RRCR input 4 |  |  | X | X
CustomLogic: Modbus digital signal | 12000 | 12001 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 1 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12001 | 12002 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 2 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12002 | 12003 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 3 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12003 | 12004 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 4 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12004 | 12005 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 5 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12005 | 12006 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 6 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12006 | 12007 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 7 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12007 | 12008 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 8 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12008 | 12009 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 9 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12009 | 12010 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 10 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12010 | 12011 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 11 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12011 | 12012 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 12 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12012 | 12013 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 13 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12013 | 12014 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 14 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12014 | 12015 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 15 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12015 | 12016 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 16 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12016 | 12017 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 17 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12017 | 12018 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 18 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12018 | 12019 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 19 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12019 | 12020 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 20 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12020 | 12021 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 21 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12021 | 12022 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 22 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12022 | 12023 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 23 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12023 | 12024 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 24 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12024 | 12025 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 25 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12025 | 12026 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 26 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12026 | 12027 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 27 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12027 | 12028 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 28 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12028 | 12029 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 29 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12029 | 12030 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 30 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12030 | 12031 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 31 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12031 | 12032 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 32 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12032 | 12033 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 33 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12033 | 12034 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 34 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12034 | 12035 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 35 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12035 | 12036 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 36 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12036 | 12037 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 37 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12037 | 12038 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 38 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12038 | 12039 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 39 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12039 | 12040 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 40 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12040 | 12041 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 41 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12041 | 12042 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 42 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12042 | 12043 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 43 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12043 | 12044 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 44 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12044 | 12045 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 45 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12045 | 12046 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 46 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12046 | 12047 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 47 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12047 | 12048 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 48 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12048 | 12049 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 49 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12049 | 12050 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 50 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12050 | 12051 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 51 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12051 | 12052 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 52 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12052 | 12053 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 53 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12053 | 12054 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 54 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12054 | 12055 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 55 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12055 | 12056 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 56 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12056 | 12057 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 57 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12057 | 12058 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 58 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12058 | 12059 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 59 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12059 | 12060 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 60 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12060 | 12061 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 61 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12061 | 12062 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 62 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12062 | 12063 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 63 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12063 | 12064 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 64 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12064 | 12065 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 65 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12065 | 12066 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 66 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12066 | 12067 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 67 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12067 | 12068 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 68 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12068 | 12069 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 69 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12069 | 12070 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 70 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12070 | 12071 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 71 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12071 | 12072 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 72 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12072 | 12073 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 73 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12073 | 12074 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 74 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12074 | 12075 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 75 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12075 | 12076 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 76 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12076 | 12077 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 77 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12077 | 12078 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 78 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12078 | 12079 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 79 | X | X | X | X | X | X | X
CustomLogic: Modbus digital signal | 12079 | 12080 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 80 | X | X | X | X | X | X | X
Custom parameter: Enable | 12100 | 12101 | Parameters - Custom parameters - Custom parameter 0 - Enable 0 | X | X | X | X | X | X | X
Custom parameter: Enable | 12101 | 12102 | Parameters - Custom parameters - Custom parameter 1 - Enable 1 | X | X | X | X | X | X | X
Custom parameter: Enable | 12102 | 12103 | Parameters - Custom parameters - Custom parameter 2 - Enable 2 | X | X | X | X | X | X | X
Custom parameter: Enable | 12103 | 12104 | Parameters - Custom parameters - Custom parameter 3 - Enable 3 | X | X | X | X | X | X | X
Custom parameter: Enable | 12104 | 12105 | Parameters - Custom parameters - Custom parameter 4 - Enable 4 | X | X | X | X | X | X | X
Custom parameter: Enable | 12105 | 12106 | Parameters - Custom parameters - Custom parameter 5 - Enable 5 | X | X | X | X | X | X | X
Custom parameter: Enable | 12106 | 12107 | Parameters - Custom parameters - Custom parameter 6 - Enable 6 | X | X | X | X | X | X | X
Custom parameter: Enable | 12107 | 12108 | Parameters - Custom parameters - Custom parameter 7 - Enable 7 | X | X | X | X | X | X | X
Custom parameter: Enable | 12108 | 12109 | Parameters - Custom parameters - Custom parameter 8 - Enable 8 | X | X | X | X | X | X | X
Custom parameter: Enable | 12109 | 12110 | Parameters - Custom parameters - Custom parameter 9 - Enable 9 | X | X | X | X | X | X | X
Custom parameter: Enable | 12110 | 12111 | Parameters - Custom parameters - Custom parameter 10 - Enable 10 | X | X | X | X | X | X | X
Custom parameter: Enable | 12111 | 12112 | Parameters - Custom parameters - Custom parameter 11 - Enable 11 | X | X | X | X | X | X | X
Custom parameter: Enable | 12112 | 12113 | Parameters - Custom parameters - Custom parameter 12 - Enable 12 | X | X | X | X | X | X | X
Custom parameter: Enable | 12113 | 12114 | Parameters - Custom parameters - Custom parameter 13 - Enable 13 | X | X | X | X | X | X | X
Custom parameter: Enable | 12114 | 12115 | Parameters - Custom parameters - Custom parameter 14 - Enable 14 | X | X | X | X | X | X | X
Custom parameter: Enable | 12115 | 12116 | Parameters - Custom parameters - Custom parameter 15 - Enable 15 | X | X | X | X | X | X | X
Custom parameter: Enable | 12116 | 12117 | Parameters - Custom parameters - Custom parameter 16 - Enable 16 | X | X | X | X | X | X | X
Custom parameter: Enable | 12117 | 12118 | Parameters - Custom parameters - Custom parameter 17 - Enable 17 | X | X | X | X | X | X | X
Custom parameter: Enable | 12118 | 12119 | Parameters - Custom parameters - Custom parameter 18 - Enable 18 | X | X | X | X | X | X | X
Custom parameter: Enable | 12119 | 12120 | Parameters - Custom parameters - Custom parameter 19 - Enable 19 | X | X | X | X | X | X | X
Custom parameter: Enable | 12120 | 12121 | Parameters - Custom parameters - Custom parameter 20 - Enable 20 | X | X | X | X | X | X | X
Custom parameter: Enable | 12121 | 12122 | Parameters - Custom parameters - Custom parameter 21 - Enable 21 | X | X | X | X | X | X | X
Custom parameter: Enable | 12122 | 12123 | Parameters - Custom parameters - Custom parameter 22 - Enable 22 | X | X | X | X | X | X | X
Custom parameter: Enable | 12123 | 12124 | Parameters - Custom parameters - Custom parameter 23 - Enable 23 | X | X | X | X | X | X | X
Custom parameter: Enable | 12124 | 12125 | Parameters - Custom parameters - Custom parameter 24 - Enable 24 | X | X | X | X | X | X | X
Custom parameter: Enable | 12125 | 12126 | Parameters - Custom parameters - Custom parameter 25 - Enable 25 | X | X | X | X | X | X | X
Custom parameter: Enable | 12126 | 12127 | Parameters - Custom parameters - Custom parameter 26 - Enable 26 | X | X | X | X | X | X | X
Custom parameter: Enable | 12127 | 12128 | Parameters - Custom parameters - Custom parameter 27 - Enable 27 | X | X | X | X | X | X | X
Custom parameter: Enable | 12128 | 12129 | Parameters - Custom parameters - Custom parameter 28 - Enable 28 | X | X | X | X | X | X | X
Custom parameter: Enable | 12129 | 12130 | Parameters - Custom parameters - Custom parameter 29 - Enable 29 | X | X | X | X | X | X | X
Custom parameter: Enable | 12130 | 12131 | Parameters - Custom parameters - Custom parameter 30 - Enable 30 | X | X | X | X | X | X | X
Custom parameter: Enable | 12131 | 12132 | Parameters - Custom parameters - Custom parameter 31 - Enable 31 | X | X | X | X | X | X | X
Custom parameter: Enable | 12132 | 12133 | Parameters - Custom parameters - Custom parameter 32 - Enable 32 | X | X | X | X | X | X | X
Custom parameter: Enable | 12133 | 12134 | Parameters - Custom parameters - Custom parameter 33 - Enable 33 | X | X | X | X | X | X | X
Custom parameter: Enable | 12134 | 12135 | Parameters - Custom parameters - Custom parameter 34 - Enable 34 | X | X | X | X | X | X | X
Custom parameter: Enable | 12135 | 12136 | Parameters - Custom parameters - Custom parameter 35 - Enable 35 | X | X | X | X | X | X | X
Custom parameter: Enable | 12136 | 12137 | Parameters - Custom parameters - Custom parameter 36 - Enable 36 | X | X | X | X | X | X | X
Custom parameter: Enable | 12137 | 12138 | Parameters - Custom parameters - Custom parameter 37 - Enable 37 | X | X | X | X | X | X | X
Custom parameter: Enable | 12138 | 12139 | Parameters - Custom parameters - Custom parameter 38 - Enable 38 | X | X | X | X | X | X | X
Custom parameter: Enable | 12139 | 12140 | Parameters - Custom parameters - Custom parameter 39 - Enable 39 | X | X | X | X | X | X | X
Custom parameter: Enable | 12140 | 12141 | Parameters - Custom parameters - Custom parameter 40 - Enable 40 | X | X | X | X | X | X | X
Custom parameter: Enable | 12141 | 12142 | Parameters - Custom parameters - Custom parameter 41 - Enable 41 | X | X | X | X | X | X | X
Custom parameter: Enable | 12142 | 12143 | Parameters - Custom parameters - Custom parameter 42 - Enable 42 | X | X | X | X | X | X | X
Custom parameter: Enable | 12143 | 12144 | Parameters - Custom parameters - Custom parameter 43 - Enable 43 | X | X | X | X | X | X | X
Custom parameter: Enable | 12144 | 12145 | Parameters - Custom parameters - Custom parameter 44 - Enable 44 | X | X | X | X | X | X | X
Custom parameter: Enable | 12145 | 12146 | Parameters - Custom parameters - Custom parameter 45 - Enable 45 | X | X | X | X | X | X | X
Custom parameter: Enable | 12146 | 12147 | Parameters - Custom parameters - Custom parameter 46 - Enable 46 | X | X | X | X | X | X | X
Custom parameter: Enable | 12147 | 12148 | Parameters - Custom parameters - Custom parameter 47 - Enable 47 | X | X | X | X | X | X | X
Custom parameter: Enable | 12148 | 12149 | Parameters - Custom parameters - Custom parameter 48 - Enable 48 | X | X | X | X | X | X | X
Custom parameter: Enable | 12149 | 12150 | Parameters - Custom parameters - Custom parameter 49 - Enable 49 | X | X | X | X | X | X | X
Custom logic: digital input | 12300 | 12301 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12301 | 12302 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12302 | 12303 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12303 | 12304 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12304 | 12305 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12305 | 12306 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12306 | 12307 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12307 | 12308 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12308 | 12309 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12309 | 12310 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12310 | 12311 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12311 | 12312 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12312 | 12313 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12313 | 12314 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12314 | 12315 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12315 | 12316 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12316 | 12317 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12317 | 12318 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12318 | 12319 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12319 | 12320 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12320 | 12321 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12321 | 12322 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12322 | 12323 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12323 | 12324 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12324 | 12325 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12325 | 12326 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12326 | 12327 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12327 | 12328 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12328 | 12329 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12329 | 12330 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12330 | 12331 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12331 | 12332 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12332 | 12333 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12333 | 12334 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12334 | 12335 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12335 | 12336 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12336 | 12337 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12337 | 12338 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12338 | 12339 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12339 | 12340 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12340 | 12341 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12341 | 12342 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12342 | 12343 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12343 | 12344 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12344 | 12345 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12345 | 12346 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12346 | 12347 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12347 | 12348 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12348 | 12349 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12349 | 12350 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12350 | 12351 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12351 | 12352 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12352 | 12353 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12353 | 12354 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12354 | 12355 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12355 | 12356 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12356 | 12357 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12357 | 12358 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12358 | 12359 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12359 | 12360 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12360 | 12361 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12361 | 12362 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12362 | 12363 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12363 | 12364 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12364 | 12365 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12365 | 12366 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12366 | 12367 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12367 | 12368 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12368 | 12369 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12369 | 12370 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12370 | 12371 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12371 | 12372 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12372 | 12373 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12373 | 12374 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12374 | 12375 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12375 | 12376 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12376 | 12377 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12377 | 12378 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12378 | 12379 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Custom logic: digital input | 12379 | 12380 | Functions - Digital input functions - Local - CustomLogic - Inputs - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16000 | 16001 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16001 | 16002 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16002 | 16003 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16003 | 16004 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16004 | 16005 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16005 | 16006 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16006 | 16007 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16007 | 16008 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16008 | 16009 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16009 | 16010 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16010 | 16011 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16011 | 16012 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16012 | 16013 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16013 | 16014 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16014 | 16015 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16015 | 16016 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16016 | 16017 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16017 | 16018 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16018 | 16019 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16019 | 16020 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16020 | 16021 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16021 | 16022 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16022 | 16023 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16023 | 16024 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16024 | 16025 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16025 | 16026 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16026 | 16027 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16027 | 16028 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16028 | 16029 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16029 | 16030 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16030 | 16031 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16031 | 16032 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16032 | 16033 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16033 | 16034 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16034 | 16035 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16035 | 16036 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16036 | 16037 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16037 | 16038 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16038 | 16039 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16039 | 16040 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16040 | 16041 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16041 | 16042 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16042 | 16043 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16043 | 16044 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16044 | 16045 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16045 | 16046 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16046 | 16047 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16047 | 16048 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16048 | 16049 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16049 | 16050 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16050 | 16051 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16051 | 16052 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16052 | 16053 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16053 | 16054 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16054 | 16055 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16055 | 16056 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16056 | 16057 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16057 | 16058 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16058 | 16059 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16059 | 16060 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16060 | 16061 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16061 | 16062 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16062 | 16063 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16063 | 16064 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16064 | 16065 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16065 | 16066 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16066 | 16067 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16067 | 16068 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16068 | 16069 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16069 | 16070 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16070 | 16071 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16071 | 16072 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16072 | 16073 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16073 | 16074 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16074 | 16075 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16075 | 16076 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16076 | 16077 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16077 | 16078 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16078 | 16079 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16079 | 16080 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16080 | 16081 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16081 | 16082 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16082 | 16083 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16083 | 16084 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16084 | 16085 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16085 | 16086 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16086 | 16087 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16087 | 16088 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16088 | 16089 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16089 | 16090 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16090 | 16091 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16091 | 16092 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16092 | 16093 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16093 | 16094 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16094 | 16095 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16095 | 16096 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16096 | 16097 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16097 | 16098 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16098 | 16099 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Codesys digital inputs | 16099 | 16100 | Functions - Digital input functions - Local - CODESYS - Custom digital input | X | X | X | X | X | X | X
Alarm parameter: Enable | 20000 | 20001 | Application initialisation error | X | X | X | X | X | X | X
Alarm parameter: Enable | 20001 | 20002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm parameter: Enable | 20002 | 20003 | Preliminary software | X | X | X | X | X | X | X
Alarm parameter: Enable | 20003 | 20004 | Parameters - Engine - Stop sequence - Stop failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20004 | 20005 | Parameters - Engine - Start sequence - Start failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20005 | 20006 | Parameters - Engine - Start sequence - Crank failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20006 | 20007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20007 | 20008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20008 | 20009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20009 | 20010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20010 | 20011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Configuration - Flags - Magnetic pickup wire break alarm | X |  | X | X | X
Alarm parameter: Enable | 20011 | 20012 | Parameters - Engine - Stop sequence - Externally stopped - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20013 | 20014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20014 | 20015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20015 | 20016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20016 | 20017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20017 | 20018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20018 | 20019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20019 | 20020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20020 | 20021 | Parameters - Engine - Protections - Level - Coolant level 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20021 | 20022 | Parameters - Engine - Protections - Level - Coolant level 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20022 | 20023 | Parameters - Engine - Protections - Level - Coolant level 3 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20027 | 20028 | Parameters - Engine - Running detection - Primary running feedback failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20041 | 20042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Configuration - Flags - GB closing failure | X |  | X | X | X
Alarm parameter: Enable | 20041 | 20042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Configuration - Flags - BTB closing failure |  | X
Alarm parameter: Enable | 20041 | 20042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration - Flags - MB closing failure | [5 empty] | X | X
Alarm parameter: Enable | 20042 | 20043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Configuration - Flags - GB opening failure | X |  | X | X | X
Alarm parameter: Enable | 20042 | 20043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Configuration - Flags - BTB opening failure |  | X
Alarm parameter: Enable | 20042 | 20043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration - Flags - MB opening failure | [5 empty] | X | X
Alarm parameter: Enable | 20043 | 20044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Configuration - Flags - GB position failure | X |  | X | X | X
Alarm parameter: Enable | 20043 | 20044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Configuration - Flags - BTB position failure |  | X
Alarm parameter: Enable | 20043 | 20044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration - Flags - MB position failure | [5 empty] | X | X
Alarm parameter: Enable | 20044 | 20045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Configuration - Flags - GB configuration failure | X |  | X | X | X
Alarm parameter: Enable | 20044 | 20045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Configuration - Flags - BTB configuration failure |  | X
Alarm parameter: Enable | 20044 | 20045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration - Flags - MB configuration failure | [5 empty] | X | X
Alarm parameter: Enable | 20045 | 20046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Configuration - Flags - GB synchronisation failure | X |  | X | X | X
Alarm parameter: Enable | 20045 | 20046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Configuration - Flags - BTB synchronisation failure |  | X
Alarm parameter: Enable | 20045 | 20046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration - Flags - MB synchronisation failure | [5 empty] | X | X
Alarm parameter: Enable | 20046 | 20047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Configuration - Flags - GB de-load failure | X |  | X | X | X
Alarm parameter: Enable | 20046 | 20047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Configuration - Flags - BTB de-load failure |  | X
Alarm parameter: Enable | 20046 | 20047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration - Flags - MB de-load failure | [5 empty] | X | X
Alarm parameter: Enable | 20047 | 20048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Configuration - Flags - GB tripped (external) | X |  | X | X | X
Alarm parameter: Enable | 20047 | 20048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Configuration - Flags - BTB tripped (external) |  | X
Alarm parameter: Enable | 20047 | 20048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Configuration - Flags - MB tripped (external) | [5 empty] | X | X
Alarm parameter: Enable | 20048 | 20049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Configuration - Flags - GB short circuit | X |  | X | X | X
Alarm parameter: Enable | 20048 | 20049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Configuration - Flags - BTB short circuit |  | X
Alarm parameter: Enable | 20048 | 20049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Configuration - Flags - MB short circuit | [5 empty] | X | X
Alarm parameter: Enable | 20049 | 20050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration - Flags - MB closing failure |  |  |  | X
Alarm parameter: Enable | 20049 | 20050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Configuration - Flags - TB closing failure | [6 empty] | X
Alarm parameter: Enable | 20050 | 20051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration - Flags - MB opening failure |  |  |  | X
Alarm parameter: Enable | 20050 | 20051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Configuration - Flags - TB opening failure | [6 empty] | X
Alarm parameter: Enable | 20051 | 20052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration - Flags - MB position failure |  |  |  | X
Alarm parameter: Enable | 20051 | 20052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Configuration - Flags - TB position failure | [6 empty] | X
Alarm parameter: Enable | 20052 | 20053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration - Flags - MB configuration failure |  |  |  | X
Alarm parameter: Enable | 20052 | 20053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Configuration - Flags - TB configuration failure | [6 empty] | X
Alarm parameter: Enable | 20053 | 20054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration - Flags - MB synchronisation failure |  |  |  | X
Alarm parameter: Enable | 20053 | 20054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Configuration - Flags - TB synchronisation failure | [6 empty] | X
Alarm parameter: Enable | 20054 | 20055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration - Flags - MB de-load failure |  |  |  | X
Alarm parameter: Enable | 20054 | 20055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Configuration - Flags - TB de-load failure | [6 empty] | X
Alarm parameter: Enable | 20055 | 20056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Configuration - Flags - MB tripped (external) |  |  |  | X
Alarm parameter: Enable | 20055 | 20056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Configuration - Flags - TB tripped (external) | [6 empty] | X
Alarm parameter: Enable | 20056 | 20057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Configuration - Flags - MB short circuit |  |  |  | X
Alarm parameter: Enable | 20056 | 20057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Configuration - Flags - TB short circuit | [6 empty] | X
Alarm parameter: Enable | 20060 | 20061 | Parameters - Mains - AC setup - Phase sequence error - Configuration - Flags - Mains phase sequence error |  |  | X | X
Alarm parameter: Enable | 20060 | 20061 | Parameters - Busbar - AC setup - Phase sequence error - Configuration - Flags - Busbar phase sequence error | X |  |  |  | X | X | X
Alarm parameter: Enable | 20060 | 20061 | Parameters - Busbar B - AC setup - Phase sequence error - Configuration - Flags - Busbar B phase sequence error |  | X
Alarm parameter: Enable | 20061 | 20062 | Parameters - Generator - AC setup - Phase sequence error - Configuration - Flags - Generator phase sequence error | X |  | X | X | X
Alarm parameter: Enable | 20061 | 20062 | Parameters - Busbar A - AC setup - Phase sequence error - Configuration - Flags - Busbar A phase sequence error |  | X
Alarm parameter: Enable | 20061 | 20062 | Parameters - Mains - AC setup - Phase sequence error - Configuration - Flags - Mains phase sequence error | [5 empty] | X | X
Alarm parameter: Enable | 20062 | 20063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20103 | 20104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Configuration - Flags |  |  | X | X
Alarm parameter: Enable | 20103 | 20104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Configuration - Flags | X |  |  |  | X | X | X
Alarm parameter: Enable | 20103 | 20104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Configuration - Flags |  | X
Alarm parameter: Enable | 20104 | 20105 | Parameters - Mains - Additional protections - Vector shift - Configuration - Flags |  |  | X | X
Alarm parameter: Enable | 20104 | 20105 | Parameters - Busbar - Additional protections - Vector shift - Configuration - Flags | X |  |  |  | X | X | X
Alarm parameter: Enable | 20104 | 20105 | Parameters - Busbar B - Additional protections - Vector shift - Configuration - Flags |  | X
Alarm parameter: Enable | 20105 | 20106 | Parameters - Generator - Current protections - Inverse time over-current - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20105 | 20106 | Parameters - Busbar A - Current protections - Inverse time over-current - Configuration - Flags |  | X
Alarm parameter: Enable | 20105 | 20106 | Parameters - Mains - Current protections - Inverse time over-current - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20106 | 20107 | Parameters - Local - 4th current input - Earth inverse time over-current - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20107 | 20108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20108 | 20109 | Parameters - Generator - Additional protections - V< and Q< 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20108 | 20109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Configuration - Flags |  | X
Alarm parameter: Enable | 20108 | 20109 | Parameters - Mains - Additional protections - V< and Q< 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20109 | 20110 | Parameters - Generator - Additional protections - V< and Q< 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20109 | 20110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Configuration - Flags |  | X
Alarm parameter: Enable | 20109 | 20110 | Parameters - Mains - Additional protections - V< and Q< 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20110 | 20111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20110 | 20111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Configuration - Flags |  | X
Alarm parameter: Enable | 20110 | 20111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20111 | 20112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20111 | 20112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Configuration - Flags |  | X
Alarm parameter: Enable | 20111 | 20112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20115 | 20116 | Protection set point out of range | X | X | X | X | X | X | X
Alarm parameter: Enable | 20116 | 20117 | Parameters - Generator - Current protections - Stabilised differential current - Configuration - Flags - Stabilised differential | X |  | X | X | X
Alarm parameter: Enable | 20117 | 20118 | Parameters - Generator - Current protections - High set differential current - Configuration - Flags - High set differential | X |  | X | X | X
Alarm parameter: Enable | 20118 | 20119 | Protection set point out of range (differential current) | X |  | X | X | X
Alarm parameter: Enable | 20119 | 20120 | Parameters - Local - Mode - Not under remote control - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20121 | 20122 | Parameters - Local - Monitoring - System not OK - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20122 | 20123 | Configuration update delayed | X | X | X | X | X | X | X
Alarm parameter: Enable | 20123 | 20124 | Critical process error | X | X | X | X | X | X | X
Alarm parameter: Enable | 20124 | 20125 | Restore error | X | X | X | X | X | X | X
Alarm parameter: Enable | 20125 | 20126 | SD-card format error | X | X | X | X | X | X | X
Alarm parameter: Enable | 20126 | 20127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm parameter: Enable | 20127 | 20128 | Fieldbus configuration exceeded maximum I/O configuration | X | X | X | X | X | X | X
Alarm parameter: Enable | 20128 | 20129 | Parameters - Custom alarm - Custom alarm 0 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20129 | 20130 | Parameters - Custom alarm - Custom alarm 1 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20130 | 20131 | Parameters - Custom alarm - Custom alarm 2 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20131 | 20132 | Parameters - Custom alarm - Custom alarm 3 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20132 | 20133 | Parameters - Custom alarm - Custom alarm 4 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20133 | 20134 | Parameters - Custom alarm - Custom alarm 5 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20134 | 20135 | Parameters - Custom alarm - Custom alarm 6 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20135 | 20136 | Parameters - Custom alarm - Custom alarm 7 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20136 | 20137 | Parameters - Custom alarm - Custom alarm 8 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20137 | 20138 | Parameters - Custom alarm - Custom alarm 9 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20138 | 20139 | Parameters - Custom alarm - Custom alarm 10 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20139 | 20140 | Parameters - Custom alarm - Custom alarm 11 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20140 | 20141 | Parameters - Custom alarm - Custom alarm 12 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20141 | 20142 | Parameters - Custom alarm - Custom alarm 13 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20142 | 20143 | Parameters - Custom alarm - Custom alarm 14 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20143 | 20144 | Parameters - Custom alarm - Custom alarm 15 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20144 | 20145 | Parameters - Custom alarm - Custom alarm 16 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20145 | 20146 | Parameters - Custom alarm - Custom alarm 17 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20146 | 20147 | Parameters - Custom alarm - Custom alarm 18 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20147 | 20148 | Parameters - Custom alarm - Custom alarm 19 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20148 | 20149 | Parameters - Custom alarm - Custom alarm 20 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20149 | 20150 | Parameters - Custom alarm - Custom alarm 21 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20150 | 20151 | Parameters - Custom alarm - Custom alarm 22 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20151 | 20152 | Parameters - Custom alarm - Custom alarm 23 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20152 | 20153 | Parameters - Custom alarm - Custom alarm 24 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Enable | 20153 | 20154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Configuration - Flags - GOV regulation error | X |  | X | X | X
Alarm parameter: Enable | 20154 | 20155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Configuration - Flags - AVR regulation error | X |  | X | X | X
Alarm parameter: Enable | 20163 | 20164 | Required hardware card(s) not found | X | X | X | X | X | X | X
Alarm parameter: Enable | 20164 | 20165 | Software mismatch on hardware module(s) | X | X | X | X | X | X | X
Alarm parameter: Enable | 20165 | 20166 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration - Flags - Mains L1-L2-L3 wire break |  |  | X
Alarm parameter: Enable | 20165 | 20166 | Parameters - Busbar - AC setup - Multiple phase wire break - Configuration - Flags - Busbar L1-L2-L3 wire break | X |  |  |  | X | X
Alarm parameter: Enable | 20165 | 20166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Configuration - Flags - Busbar B L1-L2-L3 wire break |  | X
Alarm parameter: Enable | 20166 | 20167 | Parameters - Generator - AC setup - Multiple phase wire break - Configuration - Flags - Generator L1-L2-L3 wire break | X |  | X |  | X
Alarm parameter: Enable | 20166 | 20167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Configuration - Flags - Busbar A L1-L2-L3 wire break |  | X
Alarm parameter: Enable | 20166 | 20167 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration - Flags - Mains L1-L2-L3 wire break | [5 empty] | X
Alarm parameter: Enable | 20167 | 20168 | Parameters - Mains - AC setup - L1 wire break - Configuration - Flags - Mains L1 wire break |  |  | X
Alarm parameter: Enable | 20167 | 20168 | Parameters - Busbar - AC setup - L1 wire break - Configuration - Flags - Busbar L1 wire break | X |  |  |  | X | X
Alarm parameter: Enable | 20167 | 20168 | Parameters - Busbar B - AC setup - L1 wire break - Configuration - Flags - Busbar B L1 wire break |  | X
Alarm parameter: Enable | 20168 | 20169 | Parameters - Mains - AC setup - L2 wire break - Configuration - Flags - Mains L2 wire break |  |  | X
Alarm parameter: Enable | 20168 | 20169 | Parameters - Busbar - AC setup - L2 wire break - Configuration - Flags - Busbar L2 wire break | X |  |  |  | X | X
Alarm parameter: Enable | 20168 | 20169 | Parameters - Busbar B - AC setup - L2 wire break - Configuration - Flags - Busbar B L2 wire break |  | X
Alarm parameter: Enable | 20169 | 20170 | Parameters - Mains - AC setup - L3 wire break - Configuration - Flags - Mains L3 wire break |  |  | X
Alarm parameter: Enable | 20169 | 20170 | Parameters - Busbar - AC setup - L3 wire break - Configuration - Flags - Busbar L3 wire break | X |  |  |  | X | X
Alarm parameter: Enable | 20169 | 20170 | Parameters - Busbar B - AC setup - L3 wire break - Configuration - Flags - Busbar B L3 wire break |  | X
Alarm parameter: Enable | 20170 | 20171 | Parameters - Generator - AC setup - L1 wire break - Configuration - Flags - Generator L1 wire break | X |  | X |  | X
Alarm parameter: Enable | 20170 | 20171 | Parameters - Busbar A - AC setup - L1 wire break - Configuration - Flags - Busbar A L1 wire break |  | X
Alarm parameter: Enable | 20170 | 20171 | Parameters - Mains - AC setup - L1 wire break - Configuration - Flags - Mains L1 wire break | [5 empty] | X
Alarm parameter: Enable | 20171 | 20172 | Parameters - Generator - AC setup - L2 wire break - Configuration - Flags - Generator L2 wire break | X |  | X |  | X
Alarm parameter: Enable | 20171 | 20172 | Parameters - Busbar A - AC setup - L2 wire break - Configuration - Flags - Busbar A L2 wire break |  | X
Alarm parameter: Enable | 20171 | 20172 | Parameters - Mains - AC setup - L2 wire break - Configuration - Flags - Mains L2 wire break | [5 empty] | X
Alarm parameter: Enable | 20172 | 20173 | Parameters - Generator - AC setup - L3 wire break - Configuration - Flags - Generator L3 wire break | X |  | X |  | X
Alarm parameter: Enable | 20172 | 20173 | Parameters - Busbar A - AC setup - L3 wire break - Configuration - Flags - Busbar A L3 wire break |  | X
Alarm parameter: Enable | 20172 | 20173 | Parameters - Mains - AC setup - L3 wire break - Configuration - Flags - Mains L3 wire break | [5 empty] | X
Alarm parameter: Enable | 20178 | 20179 | Parameters - Mains - AC setup - Supervision alarm - Configuration - Flags - Mains supervision alarm |  |  | X | X |  | X | X
Alarm parameter: Enable | 20179 | 20180 | Parameters - Engine - Emergency stop - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20179 | 20180 | Parameters - Busbar A - Emergency stop - Configuration - Flags |  | X
Alarm parameter: Enable | 20179 | 20180 | Parameters - Mains - Emergency stop - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20180 | 20181 | Clock battery failure | X | X | X | X | X | X | X
Alarm parameter: Enable | 20181 | 20182 | Controller temperature too high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20182 | 20183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Configuration - Flags - PSM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20183 | 20184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Configuration - Flags - PSM3.1 1 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Enable | 20184 | 20185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Configuration - Flags - PSM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20185 | 20186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Configuration - Flags - PSM3.2 1 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Enable | 20186 | 20187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Configuration - Flags - PSM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20187 | 20188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Configuration - Flags - PSM3.2 2 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Enable | 20188 | 20189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Configuration - Flags - PSM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20189 | 20190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Configuration - Flags - PSM3.2 3 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Enable | 20190 | 20191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Configuration - Flags - EIM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20191 | 20192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Configuration - Flags - EIM3.1 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Enable | 20192 | 20193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Configuration - Flags - EIM3.1 2 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20193 | 20194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Configuration - Flags - EIM3.1 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Enable | 20194 | 20195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Configuration - Flags - EIM3.1 3 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20195 | 20196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Configuration - Flags - EIM3.1 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Enable | 20196 | 20197 | EIM3.1 4 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20197 | 20198 | EIM3.1 4 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Enable | 20198 | 20199 | EIM3.1 5 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20199 | 20200 | EIM3.1 5 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Enable | 20200 | 20201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Configuration - Flags - EIM3.1 1 relay 4 wire break | X | X | X | X | X | X | X
Alarm parameter: Enable | 20201 | 20202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Configuration - Flags - EIM3.1 2 relay 4 wire break | X | X | X | X | X | X | X
Alarm parameter: Enable | 20202 | 20203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Configuration - Flags - EIM3.1 3 relay 4 wire break | X | X | X | X | X | X | X
Alarm parameter: Enable | 20203 | 20204 | EIM3.1 4 relay 4 wire break | X | X | X | X | X | X | X
Alarm parameter: Enable | 20204 | 20205 | EIM3.1 5 relay 4 wire break | X | X | X | X | X | X | X
Alarm parameter: Enable | 20205 | 20206 | AC protections not running | X | X | X | X | X | X | X
Alarm parameter: Enable | 20206 | 20207 | AC data is missing | X | X | X | X | X | X | X
Alarm parameter: Enable | 20207 | 20208 | AC protections not running (differential current) | X |  | X | X | X
Alarm parameter: Enable | 20208 | 20209 | AC data is missing (differential current) | X |  | X | X | X
Alarm parameter: Enable | 20209 | 20210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Configuration - Flags - GAM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20210 | 20211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Configuration - Flags - GAM3.2 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Enable | 20211 | 20212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Configuration - Flags - GAM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20212 | 20213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Configuration - Flags - GAM3.2 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Enable | 20213 | 20214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Configuration - Flags - GAM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20214 | 20215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Configuration - Flags - GAM3.2 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Enable | 20215 | 20216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Configuration - Flags - PSM3.2 4 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20216 | 20217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Configuration - Flags - PSM3.2 4 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Enable | 20217 | 20218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Configuration - Flags - PSM3.2 5 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20218 | 20219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Configuration - Flags - PSM3.2 5 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Enable | 20219 | 20220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Configuration - Flags - PSM3.2 6 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20220 | 20221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Configuration - Flags - PSM3.2 6 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Enable | 20221 | 20222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Configuration - Flags - PSM3.2 7 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20222 | 20223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Configuration - Flags - PSM3.2 7 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Enable | 20223 | 20224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Configuration - Flags - PSM3.2 8 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20224 | 20225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Configuration - Flags - PSM3.2 8 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Enable | 20225 | 20226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Configuration - Flags - PSM3.2 9 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20226 | 20227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Configuration - Flags - PSM3.2 9 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Enable | 20228 | 20229 | Parameters - System - Monitoring - Duplicate controller ID - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20229 | 20230 | Parameters - System - Monitoring - Missing all controllers - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20231 | 20232 | Controller ID not configured | X | X | X | X | X | X | X
Alarm parameter: Enable | 20236 | 20237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20237 | 20238 | Blackout detection mismatch | X |  | X | X | X
Alarm parameter: Enable | 20240 | 20241 | Parameters - Communication - NTP - NTP server 1 not connected - Configuration - Flags - NTP server 1 could not connect | X | X | X | X | X | X | X
Alarm parameter: Enable | 20241 | 20242 | Parameters - Communication - NTP - NTP server 1 no response - Configuration - Flags - NTP server 1 is not responding | X | X | X | X | X | X | X
Alarm parameter: Enable | 20242 | 20243 | Parameters - Communication - NTP - NTP server 2 not connected - Configuration - Flags - NTP server 2 could not connect | X | X | X | X | X | X | X
Alarm parameter: Enable | 20243 | 20244 | Parameters - Communication - NTP - NTP server 2 no response - Configuration - Flags - NTP server 2 is not responding | X | X | X | X | X | X | X
Alarm parameter: Enable | 20244 | 20245 | Parameters - Communication - NTP - No NTP server time synchronisation - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20245 | 20246 | Parameters - Communication - NTP - No NTP server(s) connected - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20246 | 20247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20247 | 20248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20296 | 20297 | Controller not part of system | X | X | X | X | X | X | X
Alarm parameter: Enable | 20297 | 20298 | Different single-line configurations | X | X | X | X | X | X | X
Alarm parameter: Enable | 20298 | 20299 | Single-line missing/none active | X | X | X | X | X | X | X
Alarm parameter: Enable | 20299 | 20300 | Parameters - Communication - Modbus - Modbus communication timeout - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20300 | 20301 | Parameters - CODESYS - Monitoring - I/O config conflict - Configuration - Flags - CODESYS configuration conflict | X | X | X | X | X | X | X
Alarm parameter: Enable | 20301 | 20302 | Parameters - CODESYS - Monitoring - Application not OK - Configuration - Flags - CODESYS application not OK | X | X | X | X | X | X | X
Alarm parameter: Enable | 20302 | 20303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20303 | 20304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20304 | 20305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20305 | 20306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20306 | 20307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20307 | 20308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20308 | 20309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20309 | 20310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20310 | 20311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20311 | 20312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20312 | 20313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20313 | 20314 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20314 | 20315 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20315 | 20316 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20316 | 20317 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20317 | 20318 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20318 | 20319 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20319 | 20320 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20320 | 20321 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20321 | 20322 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20322 | 20323 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20323 | 20324 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20324 | 20325 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20325 | 20326 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20326 | 20327 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20327 | 20328 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20328 | 20329 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20329 | 20330 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20330 | 20331 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20331 | 20332 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20332 | 20333 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20333 | 20334 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20334 | 20335 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20335 | 20336 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20336 | 20337 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20337 | 20338 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20338 | 20339 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20339 | 20340 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20340 | 20341 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20341 | 20342 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20342 | 20343 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20343 | 20344 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20344 | 20345 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20345 | 20346 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20346 | 20347 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20347 | 20348 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20348 | 20349 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20349 | 20350 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20350 | 20351 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20351 | 20352 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20352 | 20353 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20353 | 20354 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20354 | 20355 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20355 | 20356 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20356 | 20357 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20357 | 20358 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20358 | 20359 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20359 | 20360 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20360 | 20361 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20361 | 20362 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20362 | 20363 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20363 | 20364 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20364 | 20365 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20365 | 20366 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20366 | 20367 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20367 | 20368 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20368 | 20369 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20369 | 20370 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20370 | 20371 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20371 | 20372 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20372 | 20373 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20373 | 20374 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20374 | 20375 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20375 | 20376 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20376 | 20377 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20377 | 20378 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20378 | 20379 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20379 | 20380 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20380 | 20381 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20381 | 20382 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20382 | 20383 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20383 | 20384 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20384 | 20385 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20385 | 20386 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20386 | 20387 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20387 | 20388 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20388 | 20389 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20389 | 20390 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20390 | 20391 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20391 | 20392 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20392 | 20393 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20393 | 20394 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20394 | 20395 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20395 | 20396 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20396 | 20397 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20397 | 20398 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20398 | 20399 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20399 | 20400 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20400 | 20401 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20401 | 20402 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20402 | 20403 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20403 | 20404 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20404 | 20405 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20405 | 20406 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20406 | 20407 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20407 | 20408 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20408 | 20409 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20409 | 20410 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20410 | 20411 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20411 | 20412 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20412 | 20413 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20413 | 20414 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20414 | 20415 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20415 | 20416 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20416 | 20417 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20417 | 20418 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20418 | 20419 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20419 | 20420 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20420 | 20421 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20421 | 20422 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20422 | 20423 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20423 | 20424 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20424 | 20425 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20425 | 20426 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20426 | 20427 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20427 | 20428 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20428 | 20429 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20429 | 20430 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20430 | 20431 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20431 | 20432 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20432 | 20433 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20433 | 20434 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20434 | 20435 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20435 | 20436 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20436 | 20437 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20437 | 20438 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20438 | 20439 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20439 | 20440 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20440 | 20441 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20441 | 20442 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20442 | 20443 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20443 | 20444 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20444 | 20445 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20445 | 20446 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20446 | 20447 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20447 | 20448 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20448 | 20449 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20449 | 20450 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20450 | 20451 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20451 | 20452 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20452 | 20453 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20453 | 20454 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20454 | 20455 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20455 | 20456 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20456 | 20457 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20457 | 20458 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20458 | 20459 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20459 | 20460 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20460 | 20461 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20461 | 20462 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20462 | 20463 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20463 | 20464 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20464 | 20465 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20465 | 20466 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20466 | 20467 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20467 | 20468 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20468 | 20469 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20469 | 20470 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20470 | 20471 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20471 | 20472 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20472 | 20473 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20473 | 20474 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20474 | 20475 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20475 | 20476 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20476 | 20477 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20477 | 20478 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20478 | 20479 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20479 | 20480 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20480 | 20481 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20481 | 20482 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20482 | 20483 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20483 | 20484 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20484 | 20485 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20485 | 20486 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20486 | 20487 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20487 | 20488 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20488 | 20489 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20489 | 20490 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20490 | 20491 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20491 | 20492 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20492 | 20493 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20493 | 20494 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20494 | 20495 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20495 | 20496 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20496 | 20497 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20497 | 20498 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20498 | 20499 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20499 | 20500 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20500 | 20501 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20501 | 20502 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20502 | 20503 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20503 | 20504 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20504 | 20505 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20505 | 20506 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20506 | 20507 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20507 | 20508 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20508 | 20509 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20509 | 20510 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20510 | 20511 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20511 | 20512 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20512 | 20513 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20513 | 20514 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20514 | 20515 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20515 | 20516 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20516 | 20517 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20517 | 20518 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20518 | 20519 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20519 | 20520 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20520 | 20521 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20521 | 20522 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20522 | 20523 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20523 | 20524 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20524 | 20525 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20525 | 20526 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20526 | 20527 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20527 | 20528 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20528 | 20529 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20529 | 20530 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20530 | 20531 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20531 | 20532 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20532 | 20533 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20533 | 20534 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20534 | 20535 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20535 | 20536 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20536 | 20537 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20537 | 20538 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20538 | 20539 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20539 | 20540 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20540 | 20541 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20541 | 20542 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20542 | 20543 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20543 | 20544 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20544 | 20545 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20545 | 20546 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20546 | 20547 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20547 | 20548 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20548 | 20549 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20549 | 20550 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20550 | 20551 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20551 | 20552 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20552 | 20553 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20553 | 20554 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20554 | 20555 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20555 | 20556 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20556 | 20557 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20557 | 20558 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20558 | 20559 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20559 | 20560 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20560 | 20561 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20561 | 20562 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20562 | 20563 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Enable | 20565 | 20566 | Parameters - Local - CustomLogic - Configuration invalid - Configuration - Flags - CustomLogic configuration invalid | X | X | X | X | X | X | X
Alarm parameter: Enable | 20566 | 20567 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Configuration - Flags - Digital AVR communication error | X |  | X | X | X
Alarm parameter: Enable | 20567 | 20568 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20568 | 20569 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20569 | 20570 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20570 | 20571 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20571 | 20572 | Parameters - Generator - Digital AVR - Alarms - Open diode - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20572 | 20573 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20573 | 20574 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20574 | 20575 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20575 | 20576 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20576 | 20577 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20577 | 20578 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20578 | 20579 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20579 | 20580 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20580 | 20581 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20581 | 20582 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20582 | 20583 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20583 | 20584 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20584 | 20585 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20585 | 20586 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20586 | 20587 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20587 | 20588 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20588 | 20589 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20589 | 20590 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20590 | 20591 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20591 | 20592 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20592 | 20593 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20593 | 20594 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20594 | 20595 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20595 | 20596 | Parameters - Generator - Digital AVR - Alarms - Motor start - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20596 | 20597 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20597 | 20598 | Parameters - Generator - Digital AVR - Alarms - Power supply - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20598 | 20599 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20599 | 20600 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20600 | 20601 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20601 | 20602 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20602 | 20603 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20603 | 20604 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20604 | 20605 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20605 | 20606 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20606 | 20607 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20607 | 20608 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20608 | 20609 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20609 | 20610 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20610 | 20611 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20611 | 20612 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20612 | 20613 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20613 | 20614 | DAVR unsupported AC configuration | X |  | X | X | X
Alarm parameter: Enable | 20614 | 20615 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Configuration - Flags - Illegal DAVR configuration | X |  | X | X | X
Alarm parameter: Enable | 20615 | 20616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Configuration - Flags - Generator under-voltage 1 | X |  | X | X | X
Alarm parameter: Enable | 20615 | 20616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Configuration - Flags - Busbar A under-voltage 1 |  | X
Alarm parameter: Enable | 20615 | 20616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Flags - Mains under-voltage 1 | [5 empty] | X | X
Alarm parameter: Enable | 20616 | 20617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Configuration - Flags - Generator under-voltage 2 | X |  | X | X | X
Alarm parameter: Enable | 20616 | 20617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Configuration - Flags - Busbar A under-voltage 2 |  | X
Alarm parameter: Enable | 20616 | 20617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Flags - Mains under-voltage 2 | [5 empty] | X | X
Alarm parameter: Enable | 20617 | 20618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Configuration - Flags - Generator under-voltage 3 | X |  | X | X | X
Alarm parameter: Enable | 20617 | 20618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Configuration - Flags - Busbar A under-voltage 3 |  | X
Alarm parameter: Enable | 20617 | 20618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Flags - Mains under-voltage 3 | [5 empty] | X | X
Alarm parameter: Enable | 20618 | 20619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Configuration - Flags - Generator over-voltage 1 | X |  | X | X | X
Alarm parameter: Enable | 20618 | 20619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Configuration - Flags - Busbar A over-voltage 1 |  | X
Alarm parameter: Enable | 20618 | 20619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Flags - Mains over-voltage 1 | [5 empty] | X | X
Alarm parameter: Enable | 20619 | 20620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Configuration - Flags - Generator over-voltage 2 | X |  | X | X | X
Alarm parameter: Enable | 20619 | 20620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Configuration - Flags - Busbar A over-voltage 2 |  | X
Alarm parameter: Enable | 20619 | 20620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Flags - Mains over-voltage 2 | [5 empty] | X | X
Alarm parameter: Enable | 20620 | 20621 | Parameters - Generator - Voltage protections - Voltage unbalance - Configuration - Flags - Generator voltage unbalance | X |  | X | X | X
Alarm parameter: Enable | 20620 | 20621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Configuration - Flags - Busbar A voltage unbalance |  | X
Alarm parameter: Enable | 20620 | 20621 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Flags - Mains voltage unbalance | [5 empty] | X | X
Alarm parameter: Enable | 20621 | 20622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Configuration - Flags - Generator negative sequence voltage | X |  | X | X | X
Alarm parameter: Enable | 20621 | 20622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Configuration - Flags - Busbar A negative sequence voltage |  | X
Alarm parameter: Enable | 20621 | 20622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Flags - Mains negative sequence voltage | [5 empty] | X | X
Alarm parameter: Enable | 20622 | 20623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Configuration - Flags - Generator zero sequence voltage | X |  | X | X | X
Alarm parameter: Enable | 20622 | 20623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Configuration - Flags - Busbar A zero sequence voltage |  | X
Alarm parameter: Enable | 20622 | 20623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Flags - Mains zero sequence voltage | [5 empty] | X | X
Alarm parameter: Enable | 20623 | 20624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Generator positive sequence under-voltage | X |  | X | X | X
Alarm parameter: Enable | 20623 | 20624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Busbar A positive sequence under-voltage |  | X
Alarm parameter: Enable | 20623 | 20624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Mains positive sequence under-voltage | [5 empty] | X | X
Alarm parameter: Enable | 20624 | 20625 | Parameters - Generator - Current protections - Over-current 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20624 | 20625 | Parameters - Busbar A - Current protections - Over-current 1 - Configuration - Flags |  | X
Alarm parameter: Enable | 20624 | 20625 | Parameters - Mains - Current protections - Over-current 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20625 | 20626 | Parameters - Generator - Current protections - Over-current 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20625 | 20626 | Parameters - Busbar A - Current protections - Over-current 2 - Configuration - Flags |  | X
Alarm parameter: Enable | 20625 | 20626 | Parameters - Mains - Current protections - Over-current 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20626 | 20627 | Parameters - Generator - Current protections - Over-current 3 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20626 | 20627 | Parameters - Busbar A - Current protections - Over-current 3 - Configuration - Flags |  | X
Alarm parameter: Enable | 20626 | 20627 | Parameters - Mains - Current protections - Over-current 3 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20627 | 20628 | Parameters - Generator - Current protections - Over-current 4 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20627 | 20628 | Parameters - Busbar A - Current protections - Over-current 4 - Configuration - Flags |  | X
Alarm parameter: Enable | 20627 | 20628 | Parameters - Mains - Current protections - Over-current 4 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20628 | 20629 | Parameters - Generator - Current protections - Fast over-current 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20628 | 20629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Configuration - Flags |  | X
Alarm parameter: Enable | 20628 | 20629 | Parameters - Mains - Current protections - Fast over-current 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20629 | 20630 | Parameters - Generator - Current protections - Fast over-current 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20629 | 20630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Configuration - Flags |  | X
Alarm parameter: Enable | 20629 | 20630 | Parameters - Mains - Current protections - Fast over-current 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20630 | 20631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20630 | 20631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Configuration - Flags |  | X
Alarm parameter: Enable | 20630 | 20631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20631 | 20632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20631 | 20632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Configuration - Flags |  | X
Alarm parameter: Enable | 20631 | 20632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20632 | 20633 | Parameters - Generator - Current protections - Directional over-current 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20632 | 20633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Configuration - Flags |  | X
Alarm parameter: Enable | 20632 | 20633 | Parameters - Mains - Current protections - Directional over-current 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20633 | 20634 | Parameters - Generator - Current protections - Directional over-current 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20633 | 20634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Configuration - Flags |  | X
Alarm parameter: Enable | 20633 | 20634 | Parameters - Mains - Current protections - Directional over-current 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20634 | 20635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Configuration - Flags |  | X
Alarm parameter: Enable | 20635 | 20636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Configuration - Flags |  | X
Alarm parameter: Enable | 20636 | 20637 | Parameters - Generator - Current protections - Negative sequence current - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20636 | 20637 | Parameters - Busbar A - Current protections - Negative sequence current - Configuration - Flags |  | X
Alarm parameter: Enable | 20636 | 20637 | Parameters - Mains - Current protections - Negative sequence current - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20637 | 20638 | Parameters - Generator - Current protections - Zero sequence current - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20637 | 20638 | Parameters - Busbar A - Current protections - Zero sequence current - Configuration - Flags |  | X
Alarm parameter: Enable | 20637 | 20638 | Parameters - Mains - Current protections - Zero sequence current - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20638 | 20639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Configuration - Flags - Generator over-frequency 1 | X |  | X | X | X
Alarm parameter: Enable | 20638 | 20639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Configuration - Flags - Busbar A over-frequency 1 |  | X
Alarm parameter: Enable | 20638 | 20639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Flags - Mains over-frequency 1 | [5 empty] | X | X
Alarm parameter: Enable | 20639 | 20640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Configuration - Flags - Generator over-frequency 2 | X |  | X | X | X
Alarm parameter: Enable | 20639 | 20640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Configuration - Flags - Busbar A over-frequency 2 |  | X
Alarm parameter: Enable | 20639 | 20640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Flags - Mains over-frequency 2 | [5 empty] | X | X
Alarm parameter: Enable | 20640 | 20641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Configuration - Flags - Generator over-frequency 3 | X |  | X | X | X
Alarm parameter: Enable | 20640 | 20641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Configuration - Flags - Busbar A over-frequency 3 |  | X
Alarm parameter: Enable | 20640 | 20641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Flags - Mains over-frequency 3 | [5 empty] | X | X
Alarm parameter: Enable | 20641 | 20642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Configuration - Flags - Generator under-frequency 1 | X |  | X | X | X
Alarm parameter: Enable | 20641 | 20642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Configuration - Flags - Busbar A under-frequency 1 |  | X
Alarm parameter: Enable | 20641 | 20642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Flags - Mains under-frequency 1 | [5 empty] | X | X
Alarm parameter: Enable | 20642 | 20643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Configuration - Flags - Generator under-frequency 2 | X |  | X | X | X
Alarm parameter: Enable | 20642 | 20643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Configuration - Flags - Busbar A under-frequency 2 |  | X
Alarm parameter: Enable | 20642 | 20643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Flags - Mains under-frequency 2 | [5 empty] | X | X
Alarm parameter: Enable | 20643 | 20644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Configuration - Flags - Generator under-frequency 3 | X |  | X | X | X
Alarm parameter: Enable | 20643 | 20644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Configuration - Flags - Busbar A under-frequency 3 |  | X
Alarm parameter: Enable | 20643 | 20644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Flags - Mains under-frequency 3 | [5 empty] | X | X
Alarm parameter: Enable | 20644 | 20645 | Parameters - Generator - Power protections - Overload 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20644 | 20645 | Parameters - Busbar A - Power protections - Power export 1 - Configuration - Flags |  | X
Alarm parameter: Enable | 20644 | 20645 | Parameters - Mains - Power protections - Overload 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20645 | 20646 | Parameters - Generator - Power protections - Overload 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20645 | 20646 | Parameters - Busbar A - Power protections - Power export 2 - Configuration - Flags |  | X
Alarm parameter: Enable | 20645 | 20646 | Parameters - Mains - Power protections - Overload 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20646 | 20647 | Parameters - Generator - Power protections - Overload 3 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20646 | 20647 | Parameters - Busbar A - Power protections - Power export 3 - Configuration - Flags |  | X
Alarm parameter: Enable | 20646 | 20647 | Parameters - Mains - Power protections - Overload 3 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20647 | 20648 | Parameters - Generator - Power protections - Overload 4 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20647 | 20648 | Parameters - Busbar A - Power protections - Power export 4 - Configuration - Flags |  | X
Alarm parameter: Enable | 20647 | 20648 | Parameters - Mains - Power protections - Overload 4 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20648 | 20649 | Parameters - Generator - Power protections - Overload 5 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20648 | 20649 | Parameters - Busbar A - Power protections - Power export 5 - Configuration - Flags |  | X
Alarm parameter: Enable | 20648 | 20649 | Parameters - Mains - Power protections - Overload 5 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20649 | 20650 | Parameters - Generator - Power protections - Reverse power 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20649 | 20650 | Parameters - Busbar A - Power protections - Power import 1 - Configuration - Flags |  | X
Alarm parameter: Enable | 20649 | 20650 | Parameters - Mains - Power protections - Reverse power 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20650 | 20651 | Parameters - Generator - Power protections - Reverse power 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20650 | 20651 | Parameters - Busbar A - Power protections - Power import 2 - Configuration - Flags |  | X
Alarm parameter: Enable | 20650 | 20651 | Parameters - Mains - Power protections - Reverse power 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20651 | 20652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20651 | 20652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Configuration - Flags |  | X
Alarm parameter: Enable | 20651 | 20652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20652 | 20653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20652 | 20653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Configuration - Flags |  | X
Alarm parameter: Enable | 20652 | 20653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20653 | 20654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20653 | 20654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Configuration - Flags |  | X
Alarm parameter: Enable | 20653 | 20654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20654 | 20655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20654 | 20655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Configuration - Flags |  | X
Alarm parameter: Enable | 20654 | 20655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Enable | 20655 | 20656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Flags - Mains over-voltage 1 |  |  | X | X
Alarm parameter: Enable | 20655 | 20656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Configuration - Flags - Busbar over-voltage 1 | X |  |  |  | X | X | X
Alarm parameter: Enable | 20655 | 20656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Configuration - Flags - Busbar B over-voltage 1 |  | X
Alarm parameter: Enable | 20656 | 20657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Flags - Mains over-voltage 2 |  |  | X | X
Alarm parameter: Enable | 20656 | 20657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Configuration - Flags - Busbar over-voltage 2 | X |  |  |  | X | X | X
Alarm parameter: Enable | 20656 | 20657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Configuration - Flags - Busbar B over-voltage 2 |  | X
Alarm parameter: Enable | 20657 | 20658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Configuration - Flags - Mains over-voltage 3 |  |  | X | X
Alarm parameter: Enable | 20657 | 20658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Configuration - Flags - Busbar over-voltage 3 | X |  |  |  | X | X | X
Alarm parameter: Enable | 20657 | 20658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Configuration - Flags - Busbar B over-voltage 3 |  | X
Alarm parameter: Enable | 20658 | 20659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Flags - Mains under-voltage 1 |  |  | X | X
Alarm parameter: Enable | 20658 | 20659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Configuration - Flags - Busbar under-voltage 1 | X |  |  |  | X | X | X
Alarm parameter: Enable | 20658 | 20659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Configuration - Flags - Busbar B under-voltage 1 |  | X
Alarm parameter: Enable | 20659 | 20660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Flags - Mains under-voltage 2 |  |  | X | X
Alarm parameter: Enable | 20659 | 20660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Configuration - Flags - Busbar under-voltage 2 | X |  |  |  | X | X | X
Alarm parameter: Enable | 20659 | 20660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Configuration - Flags - Busbar B under-voltage 2 |  | X
Alarm parameter: Enable | 20660 | 20661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Flags - Mains under-voltage 3 |  |  | X | X
Alarm parameter: Enable | 20660 | 20661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Configuration - Flags - Busbar under-voltage 3 | X |  |  |  | X | X | X
Alarm parameter: Enable | 20660 | 20661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Configuration - Flags - Busbar B under-voltage 3 |  | X
Alarm parameter: Enable | 20661 | 20662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Configuration - Flags - Mains under-voltage 4 |  |  | X | X
Alarm parameter: Enable | 20661 | 20662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Configuration - Flags - Busbar under-voltage 4 | X |  |  |  | X | X | X
Alarm parameter: Enable | 20661 | 20662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Configuration - Flags - Busbar B under-voltage 4 |  | X
Alarm parameter: Enable | 20662 | 20663 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Flags - Mains voltage unbalance |  |  | X | X
Alarm parameter: Enable | 20662 | 20663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Configuration - Flags - Busbar voltage unbalance | X |  |  |  | X | X | X
Alarm parameter: Enable | 20662 | 20663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Configuration - Flags - Busbar B voltage unbalance |  | X
Alarm parameter: Enable | 20663 | 20664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Flags - Mains over-frequency 1 |  |  | X | X
Alarm parameter: Enable | 20663 | 20664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Configuration - Flags - Busbar over-frequency 1 | X |  |  |  | X | X | X
Alarm parameter: Enable | 20663 | 20664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Configuration - Flags - Busbar B over-frequency 1 |  | X
Alarm parameter: Enable | 20664 | 20665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Flags - Mains over-frequency 2 |  |  | X | X
Alarm parameter: Enable | 20664 | 20665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Configuration - Flags - Busbar over-frequency 2 | X |  |  |  | X | X | X
Alarm parameter: Enable | 20664 | 20665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Configuration - Flags - Busbar B over-frequency 2 |  | X
Alarm parameter: Enable | 20665 | 20666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Flags - Mains over-frequency 3 |  |  | X | X
Alarm parameter: Enable | 20665 | 20666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Configuration - Flags - Busbar over-frequency 3 | X |  |  |  | X | X | X
Alarm parameter: Enable | 20665 | 20666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Configuration - Flags - Busbar B over-frequency 3 |  | X
Alarm parameter: Enable | 20666 | 20667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Flags - Mains under-frequency 1 |  |  | X | X
Alarm parameter: Enable | 20666 | 20667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Configuration - Flags - Busbar under-frequency 1 | X |  |  |  | X | X | X
Alarm parameter: Enable | 20666 | 20667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Configuration - Flags - Busbar B under-frequency 1 |  | X
Alarm parameter: Enable | 20667 | 20668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Flags - Mains under-frequency 2 |  |  | X | X
Alarm parameter: Enable | 20667 | 20668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Configuration - Flags - Busbar under-frequency 2 | X |  |  |  | X | X | X
Alarm parameter: Enable | 20667 | 20668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Configuration - Flags - Busbar B under-frequency 2 |  | X
Alarm parameter: Enable | 20668 | 20669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Flags - Mains under-frequency 3 |  |  | X | X
Alarm parameter: Enable | 20668 | 20669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Configuration - Flags - Busbar under-frequency 3 | X |  |  |  | X | X | X
Alarm parameter: Enable | 20668 | 20669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Configuration - Flags - Busbar B under-frequency 3 |  | X
Alarm parameter: Enable | 20669 | 20670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Configuration - Flags - Mains under-frequency 4 |  |  | X | X
Alarm parameter: Enable | 20669 | 20670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Configuration - Flags - Busbar under-frequency 4 | X |  |  |  | X | X | X
Alarm parameter: Enable | 20669 | 20670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Configuration - Flags - Busbar B under-frequency 4 |  | X
Alarm parameter: Enable | 20670 | 20671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Flags - Busbar negative sequence voltage |  |  | X | X
Alarm parameter: Enable | 20670 | 20671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Configuration - Flags - Busbar negative sequence voltage | X |  |  |  | X | X | X
Alarm parameter: Enable | 20670 | 20671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Configuration - Flags - Busbar B negative sequence voltage |  | X
Alarm parameter: Enable | 20671 | 20672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Flags - Busbar zero sequence voltage |  |  | X | X
Alarm parameter: Enable | 20671 | 20672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Configuration - Flags - Busbar zero sequence voltage | X |  |  |  | X | X | X
Alarm parameter: Enable | 20671 | 20672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Configuration - Flags - Busbar B zero sequence voltage |  | X
Alarm parameter: Enable | 20672 | 20673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Busbar positive sequence under-voltage |  |  | X | X
Alarm parameter: Enable | 20672 | 20673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Busbar positive sequence under-voltage | X |  |  |  | X | X | X
Alarm parameter: Enable | 20672 | 20673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Busbar B positive sequence under-voltage |  | X
Alarm parameter: Enable | 20717 | 20718 | Parameters - Engine - Maintenance - Service timer - Configuration - Flags - Service timer 1 | X |  | X | X | X
Alarm parameter: Enable | 20718 | 20719 | Parameters - Engine - Maintenance - Service timer - Configuration - Flags - Service timer 2 | X |  | X | X | X
Alarm parameter: Enable | 20719 | 20720 | Parameters - Engine - Maintenance - Service timer - Configuration - Flags - Service timer 3 | X |  | X | X | X
Alarm parameter: Enable | 20720 | 20721 | Parameters - Engine - Maintenance - Service timer - Configuration - Flags - Service timer 4 | X |  | X | X | X
Alarm parameter: Enable | 20721 | 20722 | External MB open failure | X | X | X | X | X | X | X
Alarm parameter: Enable | 20722 | 20723 | Parameters - Power management rules - Ground relay - Ground relay general failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20723 | 20724 | Parameters - Power management rules - Ground relay - Ground relay open failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20724 | 20725 | Parameters - Power management rules - Ground relay - Ground relay close failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20725 | 20726 | Parameters - Power management rules - Ground relay - Ground relay position failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20726 | 20727 | Parameters - Breakers - Close before excitation - CBE rerun failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Enable | 20727 | 20728 | Parameters - Breakers - Close before excitation - CBE failure - Configuration - Flags - Close before excitation failure | X |  | X | X | X
Alarm parameter: Enable | 20728 | 20729 | Load too high | X | X | X | X | X | X | X
Alarm parameter: Enable | 20729 | 20730 | ID to run configuration failure | [5 empty] | X | X
Alarm parameter: Enable | 20731 | 20732 | Parameters - System - Monitoring - Missing any genset controller - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20732 | 20733 | Parameters - System - Monitoring - Missing any mains controller - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20733 | 20734 | Parameters - System - Monitoring - Missing any bustie controller - Configuration - Flags - Missing any bus tie controller | X | X | X | X | X | X | X
Alarm parameter: Enable | 20734 | 20735 | Can ID not available | X | X | X | X | X | X | X
Alarm parameter: Enable | 20735 | 20736 | Duplicated CAN IDs | X | X | X | X | X | X | X
Alarm parameter: Enable | 20736 | 20737 | Parameters - Local power management - Alarms - Busbar blocked - Configuration - Flags - Busbar blocked due to position failure | X |  | X | X | X | X | X
Alarm parameter: Enable | 20737 | 20738 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Configuration - Flags - Busbar A blocked due to position failure |  | X
Alarm parameter: Enable | 20738 | 20739 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Configuration - Flags - Busbar B blocked due to position failure |  | X
Alarm parameter: Enable | 20739 | 20740 | Parameters - System - Monitoring - BTB 33 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20740 | 20741 | Parameters - System - Monitoring - BTB 34 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20741 | 20742 | Parameters - System - Monitoring - BTB 35 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20742 | 20743 | Parameters - System - Monitoring - BTB 36 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20743 | 20744 | Parameters - System - Monitoring - BTB 37 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20744 | 20745 | Parameters - System - Monitoring - BTB 38 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20745 | 20746 | Parameters - System - Monitoring - BTB 39 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20746 | 20747 | Parameters - System - Monitoring - BTB 40 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20747 | 20748 | Primary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20748 | 20749 | Primary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20749 | 20750 | Primary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20750 | 20751 | Primary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20751 | 20752 | Primary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20752 | 20753 | Primary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20753 | 20754 | Primary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20754 | 20755 | Primary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20755 | 20756 | Primary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20756 | 20757 | Primary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20757 | 20758 | Primary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20758 | 20759 | Primary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20759 | 20760 | Primary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20760 | 20761 | Primary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20761 | 20762 | Primary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20762 | 20763 | Primary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20763 | 20764 | Primary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20764 | 20765 | Primary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20765 | 20766 | Primary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20766 | 20767 | Primary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20767 | 20768 | Primary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20768 | 20769 | Primary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20769 | 20770 | Primary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20770 | 20771 | Primary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20771 | 20772 | Primary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20772 | 20773 | Primary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20773 | 20774 | Primary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20774 | 20775 | Primary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20775 | 20776 | Primary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20776 | 20777 | Primary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20777 | 20778 | Primary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20778 | 20779 | Primary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20779 | 20780 | Primary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20780 | 20781 | Primary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20781 | 20782 | Primary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20782 | 20783 | Primary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20783 | 20784 | Primary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20784 | 20785 | Primary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20785 | 20786 | Primary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20786 | 20787 | Primary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20787 | 20788 | Secondary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20788 | 20789 | Secondary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20789 | 20790 | Secondary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20790 | 20791 | Secondary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20791 | 20792 | Secondary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20792 | 20793 | Secondary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20793 | 20794 | Secondary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20794 | 20795 | Secondary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20795 | 20796 | Secondary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20796 | 20797 | Secondary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20797 | 20798 | Secondary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20798 | 20799 | Secondary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20799 | 20800 | Secondary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20800 | 20801 | Secondary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20801 | 20802 | Secondary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20802 | 20803 | Secondary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20803 | 20804 | Secondary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20804 | 20805 | Secondary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20805 | 20806 | Secondary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20806 | 20807 | Secondary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20807 | 20808 | Secondary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20808 | 20809 | Secondary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20809 | 20810 | Secondary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20810 | 20811 | Secondary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20811 | 20812 | Secondary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20812 | 20813 | Secondary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20813 | 20814 | Secondary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20814 | 20815 | Secondary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20815 | 20816 | Secondary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20816 | 20817 | Secondary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20817 | 20818 | Secondary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20818 | 20819 | Secondary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20819 | 20820 | Secondary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20820 | 20821 | Secondary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20821 | 20822 | Secondary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20822 | 20823 | Secondary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20823 | 20824 | Secondary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20824 | 20825 | Secondary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20825 | 20826 | Secondary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20826 | 20827 | Secondary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm parameter: Enable | 20827 | 20828 | Priority error | X | X | X | X | X | X | X
Alarm parameter: Enable | 20828 | 20829 | Parameters - Non-essential load trip - Trip 1 - Over-current - Configuration - Flags - NEL 1 over-current | X |  | X | X | X | X | X
Alarm parameter: Enable | 20829 | 20830 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Configuration - Flags - NEL 1 under-frequency | X |  | X | X | X | X | X
Alarm parameter: Enable | 20830 | 20831 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Configuration - Flags - NEL 1 overload 1 | X |  | X | X | X | X | X
Alarm parameter: Enable | 20831 | 20832 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Configuration - Flags - NEL 1 overload 2 | X |  | X | X | X | X | X
Alarm parameter: Enable | 20832 | 20833 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Configuration - Flags - NEL 1 reactive overload | X |  | X | X | X | X | X
Alarm parameter: Enable | 20833 | 20834 | Parameters - Non-essential load trip - Trip 2 - Over-current - Configuration - Flags - NEL 2 over-current | X |  | X | X | X | X | X
Alarm parameter: Enable | 20834 | 20835 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Configuration - Flags - NEL 2 under-frequency | X |  | X | X | X | X | X
Alarm parameter: Enable | 20835 | 20836 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Configuration - Flags - NEL 2 overload 1 | X |  | X | X | X | X | X
Alarm parameter: Enable | 20836 | 20837 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Configuration - Flags - NEL 2 overload 2 | X |  | X | X | X | X | X
Alarm parameter: Enable | 20837 | 20838 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Configuration - Flags - NEL 2 reactive overload | X |  | X | X | X | X | X
Alarm parameter: Enable | 20838 | 20839 | Parameters - Non-essential load trip - Trip 3 - Over-current - Configuration - Flags - NEL 3 over-current | X |  | X | X | X | X | X
Alarm parameter: Enable | 20839 | 20840 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Configuration - Flags - NEL 3 under-frequency | X |  | X | X | X | X | X
Alarm parameter: Enable | 20840 | 20841 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Configuration - Flags - NEL 3 overload 1 | X |  | X | X | X | X | X
Alarm parameter: Enable | 20841 | 20842 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Configuration - Flags - NEL 3 overload 2 | X |  | X | X | X | X | X
Alarm parameter: Enable | 20842 | 20843 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Configuration - Flags - NEL 3 reactive overload | X |  | X | X | X | X | X
Alarm parameter: Enable | 20843 | 20844 | Parameters - System - Monitoring - Single-line hazard - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20844 | 20845 | ID not present | X | X | X | X | X | X | X
Alarm parameter: Enable | 20845 | 20846 | Unsupported application | X | X | X | X | X | X | X
Alarm parameter: Enable | 20846 | 20847 | Application internal CAN protocol conflict | X | X | X | X | X | X | X
Alarm parameter: Enable | 20847 | 20848 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Configuration - Flags - Section P> | X | X | X | X | X | X | X
Alarm parameter: Enable | 20848 | 20849 | Dry mode: Voltage level unexpected | X |  | X | X | X
Alarm parameter: Enable | 20849 | 20850 | Invalid DAVR configuration | X |  | X | X | X
Alarm parameter: Enable | 20850 | 20851 | Parameters - Communication - DEIF network - DEIF network fork detected - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20852 | 20853 | Parameters - Communication - DEIF network - DEIF network has only one connection - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20854 | 20855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Configuration - Flags - Breaker vector mismatch | X |  | X | X | X
Alarm parameter: Enable | 20854 | 20855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Configuration - Flags - Breaker vector mismatch |  | X
Alarm parameter: Enable | 20854 | 20855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Flags - Breaker vector mismatch | [5 empty] | X | X
Alarm parameter: Enable | 20855 | 20856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Flags - Breaker vector mismatch |  |  |  | X
Alarm parameter: Enable | 20855 | 20856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Configuration - Flags - Breaker vector mismatch | [6 empty] | X
Alarm parameter: Enable | 20857 | 20858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20858 | 20859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20859 | 20860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20860 | 20861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20861 | 20862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Configuration - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Enable | 20862 | 20863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Configuration - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Enable | 20863 | 20864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Configuration - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Enable | 20864 | 20865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Configuration - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Enable | 20865 | 20866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Configuration - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Enable | 20866 | 20867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Configuration - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Enable | 20867 | 20868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Configuration - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Enable | 20868 | 20869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Configuration - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Enable | 20869 | 20870 | AC protections not running | X | X | X | X | X | X | X
Alarm parameter: Enable | 20870 | 20871 | AC data is missing | X | X | X | X | X | X | X
Alarm parameter: Enable | 20871 | 20872 | AC protections not running | X | X | X | X | X | X | X
Alarm parameter: Enable | 20872 | 20873 | AC data is missing | X | X | X | X | X | X | X
Alarm parameter: Enable | 20873 | 20874 | AC protections not running | X | X | X | X | X | X | X
Alarm parameter: Enable | 20874 | 20875 | AC data is missing | X | X | X | X | X | X | X
Alarm parameter: Enable | 20875 | 20876 | AC protections not running | X | X | X | X | X | X | X
Alarm parameter: Enable | 20876 | 20877 | AC data is missing | X | X | X | X | X | X | X
Alarm parameter: Enable | 20877 | 20878 | Live voltage detected | X | X | X | X | X | X | X
Alarm parameter: Enable | 20878 | 20879 | Internal issue detected. A restart is required soon! | X | X | X | X | X | X | X
Alarm parameter: Enable | 20879 | 20880 | Parameters - System - Monitoring - Missing controllers - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Enable | 20880 | 20881 | Card issue detected | X | X | X | X | X | X | X
Alarm parameter: Enable | 20881 | 20882 | Card configuration failed | X | X | X | X | X | X | X
Alarm parameter: Enable | 20882 | 20883 | Unknown traffic on DEIF network | X | X | X | X | X | X | X
Alarm parameter: Enable | 20883 | 20884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Configuration - Flags - Fill failure | X |  | X | X | X
Alarm parameter: Enable | 20884 | 20885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Configuration - Flags - Fill failure | X |  | X | X | X
Alarm parameter: Enable | 20885 | 20886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Configuration - Flags - Fill failure | X |  | X | X | X
Alarm parameter: Enable | 20886 | 20887 | Local IO service error | X | X | X | X | X | X | X
Alarm parameter: Enable | 20887 | 20888 | App logging failure | X | X | X | X | X | X | X
Alarm parameter: Enable | 20888 | 20889 | Event logging failure | X | X | X | X | X | X | X
Alarm parameter: Enable | 20889 | 20890 | Licence error | X | X | X | X | X | X | X
Alarm parameter: Enable | 20890 | 20891 | Brightness is dimmed according to temperature | X | X | X | X | X | X | X
Alarm parameter: Enable | 20891 | 20892 | Parameters - Grid code - Mains sync inhibit - Configuration - Flags |  |  | X | X
Alarm parameter: Enable | 20892 | 20893 | Parameters - Grid code - Capability curve - Import protection - Configuration - Flags - Power import capability curve protection |  |  | X | X
Alarm parameter: Enable | 20893 | 20894 | Parameters - Grid code - Capability curve - Export protection - Configuration - Flags - Power export capability curve protection |  |  | X | X
Alarm parameter: Enable | 20894 | 20895 | Hardware is not compatible based on module versions | X | X | X | X | X | X | X
Alarm parameter: Latch | 22000 | 22001 | Application initialisation error | X | X | X | X | X | X | X
Alarm parameter: Latch | 22001 | 22002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm parameter: Latch | 22002 | 22003 | Preliminary software | X | X | X | X | X | X | X
Alarm parameter: Latch | 22003 | 22004 | Parameters - Engine - Stop sequence - Stop failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22004 | 22005 | Parameters - Engine - Start sequence - Start failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22005 | 22006 | Parameters - Engine - Start sequence - Crank failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22006 | 22007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22007 | 22008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22008 | 22009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22009 | 22010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22010 | 22011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Configuration - Flags - Magnetic pickup wire break alarm | X |  | X | X | X
Alarm parameter: Latch | 22011 | 22012 | Parameters - Engine - Stop sequence - Externally stopped - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22013 | 22014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22014 | 22015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22015 | 22016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22016 | 22017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22017 | 22018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22018 | 22019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22019 | 22020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22020 | 22021 | Parameters - Engine - Protections - Level - Coolant level 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22021 | 22022 | Parameters - Engine - Protections - Level - Coolant level 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22022 | 22023 | Parameters - Engine - Protections - Level - Coolant level 3 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22027 | 22028 | Parameters - Engine - Running detection - Primary running feedback failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22041 | 22042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Configuration - Flags - GB closing failure | X |  | X | X | X
Alarm parameter: Latch | 22041 | 22042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Configuration - Flags - BTB closing failure |  | X
Alarm parameter: Latch | 22041 | 22042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration - Flags - MB closing failure | [5 empty] | X | X
Alarm parameter: Latch | 22042 | 22043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Configuration - Flags - GB opening failure | X |  | X | X | X
Alarm parameter: Latch | 22042 | 22043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Configuration - Flags - BTB opening failure |  | X
Alarm parameter: Latch | 22042 | 22043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration - Flags - MB opening failure | [5 empty] | X | X
Alarm parameter: Latch | 22043 | 22044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Configuration - Flags - GB position failure | X |  | X | X | X
Alarm parameter: Latch | 22043 | 22044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Configuration - Flags - BTB position failure |  | X
Alarm parameter: Latch | 22043 | 22044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration - Flags - MB position failure | [5 empty] | X | X
Alarm parameter: Latch | 22044 | 22045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Configuration - Flags - GB configuration failure | X |  | X | X | X
Alarm parameter: Latch | 22044 | 22045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Configuration - Flags - BTB configuration failure |  | X
Alarm parameter: Latch | 22044 | 22045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration - Flags - MB configuration failure | [5 empty] | X | X
Alarm parameter: Latch | 22045 | 22046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Configuration - Flags - GB synchronisation failure | X |  | X | X | X
Alarm parameter: Latch | 22045 | 22046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Configuration - Flags - BTB synchronisation failure |  | X
Alarm parameter: Latch | 22045 | 22046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration - Flags - MB synchronisation failure | [5 empty] | X | X
Alarm parameter: Latch | 22046 | 22047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Configuration - Flags - GB de-load failure | X |  | X | X | X
Alarm parameter: Latch | 22046 | 22047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Configuration - Flags - BTB de-load failure |  | X
Alarm parameter: Latch | 22046 | 22047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration - Flags - MB de-load failure | [5 empty] | X | X
Alarm parameter: Latch | 22047 | 22048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Configuration - Flags - GB tripped (external) | X |  | X | X | X
Alarm parameter: Latch | 22047 | 22048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Configuration - Flags - BTB tripped (external) |  | X
Alarm parameter: Latch | 22047 | 22048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Configuration - Flags - MB tripped (external) | [5 empty] | X | X
Alarm parameter: Latch | 22048 | 22049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Configuration - Flags - GB short circuit | X |  | X | X | X
Alarm parameter: Latch | 22048 | 22049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Configuration - Flags - BTB short circuit |  | X
Alarm parameter: Latch | 22048 | 22049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Configuration - Flags - MB short circuit | [5 empty] | X | X
Alarm parameter: Latch | 22049 | 22050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration - Flags - MB closing failure |  |  |  | X
Alarm parameter: Latch | 22049 | 22050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Configuration - Flags - TB closing failure | [6 empty] | X
Alarm parameter: Latch | 22050 | 22051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration - Flags - MB opening failure |  |  |  | X
Alarm parameter: Latch | 22050 | 22051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Configuration - Flags - TB opening failure | [6 empty] | X
Alarm parameter: Latch | 22051 | 22052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration - Flags - MB position failure |  |  |  | X
Alarm parameter: Latch | 22051 | 22052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Configuration - Flags - TB position failure | [6 empty] | X
Alarm parameter: Latch | 22052 | 22053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration - Flags - MB configuration failure |  |  |  | X
Alarm parameter: Latch | 22052 | 22053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Configuration - Flags - TB configuration failure | [6 empty] | X
Alarm parameter: Latch | 22053 | 22054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration - Flags - MB synchronisation failure |  |  |  | X
Alarm parameter: Latch | 22053 | 22054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Configuration - Flags - TB synchronisation failure | [6 empty] | X
Alarm parameter: Latch | 22054 | 22055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration - Flags - MB de-load failure |  |  |  | X
Alarm parameter: Latch | 22054 | 22055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Configuration - Flags - TB de-load failure | [6 empty] | X
Alarm parameter: Latch | 22055 | 22056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Configuration - Flags - MB tripped (external) |  |  |  | X
Alarm parameter: Latch | 22055 | 22056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Configuration - Flags - TB tripped (external) | [6 empty] | X
Alarm parameter: Latch | 22056 | 22057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Configuration - Flags - MB short circuit |  |  |  | X
Alarm parameter: Latch | 22056 | 22057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Configuration - Flags - TB short circuit | [6 empty] | X
Alarm parameter: Latch | 22060 | 22061 | Parameters - Mains - AC setup - Phase sequence error - Configuration - Flags - Mains phase sequence error |  |  | X | X
Alarm parameter: Latch | 22060 | 22061 | Parameters - Busbar - AC setup - Phase sequence error - Configuration - Flags - Busbar phase sequence error | X |  |  |  | X | X | X
Alarm parameter: Latch | 22060 | 22061 | Parameters - Busbar B - AC setup - Phase sequence error - Configuration - Flags - Busbar B phase sequence error |  | X
Alarm parameter: Latch | 22061 | 22062 | Parameters - Generator - AC setup - Phase sequence error - Configuration - Flags - Generator phase sequence error | X |  | X | X | X
Alarm parameter: Latch | 22061 | 22062 | Parameters - Busbar A - AC setup - Phase sequence error - Configuration - Flags - Busbar A phase sequence error |  | X
Alarm parameter: Latch | 22061 | 22062 | Parameters - Mains - AC setup - Phase sequence error - Configuration - Flags - Mains phase sequence error | [5 empty] | X | X
Alarm parameter: Latch | 22062 | 22063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22103 | 22104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Configuration - Flags |  |  | X | X
Alarm parameter: Latch | 22103 | 22104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Configuration - Flags | X |  |  |  | X | X | X
Alarm parameter: Latch | 22103 | 22104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Configuration - Flags |  | X
Alarm parameter: Latch | 22104 | 22105 | Parameters - Mains - Additional protections - Vector shift - Configuration - Flags |  |  | X | X
Alarm parameter: Latch | 22104 | 22105 | Parameters - Busbar - Additional protections - Vector shift - Configuration - Flags | X |  |  |  | X | X | X
Alarm parameter: Latch | 22104 | 22105 | Parameters - Busbar B - Additional protections - Vector shift - Configuration - Flags |  | X
Alarm parameter: Latch | 22105 | 22106 | Parameters - Generator - Current protections - Inverse time over-current - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22105 | 22106 | Parameters - Busbar A - Current protections - Inverse time over-current - Configuration - Flags |  | X
Alarm parameter: Latch | 22105 | 22106 | Parameters - Mains - Current protections - Inverse time over-current - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22106 | 22107 | Parameters - Local - 4th current input - Earth inverse time over-current - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22107 | 22108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22108 | 22109 | Parameters - Generator - Additional protections - V< and Q< 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22108 | 22109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Configuration - Flags |  | X
Alarm parameter: Latch | 22108 | 22109 | Parameters - Mains - Additional protections - V< and Q< 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22109 | 22110 | Parameters - Generator - Additional protections - V< and Q< 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22109 | 22110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Configuration - Flags |  | X
Alarm parameter: Latch | 22109 | 22110 | Parameters - Mains - Additional protections - V< and Q< 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22110 | 22111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22110 | 22111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Configuration - Flags |  | X
Alarm parameter: Latch | 22110 | 22111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22111 | 22112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22111 | 22112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Configuration - Flags |  | X
Alarm parameter: Latch | 22111 | 22112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22115 | 22116 | Protection set point out of range | X | X | X | X | X | X | X
Alarm parameter: Latch | 22116 | 22117 | Parameters - Generator - Current protections - Stabilised differential current - Configuration - Flags - Stabilised differential | X |  | X | X | X
Alarm parameter: Latch | 22117 | 22118 | Parameters - Generator - Current protections - High set differential current - Configuration - Flags - High set differential | X |  | X | X | X
Alarm parameter: Latch | 22118 | 22119 | Protection set point out of range (differential current) | X |  | X | X | X
Alarm parameter: Latch | 22119 | 22120 | Parameters - Local - Mode - Not under remote control - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22121 | 22122 | Parameters - Local - Monitoring - System not OK - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22122 | 22123 | Configuration update delayed | X | X | X | X | X | X | X
Alarm parameter: Latch | 22123 | 22124 | Critical process error | X | X | X | X | X | X | X
Alarm parameter: Latch | 22124 | 22125 | Restore error | X | X | X | X | X | X | X
Alarm parameter: Latch | 22125 | 22126 | SD-card format error | X | X | X | X | X | X | X
Alarm parameter: Latch | 22126 | 22127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm parameter: Latch | 22127 | 22128 | Fieldbus configuration exceeded maximum I/O configuration | X | X | X | X | X | X | X
Alarm parameter: Latch | 22128 | 22129 | Parameters - Custom alarm - Custom alarm 0 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22129 | 22130 | Parameters - Custom alarm - Custom alarm 1 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22130 | 22131 | Parameters - Custom alarm - Custom alarm 2 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22131 | 22132 | Parameters - Custom alarm - Custom alarm 3 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22132 | 22133 | Parameters - Custom alarm - Custom alarm 4 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22133 | 22134 | Parameters - Custom alarm - Custom alarm 5 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22134 | 22135 | Parameters - Custom alarm - Custom alarm 6 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22135 | 22136 | Parameters - Custom alarm - Custom alarm 7 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22136 | 22137 | Parameters - Custom alarm - Custom alarm 8 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22137 | 22138 | Parameters - Custom alarm - Custom alarm 9 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22138 | 22139 | Parameters - Custom alarm - Custom alarm 10 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22139 | 22140 | Parameters - Custom alarm - Custom alarm 11 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22140 | 22141 | Parameters - Custom alarm - Custom alarm 12 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22141 | 22142 | Parameters - Custom alarm - Custom alarm 13 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22142 | 22143 | Parameters - Custom alarm - Custom alarm 14 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22143 | 22144 | Parameters - Custom alarm - Custom alarm 15 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22144 | 22145 | Parameters - Custom alarm - Custom alarm 16 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22145 | 22146 | Parameters - Custom alarm - Custom alarm 17 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22146 | 22147 | Parameters - Custom alarm - Custom alarm 18 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22147 | 22148 | Parameters - Custom alarm - Custom alarm 19 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22148 | 22149 | Parameters - Custom alarm - Custom alarm 20 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22149 | 22150 | Parameters - Custom alarm - Custom alarm 21 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22150 | 22151 | Parameters - Custom alarm - Custom alarm 22 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22151 | 22152 | Parameters - Custom alarm - Custom alarm 23 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22152 | 22153 | Parameters - Custom alarm - Custom alarm 24 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm parameter: Latch | 22153 | 22154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Configuration - Flags - GOV regulation error | X |  | X | X | X
Alarm parameter: Latch | 22154 | 22155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Configuration - Flags - AVR regulation error | X |  | X | X | X
Alarm parameter: Latch | 22163 | 22164 | Required hardware card(s) not found | X | X | X | X | X | X | X
Alarm parameter: Latch | 22164 | 22165 | Software mismatch on hardware module(s) | X | X | X | X | X | X | X
Alarm parameter: Latch | 22165 | 22166 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration - Flags - Mains L1-L2-L3 wire break |  |  | X
Alarm parameter: Latch | 22165 | 22166 | Parameters - Busbar - AC setup - Multiple phase wire break - Configuration - Flags - Busbar L1-L2-L3 wire break | X |  |  |  | X | X
Alarm parameter: Latch | 22165 | 22166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Configuration - Flags - Busbar B L1-L2-L3 wire break |  | X
Alarm parameter: Latch | 22166 | 22167 | Parameters - Generator - AC setup - Multiple phase wire break - Configuration - Flags - Generator L1-L2-L3 wire break | X |  | X |  | X
Alarm parameter: Latch | 22166 | 22167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Configuration - Flags - Busbar A L1-L2-L3 wire break |  | X
Alarm parameter: Latch | 22166 | 22167 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration - Flags - Mains L1-L2-L3 wire break | [5 empty] | X
Alarm parameter: Latch | 22167 | 22168 | Parameters - Mains - AC setup - L1 wire break - Configuration - Flags - Mains L1 wire break |  |  | X
Alarm parameter: Latch | 22167 | 22168 | Parameters - Busbar - AC setup - L1 wire break - Configuration - Flags - Busbar L1 wire break | X |  |  |  | X | X
Alarm parameter: Latch | 22167 | 22168 | Parameters - Busbar B - AC setup - L1 wire break - Configuration - Flags - Busbar B L1 wire break |  | X
Alarm parameter: Latch | 22168 | 22169 | Parameters - Mains - AC setup - L2 wire break - Configuration - Flags - Mains L2 wire break |  |  | X
Alarm parameter: Latch | 22168 | 22169 | Parameters - Busbar - AC setup - L2 wire break - Configuration - Flags - Busbar L2 wire break | X |  |  |  | X | X
Alarm parameter: Latch | 22168 | 22169 | Parameters - Busbar B - AC setup - L2 wire break - Configuration - Flags - Busbar B L2 wire break |  | X
Alarm parameter: Latch | 22169 | 22170 | Parameters - Mains - AC setup - L3 wire break - Configuration - Flags - Mains L3 wire break |  |  | X
Alarm parameter: Latch | 22169 | 22170 | Parameters - Busbar - AC setup - L3 wire break - Configuration - Flags - Busbar L3 wire break | X |  |  |  | X | X
Alarm parameter: Latch | 22169 | 22170 | Parameters - Busbar B - AC setup - L3 wire break - Configuration - Flags - Busbar B L3 wire break |  | X
Alarm parameter: Latch | 22170 | 22171 | Parameters - Generator - AC setup - L1 wire break - Configuration - Flags - Generator L1 wire break | X |  | X |  | X
Alarm parameter: Latch | 22170 | 22171 | Parameters - Busbar A - AC setup - L1 wire break - Configuration - Flags - Busbar A L1 wire break |  | X
Alarm parameter: Latch | 22170 | 22171 | Parameters - Mains - AC setup - L1 wire break - Configuration - Flags - Mains L1 wire break | [5 empty] | X
Alarm parameter: Latch | 22171 | 22172 | Parameters - Generator - AC setup - L2 wire break - Configuration - Flags - Generator L2 wire break | X |  | X |  | X
Alarm parameter: Latch | 22171 | 22172 | Parameters - Busbar A - AC setup - L2 wire break - Configuration - Flags - Busbar A L2 wire break |  | X
Alarm parameter: Latch | 22171 | 22172 | Parameters - Mains - AC setup - L2 wire break - Configuration - Flags - Mains L2 wire break | [5 empty] | X
Alarm parameter: Latch | 22172 | 22173 | Parameters - Generator - AC setup - L3 wire break - Configuration - Flags - Generator L3 wire break | X |  | X |  | X
Alarm parameter: Latch | 22172 | 22173 | Parameters - Busbar A - AC setup - L3 wire break - Configuration - Flags - Busbar A L3 wire break |  | X
Alarm parameter: Latch | 22172 | 22173 | Parameters - Mains - AC setup - L3 wire break - Configuration - Flags - Mains L3 wire break | [5 empty] | X
Alarm parameter: Latch | 22178 | 22179 | Parameters - Mains - AC setup - Supervision alarm - Configuration - Flags - Mains supervision alarm |  |  | X | X |  | X | X
Alarm parameter: Latch | 22179 | 22180 | Parameters - Engine - Emergency stop - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22179 | 22180 | Parameters - Busbar A - Emergency stop - Configuration - Flags |  | X
Alarm parameter: Latch | 22179 | 22180 | Parameters - Mains - Emergency stop - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22180 | 22181 | Clock battery failure | X | X | X | X | X | X | X
Alarm parameter: Latch | 22181 | 22182 | Controller temperature too high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22182 | 22183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Configuration - Flags - PSM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22183 | 22184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Configuration - Flags - PSM3.1 1 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Latch | 22184 | 22185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Configuration - Flags - PSM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22185 | 22186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Configuration - Flags - PSM3.2 1 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Latch | 22186 | 22187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Configuration - Flags - PSM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22187 | 22188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Configuration - Flags - PSM3.2 2 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Latch | 22188 | 22189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Configuration - Flags - PSM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22189 | 22190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Configuration - Flags - PSM3.2 3 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Latch | 22190 | 22191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Configuration - Flags - EIM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22191 | 22192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Configuration - Flags - EIM3.1 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Latch | 22192 | 22193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Configuration - Flags - EIM3.1 2 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22193 | 22194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Configuration - Flags - EIM3.1 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Latch | 22194 | 22195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Configuration - Flags - EIM3.1 3 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22195 | 22196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Configuration - Flags - EIM3.1 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Latch | 22196 | 22197 | EIM3.1 4 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22197 | 22198 | EIM3.1 4 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Latch | 22198 | 22199 | EIM3.1 5 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22199 | 22200 | EIM3.1 5 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Latch | 22200 | 22201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Configuration - Flags - EIM3.1 1 relay 4 wire break | X | X | X | X | X | X | X
Alarm parameter: Latch | 22201 | 22202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Configuration - Flags - EIM3.1 2 relay 4 wire break | X | X | X | X | X | X | X
Alarm parameter: Latch | 22202 | 22203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Configuration - Flags - EIM3.1 3 relay 4 wire break | X | X | X | X | X | X | X
Alarm parameter: Latch | 22203 | 22204 | EIM3.1 4 relay 4 wire break | X | X | X | X | X | X | X
Alarm parameter: Latch | 22204 | 22205 | EIM3.1 5 relay 4 wire break | X | X | X | X | X | X | X
Alarm parameter: Latch | 22205 | 22206 | AC protections not running | X | X | X | X | X | X | X
Alarm parameter: Latch | 22206 | 22207 | AC data is missing | X | X | X | X | X | X | X
Alarm parameter: Latch | 22207 | 22208 | AC protections not running (differential current) | X |  | X | X | X
Alarm parameter: Latch | 22208 | 22209 | AC data is missing (differential current) | X |  | X | X | X
Alarm parameter: Latch | 22209 | 22210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Configuration - Flags - GAM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22210 | 22211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Configuration - Flags - GAM3.2 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Latch | 22211 | 22212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Configuration - Flags - GAM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22212 | 22213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Configuration - Flags - GAM3.2 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Latch | 22213 | 22214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Configuration - Flags - GAM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22214 | 22215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Configuration - Flags - GAM3.2 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm parameter: Latch | 22215 | 22216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Configuration - Flags - PSM3.2 4 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22216 | 22217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Configuration - Flags - PSM3.2 4 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Latch | 22217 | 22218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Configuration - Flags - PSM3.2 5 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22218 | 22219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Configuration - Flags - PSM3.2 5 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Latch | 22219 | 22220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Configuration - Flags - PSM3.2 6 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22220 | 22221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Configuration - Flags - PSM3.2 6 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Latch | 22221 | 22222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Configuration - Flags - PSM3.2 7 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22222 | 22223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Configuration - Flags - PSM3.2 7 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Latch | 22223 | 22224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Configuration - Flags - PSM3.2 8 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22224 | 22225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Configuration - Flags - PSM3.2 8 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Latch | 22225 | 22226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Configuration - Flags - PSM3.2 9 supply voltage high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22226 | 22227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Configuration - Flags - PSM3.2 9 supply voltage low | X | X | X | X | X | X | X
Alarm parameter: Latch | 22228 | 22229 | Parameters - System - Monitoring - Duplicate controller ID - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22229 | 22230 | Parameters - System - Monitoring - Missing all controllers - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22231 | 22232 | Controller ID not configured | X | X | X | X | X | X | X
Alarm parameter: Latch | 22236 | 22237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22237 | 22238 | Blackout detection mismatch | X |  | X | X | X
Alarm parameter: Latch | 22240 | 22241 | Parameters - Communication - NTP - NTP server 1 not connected - Configuration - Flags - NTP server 1 could not connect | X | X | X | X | X | X | X
Alarm parameter: Latch | 22241 | 22242 | Parameters - Communication - NTP - NTP server 1 no response - Configuration - Flags - NTP server 1 is not responding | X | X | X | X | X | X | X
Alarm parameter: Latch | 22242 | 22243 | Parameters - Communication - NTP - NTP server 2 not connected - Configuration - Flags - NTP server 2 could not connect | X | X | X | X | X | X | X
Alarm parameter: Latch | 22243 | 22244 | Parameters - Communication - NTP - NTP server 2 no response - Configuration - Flags - NTP server 2 is not responding | X | X | X | X | X | X | X
Alarm parameter: Latch | 22244 | 22245 | Parameters - Communication - NTP - No NTP server time synchronisation - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22245 | 22246 | Parameters - Communication - NTP - No NTP server(s) connected - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22246 | 22247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22247 | 22248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22296 | 22297 | Controller not part of system | X | X | X | X | X | X | X
Alarm parameter: Latch | 22297 | 22298 | Different single-line configurations | X | X | X | X | X | X | X
Alarm parameter: Latch | 22298 | 22299 | Single-line missing/none active | X | X | X | X | X | X | X
Alarm parameter: Latch | 22299 | 22300 | Parameters - Communication - Modbus - Modbus communication timeout - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22300 | 22301 | Parameters - CODESYS - Monitoring - I/O config conflict - Configuration - Flags - CODESYS configuration conflict | X | X | X | X | X | X | X
Alarm parameter: Latch | 22301 | 22302 | Parameters - CODESYS - Monitoring - Application not OK - Configuration - Flags - CODESYS application not OK | X | X | X | X | X | X | X
Alarm parameter: Latch | 22302 | 22303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22303 | 22304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22304 | 22305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22305 | 22306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22306 | 22307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22307 | 22308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22308 | 22309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22309 | 22310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22310 | 22311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22311 | 22312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22312 | 22313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22313 | 22314 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22314 | 22315 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22315 | 22316 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22316 | 22317 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22317 | 22318 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22318 | 22319 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22319 | 22320 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22320 | 22321 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22321 | 22322 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22322 | 22323 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22323 | 22324 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22324 | 22325 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22325 | 22326 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22326 | 22327 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22327 | 22328 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22328 | 22329 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22329 | 22330 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22330 | 22331 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22331 | 22332 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22332 | 22333 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22333 | 22334 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22334 | 22335 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22335 | 22336 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22336 | 22337 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22337 | 22338 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22338 | 22339 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22339 | 22340 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22340 | 22341 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22341 | 22342 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22342 | 22343 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22343 | 22344 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22344 | 22345 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22345 | 22346 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22346 | 22347 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22347 | 22348 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22348 | 22349 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22349 | 22350 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22350 | 22351 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22351 | 22352 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22352 | 22353 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22353 | 22354 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22354 | 22355 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22355 | 22356 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22356 | 22357 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22357 | 22358 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22358 | 22359 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22359 | 22360 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22360 | 22361 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22361 | 22362 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22362 | 22363 | Digital custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22363 | 22364 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22364 | 22365 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22365 | 22366 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22366 | 22367 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22367 | 22368 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22368 | 22369 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22369 | 22370 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22370 | 22371 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22371 | 22372 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22372 | 22373 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22373 | 22374 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22374 | 22375 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22375 | 22376 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22376 | 22377 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22377 | 22378 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22378 | 22379 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22379 | 22380 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22380 | 22381 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22381 | 22382 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22382 | 22383 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22383 | 22384 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22384 | 22385 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22385 | 22386 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22386 | 22387 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22387 | 22388 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22388 | 22389 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22389 | 22390 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22390 | 22391 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22391 | 22392 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22392 | 22393 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22393 | 22394 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22394 | 22395 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22395 | 22396 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22396 | 22397 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22397 | 22398 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22398 | 22399 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22399 | 22400 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22400 | 22401 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22401 | 22402 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22402 | 22403 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22403 | 22404 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22404 | 22405 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22405 | 22406 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22406 | 22407 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22407 | 22408 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22408 | 22409 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22409 | 22410 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22410 | 22411 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22411 | 22412 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22412 | 22413 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22413 | 22414 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22414 | 22415 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22415 | 22416 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22416 | 22417 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22417 | 22418 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22418 | 22419 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22419 | 22420 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22420 | 22421 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22421 | 22422 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22422 | 22423 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22423 | 22424 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22424 | 22425 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22425 | 22426 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22426 | 22427 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22427 | 22428 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22428 | 22429 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22429 | 22430 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22430 | 22431 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22431 | 22432 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22432 | 22433 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22433 | 22434 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22434 | 22435 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22435 | 22436 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22436 | 22437 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22437 | 22438 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22438 | 22439 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22439 | 22440 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22440 | 22441 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22441 | 22442 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22442 | 22443 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22443 | 22444 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22444 | 22445 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22445 | 22446 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22446 | 22447 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22447 | 22448 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22448 | 22449 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22449 | 22450 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22450 | 22451 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22451 | 22452 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22452 | 22453 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22453 | 22454 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22454 | 22455 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22455 | 22456 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22456 | 22457 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22457 | 22458 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22458 | 22459 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22459 | 22460 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22460 | 22461 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22461 | 22462 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22462 | 22463 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22463 | 22464 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22464 | 22465 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22465 | 22466 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22466 | 22467 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22467 | 22468 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22468 | 22469 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22469 | 22470 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22470 | 22471 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22471 | 22472 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22472 | 22473 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22473 | 22474 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22474 | 22475 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22475 | 22476 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22476 | 22477 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22477 | 22478 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22478 | 22479 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22479 | 22480 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22480 | 22481 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22481 | 22482 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22482 | 22483 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22483 | 22484 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22484 | 22485 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22485 | 22486 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22486 | 22487 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22487 | 22488 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22488 | 22489 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22489 | 22490 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22490 | 22491 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22491 | 22492 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22492 | 22493 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22493 | 22494 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22494 | 22495 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22495 | 22496 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22496 | 22497 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22497 | 22498 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22498 | 22499 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22499 | 22500 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22500 | 22501 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22501 | 22502 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22502 | 22503 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22503 | 22504 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22504 | 22505 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22505 | 22506 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22506 | 22507 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22507 | 22508 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22508 | 22509 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22509 | 22510 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22510 | 22511 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22511 | 22512 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22512 | 22513 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22513 | 22514 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22514 | 22515 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22515 | 22516 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22516 | 22517 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22517 | 22518 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22518 | 22519 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22519 | 22520 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22520 | 22521 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22521 | 22522 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22522 | 22523 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22523 | 22524 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22524 | 22525 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22525 | 22526 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22526 | 22527 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22527 | 22528 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22528 | 22529 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22529 | 22530 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22530 | 22531 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22531 | 22532 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22532 | 22533 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22533 | 22534 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22534 | 22535 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22535 | 22536 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22536 | 22537 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22537 | 22538 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22538 | 22539 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22539 | 22540 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22540 | 22541 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22541 | 22542 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22542 | 22543 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22543 | 22544 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22544 | 22545 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22545 | 22546 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22546 | 22547 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22547 | 22548 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22548 | 22549 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22549 | 22550 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22550 | 22551 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22551 | 22552 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22552 | 22553 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22553 | 22554 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22554 | 22555 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22555 | 22556 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22556 | 22557 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22557 | 22558 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22558 | 22559 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22559 | 22560 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22560 | 22561 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22561 | 22562 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22562 | 22563 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm parameter: Latch | 22565 | 22566 | Parameters - Local - CustomLogic - Configuration invalid - Configuration - Flags - CustomLogic configuration invalid | X | X | X | X | X | X | X
Alarm parameter: Latch | 22566 | 22567 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Configuration - Flags - Digital AVR communication error | X |  | X | X | X
Alarm parameter: Latch | 22567 | 22568 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22568 | 22569 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22569 | 22570 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22570 | 22571 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22571 | 22572 | Parameters - Generator - Digital AVR - Alarms - Open diode - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22572 | 22573 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22573 | 22574 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22574 | 22575 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22575 | 22576 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22576 | 22577 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22577 | 22578 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22578 | 22579 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22579 | 22580 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22580 | 22581 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22581 | 22582 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22582 | 22583 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22583 | 22584 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22584 | 22585 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22585 | 22586 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22586 | 22587 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22587 | 22588 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22588 | 22589 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22589 | 22590 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22590 | 22591 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22591 | 22592 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22592 | 22593 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22593 | 22594 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22594 | 22595 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22595 | 22596 | Parameters - Generator - Digital AVR - Alarms - Motor start - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22596 | 22597 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22597 | 22598 | Parameters - Generator - Digital AVR - Alarms - Power supply - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22598 | 22599 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22599 | 22600 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22600 | 22601 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22601 | 22602 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22602 | 22603 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22603 | 22604 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22604 | 22605 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22605 | 22606 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22606 | 22607 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22607 | 22608 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22608 | 22609 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22609 | 22610 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22610 | 22611 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22611 | 22612 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22612 | 22613 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22613 | 22614 | DAVR unsupported AC configuration | X |  | X | X | X
Alarm parameter: Latch | 22614 | 22615 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Configuration - Flags - Illegal DAVR configuration | X |  | X | X | X
Alarm parameter: Latch | 22615 | 22616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Configuration - Flags - Generator under-voltage 1 | X |  | X | X | X
Alarm parameter: Latch | 22615 | 22616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Configuration - Flags - Busbar A under-voltage 1 |  | X
Alarm parameter: Latch | 22615 | 22616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Flags - Mains under-voltage 1 | [5 empty] | X | X
Alarm parameter: Latch | 22616 | 22617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Configuration - Flags - Generator under-voltage 2 | X |  | X | X | X
Alarm parameter: Latch | 22616 | 22617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Configuration - Flags - Busbar A under-voltage 2 |  | X
Alarm parameter: Latch | 22616 | 22617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Flags - Mains under-voltage 2 | [5 empty] | X | X
Alarm parameter: Latch | 22617 | 22618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Configuration - Flags - Generator under-voltage 3 | X |  | X | X | X
Alarm parameter: Latch | 22617 | 22618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Configuration - Flags - Busbar A under-voltage 3 |  | X
Alarm parameter: Latch | 22617 | 22618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Flags - Mains under-voltage 3 | [5 empty] | X | X
Alarm parameter: Latch | 22618 | 22619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Configuration - Flags - Generator over-voltage 1 | X |  | X | X | X
Alarm parameter: Latch | 22618 | 22619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Configuration - Flags - Busbar A over-voltage 1 |  | X
Alarm parameter: Latch | 22618 | 22619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Flags - Mains over-voltage 1 | [5 empty] | X | X
Alarm parameter: Latch | 22619 | 22620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Configuration - Flags - Generator over-voltage 2 | X |  | X | X | X
Alarm parameter: Latch | 22619 | 22620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Configuration - Flags - Busbar A over-voltage 2 |  | X
Alarm parameter: Latch | 22619 | 22620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Flags - Mains over-voltage 2 | [5 empty] | X | X
Alarm parameter: Latch | 22620 | 22621 | Parameters - Generator - Voltage protections - Voltage unbalance - Configuration - Flags - Generator voltage unbalance | X |  | X | X | X
Alarm parameter: Latch | 22620 | 22621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Configuration - Flags - Busbar A voltage unbalance |  | X
Alarm parameter: Latch | 22620 | 22621 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Flags - Mains voltage unbalance | [5 empty] | X | X
Alarm parameter: Latch | 22621 | 22622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Configuration - Flags - Generator negative sequence voltage | X |  | X | X | X
Alarm parameter: Latch | 22621 | 22622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Configuration - Flags - Busbar A negative sequence voltage |  | X
Alarm parameter: Latch | 22621 | 22622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Flags - Mains negative sequence voltage | [5 empty] | X | X
Alarm parameter: Latch | 22622 | 22623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Configuration - Flags - Generator zero sequence voltage | X |  | X | X | X
Alarm parameter: Latch | 22622 | 22623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Configuration - Flags - Busbar A zero sequence voltage |  | X
Alarm parameter: Latch | 22622 | 22623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Flags - Mains zero sequence voltage | [5 empty] | X | X
Alarm parameter: Latch | 22623 | 22624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Generator positive sequence under-voltage | X |  | X | X | X
Alarm parameter: Latch | 22623 | 22624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Busbar A positive sequence under-voltage |  | X
Alarm parameter: Latch | 22623 | 22624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Mains positive sequence under-voltage | [5 empty] | X | X
Alarm parameter: Latch | 22624 | 22625 | Parameters - Generator - Current protections - Over-current 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22624 | 22625 | Parameters - Busbar A - Current protections - Over-current 1 - Configuration - Flags |  | X
Alarm parameter: Latch | 22624 | 22625 | Parameters - Mains - Current protections - Over-current 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22625 | 22626 | Parameters - Generator - Current protections - Over-current 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22625 | 22626 | Parameters - Busbar A - Current protections - Over-current 2 - Configuration - Flags |  | X
Alarm parameter: Latch | 22625 | 22626 | Parameters - Mains - Current protections - Over-current 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22626 | 22627 | Parameters - Generator - Current protections - Over-current 3 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22626 | 22627 | Parameters - Busbar A - Current protections - Over-current 3 - Configuration - Flags |  | X
Alarm parameter: Latch | 22626 | 22627 | Parameters - Mains - Current protections - Over-current 3 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22627 | 22628 | Parameters - Generator - Current protections - Over-current 4 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22627 | 22628 | Parameters - Busbar A - Current protections - Over-current 4 - Configuration - Flags |  | X
Alarm parameter: Latch | 22627 | 22628 | Parameters - Mains - Current protections - Over-current 4 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22628 | 22629 | Parameters - Generator - Current protections - Fast over-current 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22628 | 22629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Configuration - Flags |  | X
Alarm parameter: Latch | 22628 | 22629 | Parameters - Mains - Current protections - Fast over-current 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22629 | 22630 | Parameters - Generator - Current protections - Fast over-current 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22629 | 22630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Configuration - Flags |  | X
Alarm parameter: Latch | 22629 | 22630 | Parameters - Mains - Current protections - Fast over-current 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22630 | 22631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22630 | 22631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Configuration - Flags |  | X
Alarm parameter: Latch | 22630 | 22631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22631 | 22632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22631 | 22632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Configuration - Flags |  | X
Alarm parameter: Latch | 22631 | 22632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22632 | 22633 | Parameters - Generator - Current protections - Directional over-current 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22632 | 22633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Configuration - Flags |  | X
Alarm parameter: Latch | 22632 | 22633 | Parameters - Mains - Current protections - Directional over-current 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22633 | 22634 | Parameters - Generator - Current protections - Directional over-current 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22633 | 22634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Configuration - Flags |  | X
Alarm parameter: Latch | 22633 | 22634 | Parameters - Mains - Current protections - Directional over-current 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22634 | 22635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Configuration - Flags |  | X
Alarm parameter: Latch | 22635 | 22636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Configuration - Flags |  | X
Alarm parameter: Latch | 22636 | 22637 | Parameters - Generator - Current protections - Negative sequence current - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22636 | 22637 | Parameters - Busbar A - Current protections - Negative sequence current - Configuration - Flags |  | X
Alarm parameter: Latch | 22636 | 22637 | Parameters - Mains - Current protections - Negative sequence current - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22637 | 22638 | Parameters - Generator - Current protections - Zero sequence current - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22637 | 22638 | Parameters - Busbar A - Current protections - Zero sequence current - Configuration - Flags |  | X
Alarm parameter: Latch | 22637 | 22638 | Parameters - Mains - Current protections - Zero sequence current - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22638 | 22639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Configuration - Flags - Generator over-frequency 1 | X |  | X | X | X
Alarm parameter: Latch | 22638 | 22639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Configuration - Flags - Busbar A over-frequency 1 |  | X
Alarm parameter: Latch | 22638 | 22639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Flags - Mains over-frequency 1 | [5 empty] | X | X
Alarm parameter: Latch | 22639 | 22640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Configuration - Flags - Generator over-frequency 2 | X |  | X | X | X
Alarm parameter: Latch | 22639 | 22640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Configuration - Flags - Busbar A over-frequency 2 |  | X
Alarm parameter: Latch | 22639 | 22640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Flags - Mains over-frequency 2 | [5 empty] | X | X
Alarm parameter: Latch | 22640 | 22641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Configuration - Flags - Generator over-frequency 3 | X |  | X | X | X
Alarm parameter: Latch | 22640 | 22641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Configuration - Flags - Busbar A over-frequency 3 |  | X
Alarm parameter: Latch | 22640 | 22641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Flags - Mains over-frequency 3 | [5 empty] | X | X
Alarm parameter: Latch | 22641 | 22642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Configuration - Flags - Generator under-frequency 1 | X |  | X | X | X
Alarm parameter: Latch | 22641 | 22642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Configuration - Flags - Busbar A under-frequency 1 |  | X
Alarm parameter: Latch | 22641 | 22642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Flags - Mains under-frequency 1 | [5 empty] | X | X
Alarm parameter: Latch | 22642 | 22643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Configuration - Flags - Generator under-frequency 2 | X |  | X | X | X
Alarm parameter: Latch | 22642 | 22643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Configuration - Flags - Busbar A under-frequency 2 |  | X
Alarm parameter: Latch | 22642 | 22643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Flags - Mains under-frequency 2 | [5 empty] | X | X
Alarm parameter: Latch | 22643 | 22644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Configuration - Flags - Generator under-frequency 3 | X |  | X | X | X
Alarm parameter: Latch | 22643 | 22644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Configuration - Flags - Busbar A under-frequency 3 |  | X
Alarm parameter: Latch | 22643 | 22644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Flags - Mains under-frequency 3 | [5 empty] | X | X
Alarm parameter: Latch | 22644 | 22645 | Parameters - Generator - Power protections - Overload 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22644 | 22645 | Parameters - Busbar A - Power protections - Power export 1 - Configuration - Flags |  | X
Alarm parameter: Latch | 22644 | 22645 | Parameters - Mains - Power protections - Overload 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22645 | 22646 | Parameters - Generator - Power protections - Overload 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22645 | 22646 | Parameters - Busbar A - Power protections - Power export 2 - Configuration - Flags |  | X
Alarm parameter: Latch | 22645 | 22646 | Parameters - Mains - Power protections - Overload 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22646 | 22647 | Parameters - Generator - Power protections - Overload 3 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22646 | 22647 | Parameters - Busbar A - Power protections - Power export 3 - Configuration - Flags |  | X
Alarm parameter: Latch | 22646 | 22647 | Parameters - Mains - Power protections - Overload 3 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22647 | 22648 | Parameters - Generator - Power protections - Overload 4 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22647 | 22648 | Parameters - Busbar A - Power protections - Power export 4 - Configuration - Flags |  | X
Alarm parameter: Latch | 22647 | 22648 | Parameters - Mains - Power protections - Overload 4 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22648 | 22649 | Parameters - Generator - Power protections - Overload 5 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22648 | 22649 | Parameters - Busbar A - Power protections - Power export 5 - Configuration - Flags |  | X
Alarm parameter: Latch | 22648 | 22649 | Parameters - Mains - Power protections - Overload 5 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22649 | 22650 | Parameters - Generator - Power protections - Reverse power 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22649 | 22650 | Parameters - Busbar A - Power protections - Power import 1 - Configuration - Flags |  | X
Alarm parameter: Latch | 22649 | 22650 | Parameters - Mains - Power protections - Reverse power 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22650 | 22651 | Parameters - Generator - Power protections - Reverse power 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22650 | 22651 | Parameters - Busbar A - Power protections - Power import 2 - Configuration - Flags |  | X
Alarm parameter: Latch | 22650 | 22651 | Parameters - Mains - Power protections - Reverse power 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22651 | 22652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22651 | 22652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Configuration - Flags |  | X
Alarm parameter: Latch | 22651 | 22652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22652 | 22653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22652 | 22653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Configuration - Flags |  | X
Alarm parameter: Latch | 22652 | 22653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22653 | 22654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22653 | 22654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Configuration - Flags |  | X
Alarm parameter: Latch | 22653 | 22654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22654 | 22655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22654 | 22655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Configuration - Flags |  | X
Alarm parameter: Latch | 22654 | 22655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Configuration - Flags | [5 empty] | X | X
Alarm parameter: Latch | 22655 | 22656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Flags - Mains over-voltage 1 |  |  | X | X
Alarm parameter: Latch | 22655 | 22656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Configuration - Flags - Busbar over-voltage 1 | X |  |  |  | X | X | X
Alarm parameter: Latch | 22655 | 22656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Configuration - Flags - Busbar B over-voltage 1 |  | X
Alarm parameter: Latch | 22656 | 22657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Flags - Mains over-voltage 2 |  |  | X | X
Alarm parameter: Latch | 22656 | 22657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Configuration - Flags - Busbar over-voltage 2 | X |  |  |  | X | X | X
Alarm parameter: Latch | 22656 | 22657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Configuration - Flags - Busbar B over-voltage 2 |  | X
Alarm parameter: Latch | 22657 | 22658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Configuration - Flags - Mains over-voltage 3 |  |  | X | X
Alarm parameter: Latch | 22657 | 22658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Configuration - Flags - Busbar over-voltage 3 | X |  |  |  | X | X | X
Alarm parameter: Latch | 22657 | 22658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Configuration - Flags - Busbar B over-voltage 3 |  | X
Alarm parameter: Latch | 22658 | 22659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Flags - Mains under-voltage 1 |  |  | X | X
Alarm parameter: Latch | 22658 | 22659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Configuration - Flags - Busbar under-voltage 1 | X |  |  |  | X | X | X
Alarm parameter: Latch | 22658 | 22659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Configuration - Flags - Busbar B under-voltage 1 |  | X
Alarm parameter: Latch | 22659 | 22660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Flags - Mains under-voltage 2 |  |  | X | X
Alarm parameter: Latch | 22659 | 22660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Configuration - Flags - Busbar under-voltage 2 | X |  |  |  | X | X | X
Alarm parameter: Latch | 22659 | 22660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Configuration - Flags - Busbar B under-voltage 2 |  | X
Alarm parameter: Latch | 22660 | 22661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Flags - Mains under-voltage 3 |  |  | X | X
Alarm parameter: Latch | 22660 | 22661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Configuration - Flags - Busbar under-voltage 3 | X |  |  |  | X | X | X
Alarm parameter: Latch | 22660 | 22661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Configuration - Flags - Busbar B under-voltage 3 |  | X
Alarm parameter: Latch | 22661 | 22662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Configuration - Flags - Mains under-voltage 4 |  |  | X | X
Alarm parameter: Latch | 22661 | 22662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Configuration - Flags - Busbar under-voltage 4 | X |  |  |  | X | X | X
Alarm parameter: Latch | 22661 | 22662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Configuration - Flags - Busbar B under-voltage 4 |  | X
Alarm parameter: Latch | 22662 | 22663 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Flags - Mains voltage unbalance |  |  | X | X
Alarm parameter: Latch | 22662 | 22663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Configuration - Flags - Busbar voltage unbalance | X |  |  |  | X | X | X
Alarm parameter: Latch | 22662 | 22663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Configuration - Flags - Busbar B voltage unbalance |  | X
Alarm parameter: Latch | 22663 | 22664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Flags - Mains over-frequency 1 |  |  | X | X
Alarm parameter: Latch | 22663 | 22664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Configuration - Flags - Busbar over-frequency 1 | X |  |  |  | X | X | X
Alarm parameter: Latch | 22663 | 22664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Configuration - Flags - Busbar B over-frequency 1 |  | X
Alarm parameter: Latch | 22664 | 22665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Flags - Mains over-frequency 2 |  |  | X | X
Alarm parameter: Latch | 22664 | 22665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Configuration - Flags - Busbar over-frequency 2 | X |  |  |  | X | X | X
Alarm parameter: Latch | 22664 | 22665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Configuration - Flags - Busbar B over-frequency 2 |  | X
Alarm parameter: Latch | 22665 | 22666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Flags - Mains over-frequency 3 |  |  | X | X
Alarm parameter: Latch | 22665 | 22666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Configuration - Flags - Busbar over-frequency 3 | X |  |  |  | X | X | X
Alarm parameter: Latch | 22665 | 22666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Configuration - Flags - Busbar B over-frequency 3 |  | X
Alarm parameter: Latch | 22666 | 22667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Flags - Mains under-frequency 1 |  |  | X | X
Alarm parameter: Latch | 22666 | 22667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Configuration - Flags - Busbar under-frequency 1 | X |  |  |  | X | X | X
Alarm parameter: Latch | 22666 | 22667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Configuration - Flags - Busbar B under-frequency 1 |  | X
Alarm parameter: Latch | 22667 | 22668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Flags - Mains under-frequency 2 |  |  | X | X
Alarm parameter: Latch | 22667 | 22668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Configuration - Flags - Busbar under-frequency 2 | X |  |  |  | X | X | X
Alarm parameter: Latch | 22667 | 22668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Configuration - Flags - Busbar B under-frequency 2 |  | X
Alarm parameter: Latch | 22668 | 22669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Flags - Mains under-frequency 3 |  |  | X | X
Alarm parameter: Latch | 22668 | 22669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Configuration - Flags - Busbar under-frequency 3 | X |  |  |  | X | X | X
Alarm parameter: Latch | 22668 | 22669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Configuration - Flags - Busbar B under-frequency 3 |  | X
Alarm parameter: Latch | 22669 | 22670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Configuration - Flags - Mains under-frequency 4 |  |  | X | X
Alarm parameter: Latch | 22669 | 22670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Configuration - Flags - Busbar under-frequency 4 | X |  |  |  | X | X | X
Alarm parameter: Latch | 22669 | 22670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Configuration - Flags - Busbar B under-frequency 4 |  | X
Alarm parameter: Latch | 22670 | 22671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Flags - Busbar negative sequence voltage |  |  | X | X
Alarm parameter: Latch | 22670 | 22671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Configuration - Flags - Busbar negative sequence voltage | X |  |  |  | X | X | X
Alarm parameter: Latch | 22670 | 22671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Configuration - Flags - Busbar B negative sequence voltage |  | X
Alarm parameter: Latch | 22671 | 22672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Flags - Busbar zero sequence voltage |  |  | X | X
Alarm parameter: Latch | 22671 | 22672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Configuration - Flags - Busbar zero sequence voltage | X |  |  |  | X | X | X
Alarm parameter: Latch | 22671 | 22672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Configuration - Flags - Busbar B zero sequence voltage |  | X
Alarm parameter: Latch | 22672 | 22673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Busbar positive sequence under-voltage |  |  | X | X
Alarm parameter: Latch | 22672 | 22673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Busbar positive sequence under-voltage | X |  |  |  | X | X | X
Alarm parameter: Latch | 22672 | 22673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Busbar B positive sequence under-voltage |  | X
Alarm parameter: Latch | 22717 | 22718 | Parameters - Engine - Maintenance - Service timer - Configuration - Flags - Service timer 1 | X |  | X | X | X
Alarm parameter: Latch | 22718 | 22719 | Parameters - Engine - Maintenance - Service timer - Configuration - Flags - Service timer 2 | X |  | X | X | X
Alarm parameter: Latch | 22719 | 22720 | Parameters - Engine - Maintenance - Service timer - Configuration - Flags - Service timer 3 | X |  | X | X | X
Alarm parameter: Latch | 22720 | 22721 | Parameters - Engine - Maintenance - Service timer - Configuration - Flags - Service timer 4 | X |  | X | X | X
Alarm parameter: Latch | 22721 | 22722 | External MB open failure | X | X | X | X | X | X | X
Alarm parameter: Latch | 22722 | 22723 | Parameters - Power management rules - Ground relay - Ground relay general failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22723 | 22724 | Parameters - Power management rules - Ground relay - Ground relay open failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22724 | 22725 | Parameters - Power management rules - Ground relay - Ground relay close failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22725 | 22726 | Parameters - Power management rules - Ground relay - Ground relay position failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22726 | 22727 | Parameters - Breakers - Close before excitation - CBE rerun failure - Configuration - Flags | X |  | X | X | X
Alarm parameter: Latch | 22727 | 22728 | Parameters - Breakers - Close before excitation - CBE failure - Configuration - Flags - Close before excitation failure | X |  | X | X | X
Alarm parameter: Latch | 22728 | 22729 | Load too high | X | X | X | X | X | X | X
Alarm parameter: Latch | 22729 | 22730 | ID to run configuration failure | [5 empty] | X | X
Alarm parameter: Latch | 22731 | 22732 | Parameters - System - Monitoring - Missing any genset controller - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22732 | 22733 | Parameters - System - Monitoring - Missing any mains controller - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22733 | 22734 | Parameters - System - Monitoring - Missing any bustie controller - Configuration - Flags - Missing any bus tie controller | X | X | X | X | X | X | X
Alarm parameter: Latch | 22734 | 22735 | Can ID not available | X | X | X | X | X | X | X
Alarm parameter: Latch | 22735 | 22736 | Duplicated CAN IDs | X | X | X | X | X | X | X
Alarm parameter: Latch | 22736 | 22737 | Parameters - Local power management - Alarms - Busbar blocked - Configuration - Flags - Busbar blocked due to position failure | X |  | X | X | X | X | X
Alarm parameter: Latch | 22737 | 22738 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Configuration - Flags - Busbar A blocked due to position failure |  | X
Alarm parameter: Latch | 22738 | 22739 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Configuration - Flags - Busbar B blocked due to position failure |  | X
Alarm parameter: Latch | 22739 | 22740 | Parameters - System - Monitoring - BTB 33 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22740 | 22741 | Parameters - System - Monitoring - BTB 34 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22741 | 22742 | Parameters - System - Monitoring - BTB 35 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22742 | 22743 | Parameters - System - Monitoring - BTB 36 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22743 | 22744 | Parameters - System - Monitoring - BTB 37 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22744 | 22745 | Parameters - System - Monitoring - BTB 38 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22745 | 22746 | Parameters - System - Monitoring - BTB 39 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22746 | 22747 | Parameters - System - Monitoring - BTB 40 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22747 | 22748 | Primary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22748 | 22749 | Primary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22749 | 22750 | Primary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22750 | 22751 | Primary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22751 | 22752 | Primary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22752 | 22753 | Primary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22753 | 22754 | Primary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22754 | 22755 | Primary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22755 | 22756 | Primary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22756 | 22757 | Primary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22757 | 22758 | Primary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22758 | 22759 | Primary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22759 | 22760 | Primary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22760 | 22761 | Primary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22761 | 22762 | Primary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22762 | 22763 | Primary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22763 | 22764 | Primary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22764 | 22765 | Primary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22765 | 22766 | Primary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22766 | 22767 | Primary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22767 | 22768 | Primary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22768 | 22769 | Primary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22769 | 22770 | Primary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22770 | 22771 | Primary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22771 | 22772 | Primary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22772 | 22773 | Primary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22773 | 22774 | Primary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22774 | 22775 | Primary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22775 | 22776 | Primary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22776 | 22777 | Primary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22777 | 22778 | Primary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22778 | 22779 | Primary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22779 | 22780 | Primary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22780 | 22781 | Primary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22781 | 22782 | Primary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22782 | 22783 | Primary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22783 | 22784 | Primary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22784 | 22785 | Primary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22785 | 22786 | Primary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22786 | 22787 | Primary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22787 | 22788 | Secondary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22788 | 22789 | Secondary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22789 | 22790 | Secondary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22790 | 22791 | Secondary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22791 | 22792 | Secondary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22792 | 22793 | Secondary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22793 | 22794 | Secondary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22794 | 22795 | Secondary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22795 | 22796 | Secondary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22796 | 22797 | Secondary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22797 | 22798 | Secondary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22798 | 22799 | Secondary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22799 | 22800 | Secondary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22800 | 22801 | Secondary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22801 | 22802 | Secondary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22802 | 22803 | Secondary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22803 | 22804 | Secondary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22804 | 22805 | Secondary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22805 | 22806 | Secondary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22806 | 22807 | Secondary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22807 | 22808 | Secondary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22808 | 22809 | Secondary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22809 | 22810 | Secondary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22810 | 22811 | Secondary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22811 | 22812 | Secondary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22812 | 22813 | Secondary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22813 | 22814 | Secondary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22814 | 22815 | Secondary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22815 | 22816 | Secondary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22816 | 22817 | Secondary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22817 | 22818 | Secondary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22818 | 22819 | Secondary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22819 | 22820 | Secondary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22820 | 22821 | Secondary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22821 | 22822 | Secondary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22822 | 22823 | Secondary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22823 | 22824 | Secondary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22824 | 22825 | Secondary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22825 | 22826 | Secondary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22826 | 22827 | Secondary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm parameter: Latch | 22827 | 22828 | Priority error | X | X | X | X | X | X | X
Alarm parameter: Latch | 22828 | 22829 | Parameters - Non-essential load trip - Trip 1 - Over-current - Configuration - Flags - NEL 1 over-current | X |  | X | X | X | X | X
Alarm parameter: Latch | 22829 | 22830 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Configuration - Flags - NEL 1 under-frequency | X |  | X | X | X | X | X
Alarm parameter: Latch | 22830 | 22831 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Configuration - Flags - NEL 1 overload 1 | X |  | X | X | X | X | X
Alarm parameter: Latch | 22831 | 22832 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Configuration - Flags - NEL 1 overload 2 | X |  | X | X | X | X | X
Alarm parameter: Latch | 22832 | 22833 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Configuration - Flags - NEL 1 reactive overload | X |  | X | X | X | X | X
Alarm parameter: Latch | 22833 | 22834 | Parameters - Non-essential load trip - Trip 2 - Over-current - Configuration - Flags - NEL 2 over-current | X |  | X | X | X | X | X
Alarm parameter: Latch | 22834 | 22835 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Configuration - Flags - NEL 2 under-frequency | X |  | X | X | X | X | X
Alarm parameter: Latch | 22835 | 22836 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Configuration - Flags - NEL 2 overload 1 | X |  | X | X | X | X | X
Alarm parameter: Latch | 22836 | 22837 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Configuration - Flags - NEL 2 overload 2 | X |  | X | X | X | X | X
Alarm parameter: Latch | 22837 | 22838 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Configuration - Flags - NEL 2 reactive overload | X |  | X | X | X | X | X
Alarm parameter: Latch | 22838 | 22839 | Parameters - Non-essential load trip - Trip 3 - Over-current - Configuration - Flags - NEL 3 over-current | X |  | X | X | X | X | X
Alarm parameter: Latch | 22839 | 22840 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Configuration - Flags - NEL 3 under-frequency | X |  | X | X | X | X | X
Alarm parameter: Latch | 22840 | 22841 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Configuration - Flags - NEL 3 overload 1 | X |  | X | X | X | X | X
Alarm parameter: Latch | 22841 | 22842 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Configuration - Flags - NEL 3 overload 2 | X |  | X | X | X | X | X
Alarm parameter: Latch | 22842 | 22843 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Configuration - Flags - NEL 3 reactive overload | X |  | X | X | X | X | X
Alarm parameter: Latch | 22843 | 22844 | Parameters - System - Monitoring - Single-line hazard - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22844 | 22845 | ID not present | X | X | X | X | X | X | X
Alarm parameter: Latch | 22845 | 22846 | Unsupported application | X | X | X | X | X | X | X
Alarm parameter: Latch | 22846 | 22847 | Application internal CAN protocol conflict | X | X | X | X | X | X | X
Alarm parameter: Latch | 22847 | 22848 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Configuration - Flags - Section P> | X | X | X | X | X | X | X
Alarm parameter: Latch | 22848 | 22849 | Dry mode: Voltage level unexpected | X |  | X | X | X
Alarm parameter: Latch | 22849 | 22850 | Invalid DAVR configuration | X |  | X | X | X
Alarm parameter: Latch | 22850 | 22851 | Parameters - Communication - DEIF network - DEIF network fork detected - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22852 | 22853 | Parameters - Communication - DEIF network - DEIF network has only one connection - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22854 | 22855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Configuration - Flags - Breaker vector mismatch | X |  | X | X | X
Alarm parameter: Latch | 22854 | 22855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Configuration - Flags - Breaker vector mismatch |  | X
Alarm parameter: Latch | 22854 | 22855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Flags - Breaker vector mismatch | [5 empty] | X | X
Alarm parameter: Latch | 22855 | 22856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Flags - Breaker vector mismatch |  |  |  | X
Alarm parameter: Latch | 22855 | 22856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Configuration - Flags - Breaker vector mismatch | [6 empty] | X
Alarm parameter: Latch | 22857 | 22858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22858 | 22859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22859 | 22860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22860 | 22861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22861 | 22862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Configuration - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Latch | 22862 | 22863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Configuration - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Latch | 22863 | 22864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Configuration - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Latch | 22864 | 22865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Configuration - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Latch | 22865 | 22866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Configuration - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Latch | 22866 | 22867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Configuration - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Latch | 22867 | 22868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Configuration - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Latch | 22868 | 22869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Configuration - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm parameter: Latch | 22869 | 22870 | AC protections not running | X | X | X | X | X | X | X
Alarm parameter: Latch | 22870 | 22871 | AC data is missing | X | X | X | X | X | X | X
Alarm parameter: Latch | 22871 | 22872 | AC protections not running | X | X | X | X | X | X | X
Alarm parameter: Latch | 22872 | 22873 | AC data is missing | X | X | X | X | X | X | X
Alarm parameter: Latch | 22873 | 22874 | AC protections not running | X | X | X | X | X | X | X
Alarm parameter: Latch | 22874 | 22875 | AC data is missing | X | X | X | X | X | X | X
Alarm parameter: Latch | 22875 | 22876 | AC protections not running | X | X | X | X | X | X | X
Alarm parameter: Latch | 22876 | 22877 | AC data is missing | X | X | X | X | X | X | X
Alarm parameter: Latch | 22877 | 22878 | Live voltage detected | X | X | X | X | X | X | X
Alarm parameter: Latch | 22878 | 22879 | Internal issue detected. A restart is required soon! | X | X | X | X | X | X | X
Alarm parameter: Latch | 22879 | 22880 | Parameters - System - Monitoring - Missing controllers - Configuration - Flags | X | X | X | X | X | X | X
Alarm parameter: Latch | 22880 | 22881 | Card issue detected | X | X | X | X | X | X | X
Alarm parameter: Latch | 22881 | 22882 | Card configuration failed | X | X | X | X | X | X | X
Alarm parameter: Latch | 22882 | 22883 | Unknown traffic on DEIF network | X | X | X | X | X | X | X
Alarm parameter: Latch | 22883 | 22884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Configuration - Flags - Fill failure | X |  | X | X | X
Alarm parameter: Latch | 22884 | 22885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Configuration - Flags - Fill failure | X |  | X | X | X
Alarm parameter: Latch | 22885 | 22886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Configuration - Flags - Fill failure | X |  | X | X | X
Alarm parameter: Latch | 22886 | 22887 | Local IO service error | X | X | X | X | X | X | X
Alarm parameter: Latch | 22887 | 22888 | App logging failure | X | X | X | X | X | X | X
Alarm parameter: Latch | 22888 | 22889 | Event logging failure | X | X | X | X | X | X | X
Alarm parameter: Latch | 22889 | 22890 | Licence error | X | X | X | X | X | X | X
Alarm parameter: Latch | 22890 | 22891 | Brightness is dimmed according to temperature | X | X | X | X | X | X | X
Alarm parameter: Latch | 22891 | 22892 | Parameters - Grid code - Mains sync inhibit - Configuration - Flags |  |  | X | X
Alarm parameter: Latch | 22892 | 22893 | Parameters - Grid code - Capability curve - Import protection - Configuration - Flags - Power import capability curve protection |  |  | X | X
Alarm parameter: Latch | 22893 | 22894 | Parameters - Grid code - Capability curve - Export protection - Configuration - Flags - Power export capability curve protection |  |  | X | X
Alarm parameter: Latch | 22894 | 22895 | Hardware is not compatible based on module versions | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24000 | 24001 | Application initialisation error | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24001 | 24002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24002 | 24003 | Preliminary software | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24003 | 24004 | Parameters - Engine - Stop sequence - Stop failure - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24004 | 24005 | Parameters - Engine - Start sequence - Start failure - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24005 | 24006 | Parameters - Engine - Start sequence - Crank failure - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24006 | 24007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24007 | 24008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24008 | 24009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24009 | 24010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24010 | 24011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Commands - Magnetic pickup wire break alarm | X |  | X | X | X
Alarm action: Acknowledge alarm | 24011 | 24012 | Parameters - Engine - Stop sequence - Externally stopped - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24013 | 24014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24014 | 24015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24015 | 24016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24016 | 24017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24017 | 24018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24018 | 24019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24019 | 24020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24020 | 24021 | Parameters - Engine - Protections - Level - Coolant level 1 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24021 | 24022 | Parameters - Engine - Protections - Level - Coolant level 2 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24022 | 24023 | Parameters - Engine - Protections - Level - Coolant level 3 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24027 | 24028 | Parameters - Engine - Running detection - Primary running feedback failure - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24041 | 24042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Commands - GB closing failure | X |  | X | X | X
Alarm action: Acknowledge alarm | 24041 | 24042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Commands - BTB closing failure |  | X
Alarm action: Acknowledge alarm | 24041 | 24042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Commands - MB closing failure | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24042 | 24043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Commands - GB opening failure | X |  | X | X | X
Alarm action: Acknowledge alarm | 24042 | 24043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Commands - BTB opening failure |  | X
Alarm action: Acknowledge alarm | 24042 | 24043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Commands - MB opening failure | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24043 | 24044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Commands - GB position failure | X |  | X | X | X
Alarm action: Acknowledge alarm | 24043 | 24044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Commands - BTB position failure |  | X
Alarm action: Acknowledge alarm | 24043 | 24044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Commands - MB position failure | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24044 | 24045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Commands - GB configuration failure | X |  | X | X | X
Alarm action: Acknowledge alarm | 24044 | 24045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Commands - BTB configuration failure |  | X
Alarm action: Acknowledge alarm | 24044 | 24045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Commands - MB configuration failure | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24045 | 24046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Commands - GB synchronisation failure | X |  | X | X | X
Alarm action: Acknowledge alarm | 24045 | 24046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Commands - BTB synchronisation failure |  | X
Alarm action: Acknowledge alarm | 24045 | 24046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Commands - MB synchronisation failure | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24046 | 24047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Commands - GB de-load failure | X |  | X | X | X
Alarm action: Acknowledge alarm | 24046 | 24047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Commands - BTB de-load failure |  | X
Alarm action: Acknowledge alarm | 24046 | 24047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Commands - MB de-load failure | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24047 | 24048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Commands - GB tripped (external) | X |  | X | X | X
Alarm action: Acknowledge alarm | 24047 | 24048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Commands - BTB tripped (external) |  | X
Alarm action: Acknowledge alarm | 24047 | 24048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Commands - MB tripped (external) | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24048 | 24049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Commands - GB short circuit | X |  | X | X | X
Alarm action: Acknowledge alarm | 24048 | 24049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Commands - BTB short circuit |  | X
Alarm action: Acknowledge alarm | 24048 | 24049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Commands - MB short circuit | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24049 | 24050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Commands - MB closing failure |  |  |  | X
Alarm action: Acknowledge alarm | 24049 | 24050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Commands - TB closing failure | [6 empty] | X
Alarm action: Acknowledge alarm | 24050 | 24051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Commands - MB opening failure |  |  |  | X
Alarm action: Acknowledge alarm | 24050 | 24051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Commands - TB opening failure | [6 empty] | X
Alarm action: Acknowledge alarm | 24051 | 24052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Commands - MB position failure |  |  |  | X
Alarm action: Acknowledge alarm | 24051 | 24052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Commands - TB position failure | [6 empty] | X
Alarm action: Acknowledge alarm | 24052 | 24053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Commands - MB configuration failure |  |  |  | X
Alarm action: Acknowledge alarm | 24052 | 24053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Commands - TB configuration failure | [6 empty] | X
Alarm action: Acknowledge alarm | 24053 | 24054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Commands - MB synchronisation failure |  |  |  | X
Alarm action: Acknowledge alarm | 24053 | 24054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Commands - TB synchronisation failure | [6 empty] | X
Alarm action: Acknowledge alarm | 24054 | 24055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Commands - MB de-load failure |  |  |  | X
Alarm action: Acknowledge alarm | 24054 | 24055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Commands - TB de-load failure | [6 empty] | X
Alarm action: Acknowledge alarm | 24055 | 24056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Commands - MB tripped (external) |  |  |  | X
Alarm action: Acknowledge alarm | 24055 | 24056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Commands - TB tripped (external) | [6 empty] | X
Alarm action: Acknowledge alarm | 24056 | 24057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Commands - MB short circuit |  |  |  | X
Alarm action: Acknowledge alarm | 24056 | 24057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Commands - TB short circuit | [6 empty] | X
Alarm action: Acknowledge alarm | 24060 | 24061 | Parameters - Mains - AC setup - Phase sequence error - Commands - Mains phase sequence error |  |  | X | X
Alarm action: Acknowledge alarm | 24060 | 24061 | Parameters - Busbar - AC setup - Phase sequence error - Commands - Busbar phase sequence error | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24060 | 24061 | Parameters - Busbar B - AC setup - Phase sequence error - Commands - Busbar B phase sequence error |  | X
Alarm action: Acknowledge alarm | 24061 | 24062 | Parameters - Generator - AC setup - Phase sequence error - Commands - Generator phase sequence error | X |  | X | X | X
Alarm action: Acknowledge alarm | 24061 | 24062 | Parameters - Busbar A - AC setup - Phase sequence error - Commands - Busbar A phase sequence error |  | X
Alarm action: Acknowledge alarm | 24061 | 24062 | Parameters - Mains - AC setup - Phase sequence error - Commands - Mains phase sequence error | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24062 | 24063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24103 | 24104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Commands |  |  | X | X
Alarm action: Acknowledge alarm | 24103 | 24104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Commands | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24103 | 24104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Commands |  | X
Alarm action: Acknowledge alarm | 24104 | 24105 | Parameters - Mains - Additional protections - Vector shift - Commands |  |  | X | X
Alarm action: Acknowledge alarm | 24104 | 24105 | Parameters - Busbar - Additional protections - Vector shift - Commands | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24104 | 24105 | Parameters - Busbar B - Additional protections - Vector shift - Commands |  | X
Alarm action: Acknowledge alarm | 24105 | 24106 | Parameters - Generator - Current protections - Inverse time over-current - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24105 | 24106 | Parameters - Busbar A - Current protections - Inverse time over-current - Commands |  | X
Alarm action: Acknowledge alarm | 24105 | 24106 | Parameters - Mains - Current protections - Inverse time over-current - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24106 | 24107 | Parameters - Local - 4th current input - Earth inverse time over-current - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24107 | 24108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24108 | 24109 | Parameters - Generator - Additional protections - V< and Q< 1 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24108 | 24109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Commands |  | X
Alarm action: Acknowledge alarm | 24108 | 24109 | Parameters - Mains - Additional protections - V< and Q< 1 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24109 | 24110 | Parameters - Generator - Additional protections - V< and Q< 2 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24109 | 24110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Commands |  | X
Alarm action: Acknowledge alarm | 24109 | 24110 | Parameters - Mains - Additional protections - V< and Q< 2 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24110 | 24111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24110 | 24111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Commands |  | X
Alarm action: Acknowledge alarm | 24110 | 24111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24111 | 24112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24111 | 24112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Commands |  | X
Alarm action: Acknowledge alarm | 24111 | 24112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24115 | 24116 | Protection set point out of range | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24116 | 24117 | Parameters - Generator - Current protections - Stabilised differential current - Commands - Stabilised differential | X |  | X | X | X
Alarm action: Acknowledge alarm | 24117 | 24118 | Parameters - Generator - Current protections - High set differential current - Commands - High set differential | X |  | X | X | X
Alarm action: Acknowledge alarm | 24118 | 24119 | Protection set point out of range (differential current) | X |  | X | X | X
Alarm action: Acknowledge alarm | 24119 | 24120 | Parameters - Local - Mode - Not under remote control - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24121 | 24122 | Parameters - Local - Monitoring - System not OK - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24122 | 24123 | Configuration update delayed | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24123 | 24124 | Critical process error | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24124 | 24125 | Restore error | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24125 | 24126 | SD-card format error | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24126 | 24127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24127 | 24128 | Fieldbus configuration exceeded maximum I/O configuration | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24128 | 24129 | Parameters - Custom alarm - Custom alarm 0 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24129 | 24130 | Parameters - Custom alarm - Custom alarm 1 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24130 | 24131 | Parameters - Custom alarm - Custom alarm 2 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24131 | 24132 | Parameters - Custom alarm - Custom alarm 3 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24132 | 24133 | Parameters - Custom alarm - Custom alarm 4 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24133 | 24134 | Parameters - Custom alarm - Custom alarm 5 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24134 | 24135 | Parameters - Custom alarm - Custom alarm 6 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24135 | 24136 | Parameters - Custom alarm - Custom alarm 7 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24136 | 24137 | Parameters - Custom alarm - Custom alarm 8 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24137 | 24138 | Parameters - Custom alarm - Custom alarm 9 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24138 | 24139 | Parameters - Custom alarm - Custom alarm 10 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24139 | 24140 | Parameters - Custom alarm - Custom alarm 11 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24140 | 24141 | Parameters - Custom alarm - Custom alarm 12 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24141 | 24142 | Parameters - Custom alarm - Custom alarm 13 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24142 | 24143 | Parameters - Custom alarm - Custom alarm 14 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24143 | 24144 | Parameters - Custom alarm - Custom alarm 15 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24144 | 24145 | Parameters - Custom alarm - Custom alarm 16 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24145 | 24146 | Parameters - Custom alarm - Custom alarm 17 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24146 | 24147 | Parameters - Custom alarm - Custom alarm 18 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24147 | 24148 | Parameters - Custom alarm - Custom alarm 19 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24148 | 24149 | Parameters - Custom alarm - Custom alarm 20 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24149 | 24150 | Parameters - Custom alarm - Custom alarm 21 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24150 | 24151 | Parameters - Custom alarm - Custom alarm 22 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24151 | 24152 | Parameters - Custom alarm - Custom alarm 23 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24152 | 24153 | Parameters - Custom alarm - Custom alarm 24 - Commands - | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24153 | 24154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Commands - GOV regulation error | X |  | X | X | X
Alarm action: Acknowledge alarm | 24154 | 24155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Commands - AVR regulation error | X |  | X | X | X
Alarm action: Acknowledge alarm | 24163 | 24164 | Required hardware card(s) not found | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24164 | 24165 | Software mismatch on hardware module(s) | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24165 | 24166 | Parameters - Mains - AC setup - Multiple phase wire break - Commands - Mains L1-L2-L3 wire break |  |  | X
Alarm action: Acknowledge alarm | 24165 | 24166 | Parameters - Busbar - AC setup - Multiple phase wire break - Commands - Busbar L1-L2-L3 wire break | X |  |  |  | X | X
Alarm action: Acknowledge alarm | 24165 | 24166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Commands - Busbar B L1-L2-L3 wire break |  | X
Alarm action: Acknowledge alarm | 24166 | 24167 | Parameters - Generator - AC setup - Multiple phase wire break - Commands - Generator L1-L2-L3 wire break | X |  | X |  | X
Alarm action: Acknowledge alarm | 24166 | 24167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Commands - Busbar A L1-L2-L3 wire break |  | X
Alarm action: Acknowledge alarm | 24166 | 24167 | Parameters - Mains - AC setup - Multiple phase wire break - Commands - Mains L1-L2-L3 wire break | [5 empty] | X
Alarm action: Acknowledge alarm | 24167 | 24168 | Parameters - Mains - AC setup - L1 wire break - Commands - Mains L1 wire break |  |  | X
Alarm action: Acknowledge alarm | 24167 | 24168 | Parameters - Busbar - AC setup - L1 wire break - Commands - Busbar L1 wire break | X |  |  |  | X | X
Alarm action: Acknowledge alarm | 24167 | 24168 | Parameters - Busbar B - AC setup - L1 wire break - Commands - Busbar B L1 wire break |  | X
Alarm action: Acknowledge alarm | 24168 | 24169 | Parameters - Mains - AC setup - L2 wire break - Commands - Mains L2 wire break |  |  | X
Alarm action: Acknowledge alarm | 24168 | 24169 | Parameters - Busbar - AC setup - L2 wire break - Commands - Busbar L2 wire break | X |  |  |  | X | X
Alarm action: Acknowledge alarm | 24168 | 24169 | Parameters - Busbar B - AC setup - L2 wire break - Commands - Busbar B L2 wire break |  | X
Alarm action: Acknowledge alarm | 24169 | 24170 | Parameters - Mains - AC setup - L3 wire break - Commands - Mains L3 wire break |  |  | X
Alarm action: Acknowledge alarm | 24169 | 24170 | Parameters - Busbar - AC setup - L3 wire break - Commands - Busbar L3 wire break | X |  |  |  | X | X
Alarm action: Acknowledge alarm | 24169 | 24170 | Parameters - Busbar B - AC setup - L3 wire break - Commands - Busbar B L3 wire break |  | X
Alarm action: Acknowledge alarm | 24170 | 24171 | Parameters - Generator - AC setup - L1 wire break - Commands - Generator L1 wire break | X |  | X |  | X
Alarm action: Acknowledge alarm | 24170 | 24171 | Parameters - Busbar A - AC setup - L1 wire break - Commands - Busbar A L1 wire break |  | X
Alarm action: Acknowledge alarm | 24170 | 24171 | Parameters - Mains - AC setup - L1 wire break - Commands - Mains L1 wire break | [5 empty] | X
Alarm action: Acknowledge alarm | 24171 | 24172 | Parameters - Generator - AC setup - L2 wire break - Commands - Generator L2 wire break | X |  | X |  | X
Alarm action: Acknowledge alarm | 24171 | 24172 | Parameters - Busbar A - AC setup - L2 wire break - Commands - Busbar A L2 wire break |  | X
Alarm action: Acknowledge alarm | 24171 | 24172 | Parameters - Mains - AC setup - L2 wire break - Commands - Mains L2 wire break | [5 empty] | X
Alarm action: Acknowledge alarm | 24172 | 24173 | Parameters - Generator - AC setup - L3 wire break - Commands - Generator L3 wire break | X |  | X |  | X
Alarm action: Acknowledge alarm | 24172 | 24173 | Parameters - Busbar A - AC setup - L3 wire break - Commands - Busbar A L3 wire break |  | X
Alarm action: Acknowledge alarm | 24172 | 24173 | Parameters - Mains - AC setup - L3 wire break - Commands - Mains L3 wire break | [5 empty] | X
Alarm action: Acknowledge alarm | 24178 | 24179 | Parameters - Mains - AC setup - Supervision alarm - Commands - Mains supervision alarm |  |  | X | X |  | X | X
Alarm action: Acknowledge alarm | 24179 | 24180 | Parameters - Engine - Emergency stop - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24179 | 24180 | Parameters - Busbar A - Emergency stop - Commands |  | X
Alarm action: Acknowledge alarm | 24179 | 24180 | Parameters - Mains - Emergency stop - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24180 | 24181 | Clock battery failure | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24181 | 24182 | Controller temperature too high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24182 | 24183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Commands - PSM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24183 | 24184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Commands - PSM3.1 1 supply voltage low | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24184 | 24185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Commands - PSM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24185 | 24186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Commands - PSM3.2 1 supply voltage low | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24186 | 24187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Commands - PSM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24187 | 24188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Commands - PSM3.2 2 supply voltage low | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24188 | 24189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Commands - PSM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24189 | 24190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Commands - PSM3.2 3 supply voltage low | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24190 | 24191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Commands - EIM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24191 | 24192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Commands - EIM3.1 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24192 | 24193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Commands - EIM3.1 2 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24193 | 24194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Commands - EIM3.1 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24194 | 24195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Commands - EIM3.1 3 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24195 | 24196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Commands - EIM3.1 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24196 | 24197 | EIM3.1 4 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24197 | 24198 | EIM3.1 4 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24198 | 24199 | EIM3.1 5 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24199 | 24200 | EIM3.1 5 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24200 | 24201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Commands - EIM3.1 1 relay 4 wire break | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24201 | 24202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Commands - EIM3.1 2 relay 4 wire break | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24202 | 24203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Commands - EIM3.1 3 relay 4 wire break | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24203 | 24204 | EIM3.1 4 relay 4 wire break | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24204 | 24205 | EIM3.1 5 relay 4 wire break | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24205 | 24206 | AC protections not running | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24206 | 24207 | AC data is missing | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24207 | 24208 | AC protections not running (differential current) | X |  | X | X | X
Alarm action: Acknowledge alarm | 24208 | 24209 | AC data is missing (differential current) | X |  | X | X | X
Alarm action: Acknowledge alarm | 24209 | 24210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Commands - GAM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24210 | 24211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Commands - GAM3.2 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24211 | 24212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Commands - GAM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24212 | 24213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Commands - GAM3.2 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24213 | 24214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Commands - GAM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24214 | 24215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Commands - GAM3.2 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24215 | 24216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Commands - PSM3.2 4 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24216 | 24217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Commands - PSM3.2 4 supply voltage low | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24217 | 24218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Commands - PSM3.2 5 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24218 | 24219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Commands - PSM3.2 5 supply voltage low | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24219 | 24220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Commands - PSM3.2 6 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24220 | 24221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Commands - PSM3.2 6 supply voltage low | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24221 | 24222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Commands - PSM3.2 7 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24222 | 24223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Commands - PSM3.2 7 supply voltage low | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24223 | 24224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Commands - PSM3.2 8 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24224 | 24225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Commands - PSM3.2 8 supply voltage low | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24225 | 24226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Commands - PSM3.2 9 supply voltage high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24226 | 24227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Commands - PSM3.2 9 supply voltage low | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24228 | 24229 | Parameters - System - Monitoring - Duplicate controller ID - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24229 | 24230 | Parameters - System - Monitoring - Missing all controllers - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24231 | 24232 | Controller ID not configured | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24236 | 24237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24237 | 24238 | Blackout detection mismatch | X |  | X | X | X
Alarm action: Acknowledge alarm | 24240 | 24241 | Parameters - Communication - NTP - NTP server 1 not connected - Commands - NTP server 1 could not connect | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24241 | 24242 | Parameters - Communication - NTP - NTP server 1 no response - Commands - NTP server 1 is not responding | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24242 | 24243 | Parameters - Communication - NTP - NTP server 2 not connected - Commands - NTP server 2 could not connect | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24243 | 24244 | Parameters - Communication - NTP - NTP server 2 no response - Commands - NTP server 2 is not responding | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24244 | 24245 | Parameters - Communication - NTP - No NTP server time synchronisation - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24245 | 24246 | Parameters - Communication - NTP - No NTP server(s) connected - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24246 | 24247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24247 | 24248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24296 | 24297 | Controller not part of system | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24297 | 24298 | Different single-line configurations | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24298 | 24299 | Single-line missing/none active | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24299 | 24300 | Parameters - Communication - Modbus - Modbus communication timeout - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24300 | 24301 | Parameters - CODESYS - Monitoring - I/O config conflict - Commands - CODESYS configuration conflict | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24301 | 24302 | Parameters - CODESYS - Monitoring - Application not OK - Commands - CODESYS application not OK | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24302 | 24303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24303 | 24304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24304 | 24305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24305 | 24306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24306 | 24307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24307 | 24308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24308 | 24309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24309 | 24310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24310 | 24311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24311 | 24312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24312 | 24313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24313 | 24314 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24314 | 24315 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24315 | 24316 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24316 | 24317 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24317 | 24318 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24318 | 24319 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24319 | 24320 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24320 | 24321 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24321 | 24322 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24322 | 24323 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24323 | 24324 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24324 | 24325 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24325 | 24326 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24326 | 24327 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24327 | 24328 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24328 | 24329 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24329 | 24330 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24330 | 24331 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24331 | 24332 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24332 | 24333 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24333 | 24334 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24334 | 24335 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24335 | 24336 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24336 | 24337 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24337 | 24338 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24338 | 24339 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24339 | 24340 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24340 | 24341 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24341 | 24342 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24342 | 24343 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24343 | 24344 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24344 | 24345 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24345 | 24346 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24346 | 24347 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24347 | 24348 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24348 | 24349 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24349 | 24350 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24350 | 24351 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24351 | 24352 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24352 | 24353 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24353 | 24354 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24354 | 24355 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24355 | 24356 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24356 | 24357 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24357 | 24358 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24358 | 24359 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24359 | 24360 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24360 | 24361 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24361 | 24362 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24362 | 24363 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24363 | 24364 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24364 | 24365 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24365 | 24366 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24366 | 24367 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24367 | 24368 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24368 | 24369 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24369 | 24370 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24370 | 24371 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24371 | 24372 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24372 | 24373 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24373 | 24374 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24374 | 24375 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24375 | 24376 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24376 | 24377 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24377 | 24378 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24378 | 24379 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24379 | 24380 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24380 | 24381 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24381 | 24382 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24382 | 24383 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24383 | 24384 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24384 | 24385 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24385 | 24386 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24386 | 24387 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24387 | 24388 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24388 | 24389 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24389 | 24390 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24390 | 24391 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24391 | 24392 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24392 | 24393 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24393 | 24394 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24394 | 24395 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24395 | 24396 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24396 | 24397 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24397 | 24398 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24398 | 24399 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24399 | 24400 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24400 | 24401 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24401 | 24402 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24402 | 24403 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24403 | 24404 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24404 | 24405 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24405 | 24406 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24406 | 24407 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24407 | 24408 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24408 | 24409 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24409 | 24410 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24410 | 24411 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24411 | 24412 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24412 | 24413 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24413 | 24414 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24414 | 24415 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24415 | 24416 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24416 | 24417 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24417 | 24418 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24418 | 24419 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24419 | 24420 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24420 | 24421 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24421 | 24422 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24422 | 24423 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24423 | 24424 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24424 | 24425 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24425 | 24426 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24426 | 24427 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24427 | 24428 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24428 | 24429 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24429 | 24430 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24430 | 24431 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24431 | 24432 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24432 | 24433 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24433 | 24434 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24434 | 24435 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24435 | 24436 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24436 | 24437 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24437 | 24438 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24438 | 24439 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24439 | 24440 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24440 | 24441 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24441 | 24442 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24442 | 24443 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24443 | 24444 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24444 | 24445 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24445 | 24446 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24446 | 24447 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24447 | 24448 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24448 | 24449 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24449 | 24450 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24450 | 24451 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24451 | 24452 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24452 | 24453 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24453 | 24454 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24454 | 24455 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24455 | 24456 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24456 | 24457 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24457 | 24458 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24458 | 24459 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24459 | 24460 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24460 | 24461 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24461 | 24462 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24462 | 24463 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24463 | 24464 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24464 | 24465 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24465 | 24466 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24466 | 24467 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24467 | 24468 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24468 | 24469 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24469 | 24470 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24470 | 24471 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24471 | 24472 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24472 | 24473 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24473 | 24474 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24474 | 24475 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24475 | 24476 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24476 | 24477 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24477 | 24478 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24478 | 24479 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24479 | 24480 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24480 | 24481 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24481 | 24482 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24482 | 24483 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24483 | 24484 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24484 | 24485 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24485 | 24486 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24486 | 24487 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24487 | 24488 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24488 | 24489 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24489 | 24490 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24490 | 24491 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24491 | 24492 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24492 | 24493 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24493 | 24494 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24494 | 24495 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24495 | 24496 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24496 | 24497 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24497 | 24498 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24498 | 24499 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24499 | 24500 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24500 | 24501 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24501 | 24502 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24502 | 24503 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24503 | 24504 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24504 | 24505 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24505 | 24506 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24506 | 24507 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24507 | 24508 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24508 | 24509 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24509 | 24510 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24510 | 24511 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24511 | 24512 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24512 | 24513 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24513 | 24514 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24514 | 24515 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24515 | 24516 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24516 | 24517 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24517 | 24518 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24518 | 24519 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24519 | 24520 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24520 | 24521 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24521 | 24522 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24522 | 24523 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24523 | 24524 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24524 | 24525 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24525 | 24526 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24526 | 24527 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24527 | 24528 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24528 | 24529 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24529 | 24530 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24530 | 24531 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24531 | 24532 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24532 | 24533 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24533 | 24534 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24534 | 24535 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24535 | 24536 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24536 | 24537 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24537 | 24538 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24538 | 24539 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24539 | 24540 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24540 | 24541 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24541 | 24542 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24542 | 24543 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24543 | 24544 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24544 | 24545 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24545 | 24546 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24546 | 24547 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24547 | 24548 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24548 | 24549 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24549 | 24550 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24550 | 24551 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24551 | 24552 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24552 | 24553 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24553 | 24554 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24554 | 24555 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24555 | 24556 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24556 | 24557 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24557 | 24558 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24558 | 24559 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24559 | 24560 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24560 | 24561 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24561 | 24562 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24562 | 24563 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24565 | 24566 | Parameters - Local - CustomLogic - Configuration invalid - Commands - CustomLogic configuration invalid | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24566 | 24567 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Commands - Digital AVR communication error | X |  | X | X | X
Alarm action: Acknowledge alarm | 24567 | 24568 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24568 | 24569 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24569 | 24570 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24570 | 24571 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24571 | 24572 | Parameters - Generator - Digital AVR - Alarms - Open diode - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24572 | 24573 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24573 | 24574 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24574 | 24575 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24575 | 24576 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24576 | 24577 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24577 | 24578 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24578 | 24579 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24579 | 24580 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24580 | 24581 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24581 | 24582 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24582 | 24583 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24583 | 24584 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24584 | 24585 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24585 | 24586 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24586 | 24587 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24587 | 24588 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24588 | 24589 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24589 | 24590 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24590 | 24591 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24591 | 24592 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24592 | 24593 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24593 | 24594 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24594 | 24595 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24595 | 24596 | Parameters - Generator - Digital AVR - Alarms - Motor start - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24596 | 24597 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24597 | 24598 | Parameters - Generator - Digital AVR - Alarms - Power supply - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24598 | 24599 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24599 | 24600 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24600 | 24601 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24601 | 24602 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24602 | 24603 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24603 | 24604 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24604 | 24605 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24605 | 24606 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24606 | 24607 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24607 | 24608 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24608 | 24609 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24609 | 24610 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24610 | 24611 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24611 | 24612 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24612 | 24613 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24613 | 24614 | DAVR unsupported AC configuration | X |  | X | X | X
Alarm action: Acknowledge alarm | 24614 | 24615 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Commands - Illegal DAVR configuration | X |  | X | X | X
Alarm action: Acknowledge alarm | 24615 | 24616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Commands - Generator under-voltage 1 | X |  | X | X | X
Alarm action: Acknowledge alarm | 24615 | 24616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Commands - Busbar A under-voltage 1 |  | X
Alarm action: Acknowledge alarm | 24615 | 24616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Commands - Mains under-voltage 1 | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24616 | 24617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Commands - Generator under-voltage 2 | X |  | X | X | X
Alarm action: Acknowledge alarm | 24616 | 24617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Commands - Busbar A under-voltage 2 |  | X
Alarm action: Acknowledge alarm | 24616 | 24617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Commands - Mains under-voltage 2 | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24617 | 24618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Commands - Generator under-voltage 3 | X |  | X | X | X
Alarm action: Acknowledge alarm | 24617 | 24618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Commands - Busbar A under-voltage 3 |  | X
Alarm action: Acknowledge alarm | 24617 | 24618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Commands - Mains under-voltage 3 | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24618 | 24619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Commands - Generator over-voltage 1 | X |  | X | X | X
Alarm action: Acknowledge alarm | 24618 | 24619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Commands - Busbar A over-voltage 1 |  | X
Alarm action: Acknowledge alarm | 24618 | 24619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Commands - Mains over-voltage 1 | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24619 | 24620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Commands - Generator over-voltage 2 | X |  | X | X | X
Alarm action: Acknowledge alarm | 24619 | 24620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Commands - Busbar A over-voltage 2 |  | X
Alarm action: Acknowledge alarm | 24619 | 24620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Commands - Mains over-voltage 2 | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24620 | 24621 | Parameters - Generator - Voltage protections - Voltage unbalance - Commands - Generator voltage unbalance | X |  | X | X | X
Alarm action: Acknowledge alarm | 24620 | 24621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Commands - Busbar A voltage unbalance |  | X
Alarm action: Acknowledge alarm | 24620 | 24621 | Parameters - Mains - Voltage protections - Voltage unbalance - Commands - Mains voltage unbalance | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24621 | 24622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Commands - Generator negative sequence voltage | X |  | X | X | X
Alarm action: Acknowledge alarm | 24621 | 24622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Commands - Busbar A negative sequence voltage |  | X
Alarm action: Acknowledge alarm | 24621 | 24622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Commands - Mains negative sequence voltage | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24622 | 24623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Commands - Generator zero sequence voltage | X |  | X | X | X
Alarm action: Acknowledge alarm | 24622 | 24623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Commands - Busbar A zero sequence voltage |  | X
Alarm action: Acknowledge alarm | 24622 | 24623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Commands - Mains zero sequence voltage | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24623 | 24624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Commands - Generator positive sequence under-voltage | X |  | X | X | X
Alarm action: Acknowledge alarm | 24623 | 24624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Commands - Busbar A positive sequence under-voltage |  | X
Alarm action: Acknowledge alarm | 24623 | 24624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Commands - Mains positive sequence under-voltage | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24624 | 24625 | Parameters - Generator - Current protections - Over-current 1 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24624 | 24625 | Parameters - Busbar A - Current protections - Over-current 1 - Commands |  | X
Alarm action: Acknowledge alarm | 24624 | 24625 | Parameters - Mains - Current protections - Over-current 1 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24625 | 24626 | Parameters - Generator - Current protections - Over-current 2 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24625 | 24626 | Parameters - Busbar A - Current protections - Over-current 2 - Commands |  | X
Alarm action: Acknowledge alarm | 24625 | 24626 | Parameters - Mains - Current protections - Over-current 2 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24626 | 24627 | Parameters - Generator - Current protections - Over-current 3 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24626 | 24627 | Parameters - Busbar A - Current protections - Over-current 3 - Commands |  | X
Alarm action: Acknowledge alarm | 24626 | 24627 | Parameters - Mains - Current protections - Over-current 3 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24627 | 24628 | Parameters - Generator - Current protections - Over-current 4 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24627 | 24628 | Parameters - Busbar A - Current protections - Over-current 4 - Commands |  | X
Alarm action: Acknowledge alarm | 24627 | 24628 | Parameters - Mains - Current protections - Over-current 4 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24628 | 24629 | Parameters - Generator - Current protections - Fast over-current 1 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24628 | 24629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Commands |  | X
Alarm action: Acknowledge alarm | 24628 | 24629 | Parameters - Mains - Current protections - Fast over-current 1 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24629 | 24630 | Parameters - Generator - Current protections - Fast over-current 2 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24629 | 24630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Commands |  | X
Alarm action: Acknowledge alarm | 24629 | 24630 | Parameters - Mains - Current protections - Fast over-current 2 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24630 | 24631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24630 | 24631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Commands |  | X
Alarm action: Acknowledge alarm | 24630 | 24631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24631 | 24632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24631 | 24632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Commands |  | X
Alarm action: Acknowledge alarm | 24631 | 24632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24632 | 24633 | Parameters - Generator - Current protections - Directional over-current 1 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24632 | 24633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Commands |  | X
Alarm action: Acknowledge alarm | 24632 | 24633 | Parameters - Mains - Current protections - Directional over-current 1 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24633 | 24634 | Parameters - Generator - Current protections - Directional over-current 2 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24633 | 24634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Commands |  | X
Alarm action: Acknowledge alarm | 24633 | 24634 | Parameters - Mains - Current protections - Directional over-current 2 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24634 | 24635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Commands |  | X
Alarm action: Acknowledge alarm | 24635 | 24636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Commands |  | X
Alarm action: Acknowledge alarm | 24636 | 24637 | Parameters - Generator - Current protections - Negative sequence current - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24636 | 24637 | Parameters - Busbar A - Current protections - Negative sequence current - Commands |  | X
Alarm action: Acknowledge alarm | 24636 | 24637 | Parameters - Mains - Current protections - Negative sequence current - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24637 | 24638 | Parameters - Generator - Current protections - Zero sequence current - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24637 | 24638 | Parameters - Busbar A - Current protections - Zero sequence current - Commands |  | X
Alarm action: Acknowledge alarm | 24637 | 24638 | Parameters - Mains - Current protections - Zero sequence current - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24638 | 24639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Commands - Generator over-frequency 1 | X |  | X | X | X
Alarm action: Acknowledge alarm | 24638 | 24639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Commands - Busbar A over-frequency 1 |  | X
Alarm action: Acknowledge alarm | 24638 | 24639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Commands - Mains over-frequency 1 | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24639 | 24640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Commands - Generator over-frequency 2 | X |  | X | X | X
Alarm action: Acknowledge alarm | 24639 | 24640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Commands - Busbar A over-frequency 2 |  | X
Alarm action: Acknowledge alarm | 24639 | 24640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Commands - Mains over-frequency 2 | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24640 | 24641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Commands - Generator over-frequency 3 | X |  | X | X | X
Alarm action: Acknowledge alarm | 24640 | 24641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Commands - Busbar A over-frequency 3 |  | X
Alarm action: Acknowledge alarm | 24640 | 24641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Commands - Mains over-frequency 3 | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24641 | 24642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Commands - Generator under-frequency 1 | X |  | X | X | X
Alarm action: Acknowledge alarm | 24641 | 24642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Commands - Busbar A under-frequency 1 |  | X
Alarm action: Acknowledge alarm | 24641 | 24642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Commands - Mains under-frequency 1 | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24642 | 24643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Commands - Generator under-frequency 2 | X |  | X | X | X
Alarm action: Acknowledge alarm | 24642 | 24643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Commands - Busbar A under-frequency 2 |  | X
Alarm action: Acknowledge alarm | 24642 | 24643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Commands - Mains under-frequency 2 | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24643 | 24644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Commands - Generator under-frequency 3 | X |  | X | X | X
Alarm action: Acknowledge alarm | 24643 | 24644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Commands - Busbar A under-frequency 3 |  | X
Alarm action: Acknowledge alarm | 24643 | 24644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Commands - Mains under-frequency 3 | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24644 | 24645 | Parameters - Generator - Power protections - Overload 1 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24644 | 24645 | Parameters - Busbar A - Power protections - Power export 1 - Commands |  | X
Alarm action: Acknowledge alarm | 24644 | 24645 | Parameters - Mains - Power protections - Overload 1 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24645 | 24646 | Parameters - Generator - Power protections - Overload 2 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24645 | 24646 | Parameters - Busbar A - Power protections - Power export 2 - Commands |  | X
Alarm action: Acknowledge alarm | 24645 | 24646 | Parameters - Mains - Power protections - Overload 2 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24646 | 24647 | Parameters - Generator - Power protections - Overload 3 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24646 | 24647 | Parameters - Busbar A - Power protections - Power export 3 - Commands |  | X
Alarm action: Acknowledge alarm | 24646 | 24647 | Parameters - Mains - Power protections - Overload 3 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24647 | 24648 | Parameters - Generator - Power protections - Overload 4 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24647 | 24648 | Parameters - Busbar A - Power protections - Power export 4 - Commands |  | X
Alarm action: Acknowledge alarm | 24647 | 24648 | Parameters - Mains - Power protections - Overload 4 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24648 | 24649 | Parameters - Generator - Power protections - Overload 5 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24648 | 24649 | Parameters - Busbar A - Power protections - Power export 5 - Commands |  | X
Alarm action: Acknowledge alarm | 24648 | 24649 | Parameters - Mains - Power protections - Overload 5 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24649 | 24650 | Parameters - Generator - Power protections - Reverse power 1 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24649 | 24650 | Parameters - Busbar A - Power protections - Power import 1 - Commands |  | X
Alarm action: Acknowledge alarm | 24649 | 24650 | Parameters - Mains - Power protections - Reverse power 1 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24650 | 24651 | Parameters - Generator - Power protections - Reverse power 2 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24650 | 24651 | Parameters - Busbar A - Power protections - Power import 2 - Commands |  | X
Alarm action: Acknowledge alarm | 24650 | 24651 | Parameters - Mains - Power protections - Reverse power 2 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24651 | 24652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24651 | 24652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Commands |  | X
Alarm action: Acknowledge alarm | 24651 | 24652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24652 | 24653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24652 | 24653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Commands |  | X
Alarm action: Acknowledge alarm | 24652 | 24653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24653 | 24654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24653 | 24654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Commands |  | X
Alarm action: Acknowledge alarm | 24653 | 24654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24654 | 24655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24654 | 24655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Commands |  | X
Alarm action: Acknowledge alarm | 24654 | 24655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Commands | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24655 | 24656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Commands - Mains over-voltage 1 |  |  | X | X
Alarm action: Acknowledge alarm | 24655 | 24656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Commands - Busbar over-voltage 1 | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24655 | 24656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Commands - Busbar B over-voltage 1 |  | X
Alarm action: Acknowledge alarm | 24656 | 24657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Commands - Mains over-voltage 2 |  |  | X | X
Alarm action: Acknowledge alarm | 24656 | 24657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Commands - Busbar over-voltage 2 | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24656 | 24657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Commands - Busbar B over-voltage 2 |  | X
Alarm action: Acknowledge alarm | 24657 | 24658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Commands - Mains over-voltage 3 |  |  | X | X
Alarm action: Acknowledge alarm | 24657 | 24658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Commands - Busbar over-voltage 3 | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24657 | 24658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Commands - Busbar B over-voltage 3 |  | X
Alarm action: Acknowledge alarm | 24658 | 24659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Commands - Mains under-voltage 1 |  |  | X | X
Alarm action: Acknowledge alarm | 24658 | 24659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Commands - Busbar under-voltage 1 | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24658 | 24659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Commands - Busbar B under-voltage 1 |  | X
Alarm action: Acknowledge alarm | 24659 | 24660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Commands - Mains under-voltage 2 |  |  | X | X
Alarm action: Acknowledge alarm | 24659 | 24660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Commands - Busbar under-voltage 2 | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24659 | 24660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Commands - Busbar B under-voltage 2 |  | X
Alarm action: Acknowledge alarm | 24660 | 24661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Commands - Mains under-voltage 3 |  |  | X | X
Alarm action: Acknowledge alarm | 24660 | 24661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Commands - Busbar under-voltage 3 | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24660 | 24661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Commands - Busbar B under-voltage 3 |  | X
Alarm action: Acknowledge alarm | 24661 | 24662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Commands - Mains under-voltage 4 |  |  | X | X
Alarm action: Acknowledge alarm | 24661 | 24662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Commands - Busbar under-voltage 4 | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24661 | 24662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Commands - Busbar B under-voltage 4 |  | X
Alarm action: Acknowledge alarm | 24662 | 24663 | Parameters - Mains - Voltage protections - Voltage unbalance - Commands - Mains voltage unbalance |  |  | X | X
Alarm action: Acknowledge alarm | 24662 | 24663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Commands - Busbar voltage unbalance | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24662 | 24663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Commands - Busbar B voltage unbalance |  | X
Alarm action: Acknowledge alarm | 24663 | 24664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Commands - Mains over-frequency 1 |  |  | X | X
Alarm action: Acknowledge alarm | 24663 | 24664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Commands - Busbar over-frequency 1 | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24663 | 24664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Commands - Busbar B over-frequency 1 |  | X
Alarm action: Acknowledge alarm | 24664 | 24665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Commands - Mains over-frequency 2 |  |  | X | X
Alarm action: Acknowledge alarm | 24664 | 24665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Commands - Busbar over-frequency 2 | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24664 | 24665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Commands - Busbar B over-frequency 2 |  | X
Alarm action: Acknowledge alarm | 24665 | 24666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Commands - Mains over-frequency 3 |  |  | X | X
Alarm action: Acknowledge alarm | 24665 | 24666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Commands - Busbar over-frequency 3 | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24665 | 24666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Commands - Busbar B over-frequency 3 |  | X
Alarm action: Acknowledge alarm | 24666 | 24667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Commands - Mains under-frequency 1 |  |  | X | X
Alarm action: Acknowledge alarm | 24666 | 24667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Commands - Busbar under-frequency 1 | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24666 | 24667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Commands - Busbar B under-frequency 1 |  | X
Alarm action: Acknowledge alarm | 24667 | 24668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Commands - Mains under-frequency 2 |  |  | X | X
Alarm action: Acknowledge alarm | 24667 | 24668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Commands - Busbar under-frequency 2 | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24667 | 24668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Commands - Busbar B under-frequency 2 |  | X
Alarm action: Acknowledge alarm | 24668 | 24669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Commands - Mains under-frequency 3 |  |  | X | X
Alarm action: Acknowledge alarm | 24668 | 24669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Commands - Busbar under-frequency 3 | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24668 | 24669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Commands - Busbar B under-frequency 3 |  | X
Alarm action: Acknowledge alarm | 24669 | 24670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Commands - Mains under-frequency 4 |  |  | X | X
Alarm action: Acknowledge alarm | 24669 | 24670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Commands - Busbar under-frequency 4 | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24669 | 24670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Commands - Busbar B under-frequency 4 |  | X
Alarm action: Acknowledge alarm | 24670 | 24671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Commands - Busbar negative sequence voltage |  |  | X | X
Alarm action: Acknowledge alarm | 24670 | 24671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Commands - Busbar negative sequence voltage | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24670 | 24671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Commands - Busbar B negative sequence voltage |  | X
Alarm action: Acknowledge alarm | 24671 | 24672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Commands - Busbar zero sequence voltage |  |  | X | X
Alarm action: Acknowledge alarm | 24671 | 24672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Commands - Busbar zero sequence voltage | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24671 | 24672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Commands - Busbar B zero sequence voltage |  | X
Alarm action: Acknowledge alarm | 24672 | 24673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Commands - Busbar positive sequence under-voltage |  |  | X | X
Alarm action: Acknowledge alarm | 24672 | 24673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Commands - Busbar positive sequence under-voltage | X |  |  |  | X | X | X
Alarm action: Acknowledge alarm | 24672 | 24673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Commands - Busbar B positive sequence under-voltage |  | X
Alarm action: Acknowledge alarm | 24717 | 24718 | Parameters - Engine - Maintenance - Service timer - Commands - Service timer 1 | X |  | X | X | X
Alarm action: Acknowledge alarm | 24718 | 24719 | Parameters - Engine - Maintenance - Service timer - Commands - Service timer 2 | X |  | X | X | X
Alarm action: Acknowledge alarm | 24719 | 24720 | Parameters - Engine - Maintenance - Service timer - Commands - Service timer 3 | X |  | X | X | X
Alarm action: Acknowledge alarm | 24720 | 24721 | Parameters - Engine - Maintenance - Service timer - Commands - Service timer 4 | X |  | X | X | X
Alarm action: Acknowledge alarm | 24721 | 24722 | External MB open failure | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24722 | 24723 | Parameters - Power management rules - Ground relay - Ground relay general failure - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24723 | 24724 | Parameters - Power management rules - Ground relay - Ground relay open failure - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24724 | 24725 | Parameters - Power management rules - Ground relay - Ground relay close failure - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24725 | 24726 | Parameters - Power management rules - Ground relay - Ground relay position failure - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24726 | 24727 | Parameters - Breakers - Close before excitation - CBE rerun failure - Commands | X |  | X | X | X
Alarm action: Acknowledge alarm | 24727 | 24728 | Parameters - Breakers - Close before excitation - CBE failure - Commands - Close before excitation failure | X |  | X | X | X
Alarm action: Acknowledge alarm | 24728 | 24729 | Load too high | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24729 | 24730 | ID to run configuration failure | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24731 | 24732 | Parameters - System - Monitoring - Missing any genset controller - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24732 | 24733 | Parameters - System - Monitoring - Missing any mains controller - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24733 | 24734 | Parameters - System - Monitoring - Missing any bustie controller - Commands - Missing any bus tie controller | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24734 | 24735 | Can ID not available | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24735 | 24736 | Duplicated CAN IDs | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24736 | 24737 | Parameters - Local power management - Alarms - Busbar blocked - Commands - Busbar blocked due to position failure | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24737 | 24738 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Commands - Busbar A blocked due to position failure |  | X
Alarm action: Acknowledge alarm | 24738 | 24739 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Commands - Busbar B blocked due to position failure |  | X
Alarm action: Acknowledge alarm | 24739 | 24740 | Parameters - System - Monitoring - BTB 33 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24740 | 24741 | Parameters - System - Monitoring - BTB 34 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24741 | 24742 | Parameters - System - Monitoring - BTB 35 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24742 | 24743 | Parameters - System - Monitoring - BTB 36 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24743 | 24744 | Parameters - System - Monitoring - BTB 37 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24744 | 24745 | Parameters - System - Monitoring - BTB 38 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24745 | 24746 | Parameters - System - Monitoring - BTB 39 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24746 | 24747 | Parameters - System - Monitoring - BTB 40 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24747 | 24748 | Primary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24748 | 24749 | Primary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24749 | 24750 | Primary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24750 | 24751 | Primary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24751 | 24752 | Primary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24752 | 24753 | Primary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24753 | 24754 | Primary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24754 | 24755 | Primary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24755 | 24756 | Primary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24756 | 24757 | Primary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24757 | 24758 | Primary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24758 | 24759 | Primary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24759 | 24760 | Primary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24760 | 24761 | Primary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24761 | 24762 | Primary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24762 | 24763 | Primary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24763 | 24764 | Primary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24764 | 24765 | Primary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24765 | 24766 | Primary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24766 | 24767 | Primary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24767 | 24768 | Primary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24768 | 24769 | Primary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24769 | 24770 | Primary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24770 | 24771 | Primary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24771 | 24772 | Primary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24772 | 24773 | Primary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24773 | 24774 | Primary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24774 | 24775 | Primary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24775 | 24776 | Primary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24776 | 24777 | Primary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24777 | 24778 | Primary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24778 | 24779 | Primary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24779 | 24780 | Primary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24780 | 24781 | Primary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24781 | 24782 | Primary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24782 | 24783 | Primary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24783 | 24784 | Primary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24784 | 24785 | Primary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24785 | 24786 | Primary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24786 | 24787 | Primary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24787 | 24788 | Secondary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24788 | 24789 | Secondary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24789 | 24790 | Secondary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24790 | 24791 | Secondary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24791 | 24792 | Secondary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24792 | 24793 | Secondary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24793 | 24794 | Secondary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24794 | 24795 | Secondary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24795 | 24796 | Secondary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24796 | 24797 | Secondary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24797 | 24798 | Secondary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24798 | 24799 | Secondary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24799 | 24800 | Secondary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24800 | 24801 | Secondary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24801 | 24802 | Secondary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24802 | 24803 | Secondary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24803 | 24804 | Secondary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24804 | 24805 | Secondary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24805 | 24806 | Secondary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24806 | 24807 | Secondary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24807 | 24808 | Secondary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24808 | 24809 | Secondary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24809 | 24810 | Secondary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24810 | 24811 | Secondary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24811 | 24812 | Secondary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24812 | 24813 | Secondary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24813 | 24814 | Secondary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24814 | 24815 | Secondary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24815 | 24816 | Secondary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24816 | 24817 | Secondary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24817 | 24818 | Secondary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24818 | 24819 | Secondary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24819 | 24820 | Secondary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24820 | 24821 | Secondary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24821 | 24822 | Secondary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24822 | 24823 | Secondary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24823 | 24824 | Secondary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24824 | 24825 | Secondary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24825 | 24826 | Secondary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24826 | 24827 | Secondary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24827 | 24828 | Priority error | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24828 | 24829 | Parameters - Non-essential load trip - Trip 1 - Over-current - Commands - NEL 1 over-current | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24829 | 24830 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Commands - NEL 1 under-frequency | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24830 | 24831 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Commands - NEL 1 overload 1 | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24831 | 24832 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Commands - NEL 1 overload 2 | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24832 | 24833 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Commands - NEL 1 reactive overload | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24833 | 24834 | Parameters - Non-essential load trip - Trip 2 - Over-current - Commands - NEL 2 over-current | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24834 | 24835 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Commands - NEL 2 under-frequency | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24835 | 24836 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Commands - NEL 2 overload 1 | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24836 | 24837 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Commands - NEL 2 overload 2 | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24837 | 24838 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Commands - NEL 2 reactive overload | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24838 | 24839 | Parameters - Non-essential load trip - Trip 3 - Over-current - Commands - NEL 3 over-current | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24839 | 24840 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Commands - NEL 3 under-frequency | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24840 | 24841 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Commands - NEL 3 overload 1 | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24841 | 24842 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Commands - NEL 3 overload 2 | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24842 | 24843 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Commands - NEL 3 reactive overload | X |  | X | X | X | X | X
Alarm action: Acknowledge alarm | 24843 | 24844 | Parameters - System - Monitoring - Single-line hazard - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24844 | 24845 | ID not present | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24845 | 24846 | Unsupported application | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24846 | 24847 | Application internal CAN protocol conflict | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24847 | 24848 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Commands - Section P> | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24848 | 24849 | Dry mode: Voltage level unexpected | X |  | X | X | X
Alarm action: Acknowledge alarm | 24849 | 24850 | Invalid DAVR configuration | X |  | X | X | X
Alarm action: Acknowledge alarm | 24850 | 24851 | Parameters - Communication - DEIF network - DEIF network fork detected - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24852 | 24853 | Parameters - Communication - DEIF network - DEIF network has only one connection - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24854 | 24855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Commands - Breaker vector mismatch | X |  | X | X | X
Alarm action: Acknowledge alarm | 24854 | 24855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Commands - Breaker vector mismatch |  | X
Alarm action: Acknowledge alarm | 24854 | 24855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Commands - Breaker vector mismatch | [5 empty] | X | X
Alarm action: Acknowledge alarm | 24855 | 24856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Commands - Breaker vector mismatch |  |  |  | X
Alarm action: Acknowledge alarm | 24855 | 24856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Commands - Breaker vector mismatch | [6 empty] | X
Alarm action: Acknowledge alarm | 24857 | 24858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24858 | 24859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24859 | 24860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24860 | 24861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24861 | 24862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Commands - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24862 | 24863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Commands - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24863 | 24864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Commands - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24864 | 24865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Commands - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24865 | 24866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Commands - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24866 | 24867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Commands - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24867 | 24868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Commands - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24868 | 24869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Commands - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24869 | 24870 | AC protections not running | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24870 | 24871 | AC data is missing | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24871 | 24872 | AC protections not running | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24872 | 24873 | AC data is missing | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24873 | 24874 | AC protections not running | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24874 | 24875 | AC data is missing | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24875 | 24876 | AC protections not running | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24876 | 24877 | AC data is missing | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24877 | 24878 | Live voltage detected | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24878 | 24879 | Internal issue detected. A restart is required soon! | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24879 | 24880 | Parameters - System - Monitoring - Missing controllers - Commands | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24880 | 24881 | Card issue detected | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24881 | 24882 | Card configuration failed | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24882 | 24883 | Unknown traffic on DEIF network | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24883 | 24884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Commands - Fill failure | X |  | X | X | X
Alarm action: Acknowledge alarm | 24884 | 24885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Commands - Fill failure | X |  | X | X | X
Alarm action: Acknowledge alarm | 24885 | 24886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Commands - Fill failure | X |  | X | X | X
Alarm action: Acknowledge alarm | 24886 | 24887 | Local IO service error | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24887 | 24888 | App logging failure | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24888 | 24889 | Event logging failure | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24889 | 24890 | Licence error | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24890 | 24891 | Brightness is dimmed according to temperature | X | X | X | X | X | X | X
Alarm action: Acknowledge alarm | 24891 | 24892 | Parameters - Grid code - Mains sync inhibit - Commands |  |  | X | X
Alarm action: Acknowledge alarm | 24892 | 24893 | Parameters - Grid code - Capability curve - Import protection - Commands - Power import capability curve protection |  |  | X | X
Alarm action: Acknowledge alarm | 24893 | 24894 | Parameters - Grid code - Capability curve - Export protection - Commands - Power export capability curve protection |  |  | X | X
Alarm action: Acknowledge alarm | 24894 | 24895 | Hardware is not compatible based on module versions | X | X | X | X | X | X | X
Alarm action: Reset latch | 26000 | 26001 | Application initialisation error | X | X | X | X | X | X | X
Alarm action: Reset latch | 26001 | 26002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm action: Reset latch | 26002 | 26003 | Preliminary software | X | X | X | X | X | X | X
Alarm action: Reset latch | 26003 | 26004 | Parameters - Engine - Stop sequence - Stop failure - Commands | X |  | X | X | X
Alarm action: Reset latch | 26004 | 26005 | Parameters - Engine - Start sequence - Start failure - Commands | X |  | X | X | X
Alarm action: Reset latch | 26005 | 26006 | Parameters - Engine - Start sequence - Crank failure - Commands | X |  | X | X | X
Alarm action: Reset latch | 26006 | 26007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26007 | 26008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26008 | 26009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26009 | 26010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26010 | 26011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Commands - Magnetic pickup wire break alarm | X |  | X | X | X
Alarm action: Reset latch | 26011 | 26012 | Parameters - Engine - Stop sequence - Externally stopped - Commands | X |  | X | X | X
Alarm action: Reset latch | 26013 | 26014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26014 | 26015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26015 | 26016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26016 | 26017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26017 | 26018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26018 | 26019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26019 | 26020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26020 | 26021 | Parameters - Engine - Protections - Level - Coolant level 1 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26021 | 26022 | Parameters - Engine - Protections - Level - Coolant level 2 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26022 | 26023 | Parameters - Engine - Protections - Level - Coolant level 3 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26027 | 26028 | Parameters - Engine - Running detection - Primary running feedback failure - Commands | X |  | X | X | X
Alarm action: Reset latch | 26041 | 26042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Commands - GB closing failure | X |  | X | X | X
Alarm action: Reset latch | 26041 | 26042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Commands - BTB closing failure |  | X
Alarm action: Reset latch | 26041 | 26042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Commands - MB closing failure | [5 empty] | X | X
Alarm action: Reset latch | 26042 | 26043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Commands - GB opening failure | X |  | X | X | X
Alarm action: Reset latch | 26042 | 26043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Commands - BTB opening failure |  | X
Alarm action: Reset latch | 26042 | 26043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Commands - MB opening failure | [5 empty] | X | X
Alarm action: Reset latch | 26043 | 26044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Commands - GB position failure | X |  | X | X | X
Alarm action: Reset latch | 26043 | 26044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Commands - BTB position failure |  | X
Alarm action: Reset latch | 26043 | 26044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Commands - MB position failure | [5 empty] | X | X
Alarm action: Reset latch | 26044 | 26045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Commands - GB configuration failure | X |  | X | X | X
Alarm action: Reset latch | 26044 | 26045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Commands - BTB configuration failure |  | X
Alarm action: Reset latch | 26044 | 26045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Commands - MB configuration failure | [5 empty] | X | X
Alarm action: Reset latch | 26045 | 26046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Commands - GB synchronisation failure | X |  | X | X | X
Alarm action: Reset latch | 26045 | 26046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Commands - BTB synchronisation failure |  | X
Alarm action: Reset latch | 26045 | 26046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Commands - MB synchronisation failure | [5 empty] | X | X
Alarm action: Reset latch | 26046 | 26047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Commands - GB de-load failure | X |  | X | X | X
Alarm action: Reset latch | 26046 | 26047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Commands - BTB de-load failure |  | X
Alarm action: Reset latch | 26046 | 26047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Commands - MB de-load failure | [5 empty] | X | X
Alarm action: Reset latch | 26047 | 26048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Commands - GB tripped (external) | X |  | X | X | X
Alarm action: Reset latch | 26047 | 26048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Commands - BTB tripped (external) |  | X
Alarm action: Reset latch | 26047 | 26048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Commands - MB tripped (external) | [5 empty] | X | X
Alarm action: Reset latch | 26048 | 26049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Commands - GB short circuit | X |  | X | X | X
Alarm action: Reset latch | 26048 | 26049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Commands - BTB short circuit |  | X
Alarm action: Reset latch | 26048 | 26049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Commands - MB short circuit | [5 empty] | X | X
Alarm action: Reset latch | 26049 | 26050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Commands - MB closing failure |  |  |  | X
Alarm action: Reset latch | 26049 | 26050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Commands - TB closing failure | [6 empty] | X
Alarm action: Reset latch | 26050 | 26051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Commands - MB opening failure |  |  |  | X
Alarm action: Reset latch | 26050 | 26051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Commands - TB opening failure | [6 empty] | X
Alarm action: Reset latch | 26051 | 26052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Commands - MB position failure |  |  |  | X
Alarm action: Reset latch | 26051 | 26052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Commands - TB position failure | [6 empty] | X
Alarm action: Reset latch | 26052 | 26053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Commands - MB configuration failure |  |  |  | X
Alarm action: Reset latch | 26052 | 26053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Commands - TB configuration failure | [6 empty] | X
Alarm action: Reset latch | 26053 | 26054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Commands - MB synchronisation failure |  |  |  | X
Alarm action: Reset latch | 26053 | 26054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Commands - TB synchronisation failure | [6 empty] | X
Alarm action: Reset latch | 26054 | 26055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Commands - MB de-load failure |  |  |  | X
Alarm action: Reset latch | 26054 | 26055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Commands - TB de-load failure | [6 empty] | X
Alarm action: Reset latch | 26055 | 26056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Commands - MB tripped (external) |  |  |  | X
Alarm action: Reset latch | 26055 | 26056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Commands - TB tripped (external) | [6 empty] | X
Alarm action: Reset latch | 26056 | 26057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Commands - MB short circuit |  |  |  | X
Alarm action: Reset latch | 26056 | 26057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Commands - TB short circuit | [6 empty] | X
Alarm action: Reset latch | 26060 | 26061 | Parameters - Mains - AC setup - Phase sequence error - Commands - Mains phase sequence error |  |  | X | X
Alarm action: Reset latch | 26060 | 26061 | Parameters - Busbar - AC setup - Phase sequence error - Commands - Busbar phase sequence error | X |  |  |  | X | X | X
Alarm action: Reset latch | 26060 | 26061 | Parameters - Busbar B - AC setup - Phase sequence error - Commands - Busbar B phase sequence error |  | X
Alarm action: Reset latch | 26061 | 26062 | Parameters - Generator - AC setup - Phase sequence error - Commands - Generator phase sequence error | X |  | X | X | X
Alarm action: Reset latch | 26061 | 26062 | Parameters - Busbar A - AC setup - Phase sequence error - Commands - Busbar A phase sequence error |  | X
Alarm action: Reset latch | 26061 | 26062 | Parameters - Mains - AC setup - Phase sequence error - Commands - Mains phase sequence error | [5 empty] | X | X
Alarm action: Reset latch | 26062 | 26063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Commands | X |  | X | X | X
Alarm action: Reset latch | 26103 | 26104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Commands |  |  | X | X
Alarm action: Reset latch | 26103 | 26104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Commands | X |  |  |  | X | X | X
Alarm action: Reset latch | 26103 | 26104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Commands |  | X
Alarm action: Reset latch | 26104 | 26105 | Parameters - Mains - Additional protections - Vector shift - Commands |  |  | X | X
Alarm action: Reset latch | 26104 | 26105 | Parameters - Busbar - Additional protections - Vector shift - Commands | X |  |  |  | X | X | X
Alarm action: Reset latch | 26104 | 26105 | Parameters - Busbar B - Additional protections - Vector shift - Commands |  | X
Alarm action: Reset latch | 26105 | 26106 | Parameters - Generator - Current protections - Inverse time over-current - Commands | X |  | X | X | X
Alarm action: Reset latch | 26105 | 26106 | Parameters - Busbar A - Current protections - Inverse time over-current - Commands |  | X
Alarm action: Reset latch | 26105 | 26106 | Parameters - Mains - Current protections - Inverse time over-current - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26106 | 26107 | Parameters - Local - 4th current input - Earth inverse time over-current - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26107 | 26108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26108 | 26109 | Parameters - Generator - Additional protections - V< and Q< 1 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26108 | 26109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Commands |  | X
Alarm action: Reset latch | 26108 | 26109 | Parameters - Mains - Additional protections - V< and Q< 1 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26109 | 26110 | Parameters - Generator - Additional protections - V< and Q< 2 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26109 | 26110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Commands |  | X
Alarm action: Reset latch | 26109 | 26110 | Parameters - Mains - Additional protections - V< and Q< 2 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26110 | 26111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26110 | 26111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Commands |  | X
Alarm action: Reset latch | 26110 | 26111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26111 | 26112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26111 | 26112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Commands |  | X
Alarm action: Reset latch | 26111 | 26112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26115 | 26116 | Protection set point out of range | X | X | X | X | X | X | X
Alarm action: Reset latch | 26116 | 26117 | Parameters - Generator - Current protections - Stabilised differential current - Commands - Stabilised differential | X |  | X | X | X
Alarm action: Reset latch | 26117 | 26118 | Parameters - Generator - Current protections - High set differential current - Commands - High set differential | X |  | X | X | X
Alarm action: Reset latch | 26118 | 26119 | Protection set point out of range (differential current) | X |  | X | X | X
Alarm action: Reset latch | 26119 | 26120 | Parameters - Local - Mode - Not under remote control - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26121 | 26122 | Parameters - Local - Monitoring - System not OK - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26122 | 26123 | Configuration update delayed | X | X | X | X | X | X | X
Alarm action: Reset latch | 26123 | 26124 | Critical process error | X | X | X | X | X | X | X
Alarm action: Reset latch | 26124 | 26125 | Restore error | X | X | X | X | X | X | X
Alarm action: Reset latch | 26125 | 26126 | SD-card format error | X | X | X | X | X | X | X
Alarm action: Reset latch | 26126 | 26127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm action: Reset latch | 26127 | 26128 | Fieldbus configuration exceeded maximum I/O configuration | X | X | X | X | X | X | X
Alarm action: Reset latch | 26128 | 26129 | Parameters - Custom alarm - Custom alarm 0 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26129 | 26130 | Parameters - Custom alarm - Custom alarm 1 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26130 | 26131 | Parameters - Custom alarm - Custom alarm 2 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26131 | 26132 | Parameters - Custom alarm - Custom alarm 3 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26132 | 26133 | Parameters - Custom alarm - Custom alarm 4 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26133 | 26134 | Parameters - Custom alarm - Custom alarm 5 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26134 | 26135 | Parameters - Custom alarm - Custom alarm 6 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26135 | 26136 | Parameters - Custom alarm - Custom alarm 7 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26136 | 26137 | Parameters - Custom alarm - Custom alarm 8 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26137 | 26138 | Parameters - Custom alarm - Custom alarm 9 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26138 | 26139 | Parameters - Custom alarm - Custom alarm 10 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26139 | 26140 | Parameters - Custom alarm - Custom alarm 11 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26140 | 26141 | Parameters - Custom alarm - Custom alarm 12 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26141 | 26142 | Parameters - Custom alarm - Custom alarm 13 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26142 | 26143 | Parameters - Custom alarm - Custom alarm 14 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26143 | 26144 | Parameters - Custom alarm - Custom alarm 15 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26144 | 26145 | Parameters - Custom alarm - Custom alarm 16 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26145 | 26146 | Parameters - Custom alarm - Custom alarm 17 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26146 | 26147 | Parameters - Custom alarm - Custom alarm 18 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26147 | 26148 | Parameters - Custom alarm - Custom alarm 19 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26148 | 26149 | Parameters - Custom alarm - Custom alarm 20 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26149 | 26150 | Parameters - Custom alarm - Custom alarm 21 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26150 | 26151 | Parameters - Custom alarm - Custom alarm 22 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26151 | 26152 | Parameters - Custom alarm - Custom alarm 23 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26152 | 26153 | Parameters - Custom alarm - Custom alarm 24 - Commands - | X | X | X | X | X | X | X
Alarm action: Reset latch | 26153 | 26154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Commands - GOV regulation error | X |  | X | X | X
Alarm action: Reset latch | 26154 | 26155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Commands - AVR regulation error | X |  | X | X | X
Alarm action: Reset latch | 26163 | 26164 | Required hardware card(s) not found | X | X | X | X | X | X | X
Alarm action: Reset latch | 26164 | 26165 | Software mismatch on hardware module(s) | X | X | X | X | X | X | X
Alarm action: Reset latch | 26165 | 26166 | Parameters - Mains - AC setup - Multiple phase wire break - Commands - Mains L1-L2-L3 wire break |  |  | X
Alarm action: Reset latch | 26165 | 26166 | Parameters - Busbar - AC setup - Multiple phase wire break - Commands - Busbar L1-L2-L3 wire break | X |  |  |  | X | X
Alarm action: Reset latch | 26165 | 26166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Commands - Busbar B L1-L2-L3 wire break |  | X
Alarm action: Reset latch | 26166 | 26167 | Parameters - Generator - AC setup - Multiple phase wire break - Commands - Generator L1-L2-L3 wire break | X |  | X |  | X
Alarm action: Reset latch | 26166 | 26167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Commands - Busbar A L1-L2-L3 wire break |  | X
Alarm action: Reset latch | 26166 | 26167 | Parameters - Mains - AC setup - Multiple phase wire break - Commands - Mains L1-L2-L3 wire break | [5 empty] | X
Alarm action: Reset latch | 26167 | 26168 | Parameters - Mains - AC setup - L1 wire break - Commands - Mains L1 wire break |  |  | X
Alarm action: Reset latch | 26167 | 26168 | Parameters - Busbar - AC setup - L1 wire break - Commands - Busbar L1 wire break | X |  |  |  | X | X
Alarm action: Reset latch | 26167 | 26168 | Parameters - Busbar B - AC setup - L1 wire break - Commands - Busbar B L1 wire break |  | X
Alarm action: Reset latch | 26168 | 26169 | Parameters - Mains - AC setup - L2 wire break - Commands - Mains L2 wire break |  |  | X
Alarm action: Reset latch | 26168 | 26169 | Parameters - Busbar - AC setup - L2 wire break - Commands - Busbar L2 wire break | X |  |  |  | X | X
Alarm action: Reset latch | 26168 | 26169 | Parameters - Busbar B - AC setup - L2 wire break - Commands - Busbar B L2 wire break |  | X
Alarm action: Reset latch | 26169 | 26170 | Parameters - Mains - AC setup - L3 wire break - Commands - Mains L3 wire break |  |  | X
Alarm action: Reset latch | 26169 | 26170 | Parameters - Busbar - AC setup - L3 wire break - Commands - Busbar L3 wire break | X |  |  |  | X | X
Alarm action: Reset latch | 26169 | 26170 | Parameters - Busbar B - AC setup - L3 wire break - Commands - Busbar B L3 wire break |  | X
Alarm action: Reset latch | 26170 | 26171 | Parameters - Generator - AC setup - L1 wire break - Commands - Generator L1 wire break | X |  | X |  | X
Alarm action: Reset latch | 26170 | 26171 | Parameters - Busbar A - AC setup - L1 wire break - Commands - Busbar A L1 wire break |  | X
Alarm action: Reset latch | 26170 | 26171 | Parameters - Mains - AC setup - L1 wire break - Commands - Mains L1 wire break | [5 empty] | X
Alarm action: Reset latch | 26171 | 26172 | Parameters - Generator - AC setup - L2 wire break - Commands - Generator L2 wire break | X |  | X |  | X
Alarm action: Reset latch | 26171 | 26172 | Parameters - Busbar A - AC setup - L2 wire break - Commands - Busbar A L2 wire break |  | X
Alarm action: Reset latch | 26171 | 26172 | Parameters - Mains - AC setup - L2 wire break - Commands - Mains L2 wire break | [5 empty] | X
Alarm action: Reset latch | 26172 | 26173 | Parameters - Generator - AC setup - L3 wire break - Commands - Generator L3 wire break | X |  | X |  | X
Alarm action: Reset latch | 26172 | 26173 | Parameters - Busbar A - AC setup - L3 wire break - Commands - Busbar A L3 wire break |  | X
Alarm action: Reset latch | 26172 | 26173 | Parameters - Mains - AC setup - L3 wire break - Commands - Mains L3 wire break | [5 empty] | X
Alarm action: Reset latch | 26178 | 26179 | Parameters - Mains - AC setup - Supervision alarm - Commands - Mains supervision alarm |  |  | X | X |  | X | X
Alarm action: Reset latch | 26179 | 26180 | Parameters - Engine - Emergency stop - Commands | X |  | X | X | X
Alarm action: Reset latch | 26179 | 26180 | Parameters - Busbar A - Emergency stop - Commands |  | X
Alarm action: Reset latch | 26179 | 26180 | Parameters - Mains - Emergency stop - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26180 | 26181 | Clock battery failure | X | X | X | X | X | X | X
Alarm action: Reset latch | 26181 | 26182 | Controller temperature too high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26182 | 26183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Commands - PSM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26183 | 26184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Commands - PSM3.1 1 supply voltage low | X | X | X | X | X | X | X
Alarm action: Reset latch | 26184 | 26185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Commands - PSM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26185 | 26186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Commands - PSM3.2 1 supply voltage low | X | X | X | X | X | X | X
Alarm action: Reset latch | 26186 | 26187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Commands - PSM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26187 | 26188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Commands - PSM3.2 2 supply voltage low | X | X | X | X | X | X | X
Alarm action: Reset latch | 26188 | 26189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Commands - PSM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26189 | 26190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Commands - PSM3.2 3 supply voltage low | X | X | X | X | X | X | X
Alarm action: Reset latch | 26190 | 26191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Commands - EIM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26191 | 26192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Commands - EIM3.1 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Reset latch | 26192 | 26193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Commands - EIM3.1 2 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26193 | 26194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Commands - EIM3.1 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Reset latch | 26194 | 26195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Commands - EIM3.1 3 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26195 | 26196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Commands - EIM3.1 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Reset latch | 26196 | 26197 | EIM3.1 4 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26197 | 26198 | EIM3.1 4 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Reset latch | 26198 | 26199 | EIM3.1 5 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26199 | 26200 | EIM3.1 5 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Reset latch | 26200 | 26201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Commands - EIM3.1 1 relay 4 wire break | X | X | X | X | X | X | X
Alarm action: Reset latch | 26201 | 26202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Commands - EIM3.1 2 relay 4 wire break | X | X | X | X | X | X | X
Alarm action: Reset latch | 26202 | 26203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Commands - EIM3.1 3 relay 4 wire break | X | X | X | X | X | X | X
Alarm action: Reset latch | 26203 | 26204 | EIM3.1 4 relay 4 wire break | X | X | X | X | X | X | X
Alarm action: Reset latch | 26204 | 26205 | EIM3.1 5 relay 4 wire break | X | X | X | X | X | X | X
Alarm action: Reset latch | 26205 | 26206 | AC protections not running | X | X | X | X | X | X | X
Alarm action: Reset latch | 26206 | 26207 | AC data is missing | X | X | X | X | X | X | X
Alarm action: Reset latch | 26207 | 26208 | AC protections not running (differential current) | X |  | X | X | X
Alarm action: Reset latch | 26208 | 26209 | AC data is missing (differential current) | X |  | X | X | X
Alarm action: Reset latch | 26209 | 26210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Commands - GAM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26210 | 26211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Commands - GAM3.2 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Reset latch | 26211 | 26212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Commands - GAM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26212 | 26213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Commands - GAM3.2 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Reset latch | 26213 | 26214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Commands - GAM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26214 | 26215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Commands - GAM3.2 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Reset latch | 26215 | 26216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Commands - PSM3.2 4 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26216 | 26217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Commands - PSM3.2 4 supply voltage low | X | X | X | X | X | X | X
Alarm action: Reset latch | 26217 | 26218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Commands - PSM3.2 5 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26218 | 26219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Commands - PSM3.2 5 supply voltage low | X | X | X | X | X | X | X
Alarm action: Reset latch | 26219 | 26220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Commands - PSM3.2 6 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26220 | 26221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Commands - PSM3.2 6 supply voltage low | X | X | X | X | X | X | X
Alarm action: Reset latch | 26221 | 26222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Commands - PSM3.2 7 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26222 | 26223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Commands - PSM3.2 7 supply voltage low | X | X | X | X | X | X | X
Alarm action: Reset latch | 26223 | 26224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Commands - PSM3.2 8 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26224 | 26225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Commands - PSM3.2 8 supply voltage low | X | X | X | X | X | X | X
Alarm action: Reset latch | 26225 | 26226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Commands - PSM3.2 9 supply voltage high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26226 | 26227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Commands - PSM3.2 9 supply voltage low | X | X | X | X | X | X | X
Alarm action: Reset latch | 26228 | 26229 | Parameters - System - Monitoring - Duplicate controller ID - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26229 | 26230 | Parameters - System - Monitoring - Missing all controllers - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26231 | 26232 | Controller ID not configured | X | X | X | X | X | X | X
Alarm action: Reset latch | 26236 | 26237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26237 | 26238 | Blackout detection mismatch | X |  | X | X | X
Alarm action: Reset latch | 26240 | 26241 | Parameters - Communication - NTP - NTP server 1 not connected - Commands - NTP server 1 could not connect | X | X | X | X | X | X | X
Alarm action: Reset latch | 26241 | 26242 | Parameters - Communication - NTP - NTP server 1 no response - Commands - NTP server 1 is not responding | X | X | X | X | X | X | X
Alarm action: Reset latch | 26242 | 26243 | Parameters - Communication - NTP - NTP server 2 not connected - Commands - NTP server 2 could not connect | X | X | X | X | X | X | X
Alarm action: Reset latch | 26243 | 26244 | Parameters - Communication - NTP - NTP server 2 no response - Commands - NTP server 2 is not responding | X | X | X | X | X | X | X
Alarm action: Reset latch | 26244 | 26245 | Parameters - Communication - NTP - No NTP server time synchronisation - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26245 | 26246 | Parameters - Communication - NTP - No NTP server(s) connected - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26246 | 26247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26247 | 26248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26296 | 26297 | Controller not part of system | X | X | X | X | X | X | X
Alarm action: Reset latch | 26297 | 26298 | Different single-line configurations | X | X | X | X | X | X | X
Alarm action: Reset latch | 26298 | 26299 | Single-line missing/none active | X | X | X | X | X | X | X
Alarm action: Reset latch | 26299 | 26300 | Parameters - Communication - Modbus - Modbus communication timeout - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26300 | 26301 | Parameters - CODESYS - Monitoring - I/O config conflict - Commands - CODESYS configuration conflict | X | X | X | X | X | X | X
Alarm action: Reset latch | 26301 | 26302 | Parameters - CODESYS - Monitoring - Application not OK - Commands - CODESYS application not OK | X | X | X | X | X | X | X
Alarm action: Reset latch | 26302 | 26303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Commands | X |  | X | X | X
Alarm action: Reset latch | 26303 | 26304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Commands | X |  | X | X | X
Alarm action: Reset latch | 26304 | 26305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Commands | X |  | X | X | X
Alarm action: Reset latch | 26305 | 26306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Commands | X |  | X | X | X
Alarm action: Reset latch | 26306 | 26307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Commands | X |  | X | X | X
Alarm action: Reset latch | 26307 | 26308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Commands | X |  | X | X | X
Alarm action: Reset latch | 26308 | 26309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Commands | X |  | X | X | X
Alarm action: Reset latch | 26309 | 26310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Commands | X |  | X | X | X
Alarm action: Reset latch | 26310 | 26311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Commands | X |  | X | X | X
Alarm action: Reset latch | 26311 | 26312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26312 | 26313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26313 | 26314 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26314 | 26315 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26315 | 26316 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26316 | 26317 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26317 | 26318 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26318 | 26319 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26319 | 26320 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26320 | 26321 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26321 | 26322 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26322 | 26323 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26323 | 26324 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26324 | 26325 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26325 | 26326 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26326 | 26327 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26327 | 26328 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26328 | 26329 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26329 | 26330 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26330 | 26331 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26331 | 26332 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26332 | 26333 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26333 | 26334 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26334 | 26335 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26335 | 26336 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26336 | 26337 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26337 | 26338 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26338 | 26339 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26339 | 26340 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26340 | 26341 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26341 | 26342 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26342 | 26343 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26343 | 26344 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26344 | 26345 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26345 | 26346 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26346 | 26347 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26347 | 26348 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26348 | 26349 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26349 | 26350 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26350 | 26351 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26351 | 26352 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26352 | 26353 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26353 | 26354 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26354 | 26355 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26355 | 26356 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26356 | 26357 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26357 | 26358 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26358 | 26359 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26359 | 26360 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26360 | 26361 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26361 | 26362 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26362 | 26363 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26363 | 26364 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26364 | 26365 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26365 | 26366 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26366 | 26367 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26367 | 26368 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26368 | 26369 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26369 | 26370 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26370 | 26371 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26371 | 26372 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26372 | 26373 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26373 | 26374 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26374 | 26375 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26375 | 26376 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26376 | 26377 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26377 | 26378 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26378 | 26379 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26379 | 26380 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26380 | 26381 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26381 | 26382 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26382 | 26383 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26383 | 26384 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26384 | 26385 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26385 | 26386 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26386 | 26387 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26387 | 26388 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26388 | 26389 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26389 | 26390 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26390 | 26391 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26391 | 26392 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26392 | 26393 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26393 | 26394 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26394 | 26395 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26395 | 26396 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26396 | 26397 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26397 | 26398 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26398 | 26399 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26399 | 26400 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26400 | 26401 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26401 | 26402 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26402 | 26403 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26403 | 26404 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26404 | 26405 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26405 | 26406 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26406 | 26407 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26407 | 26408 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26408 | 26409 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26409 | 26410 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26410 | 26411 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26411 | 26412 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26412 | 26413 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26413 | 26414 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26414 | 26415 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26415 | 26416 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26416 | 26417 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26417 | 26418 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26418 | 26419 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26419 | 26420 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26420 | 26421 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26421 | 26422 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26422 | 26423 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26423 | 26424 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26424 | 26425 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26425 | 26426 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26426 | 26427 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26427 | 26428 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26428 | 26429 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26429 | 26430 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26430 | 26431 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26431 | 26432 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26432 | 26433 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26433 | 26434 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26434 | 26435 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26435 | 26436 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26436 | 26437 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26437 | 26438 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26438 | 26439 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26439 | 26440 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26440 | 26441 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26441 | 26442 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26442 | 26443 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26443 | 26444 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26444 | 26445 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26445 | 26446 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26446 | 26447 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26447 | 26448 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26448 | 26449 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26449 | 26450 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26450 | 26451 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26451 | 26452 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26452 | 26453 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26453 | 26454 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26454 | 26455 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26455 | 26456 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26456 | 26457 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26457 | 26458 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26458 | 26459 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26459 | 26460 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26460 | 26461 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26461 | 26462 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26462 | 26463 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26463 | 26464 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26464 | 26465 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26465 | 26466 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26466 | 26467 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26467 | 26468 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26468 | 26469 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26469 | 26470 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26470 | 26471 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26471 | 26472 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26472 | 26473 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26473 | 26474 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26474 | 26475 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26475 | 26476 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26476 | 26477 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26477 | 26478 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26478 | 26479 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26479 | 26480 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26480 | 26481 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26481 | 26482 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26482 | 26483 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26483 | 26484 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26484 | 26485 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26485 | 26486 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26486 | 26487 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26487 | 26488 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26488 | 26489 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26489 | 26490 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26490 | 26491 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26491 | 26492 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26492 | 26493 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26493 | 26494 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26494 | 26495 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26495 | 26496 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26496 | 26497 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26497 | 26498 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26498 | 26499 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26499 | 26500 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26500 | 26501 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26501 | 26502 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26502 | 26503 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26503 | 26504 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26504 | 26505 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26505 | 26506 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26506 | 26507 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26507 | 26508 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26508 | 26509 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26509 | 26510 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26510 | 26511 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26511 | 26512 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26512 | 26513 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26513 | 26514 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26514 | 26515 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26515 | 26516 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26516 | 26517 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26517 | 26518 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26518 | 26519 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26519 | 26520 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26520 | 26521 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26521 | 26522 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26522 | 26523 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26523 | 26524 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26524 | 26525 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26525 | 26526 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26526 | 26527 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26527 | 26528 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26528 | 26529 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26529 | 26530 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26530 | 26531 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26531 | 26532 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26532 | 26533 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26533 | 26534 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26534 | 26535 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26535 | 26536 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26536 | 26537 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26537 | 26538 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26538 | 26539 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26539 | 26540 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26540 | 26541 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26541 | 26542 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26542 | 26543 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26543 | 26544 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26544 | 26545 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26545 | 26546 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26546 | 26547 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26547 | 26548 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26548 | 26549 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26549 | 26550 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26550 | 26551 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26551 | 26552 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26552 | 26553 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26553 | 26554 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26554 | 26555 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26555 | 26556 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26556 | 26557 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26557 | 26558 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26558 | 26559 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26559 | 26560 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26560 | 26561 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26561 | 26562 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26562 | 26563 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Reset latch | 26565 | 26566 | Parameters - Local - CustomLogic - Configuration invalid - Commands - CustomLogic configuration invalid | X | X | X | X | X | X | X
Alarm action: Reset latch | 26566 | 26567 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Commands - Digital AVR communication error | X |  | X | X | X
Alarm action: Reset latch | 26567 | 26568 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Commands | X |  | X | X | X
Alarm action: Reset latch | 26568 | 26569 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Commands | X |  | X | X | X
Alarm action: Reset latch | 26569 | 26570 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Commands | X |  | X | X | X
Alarm action: Reset latch | 26570 | 26571 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Commands | X |  | X | X | X
Alarm action: Reset latch | 26571 | 26572 | Parameters - Generator - Digital AVR - Alarms - Open diode - Commands | X |  | X | X | X
Alarm action: Reset latch | 26572 | 26573 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Commands | X |  | X | X | X
Alarm action: Reset latch | 26573 | 26574 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Commands | X |  | X | X | X
Alarm action: Reset latch | 26574 | 26575 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Commands | X |  | X | X | X
Alarm action: Reset latch | 26575 | 26576 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Commands | X |  | X | X | X
Alarm action: Reset latch | 26576 | 26577 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Commands | X |  | X | X | X
Alarm action: Reset latch | 26577 | 26578 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Commands | X |  | X | X | X
Alarm action: Reset latch | 26578 | 26579 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Commands | X |  | X | X | X
Alarm action: Reset latch | 26579 | 26580 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Commands | X |  | X | X | X
Alarm action: Reset latch | 26580 | 26581 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Commands | X |  | X | X | X
Alarm action: Reset latch | 26581 | 26582 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Commands | X |  | X | X | X
Alarm action: Reset latch | 26582 | 26583 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Commands | X |  | X | X | X
Alarm action: Reset latch | 26583 | 26584 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Commands | X |  | X | X | X
Alarm action: Reset latch | 26584 | 26585 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Commands | X |  | X | X | X
Alarm action: Reset latch | 26585 | 26586 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Commands | X |  | X | X | X
Alarm action: Reset latch | 26586 | 26587 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Commands | X |  | X | X | X
Alarm action: Reset latch | 26587 | 26588 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Commands | X |  | X | X | X
Alarm action: Reset latch | 26588 | 26589 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Commands | X |  | X | X | X
Alarm action: Reset latch | 26589 | 26590 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Commands | X |  | X | X | X
Alarm action: Reset latch | 26590 | 26591 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Commands | X |  | X | X | X
Alarm action: Reset latch | 26591 | 26592 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Commands | X |  | X | X | X
Alarm action: Reset latch | 26592 | 26593 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Commands | X |  | X | X | X
Alarm action: Reset latch | 26593 | 26594 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Commands | X |  | X | X | X
Alarm action: Reset latch | 26594 | 26595 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Commands | X |  | X | X | X
Alarm action: Reset latch | 26595 | 26596 | Parameters - Generator - Digital AVR - Alarms - Motor start - Commands | X |  | X | X | X
Alarm action: Reset latch | 26596 | 26597 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Commands | X |  | X | X | X
Alarm action: Reset latch | 26597 | 26598 | Parameters - Generator - Digital AVR - Alarms - Power supply - Commands | X |  | X | X | X
Alarm action: Reset latch | 26598 | 26599 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Commands | X |  | X | X | X
Alarm action: Reset latch | 26599 | 26600 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Commands | X |  | X | X | X
Alarm action: Reset latch | 26600 | 26601 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Commands | X |  | X | X | X
Alarm action: Reset latch | 26601 | 26602 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Commands | X |  | X | X | X
Alarm action: Reset latch | 26602 | 26603 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Commands | X |  | X | X | X
Alarm action: Reset latch | 26603 | 26604 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Commands | X |  | X | X | X
Alarm action: Reset latch | 26604 | 26605 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Commands | X |  | X | X | X
Alarm action: Reset latch | 26605 | 26606 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Commands | X |  | X | X | X
Alarm action: Reset latch | 26606 | 26607 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Commands | X |  | X | X | X
Alarm action: Reset latch | 26607 | 26608 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Commands | X |  | X | X | X
Alarm action: Reset latch | 26608 | 26609 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Commands | X |  | X | X | X
Alarm action: Reset latch | 26609 | 26610 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Commands | X |  | X | X | X
Alarm action: Reset latch | 26610 | 26611 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Commands | X |  | X | X | X
Alarm action: Reset latch | 26611 | 26612 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Commands | X |  | X | X | X
Alarm action: Reset latch | 26612 | 26613 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Commands | X |  | X | X | X
Alarm action: Reset latch | 26613 | 26614 | DAVR unsupported AC configuration | X |  | X | X | X
Alarm action: Reset latch | 26614 | 26615 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Commands - Illegal DAVR configuration | X |  | X | X | X
Alarm action: Reset latch | 26615 | 26616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Commands - Generator under-voltage 1 | X |  | X | X | X
Alarm action: Reset latch | 26615 | 26616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Commands - Busbar A under-voltage 1 |  | X
Alarm action: Reset latch | 26615 | 26616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Commands - Mains under-voltage 1 | [5 empty] | X | X
Alarm action: Reset latch | 26616 | 26617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Commands - Generator under-voltage 2 | X |  | X | X | X
Alarm action: Reset latch | 26616 | 26617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Commands - Busbar A under-voltage 2 |  | X
Alarm action: Reset latch | 26616 | 26617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Commands - Mains under-voltage 2 | [5 empty] | X | X
Alarm action: Reset latch | 26617 | 26618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Commands - Generator under-voltage 3 | X |  | X | X | X
Alarm action: Reset latch | 26617 | 26618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Commands - Busbar A under-voltage 3 |  | X
Alarm action: Reset latch | 26617 | 26618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Commands - Mains under-voltage 3 | [5 empty] | X | X
Alarm action: Reset latch | 26618 | 26619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Commands - Generator over-voltage 1 | X |  | X | X | X
Alarm action: Reset latch | 26618 | 26619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Commands - Busbar A over-voltage 1 |  | X
Alarm action: Reset latch | 26618 | 26619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Commands - Mains over-voltage 1 | [5 empty] | X | X
Alarm action: Reset latch | 26619 | 26620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Commands - Generator over-voltage 2 | X |  | X | X | X
Alarm action: Reset latch | 26619 | 26620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Commands - Busbar A over-voltage 2 |  | X
Alarm action: Reset latch | 26619 | 26620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Commands - Mains over-voltage 2 | [5 empty] | X | X
Alarm action: Reset latch | 26620 | 26621 | Parameters - Generator - Voltage protections - Voltage unbalance - Commands - Generator voltage unbalance | X |  | X | X | X
Alarm action: Reset latch | 26620 | 26621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Commands - Busbar A voltage unbalance |  | X
Alarm action: Reset latch | 26620 | 26621 | Parameters - Mains - Voltage protections - Voltage unbalance - Commands - Mains voltage unbalance | [5 empty] | X | X
Alarm action: Reset latch | 26621 | 26622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Commands - Generator negative sequence voltage | X |  | X | X | X
Alarm action: Reset latch | 26621 | 26622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Commands - Busbar A negative sequence voltage |  | X
Alarm action: Reset latch | 26621 | 26622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Commands - Mains negative sequence voltage | [5 empty] | X | X
Alarm action: Reset latch | 26622 | 26623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Commands - Generator zero sequence voltage | X |  | X | X | X
Alarm action: Reset latch | 26622 | 26623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Commands - Busbar A zero sequence voltage |  | X
Alarm action: Reset latch | 26622 | 26623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Commands - Mains zero sequence voltage | [5 empty] | X | X
Alarm action: Reset latch | 26623 | 26624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Commands - Generator positive sequence under-voltage | X |  | X | X | X
Alarm action: Reset latch | 26623 | 26624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Commands - Busbar A positive sequence under-voltage |  | X
Alarm action: Reset latch | 26623 | 26624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Commands - Mains positive sequence under-voltage | [5 empty] | X | X
Alarm action: Reset latch | 26624 | 26625 | Parameters - Generator - Current protections - Over-current 1 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26624 | 26625 | Parameters - Busbar A - Current protections - Over-current 1 - Commands |  | X
Alarm action: Reset latch | 26624 | 26625 | Parameters - Mains - Current protections - Over-current 1 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26625 | 26626 | Parameters - Generator - Current protections - Over-current 2 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26625 | 26626 | Parameters - Busbar A - Current protections - Over-current 2 - Commands |  | X
Alarm action: Reset latch | 26625 | 26626 | Parameters - Mains - Current protections - Over-current 2 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26626 | 26627 | Parameters - Generator - Current protections - Over-current 3 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26626 | 26627 | Parameters - Busbar A - Current protections - Over-current 3 - Commands |  | X
Alarm action: Reset latch | 26626 | 26627 | Parameters - Mains - Current protections - Over-current 3 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26627 | 26628 | Parameters - Generator - Current protections - Over-current 4 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26627 | 26628 | Parameters - Busbar A - Current protections - Over-current 4 - Commands |  | X
Alarm action: Reset latch | 26627 | 26628 | Parameters - Mains - Current protections - Over-current 4 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26628 | 26629 | Parameters - Generator - Current protections - Fast over-current 1 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26628 | 26629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Commands |  | X
Alarm action: Reset latch | 26628 | 26629 | Parameters - Mains - Current protections - Fast over-current 1 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26629 | 26630 | Parameters - Generator - Current protections - Fast over-current 2 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26629 | 26630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Commands |  | X
Alarm action: Reset latch | 26629 | 26630 | Parameters - Mains - Current protections - Fast over-current 2 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26630 | 26631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Commands | X |  | X | X | X
Alarm action: Reset latch | 26630 | 26631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Commands |  | X
Alarm action: Reset latch | 26630 | 26631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26631 | 26632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Commands | X |  | X | X | X
Alarm action: Reset latch | 26631 | 26632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Commands |  | X
Alarm action: Reset latch | 26631 | 26632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26632 | 26633 | Parameters - Generator - Current protections - Directional over-current 1 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26632 | 26633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Commands |  | X
Alarm action: Reset latch | 26632 | 26633 | Parameters - Mains - Current protections - Directional over-current 1 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26633 | 26634 | Parameters - Generator - Current protections - Directional over-current 2 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26633 | 26634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Commands |  | X
Alarm action: Reset latch | 26633 | 26634 | Parameters - Mains - Current protections - Directional over-current 2 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26634 | 26635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Commands |  | X
Alarm action: Reset latch | 26635 | 26636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Commands |  | X
Alarm action: Reset latch | 26636 | 26637 | Parameters - Generator - Current protections - Negative sequence current - Commands | X |  | X | X | X
Alarm action: Reset latch | 26636 | 26637 | Parameters - Busbar A - Current protections - Negative sequence current - Commands |  | X
Alarm action: Reset latch | 26636 | 26637 | Parameters - Mains - Current protections - Negative sequence current - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26637 | 26638 | Parameters - Generator - Current protections - Zero sequence current - Commands | X |  | X | X | X
Alarm action: Reset latch | 26637 | 26638 | Parameters - Busbar A - Current protections - Zero sequence current - Commands |  | X
Alarm action: Reset latch | 26637 | 26638 | Parameters - Mains - Current protections - Zero sequence current - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26638 | 26639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Commands - Generator over-frequency 1 | X |  | X | X | X
Alarm action: Reset latch | 26638 | 26639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Commands - Busbar A over-frequency 1 |  | X
Alarm action: Reset latch | 26638 | 26639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Commands - Mains over-frequency 1 | [5 empty] | X | X
Alarm action: Reset latch | 26639 | 26640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Commands - Generator over-frequency 2 | X |  | X | X | X
Alarm action: Reset latch | 26639 | 26640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Commands - Busbar A over-frequency 2 |  | X
Alarm action: Reset latch | 26639 | 26640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Commands - Mains over-frequency 2 | [5 empty] | X | X
Alarm action: Reset latch | 26640 | 26641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Commands - Generator over-frequency 3 | X |  | X | X | X
Alarm action: Reset latch | 26640 | 26641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Commands - Busbar A over-frequency 3 |  | X
Alarm action: Reset latch | 26640 | 26641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Commands - Mains over-frequency 3 | [5 empty] | X | X
Alarm action: Reset latch | 26641 | 26642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Commands - Generator under-frequency 1 | X |  | X | X | X
Alarm action: Reset latch | 26641 | 26642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Commands - Busbar A under-frequency 1 |  | X
Alarm action: Reset latch | 26641 | 26642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Commands - Mains under-frequency 1 | [5 empty] | X | X
Alarm action: Reset latch | 26642 | 26643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Commands - Generator under-frequency 2 | X |  | X | X | X
Alarm action: Reset latch | 26642 | 26643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Commands - Busbar A under-frequency 2 |  | X
Alarm action: Reset latch | 26642 | 26643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Commands - Mains under-frequency 2 | [5 empty] | X | X
Alarm action: Reset latch | 26643 | 26644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Commands - Generator under-frequency 3 | X |  | X | X | X
Alarm action: Reset latch | 26643 | 26644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Commands - Busbar A under-frequency 3 |  | X
Alarm action: Reset latch | 26643 | 26644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Commands - Mains under-frequency 3 | [5 empty] | X | X
Alarm action: Reset latch | 26644 | 26645 | Parameters - Generator - Power protections - Overload 1 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26644 | 26645 | Parameters - Busbar A - Power protections - Power export 1 - Commands |  | X
Alarm action: Reset latch | 26644 | 26645 | Parameters - Mains - Power protections - Overload 1 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26645 | 26646 | Parameters - Generator - Power protections - Overload 2 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26645 | 26646 | Parameters - Busbar A - Power protections - Power export 2 - Commands |  | X
Alarm action: Reset latch | 26645 | 26646 | Parameters - Mains - Power protections - Overload 2 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26646 | 26647 | Parameters - Generator - Power protections - Overload 3 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26646 | 26647 | Parameters - Busbar A - Power protections - Power export 3 - Commands |  | X
Alarm action: Reset latch | 26646 | 26647 | Parameters - Mains - Power protections - Overload 3 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26647 | 26648 | Parameters - Generator - Power protections - Overload 4 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26647 | 26648 | Parameters - Busbar A - Power protections - Power export 4 - Commands |  | X
Alarm action: Reset latch | 26647 | 26648 | Parameters - Mains - Power protections - Overload 4 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26648 | 26649 | Parameters - Generator - Power protections - Overload 5 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26648 | 26649 | Parameters - Busbar A - Power protections - Power export 5 - Commands |  | X
Alarm action: Reset latch | 26648 | 26649 | Parameters - Mains - Power protections - Overload 5 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26649 | 26650 | Parameters - Generator - Power protections - Reverse power 1 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26649 | 26650 | Parameters - Busbar A - Power protections - Power import 1 - Commands |  | X
Alarm action: Reset latch | 26649 | 26650 | Parameters - Mains - Power protections - Reverse power 1 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26650 | 26651 | Parameters - Generator - Power protections - Reverse power 2 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26650 | 26651 | Parameters - Busbar A - Power protections - Power import 2 - Commands |  | X
Alarm action: Reset latch | 26650 | 26651 | Parameters - Mains - Power protections - Reverse power 2 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26651 | 26652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26651 | 26652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Commands |  | X
Alarm action: Reset latch | 26651 | 26652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26652 | 26653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26652 | 26653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Commands |  | X
Alarm action: Reset latch | 26652 | 26653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26653 | 26654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26653 | 26654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Commands |  | X
Alarm action: Reset latch | 26653 | 26654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26654 | 26655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Commands | X |  | X | X | X
Alarm action: Reset latch | 26654 | 26655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Commands |  | X
Alarm action: Reset latch | 26654 | 26655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Commands | [5 empty] | X | X
Alarm action: Reset latch | 26655 | 26656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Commands - Mains over-voltage 1 |  |  | X | X
Alarm action: Reset latch | 26655 | 26656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Commands - Busbar over-voltage 1 | X |  |  |  | X | X | X
Alarm action: Reset latch | 26655 | 26656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Commands - Busbar B over-voltage 1 |  | X
Alarm action: Reset latch | 26656 | 26657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Commands - Mains over-voltage 2 |  |  | X | X
Alarm action: Reset latch | 26656 | 26657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Commands - Busbar over-voltage 2 | X |  |  |  | X | X | X
Alarm action: Reset latch | 26656 | 26657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Commands - Busbar B over-voltage 2 |  | X
Alarm action: Reset latch | 26657 | 26658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Commands - Mains over-voltage 3 |  |  | X | X
Alarm action: Reset latch | 26657 | 26658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Commands - Busbar over-voltage 3 | X |  |  |  | X | X | X
Alarm action: Reset latch | 26657 | 26658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Commands - Busbar B over-voltage 3 |  | X
Alarm action: Reset latch | 26658 | 26659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Commands - Mains under-voltage 1 |  |  | X | X
Alarm action: Reset latch | 26658 | 26659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Commands - Busbar under-voltage 1 | X |  |  |  | X | X | X
Alarm action: Reset latch | 26658 | 26659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Commands - Busbar B under-voltage 1 |  | X
Alarm action: Reset latch | 26659 | 26660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Commands - Mains under-voltage 2 |  |  | X | X
Alarm action: Reset latch | 26659 | 26660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Commands - Busbar under-voltage 2 | X |  |  |  | X | X | X
Alarm action: Reset latch | 26659 | 26660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Commands - Busbar B under-voltage 2 |  | X
Alarm action: Reset latch | 26660 | 26661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Commands - Mains under-voltage 3 |  |  | X | X
Alarm action: Reset latch | 26660 | 26661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Commands - Busbar under-voltage 3 | X |  |  |  | X | X | X
Alarm action: Reset latch | 26660 | 26661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Commands - Busbar B under-voltage 3 |  | X
Alarm action: Reset latch | 26661 | 26662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Commands - Mains under-voltage 4 |  |  | X | X
Alarm action: Reset latch | 26661 | 26662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Commands - Busbar under-voltage 4 | X |  |  |  | X | X | X
Alarm action: Reset latch | 26661 | 26662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Commands - Busbar B under-voltage 4 |  | X
Alarm action: Reset latch | 26662 | 26663 | Parameters - Mains - Voltage protections - Voltage unbalance - Commands - Mains voltage unbalance |  |  | X | X
Alarm action: Reset latch | 26662 | 26663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Commands - Busbar voltage unbalance | X |  |  |  | X | X | X
Alarm action: Reset latch | 26662 | 26663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Commands - Busbar B voltage unbalance |  | X
Alarm action: Reset latch | 26663 | 26664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Commands - Mains over-frequency 1 |  |  | X | X
Alarm action: Reset latch | 26663 | 26664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Commands - Busbar over-frequency 1 | X |  |  |  | X | X | X
Alarm action: Reset latch | 26663 | 26664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Commands - Busbar B over-frequency 1 |  | X
Alarm action: Reset latch | 26664 | 26665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Commands - Mains over-frequency 2 |  |  | X | X
Alarm action: Reset latch | 26664 | 26665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Commands - Busbar over-frequency 2 | X |  |  |  | X | X | X
Alarm action: Reset latch | 26664 | 26665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Commands - Busbar B over-frequency 2 |  | X
Alarm action: Reset latch | 26665 | 26666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Commands - Mains over-frequency 3 |  |  | X | X
Alarm action: Reset latch | 26665 | 26666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Commands - Busbar over-frequency 3 | X |  |  |  | X | X | X
Alarm action: Reset latch | 26665 | 26666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Commands - Busbar B over-frequency 3 |  | X
Alarm action: Reset latch | 26666 | 26667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Commands - Mains under-frequency 1 |  |  | X | X
Alarm action: Reset latch | 26666 | 26667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Commands - Busbar under-frequency 1 | X |  |  |  | X | X | X
Alarm action: Reset latch | 26666 | 26667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Commands - Busbar B under-frequency 1 |  | X
Alarm action: Reset latch | 26667 | 26668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Commands - Mains under-frequency 2 |  |  | X | X
Alarm action: Reset latch | 26667 | 26668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Commands - Busbar under-frequency 2 | X |  |  |  | X | X | X
Alarm action: Reset latch | 26667 | 26668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Commands - Busbar B under-frequency 2 |  | X
Alarm action: Reset latch | 26668 | 26669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Commands - Mains under-frequency 3 |  |  | X | X
Alarm action: Reset latch | 26668 | 26669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Commands - Busbar under-frequency 3 | X |  |  |  | X | X | X
Alarm action: Reset latch | 26668 | 26669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Commands - Busbar B under-frequency 3 |  | X
Alarm action: Reset latch | 26669 | 26670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Commands - Mains under-frequency 4 |  |  | X | X
Alarm action: Reset latch | 26669 | 26670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Commands - Busbar under-frequency 4 | X |  |  |  | X | X | X
Alarm action: Reset latch | 26669 | 26670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Commands - Busbar B under-frequency 4 |  | X
Alarm action: Reset latch | 26670 | 26671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Commands - Busbar negative sequence voltage |  |  | X | X
Alarm action: Reset latch | 26670 | 26671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Commands - Busbar negative sequence voltage | X |  |  |  | X | X | X
Alarm action: Reset latch | 26670 | 26671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Commands - Busbar B negative sequence voltage |  | X
Alarm action: Reset latch | 26671 | 26672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Commands - Busbar zero sequence voltage |  |  | X | X
Alarm action: Reset latch | 26671 | 26672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Commands - Busbar zero sequence voltage | X |  |  |  | X | X | X
Alarm action: Reset latch | 26671 | 26672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Commands - Busbar B zero sequence voltage |  | X
Alarm action: Reset latch | 26672 | 26673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Commands - Busbar positive sequence under-voltage |  |  | X | X
Alarm action: Reset latch | 26672 | 26673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Commands - Busbar positive sequence under-voltage | X |  |  |  | X | X | X
Alarm action: Reset latch | 26672 | 26673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Commands - Busbar B positive sequence under-voltage |  | X
Alarm action: Reset latch | 26717 | 26718 | Parameters - Engine - Maintenance - Service timer - Commands - Service timer 1 | X |  | X | X | X
Alarm action: Reset latch | 26718 | 26719 | Parameters - Engine - Maintenance - Service timer - Commands - Service timer 2 | X |  | X | X | X
Alarm action: Reset latch | 26719 | 26720 | Parameters - Engine - Maintenance - Service timer - Commands - Service timer 3 | X |  | X | X | X
Alarm action: Reset latch | 26720 | 26721 | Parameters - Engine - Maintenance - Service timer - Commands - Service timer 4 | X |  | X | X | X
Alarm action: Reset latch | 26721 | 26722 | External MB open failure | X | X | X | X | X | X | X
Alarm action: Reset latch | 26722 | 26723 | Parameters - Power management rules - Ground relay - Ground relay general failure - Commands | X |  | X | X | X
Alarm action: Reset latch | 26723 | 26724 | Parameters - Power management rules - Ground relay - Ground relay open failure - Commands | X |  | X | X | X
Alarm action: Reset latch | 26724 | 26725 | Parameters - Power management rules - Ground relay - Ground relay close failure - Commands | X |  | X | X | X
Alarm action: Reset latch | 26725 | 26726 | Parameters - Power management rules - Ground relay - Ground relay position failure - Commands | X |  | X | X | X
Alarm action: Reset latch | 26726 | 26727 | Parameters - Breakers - Close before excitation - CBE rerun failure - Commands | X |  | X | X | X
Alarm action: Reset latch | 26727 | 26728 | Parameters - Breakers - Close before excitation - CBE failure - Commands - Close before excitation failure | X |  | X | X | X
Alarm action: Reset latch | 26728 | 26729 | Load too high | X | X | X | X | X | X | X
Alarm action: Reset latch | 26729 | 26730 | ID to run configuration failure | [5 empty] | X | X
Alarm action: Reset latch | 26731 | 26732 | Parameters - System - Monitoring - Missing any genset controller - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26732 | 26733 | Parameters - System - Monitoring - Missing any mains controller - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26733 | 26734 | Parameters - System - Monitoring - Missing any bustie controller - Commands - Missing any bus tie controller | X | X | X | X | X | X | X
Alarm action: Reset latch | 26734 | 26735 | Can ID not available | X | X | X | X | X | X | X
Alarm action: Reset latch | 26735 | 26736 | Duplicated CAN IDs | X | X | X | X | X | X | X
Alarm action: Reset latch | 26736 | 26737 | Parameters - Local power management - Alarms - Busbar blocked - Commands - Busbar blocked due to position failure | X |  | X | X | X | X | X
Alarm action: Reset latch | 26737 | 26738 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Commands - Busbar A blocked due to position failure |  | X
Alarm action: Reset latch | 26738 | 26739 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Commands - Busbar B blocked due to position failure |  | X
Alarm action: Reset latch | 26739 | 26740 | Parameters - System - Monitoring - BTB 33 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26740 | 26741 | Parameters - System - Monitoring - BTB 34 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26741 | 26742 | Parameters - System - Monitoring - BTB 35 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26742 | 26743 | Parameters - System - Monitoring - BTB 36 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26743 | 26744 | Parameters - System - Monitoring - BTB 37 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26744 | 26745 | Parameters - System - Monitoring - BTB 38 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26745 | 26746 | Parameters - System - Monitoring - BTB 39 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26746 | 26747 | Parameters - System - Monitoring - BTB 40 position failure - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26747 | 26748 | Primary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26748 | 26749 | Primary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26749 | 26750 | Primary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26750 | 26751 | Primary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26751 | 26752 | Primary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26752 | 26753 | Primary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26753 | 26754 | Primary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26754 | 26755 | Primary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26755 | 26756 | Primary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26756 | 26757 | Primary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26757 | 26758 | Primary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26758 | 26759 | Primary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26759 | 26760 | Primary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26760 | 26761 | Primary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26761 | 26762 | Primary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26762 | 26763 | Primary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26763 | 26764 | Primary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26764 | 26765 | Primary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26765 | 26766 | Primary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26766 | 26767 | Primary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26767 | 26768 | Primary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26768 | 26769 | Primary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26769 | 26770 | Primary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26770 | 26771 | Primary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26771 | 26772 | Primary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26772 | 26773 | Primary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26773 | 26774 | Primary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26774 | 26775 | Primary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26775 | 26776 | Primary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26776 | 26777 | Primary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26777 | 26778 | Primary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26778 | 26779 | Primary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26779 | 26780 | Primary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26780 | 26781 | Primary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26781 | 26782 | Primary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26782 | 26783 | Primary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26783 | 26784 | Primary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26784 | 26785 | Primary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26785 | 26786 | Primary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26786 | 26787 | Primary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26787 | 26788 | Secondary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26788 | 26789 | Secondary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26789 | 26790 | Secondary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26790 | 26791 | Secondary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26791 | 26792 | Secondary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26792 | 26793 | Secondary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26793 | 26794 | Secondary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26794 | 26795 | Secondary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26795 | 26796 | Secondary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26796 | 26797 | Secondary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26797 | 26798 | Secondary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26798 | 26799 | Secondary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26799 | 26800 | Secondary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26800 | 26801 | Secondary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26801 | 26802 | Secondary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26802 | 26803 | Secondary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26803 | 26804 | Secondary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26804 | 26805 | Secondary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26805 | 26806 | Secondary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26806 | 26807 | Secondary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26807 | 26808 | Secondary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26808 | 26809 | Secondary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26809 | 26810 | Secondary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26810 | 26811 | Secondary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26811 | 26812 | Secondary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26812 | 26813 | Secondary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26813 | 26814 | Secondary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26814 | 26815 | Secondary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26815 | 26816 | Secondary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26816 | 26817 | Secondary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26817 | 26818 | Secondary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26818 | 26819 | Secondary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26819 | 26820 | Secondary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26820 | 26821 | Secondary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26821 | 26822 | Secondary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26822 | 26823 | Secondary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26823 | 26824 | Secondary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26824 | 26825 | Secondary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26825 | 26826 | Secondary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26826 | 26827 | Secondary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm action: Reset latch | 26827 | 26828 | Priority error | X | X | X | X | X | X | X
Alarm action: Reset latch | 26828 | 26829 | Parameters - Non-essential load trip - Trip 1 - Over-current - Commands - NEL 1 over-current | X |  | X | X | X | X | X
Alarm action: Reset latch | 26829 | 26830 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Commands - NEL 1 under-frequency | X |  | X | X | X | X | X
Alarm action: Reset latch | 26830 | 26831 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Commands - NEL 1 overload 1 | X |  | X | X | X | X | X
Alarm action: Reset latch | 26831 | 26832 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Commands - NEL 1 overload 2 | X |  | X | X | X | X | X
Alarm action: Reset latch | 26832 | 26833 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Commands - NEL 1 reactive overload | X |  | X | X | X | X | X
Alarm action: Reset latch | 26833 | 26834 | Parameters - Non-essential load trip - Trip 2 - Over-current - Commands - NEL 2 over-current | X |  | X | X | X | X | X
Alarm action: Reset latch | 26834 | 26835 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Commands - NEL 2 under-frequency | X |  | X | X | X | X | X
Alarm action: Reset latch | 26835 | 26836 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Commands - NEL 2 overload 1 | X |  | X | X | X | X | X
Alarm action: Reset latch | 26836 | 26837 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Commands - NEL 2 overload 2 | X |  | X | X | X | X | X
Alarm action: Reset latch | 26837 | 26838 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Commands - NEL 2 reactive overload | X |  | X | X | X | X | X
Alarm action: Reset latch | 26838 | 26839 | Parameters - Non-essential load trip - Trip 3 - Over-current - Commands - NEL 3 over-current | X |  | X | X | X | X | X
Alarm action: Reset latch | 26839 | 26840 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Commands - NEL 3 under-frequency | X |  | X | X | X | X | X
Alarm action: Reset latch | 26840 | 26841 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Commands - NEL 3 overload 1 | X |  | X | X | X | X | X
Alarm action: Reset latch | 26841 | 26842 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Commands - NEL 3 overload 2 | X |  | X | X | X | X | X
Alarm action: Reset latch | 26842 | 26843 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Commands - NEL 3 reactive overload | X |  | X | X | X | X | X
Alarm action: Reset latch | 26843 | 26844 | Parameters - System - Monitoring - Single-line hazard - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26844 | 26845 | ID not present | X | X | X | X | X | X | X
Alarm action: Reset latch | 26845 | 26846 | Unsupported application | X | X | X | X | X | X | X
Alarm action: Reset latch | 26846 | 26847 | Application internal CAN protocol conflict | X | X | X | X | X | X | X
Alarm action: Reset latch | 26847 | 26848 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Commands - Section P> | X | X | X | X | X | X | X
Alarm action: Reset latch | 26848 | 26849 | Dry mode: Voltage level unexpected | X |  | X | X | X
Alarm action: Reset latch | 26849 | 26850 | Invalid DAVR configuration | X |  | X | X | X
Alarm action: Reset latch | 26850 | 26851 | Parameters - Communication - DEIF network - DEIF network fork detected - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26852 | 26853 | Parameters - Communication - DEIF network - DEIF network has only one connection - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26854 | 26855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Commands - Breaker vector mismatch | X |  | X | X | X
Alarm action: Reset latch | 26854 | 26855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Commands - Breaker vector mismatch |  | X
Alarm action: Reset latch | 26854 | 26855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Commands - Breaker vector mismatch | [5 empty] | X | X
Alarm action: Reset latch | 26855 | 26856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Commands - Breaker vector mismatch |  |  |  | X
Alarm action: Reset latch | 26855 | 26856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Commands - Breaker vector mismatch | [6 empty] | X
Alarm action: Reset latch | 26857 | 26858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26858 | 26859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26859 | 26860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26860 | 26861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26861 | 26862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Commands - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm action: Reset latch | 26862 | 26863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Commands - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm action: Reset latch | 26863 | 26864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Commands - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm action: Reset latch | 26864 | 26865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Commands - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm action: Reset latch | 26865 | 26866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Commands - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm action: Reset latch | 26866 | 26867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Commands - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm action: Reset latch | 26867 | 26868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Commands - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm action: Reset latch | 26868 | 26869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Commands - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm action: Reset latch | 26869 | 26870 | AC protections not running | X | X | X | X | X | X | X
Alarm action: Reset latch | 26870 | 26871 | AC data is missing | X | X | X | X | X | X | X
Alarm action: Reset latch | 26871 | 26872 | AC protections not running | X | X | X | X | X | X | X
Alarm action: Reset latch | 26872 | 26873 | AC data is missing | X | X | X | X | X | X | X
Alarm action: Reset latch | 26873 | 26874 | AC protections not running | X | X | X | X | X | X | X
Alarm action: Reset latch | 26874 | 26875 | AC data is missing | X | X | X | X | X | X | X
Alarm action: Reset latch | 26875 | 26876 | AC protections not running | X | X | X | X | X | X | X
Alarm action: Reset latch | 26876 | 26877 | AC data is missing | X | X | X | X | X | X | X
Alarm action: Reset latch | 26877 | 26878 | Live voltage detected | X | X | X | X | X | X | X
Alarm action: Reset latch | 26878 | 26879 | Internal issue detected. A restart is required soon! | X | X | X | X | X | X | X
Alarm action: Reset latch | 26879 | 26880 | Parameters - System - Monitoring - Missing controllers - Commands | X | X | X | X | X | X | X
Alarm action: Reset latch | 26880 | 26881 | Card issue detected | X | X | X | X | X | X | X
Alarm action: Reset latch | 26881 | 26882 | Card configuration failed | X | X | X | X | X | X | X
Alarm action: Reset latch | 26882 | 26883 | Unknown traffic on DEIF network | X | X | X | X | X | X | X
Alarm action: Reset latch | 26883 | 26884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Commands - Fill failure | X |  | X | X | X
Alarm action: Reset latch | 26884 | 26885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Commands - Fill failure | X |  | X | X | X
Alarm action: Reset latch | 26885 | 26886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Commands - Fill failure | X |  | X | X | X
Alarm action: Reset latch | 26886 | 26887 | Local IO service error | X | X | X | X | X | X | X
Alarm action: Reset latch | 26887 | 26888 | App logging failure | X | X | X | X | X | X | X
Alarm action: Reset latch | 26888 | 26889 | Event logging failure | X | X | X | X | X | X | X
Alarm action: Reset latch | 26889 | 26890 | Licence error | X | X | X | X | X | X | X
Alarm action: Reset latch | 26890 | 26891 | Brightness is dimmed according to temperature | X | X | X | X | X | X | X
Alarm action: Reset latch | 26891 | 26892 | Parameters - Grid code - Mains sync inhibit - Commands |  |  | X | X
Alarm action: Reset latch | 26892 | 26893 | Parameters - Grid code - Capability curve - Import protection - Commands - Power import capability curve protection |  |  | X | X
Alarm action: Reset latch | 26893 | 26894 | Parameters - Grid code - Capability curve - Export protection - Commands - Power export capability curve protection |  |  | X | X
Alarm action: Reset latch | 26894 | 26895 | Hardware is not compatible based on module versions | X | X | X | X | X | X | X
Alarm action: Remove from service | 28000 | 28001 | Application initialisation error | X | X | X | X | X | X | X
Alarm action: Remove from service | 28001 | 28002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm action: Remove from service | 28002 | 28003 | Preliminary software | X | X | X | X | X | X | X
Alarm action: Remove from service | 28003 | 28004 | Parameters - Engine - Stop sequence - Stop failure - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28004 | 28005 | Parameters - Engine - Start sequence - Start failure - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28005 | 28006 | Parameters - Engine - Start sequence - Crank failure - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28006 | 28007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28007 | 28008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28008 | 28009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28009 | 28010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28010 | 28011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Configuration - Flags - Magnetic pickup wire break alarm | X |  | X | X | X
Alarm action: Remove from service | 28011 | 28012 | Parameters - Engine - Stop sequence - Externally stopped - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28013 | 28014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28014 | 28015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28015 | 28016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28016 | 28017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28017 | 28018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28018 | 28019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28019 | 28020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28020 | 28021 | Parameters - Engine - Protections - Level - Coolant level 1 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28021 | 28022 | Parameters - Engine - Protections - Level - Coolant level 2 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28022 | 28023 | Parameters - Engine - Protections - Level - Coolant level 3 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28027 | 28028 | Parameters - Engine - Running detection - Primary running feedback failure - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28041 | 28042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Configuration - Flags - GB closing failure | X |  | X | X | X
Alarm action: Remove from service | 28041 | 28042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Configuration - Flags - BTB closing failure |  | X
Alarm action: Remove from service | 28041 | 28042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration - Flags - MB closing failure | [5 empty] | X | X
Alarm action: Remove from service | 28042 | 28043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Configuration - Flags - GB opening failure | X |  | X | X | X
Alarm action: Remove from service | 28042 | 28043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Configuration - Flags - BTB opening failure |  | X
Alarm action: Remove from service | 28042 | 28043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration - Flags - MB opening failure | [5 empty] | X | X
Alarm action: Remove from service | 28043 | 28044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Configuration - Flags - GB position failure | X |  | X | X | X
Alarm action: Remove from service | 28043 | 28044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Configuration - Flags - BTB position failure |  | X
Alarm action: Remove from service | 28043 | 28044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration - Flags - MB position failure | [5 empty] | X | X
Alarm action: Remove from service | 28044 | 28045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Configuration - Flags - GB configuration failure | X |  | X | X | X
Alarm action: Remove from service | 28044 | 28045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Configuration - Flags - BTB configuration failure |  | X
Alarm action: Remove from service | 28044 | 28045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration - Flags - MB configuration failure | [5 empty] | X | X
Alarm action: Remove from service | 28045 | 28046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Configuration - Flags - GB synchronisation failure | X |  | X | X | X
Alarm action: Remove from service | 28045 | 28046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Configuration - Flags - BTB synchronisation failure |  | X
Alarm action: Remove from service | 28045 | 28046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration - Flags - MB synchronisation failure | [5 empty] | X | X
Alarm action: Remove from service | 28046 | 28047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Configuration - Flags - GB de-load failure | X |  | X | X | X
Alarm action: Remove from service | 28046 | 28047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Configuration - Flags - BTB de-load failure |  | X
Alarm action: Remove from service | 28046 | 28047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration - Flags - MB de-load failure | [5 empty] | X | X
Alarm action: Remove from service | 28047 | 28048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Configuration - Flags - GB tripped (external) | X |  | X | X | X
Alarm action: Remove from service | 28047 | 28048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Configuration - Flags - BTB tripped (external) |  | X
Alarm action: Remove from service | 28047 | 28048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Configuration - Flags - MB tripped (external) | [5 empty] | X | X
Alarm action: Remove from service | 28048 | 28049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Configuration - Flags - GB short circuit | X |  | X | X | X
Alarm action: Remove from service | 28048 | 28049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Configuration - Flags - BTB short circuit |  | X
Alarm action: Remove from service | 28048 | 28049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Configuration - Flags - MB short circuit | [5 empty] | X | X
Alarm action: Remove from service | 28049 | 28050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration - Flags - MB closing failure |  |  |  | X
Alarm action: Remove from service | 28049 | 28050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Configuration - Flags - TB closing failure | [6 empty] | X
Alarm action: Remove from service | 28050 | 28051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration - Flags - MB opening failure |  |  |  | X
Alarm action: Remove from service | 28050 | 28051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Configuration - Flags - TB opening failure | [6 empty] | X
Alarm action: Remove from service | 28051 | 28052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration - Flags - MB position failure |  |  |  | X
Alarm action: Remove from service | 28051 | 28052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Configuration - Flags - TB position failure | [6 empty] | X
Alarm action: Remove from service | 28052 | 28053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration - Flags - MB configuration failure |  |  |  | X
Alarm action: Remove from service | 28052 | 28053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Configuration - Flags - TB configuration failure | [6 empty] | X
Alarm action: Remove from service | 28053 | 28054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration - Flags - MB synchronisation failure |  |  |  | X
Alarm action: Remove from service | 28053 | 28054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Configuration - Flags - TB synchronisation failure | [6 empty] | X
Alarm action: Remove from service | 28054 | 28055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration - Flags - MB de-load failure |  |  |  | X
Alarm action: Remove from service | 28054 | 28055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Configuration - Flags - TB de-load failure | [6 empty] | X
Alarm action: Remove from service | 28055 | 28056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Configuration - Flags - MB tripped (external) |  |  |  | X
Alarm action: Remove from service | 28055 | 28056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Configuration - Flags - TB tripped (external) | [6 empty] | X
Alarm action: Remove from service | 28056 | 28057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Configuration - Flags - MB short circuit |  |  |  | X
Alarm action: Remove from service | 28056 | 28057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Configuration - Flags - TB short circuit | [6 empty] | X
Alarm action: Remove from service | 28060 | 28061 | Parameters - Mains - AC setup - Phase sequence error - Configuration - Flags - Mains phase sequence error |  |  | X | X
Alarm action: Remove from service | 28060 | 28061 | Parameters - Busbar - AC setup - Phase sequence error - Configuration - Flags - Busbar phase sequence error | X |  |  |  | X | X | X
Alarm action: Remove from service | 28060 | 28061 | Parameters - Busbar B - AC setup - Phase sequence error - Configuration - Flags - Busbar B phase sequence error |  | X
Alarm action: Remove from service | 28061 | 28062 | Parameters - Generator - AC setup - Phase sequence error - Configuration - Flags - Generator phase sequence error | X |  | X | X | X
Alarm action: Remove from service | 28061 | 28062 | Parameters - Busbar A - AC setup - Phase sequence error - Configuration - Flags - Busbar A phase sequence error |  | X
Alarm action: Remove from service | 28061 | 28062 | Parameters - Mains - AC setup - Phase sequence error - Configuration - Flags - Mains phase sequence error | [5 empty] | X | X
Alarm action: Remove from service | 28062 | 28063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28103 | 28104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Configuration - Flags |  |  | X | X
Alarm action: Remove from service | 28103 | 28104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Configuration - Flags | X |  |  |  | X | X | X
Alarm action: Remove from service | 28103 | 28104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Configuration - Flags |  | X
Alarm action: Remove from service | 28104 | 28105 | Parameters - Mains - Additional protections - Vector shift - Configuration - Flags |  |  | X | X
Alarm action: Remove from service | 28104 | 28105 | Parameters - Busbar - Additional protections - Vector shift - Configuration - Flags | X |  |  |  | X | X | X
Alarm action: Remove from service | 28104 | 28105 | Parameters - Busbar B - Additional protections - Vector shift - Configuration - Flags |  | X
Alarm action: Remove from service | 28105 | 28106 | Parameters - Generator - Current protections - Inverse time over-current - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28105 | 28106 | Parameters - Busbar A - Current protections - Inverse time over-current - Configuration - Flags |  | X
Alarm action: Remove from service | 28105 | 28106 | Parameters - Mains - Current protections - Inverse time over-current - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28106 | 28107 | Parameters - Local - 4th current input - Earth inverse time over-current - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28107 | 28108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28108 | 28109 | Parameters - Generator - Additional protections - V< and Q< 1 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28108 | 28109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Configuration - Flags |  | X
Alarm action: Remove from service | 28108 | 28109 | Parameters - Mains - Additional protections - V< and Q< 1 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28109 | 28110 | Parameters - Generator - Additional protections - V< and Q< 2 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28109 | 28110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Configuration - Flags |  | X
Alarm action: Remove from service | 28109 | 28110 | Parameters - Mains - Additional protections - V< and Q< 2 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28110 | 28111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28110 | 28111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Configuration - Flags |  | X
Alarm action: Remove from service | 28110 | 28111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28111 | 28112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28111 | 28112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Configuration - Flags |  | X
Alarm action: Remove from service | 28111 | 28112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28115 | 28116 | Protection set point out of range | X | X | X | X | X | X | X
Alarm action: Remove from service | 28116 | 28117 | Parameters - Generator - Current protections - Stabilised differential current - Configuration - Flags - Stabilised differential | X |  | X | X | X
Alarm action: Remove from service | 28117 | 28118 | Parameters - Generator - Current protections - High set differential current - Configuration - Flags - High set differential | X |  | X | X | X
Alarm action: Remove from service | 28118 | 28119 | Protection set point out of range (differential current) | X |  | X | X | X
Alarm action: Remove from service | 28119 | 28120 | Parameters - Local - Mode - Not under remote control - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28121 | 28122 | Parameters - Local - Monitoring - System not OK - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28122 | 28123 | Configuration update delayed | X | X | X | X | X | X | X
Alarm action: Remove from service | 28123 | 28124 | Critical process error | X | X | X | X | X | X | X
Alarm action: Remove from service | 28124 | 28125 | Restore error | X | X | X | X | X | X | X
Alarm action: Remove from service | 28125 | 28126 | SD-card format error | X | X | X | X | X | X | X
Alarm action: Remove from service | 28126 | 28127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm action: Remove from service | 28127 | 28128 | Fieldbus configuration exceeded maximum I/O configuration | X | X | X | X | X | X | X
Alarm action: Remove from service | 28128 | 28129 | Parameters - Custom alarm - Custom alarm 0 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28129 | 28130 | Parameters - Custom alarm - Custom alarm 1 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28130 | 28131 | Parameters - Custom alarm - Custom alarm 2 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28131 | 28132 | Parameters - Custom alarm - Custom alarm 3 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28132 | 28133 | Parameters - Custom alarm - Custom alarm 4 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28133 | 28134 | Parameters - Custom alarm - Custom alarm 5 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28134 | 28135 | Parameters - Custom alarm - Custom alarm 6 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28135 | 28136 | Parameters - Custom alarm - Custom alarm 7 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28136 | 28137 | Parameters - Custom alarm - Custom alarm 8 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28137 | 28138 | Parameters - Custom alarm - Custom alarm 9 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28138 | 28139 | Parameters - Custom alarm - Custom alarm 10 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28139 | 28140 | Parameters - Custom alarm - Custom alarm 11 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28140 | 28141 | Parameters - Custom alarm - Custom alarm 12 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28141 | 28142 | Parameters - Custom alarm - Custom alarm 13 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28142 | 28143 | Parameters - Custom alarm - Custom alarm 14 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28143 | 28144 | Parameters - Custom alarm - Custom alarm 15 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28144 | 28145 | Parameters - Custom alarm - Custom alarm 16 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28145 | 28146 | Parameters - Custom alarm - Custom alarm 17 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28146 | 28147 | Parameters - Custom alarm - Custom alarm 18 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28147 | 28148 | Parameters - Custom alarm - Custom alarm 19 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28148 | 28149 | Parameters - Custom alarm - Custom alarm 20 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28149 | 28150 | Parameters - Custom alarm - Custom alarm 21 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28150 | 28151 | Parameters - Custom alarm - Custom alarm 22 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28151 | 28152 | Parameters - Custom alarm - Custom alarm 23 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28152 | 28153 | Parameters - Custom alarm - Custom alarm 24 - Configuration - Flags - | X | X | X | X | X | X | X
Alarm action: Remove from service | 28153 | 28154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Configuration - Flags - GOV regulation error | X |  | X | X | X
Alarm action: Remove from service | 28154 | 28155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Configuration - Flags - AVR regulation error | X |  | X | X | X
Alarm action: Remove from service | 28163 | 28164 | Required hardware card(s) not found | X | X | X | X | X | X | X
Alarm action: Remove from service | 28164 | 28165 | Software mismatch on hardware module(s) | X | X | X | X | X | X | X
Alarm action: Remove from service | 28165 | 28166 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration - Flags - Mains L1-L2-L3 wire break |  |  | X
Alarm action: Remove from service | 28165 | 28166 | Parameters - Busbar - AC setup - Multiple phase wire break - Configuration - Flags - Busbar L1-L2-L3 wire break | X |  |  |  | X | X
Alarm action: Remove from service | 28165 | 28166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Configuration - Flags - Busbar B L1-L2-L3 wire break |  | X
Alarm action: Remove from service | 28166 | 28167 | Parameters - Generator - AC setup - Multiple phase wire break - Configuration - Flags - Generator L1-L2-L3 wire break | X |  | X |  | X
Alarm action: Remove from service | 28166 | 28167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Configuration - Flags - Busbar A L1-L2-L3 wire break |  | X
Alarm action: Remove from service | 28166 | 28167 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration - Flags - Mains L1-L2-L3 wire break | [5 empty] | X
Alarm action: Remove from service | 28167 | 28168 | Parameters - Mains - AC setup - L1 wire break - Configuration - Flags - Mains L1 wire break |  |  | X
Alarm action: Remove from service | 28167 | 28168 | Parameters - Busbar - AC setup - L1 wire break - Configuration - Flags - Busbar L1 wire break | X |  |  |  | X | X
Alarm action: Remove from service | 28167 | 28168 | Parameters - Busbar B - AC setup - L1 wire break - Configuration - Flags - Busbar B L1 wire break |  | X
Alarm action: Remove from service | 28168 | 28169 | Parameters - Mains - AC setup - L2 wire break - Configuration - Flags - Mains L2 wire break |  |  | X
Alarm action: Remove from service | 28168 | 28169 | Parameters - Busbar - AC setup - L2 wire break - Configuration - Flags - Busbar L2 wire break | X |  |  |  | X | X
Alarm action: Remove from service | 28168 | 28169 | Parameters - Busbar B - AC setup - L2 wire break - Configuration - Flags - Busbar B L2 wire break |  | X
Alarm action: Remove from service | 28169 | 28170 | Parameters - Mains - AC setup - L3 wire break - Configuration - Flags - Mains L3 wire break |  |  | X
Alarm action: Remove from service | 28169 | 28170 | Parameters - Busbar - AC setup - L3 wire break - Configuration - Flags - Busbar L3 wire break | X |  |  |  | X | X
Alarm action: Remove from service | 28169 | 28170 | Parameters - Busbar B - AC setup - L3 wire break - Configuration - Flags - Busbar B L3 wire break |  | X
Alarm action: Remove from service | 28170 | 28171 | Parameters - Generator - AC setup - L1 wire break - Configuration - Flags - Generator L1 wire break | X |  | X |  | X
Alarm action: Remove from service | 28170 | 28171 | Parameters - Busbar A - AC setup - L1 wire break - Configuration - Flags - Busbar A L1 wire break |  | X
Alarm action: Remove from service | 28170 | 28171 | Parameters - Mains - AC setup - L1 wire break - Configuration - Flags - Mains L1 wire break | [5 empty] | X
Alarm action: Remove from service | 28171 | 28172 | Parameters - Generator - AC setup - L2 wire break - Configuration - Flags - Generator L2 wire break | X |  | X |  | X
Alarm action: Remove from service | 28171 | 28172 | Parameters - Busbar A - AC setup - L2 wire break - Configuration - Flags - Busbar A L2 wire break |  | X
Alarm action: Remove from service | 28171 | 28172 | Parameters - Mains - AC setup - L2 wire break - Configuration - Flags - Mains L2 wire break | [5 empty] | X
Alarm action: Remove from service | 28172 | 28173 | Parameters - Generator - AC setup - L3 wire break - Configuration - Flags - Generator L3 wire break | X |  | X |  | X
Alarm action: Remove from service | 28172 | 28173 | Parameters - Busbar A - AC setup - L3 wire break - Configuration - Flags - Busbar A L3 wire break |  | X
Alarm action: Remove from service | 28172 | 28173 | Parameters - Mains - AC setup - L3 wire break - Configuration - Flags - Mains L3 wire break | [5 empty] | X
Alarm action: Remove from service | 28178 | 28179 | Parameters - Mains - AC setup - Supervision alarm - Configuration - Flags - Mains supervision alarm |  |  | X | X |  | X | X
Alarm action: Remove from service | 28179 | 28180 | Parameters - Engine - Emergency stop - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28179 | 28180 | Parameters - Busbar A - Emergency stop - Configuration - Flags |  | X
Alarm action: Remove from service | 28179 | 28180 | Parameters - Mains - Emergency stop - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28180 | 28181 | Clock battery failure | X | X | X | X | X | X | X
Alarm action: Remove from service | 28181 | 28182 | Controller temperature too high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28182 | 28183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Configuration - Flags - PSM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28183 | 28184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Configuration - Flags - PSM3.1 1 supply voltage low | X | X | X | X | X | X | X
Alarm action: Remove from service | 28184 | 28185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Configuration - Flags - PSM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28185 | 28186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Configuration - Flags - PSM3.2 1 supply voltage low | X | X | X | X | X | X | X
Alarm action: Remove from service | 28186 | 28187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Configuration - Flags - PSM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28187 | 28188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Configuration - Flags - PSM3.2 2 supply voltage low | X | X | X | X | X | X | X
Alarm action: Remove from service | 28188 | 28189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Configuration - Flags - PSM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28189 | 28190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Configuration - Flags - PSM3.2 3 supply voltage low | X | X | X | X | X | X | X
Alarm action: Remove from service | 28190 | 28191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Configuration - Flags - EIM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28191 | 28192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Configuration - Flags - EIM3.1 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Remove from service | 28192 | 28193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Configuration - Flags - EIM3.1 2 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28193 | 28194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Configuration - Flags - EIM3.1 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Remove from service | 28194 | 28195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Configuration - Flags - EIM3.1 3 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28195 | 28196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Configuration - Flags - EIM3.1 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Remove from service | 28196 | 28197 | EIM3.1 4 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28197 | 28198 | EIM3.1 4 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Remove from service | 28198 | 28199 | EIM3.1 5 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28199 | 28200 | EIM3.1 5 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Remove from service | 28200 | 28201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Configuration - Flags - EIM3.1 1 relay 4 wire break | X | X | X | X | X | X | X
Alarm action: Remove from service | 28201 | 28202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Configuration - Flags - EIM3.1 2 relay 4 wire break | X | X | X | X | X | X | X
Alarm action: Remove from service | 28202 | 28203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Configuration - Flags - EIM3.1 3 relay 4 wire break | X | X | X | X | X | X | X
Alarm action: Remove from service | 28203 | 28204 | EIM3.1 4 relay 4 wire break | X | X | X | X | X | X | X
Alarm action: Remove from service | 28204 | 28205 | EIM3.1 5 relay 4 wire break | X | X | X | X | X | X | X
Alarm action: Remove from service | 28205 | 28206 | AC protections not running | X | X | X | X | X | X | X
Alarm action: Remove from service | 28206 | 28207 | AC data is missing | X | X | X | X | X | X | X
Alarm action: Remove from service | 28207 | 28208 | AC protections not running (differential current) | X |  | X | X | X
Alarm action: Remove from service | 28208 | 28209 | AC data is missing (differential current) | X |  | X | X | X
Alarm action: Remove from service | 28209 | 28210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Configuration - Flags - GAM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28210 | 28211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Configuration - Flags - GAM3.2 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Remove from service | 28211 | 28212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Configuration - Flags - GAM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28212 | 28213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Configuration - Flags - GAM3.2 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Remove from service | 28213 | 28214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Configuration - Flags - GAM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28214 | 28215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Configuration - Flags - GAM3.2 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm action: Remove from service | 28215 | 28216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Configuration - Flags - PSM3.2 4 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28216 | 28217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Configuration - Flags - PSM3.2 4 supply voltage low | X | X | X | X | X | X | X
Alarm action: Remove from service | 28217 | 28218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Configuration - Flags - PSM3.2 5 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28218 | 28219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Configuration - Flags - PSM3.2 5 supply voltage low | X | X | X | X | X | X | X
Alarm action: Remove from service | 28219 | 28220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Configuration - Flags - PSM3.2 6 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28220 | 28221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Configuration - Flags - PSM3.2 6 supply voltage low | X | X | X | X | X | X | X
Alarm action: Remove from service | 28221 | 28222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Configuration - Flags - PSM3.2 7 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28222 | 28223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Configuration - Flags - PSM3.2 7 supply voltage low | X | X | X | X | X | X | X
Alarm action: Remove from service | 28223 | 28224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Configuration - Flags - PSM3.2 8 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28224 | 28225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Configuration - Flags - PSM3.2 8 supply voltage low | X | X | X | X | X | X | X
Alarm action: Remove from service | 28225 | 28226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Configuration - Flags - PSM3.2 9 supply voltage high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28226 | 28227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Configuration - Flags - PSM3.2 9 supply voltage low | X | X | X | X | X | X | X
Alarm action: Remove from service | 28228 | 28229 | Parameters - System - Monitoring - Duplicate controller ID - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28229 | 28230 | Parameters - System - Monitoring - Missing all controllers - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28231 | 28232 | Controller ID not configured | X | X | X | X | X | X | X
Alarm action: Remove from service | 28236 | 28237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28237 | 28238 | Blackout detection mismatch | X |  | X | X | X
Alarm action: Remove from service | 28240 | 28241 | Parameters - Communication - NTP - NTP server 1 not connected - Configuration - Flags - NTP server 1 could not connect | X | X | X | X | X | X | X
Alarm action: Remove from service | 28241 | 28242 | Parameters - Communication - NTP - NTP server 1 no response - Configuration - Flags - NTP server 1 is not responding | X | X | X | X | X | X | X
Alarm action: Remove from service | 28242 | 28243 | Parameters - Communication - NTP - NTP server 2 not connected - Configuration - Flags - NTP server 2 could not connect | X | X | X | X | X | X | X
Alarm action: Remove from service | 28243 | 28244 | Parameters - Communication - NTP - NTP server 2 no response - Configuration - Flags - NTP server 2 is not responding | X | X | X | X | X | X | X
Alarm action: Remove from service | 28244 | 28245 | Parameters - Communication - NTP - No NTP server time synchronisation - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28245 | 28246 | Parameters - Communication - NTP - No NTP server(s) connected - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28246 | 28247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28247 | 28248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28296 | 28297 | Controller not part of system | X | X | X | X | X | X | X
Alarm action: Remove from service | 28297 | 28298 | Different single-line configurations | X | X | X | X | X | X | X
Alarm action: Remove from service | 28298 | 28299 | Single-line missing/none active | X | X | X | X | X | X | X
Alarm action: Remove from service | 28299 | 28300 | Parameters - Communication - Modbus - Modbus communication timeout - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28300 | 28301 | Parameters - CODESYS - Monitoring - I/O config conflict - Configuration - Flags - CODESYS configuration conflict | X | X | X | X | X | X | X
Alarm action: Remove from service | 28301 | 28302 | Parameters - CODESYS - Monitoring - Application not OK - Configuration - Flags - CODESYS application not OK | X | X | X | X | X | X | X
Alarm action: Remove from service | 28302 | 28303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28303 | 28304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28304 | 28305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28305 | 28306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28306 | 28307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28307 | 28308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28308 | 28309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28309 | 28310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28310 | 28311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28311 | 28312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28312 | 28313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28313 | 28314 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28314 | 28315 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28315 | 28316 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28316 | 28317 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28317 | 28318 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28318 | 28319 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28319 | 28320 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28320 | 28321 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28321 | 28322 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28322 | 28323 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28323 | 28324 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28324 | 28325 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28325 | 28326 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28326 | 28327 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28327 | 28328 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28328 | 28329 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28329 | 28330 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28330 | 28331 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28331 | 28332 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28332 | 28333 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28333 | 28334 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28334 | 28335 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28335 | 28336 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28336 | 28337 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28337 | 28338 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28338 | 28339 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28339 | 28340 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28340 | 28341 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28341 | 28342 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28342 | 28343 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28343 | 28344 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28344 | 28345 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28345 | 28346 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28346 | 28347 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28347 | 28348 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28348 | 28349 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28349 | 28350 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28350 | 28351 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28351 | 28352 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28352 | 28353 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28353 | 28354 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28354 | 28355 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28355 | 28356 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28356 | 28357 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28357 | 28358 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28358 | 28359 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28359 | 28360 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28360 | 28361 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28361 | 28362 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28362 | 28363 | Digital custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28363 | 28364 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28364 | 28365 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28365 | 28366 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28366 | 28367 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28367 | 28368 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28368 | 28369 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28369 | 28370 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28370 | 28371 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28371 | 28372 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28372 | 28373 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28373 | 28374 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28374 | 28375 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28375 | 28376 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28376 | 28377 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28377 | 28378 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28378 | 28379 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28379 | 28380 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28380 | 28381 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28381 | 28382 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28382 | 28383 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28383 | 28384 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28384 | 28385 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28385 | 28386 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28386 | 28387 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28387 | 28388 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28388 | 28389 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28389 | 28390 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28390 | 28391 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28391 | 28392 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28392 | 28393 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28393 | 28394 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28394 | 28395 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28395 | 28396 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28396 | 28397 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28397 | 28398 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28398 | 28399 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28399 | 28400 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28400 | 28401 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28401 | 28402 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28402 | 28403 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28403 | 28404 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28404 | 28405 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28405 | 28406 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28406 | 28407 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28407 | 28408 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28408 | 28409 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28409 | 28410 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28410 | 28411 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28411 | 28412 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28412 | 28413 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28413 | 28414 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28414 | 28415 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28415 | 28416 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28416 | 28417 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28417 | 28418 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28418 | 28419 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28419 | 28420 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28420 | 28421 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28421 | 28422 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28422 | 28423 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28423 | 28424 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28424 | 28425 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28425 | 28426 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28426 | 28427 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28427 | 28428 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28428 | 28429 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28429 | 28430 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28430 | 28431 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28431 | 28432 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28432 | 28433 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28433 | 28434 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28434 | 28435 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28435 | 28436 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28436 | 28437 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28437 | 28438 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28438 | 28439 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28439 | 28440 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28440 | 28441 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28441 | 28442 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28442 | 28443 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28443 | 28444 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28444 | 28445 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28445 | 28446 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28446 | 28447 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28447 | 28448 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28448 | 28449 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28449 | 28450 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28450 | 28451 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28451 | 28452 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28452 | 28453 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28453 | 28454 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28454 | 28455 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28455 | 28456 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28456 | 28457 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28457 | 28458 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28458 | 28459 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28459 | 28460 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28460 | 28461 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28461 | 28462 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28462 | 28463 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28463 | 28464 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28464 | 28465 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28465 | 28466 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28466 | 28467 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28467 | 28468 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28468 | 28469 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28469 | 28470 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28470 | 28471 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28471 | 28472 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28472 | 28473 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28473 | 28474 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28474 | 28475 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28475 | 28476 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28476 | 28477 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28477 | 28478 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28478 | 28479 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28479 | 28480 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28480 | 28481 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28481 | 28482 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28482 | 28483 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28483 | 28484 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28484 | 28485 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28485 | 28486 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28486 | 28487 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28487 | 28488 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28488 | 28489 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28489 | 28490 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28490 | 28491 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28491 | 28492 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28492 | 28493 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28493 | 28494 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28494 | 28495 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28495 | 28496 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28496 | 28497 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28497 | 28498 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28498 | 28499 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28499 | 28500 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28500 | 28501 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28501 | 28502 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28502 | 28503 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28503 | 28504 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28504 | 28505 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28505 | 28506 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28506 | 28507 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28507 | 28508 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28508 | 28509 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28509 | 28510 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28510 | 28511 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28511 | 28512 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28512 | 28513 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28513 | 28514 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28514 | 28515 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28515 | 28516 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28516 | 28517 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28517 | 28518 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28518 | 28519 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28519 | 28520 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28520 | 28521 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28521 | 28522 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28522 | 28523 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28523 | 28524 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28524 | 28525 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28525 | 28526 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28526 | 28527 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28527 | 28528 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28528 | 28529 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28529 | 28530 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28530 | 28531 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28531 | 28532 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28532 | 28533 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28533 | 28534 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28534 | 28535 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28535 | 28536 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28536 | 28537 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28537 | 28538 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28538 | 28539 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28539 | 28540 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28540 | 28541 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28541 | 28542 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28542 | 28543 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28543 | 28544 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28544 | 28545 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28545 | 28546 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28546 | 28547 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28547 | 28548 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28548 | 28549 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28549 | 28550 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28550 | 28551 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28551 | 28552 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28552 | 28553 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28553 | 28554 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28554 | 28555 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28555 | 28556 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28556 | 28557 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28557 | 28558 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28558 | 28559 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28559 | 28560 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28560 | 28561 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28561 | 28562 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28562 | 28563 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm action: Remove from service | 28565 | 28566 | Parameters - Local - CustomLogic - Configuration invalid - Configuration - Flags - CustomLogic configuration invalid | X | X | X | X | X | X | X
Alarm action: Remove from service | 28566 | 28567 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Configuration - Flags - Digital AVR communication error | X |  | X | X | X
Alarm action: Remove from service | 28567 | 28568 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28568 | 28569 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28569 | 28570 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28570 | 28571 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28571 | 28572 | Parameters - Generator - Digital AVR - Alarms - Open diode - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28572 | 28573 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28573 | 28574 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28574 | 28575 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28575 | 28576 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28576 | 28577 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28577 | 28578 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28578 | 28579 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28579 | 28580 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28580 | 28581 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28581 | 28582 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28582 | 28583 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28583 | 28584 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28584 | 28585 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28585 | 28586 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28586 | 28587 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28587 | 28588 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28588 | 28589 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28589 | 28590 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28590 | 28591 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28591 | 28592 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28592 | 28593 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28593 | 28594 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28594 | 28595 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28595 | 28596 | Parameters - Generator - Digital AVR - Alarms - Motor start - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28596 | 28597 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28597 | 28598 | Parameters - Generator - Digital AVR - Alarms - Power supply - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28598 | 28599 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28599 | 28600 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28600 | 28601 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28601 | 28602 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28602 | 28603 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28603 | 28604 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28604 | 28605 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28605 | 28606 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28606 | 28607 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28607 | 28608 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28608 | 28609 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28609 | 28610 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28610 | 28611 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28611 | 28612 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28612 | 28613 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28613 | 28614 | DAVR unsupported AC configuration | X |  | X | X | X
Alarm action: Remove from service | 28614 | 28615 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Configuration - Flags - Illegal DAVR configuration | X |  | X | X | X
Alarm action: Remove from service | 28615 | 28616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Configuration - Flags - Generator under-voltage 1 | X |  | X | X | X
Alarm action: Remove from service | 28615 | 28616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Configuration - Flags - Busbar A under-voltage 1 |  | X
Alarm action: Remove from service | 28615 | 28616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Flags - Mains under-voltage 1 | [5 empty] | X | X
Alarm action: Remove from service | 28616 | 28617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Configuration - Flags - Generator under-voltage 2 | X |  | X | X | X
Alarm action: Remove from service | 28616 | 28617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Configuration - Flags - Busbar A under-voltage 2 |  | X
Alarm action: Remove from service | 28616 | 28617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Flags - Mains under-voltage 2 | [5 empty] | X | X
Alarm action: Remove from service | 28617 | 28618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Configuration - Flags - Generator under-voltage 3 | X |  | X | X | X
Alarm action: Remove from service | 28617 | 28618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Configuration - Flags - Busbar A under-voltage 3 |  | X
Alarm action: Remove from service | 28617 | 28618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Flags - Mains under-voltage 3 | [5 empty] | X | X
Alarm action: Remove from service | 28618 | 28619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Configuration - Flags - Generator over-voltage 1 | X |  | X | X | X
Alarm action: Remove from service | 28618 | 28619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Configuration - Flags - Busbar A over-voltage 1 |  | X
Alarm action: Remove from service | 28618 | 28619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Flags - Mains over-voltage 1 | [5 empty] | X | X
Alarm action: Remove from service | 28619 | 28620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Configuration - Flags - Generator over-voltage 2 | X |  | X | X | X
Alarm action: Remove from service | 28619 | 28620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Configuration - Flags - Busbar A over-voltage 2 |  | X
Alarm action: Remove from service | 28619 | 28620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Flags - Mains over-voltage 2 | [5 empty] | X | X
Alarm action: Remove from service | 28620 | 28621 | Parameters - Generator - Voltage protections - Voltage unbalance - Configuration - Flags - Generator voltage unbalance | X |  | X | X | X
Alarm action: Remove from service | 28620 | 28621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Configuration - Flags - Busbar A voltage unbalance |  | X
Alarm action: Remove from service | 28620 | 28621 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Flags - Mains voltage unbalance | [5 empty] | X | X
Alarm action: Remove from service | 28621 | 28622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Configuration - Flags - Generator negative sequence voltage | X |  | X | X | X
Alarm action: Remove from service | 28621 | 28622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Configuration - Flags - Busbar A negative sequence voltage |  | X
Alarm action: Remove from service | 28621 | 28622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Flags - Mains negative sequence voltage | [5 empty] | X | X
Alarm action: Remove from service | 28622 | 28623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Configuration - Flags - Generator zero sequence voltage | X |  | X | X | X
Alarm action: Remove from service | 28622 | 28623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Configuration - Flags - Busbar A zero sequence voltage |  | X
Alarm action: Remove from service | 28622 | 28623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Flags - Mains zero sequence voltage | [5 empty] | X | X
Alarm action: Remove from service | 28623 | 28624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Generator positive sequence under-voltage | X |  | X | X | X
Alarm action: Remove from service | 28623 | 28624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Busbar A positive sequence under-voltage |  | X
Alarm action: Remove from service | 28623 | 28624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Mains positive sequence under-voltage | [5 empty] | X | X
Alarm action: Remove from service | 28624 | 28625 | Parameters - Generator - Current protections - Over-current 1 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28624 | 28625 | Parameters - Busbar A - Current protections - Over-current 1 - Configuration - Flags |  | X
Alarm action: Remove from service | 28624 | 28625 | Parameters - Mains - Current protections - Over-current 1 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28625 | 28626 | Parameters - Generator - Current protections - Over-current 2 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28625 | 28626 | Parameters - Busbar A - Current protections - Over-current 2 - Configuration - Flags |  | X
Alarm action: Remove from service | 28625 | 28626 | Parameters - Mains - Current protections - Over-current 2 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28626 | 28627 | Parameters - Generator - Current protections - Over-current 3 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28626 | 28627 | Parameters - Busbar A - Current protections - Over-current 3 - Configuration - Flags |  | X
Alarm action: Remove from service | 28626 | 28627 | Parameters - Mains - Current protections - Over-current 3 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28627 | 28628 | Parameters - Generator - Current protections - Over-current 4 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28627 | 28628 | Parameters - Busbar A - Current protections - Over-current 4 - Configuration - Flags |  | X
Alarm action: Remove from service | 28627 | 28628 | Parameters - Mains - Current protections - Over-current 4 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28628 | 28629 | Parameters - Generator - Current protections - Fast over-current 1 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28628 | 28629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Configuration - Flags |  | X
Alarm action: Remove from service | 28628 | 28629 | Parameters - Mains - Current protections - Fast over-current 1 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28629 | 28630 | Parameters - Generator - Current protections - Fast over-current 2 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28629 | 28630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Configuration - Flags |  | X
Alarm action: Remove from service | 28629 | 28630 | Parameters - Mains - Current protections - Fast over-current 2 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28630 | 28631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28630 | 28631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Configuration - Flags |  | X
Alarm action: Remove from service | 28630 | 28631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28631 | 28632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28631 | 28632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Configuration - Flags |  | X
Alarm action: Remove from service | 28631 | 28632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28632 | 28633 | Parameters - Generator - Current protections - Directional over-current 1 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28632 | 28633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Configuration - Flags |  | X
Alarm action: Remove from service | 28632 | 28633 | Parameters - Mains - Current protections - Directional over-current 1 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28633 | 28634 | Parameters - Generator - Current protections - Directional over-current 2 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28633 | 28634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Configuration - Flags |  | X
Alarm action: Remove from service | 28633 | 28634 | Parameters - Mains - Current protections - Directional over-current 2 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28634 | 28635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Configuration - Flags |  | X
Alarm action: Remove from service | 28635 | 28636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Configuration - Flags |  | X
Alarm action: Remove from service | 28636 | 28637 | Parameters - Generator - Current protections - Negative sequence current - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28636 | 28637 | Parameters - Busbar A - Current protections - Negative sequence current - Configuration - Flags |  | X
Alarm action: Remove from service | 28636 | 28637 | Parameters - Mains - Current protections - Negative sequence current - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28637 | 28638 | Parameters - Generator - Current protections - Zero sequence current - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28637 | 28638 | Parameters - Busbar A - Current protections - Zero sequence current - Configuration - Flags |  | X
Alarm action: Remove from service | 28637 | 28638 | Parameters - Mains - Current protections - Zero sequence current - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28638 | 28639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Configuration - Flags - Generator over-frequency 1 | X |  | X | X | X
Alarm action: Remove from service | 28638 | 28639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Configuration - Flags - Busbar A over-frequency 1 |  | X
Alarm action: Remove from service | 28638 | 28639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Flags - Mains over-frequency 1 | [5 empty] | X | X
Alarm action: Remove from service | 28639 | 28640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Configuration - Flags - Generator over-frequency 2 | X |  | X | X | X
Alarm action: Remove from service | 28639 | 28640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Configuration - Flags - Busbar A over-frequency 2 |  | X
Alarm action: Remove from service | 28639 | 28640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Flags - Mains over-frequency 2 | [5 empty] | X | X
Alarm action: Remove from service | 28640 | 28641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Configuration - Flags - Generator over-frequency 3 | X |  | X | X | X
Alarm action: Remove from service | 28640 | 28641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Configuration - Flags - Busbar A over-frequency 3 |  | X
Alarm action: Remove from service | 28640 | 28641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Flags - Mains over-frequency 3 | [5 empty] | X | X
Alarm action: Remove from service | 28641 | 28642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Configuration - Flags - Generator under-frequency 1 | X |  | X | X | X
Alarm action: Remove from service | 28641 | 28642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Configuration - Flags - Busbar A under-frequency 1 |  | X
Alarm action: Remove from service | 28641 | 28642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Flags - Mains under-frequency 1 | [5 empty] | X | X
Alarm action: Remove from service | 28642 | 28643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Configuration - Flags - Generator under-frequency 2 | X |  | X | X | X
Alarm action: Remove from service | 28642 | 28643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Configuration - Flags - Busbar A under-frequency 2 |  | X
Alarm action: Remove from service | 28642 | 28643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Flags - Mains under-frequency 2 | [5 empty] | X | X
Alarm action: Remove from service | 28643 | 28644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Configuration - Flags - Generator under-frequency 3 | X |  | X | X | X
Alarm action: Remove from service | 28643 | 28644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Configuration - Flags - Busbar A under-frequency 3 |  | X
Alarm action: Remove from service | 28643 | 28644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Flags - Mains under-frequency 3 | [5 empty] | X | X
Alarm action: Remove from service | 28644 | 28645 | Parameters - Generator - Power protections - Overload 1 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28644 | 28645 | Parameters - Busbar A - Power protections - Power export 1 - Configuration - Flags |  | X
Alarm action: Remove from service | 28644 | 28645 | Parameters - Mains - Power protections - Overload 1 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28645 | 28646 | Parameters - Generator - Power protections - Overload 2 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28645 | 28646 | Parameters - Busbar A - Power protections - Power export 2 - Configuration - Flags |  | X
Alarm action: Remove from service | 28645 | 28646 | Parameters - Mains - Power protections - Overload 2 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28646 | 28647 | Parameters - Generator - Power protections - Overload 3 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28646 | 28647 | Parameters - Busbar A - Power protections - Power export 3 - Configuration - Flags |  | X
Alarm action: Remove from service | 28646 | 28647 | Parameters - Mains - Power protections - Overload 3 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28647 | 28648 | Parameters - Generator - Power protections - Overload 4 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28647 | 28648 | Parameters - Busbar A - Power protections - Power export 4 - Configuration - Flags |  | X
Alarm action: Remove from service | 28647 | 28648 | Parameters - Mains - Power protections - Overload 4 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28648 | 28649 | Parameters - Generator - Power protections - Overload 5 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28648 | 28649 | Parameters - Busbar A - Power protections - Power export 5 - Configuration - Flags |  | X
Alarm action: Remove from service | 28648 | 28649 | Parameters - Mains - Power protections - Overload 5 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28649 | 28650 | Parameters - Generator - Power protections - Reverse power 1 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28649 | 28650 | Parameters - Busbar A - Power protections - Power import 1 - Configuration - Flags |  | X
Alarm action: Remove from service | 28649 | 28650 | Parameters - Mains - Power protections - Reverse power 1 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28650 | 28651 | Parameters - Generator - Power protections - Reverse power 2 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28650 | 28651 | Parameters - Busbar A - Power protections - Power import 2 - Configuration - Flags |  | X
Alarm action: Remove from service | 28650 | 28651 | Parameters - Mains - Power protections - Reverse power 2 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28651 | 28652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28651 | 28652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Configuration - Flags |  | X
Alarm action: Remove from service | 28651 | 28652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28652 | 28653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28652 | 28653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Configuration - Flags |  | X
Alarm action: Remove from service | 28652 | 28653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28653 | 28654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28653 | 28654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Configuration - Flags |  | X
Alarm action: Remove from service | 28653 | 28654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28654 | 28655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28654 | 28655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Configuration - Flags |  | X
Alarm action: Remove from service | 28654 | 28655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Configuration - Flags | [5 empty] | X | X
Alarm action: Remove from service | 28655 | 28656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Flags - Mains over-voltage 1 |  |  | X | X
Alarm action: Remove from service | 28655 | 28656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Configuration - Flags - Busbar over-voltage 1 | X |  |  |  | X | X | X
Alarm action: Remove from service | 28655 | 28656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Configuration - Flags - Busbar B over-voltage 1 |  | X
Alarm action: Remove from service | 28656 | 28657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Flags - Mains over-voltage 2 |  |  | X | X
Alarm action: Remove from service | 28656 | 28657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Configuration - Flags - Busbar over-voltage 2 | X |  |  |  | X | X | X
Alarm action: Remove from service | 28656 | 28657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Configuration - Flags - Busbar B over-voltage 2 |  | X
Alarm action: Remove from service | 28657 | 28658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Configuration - Flags - Mains over-voltage 3 |  |  | X | X
Alarm action: Remove from service | 28657 | 28658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Configuration - Flags - Busbar over-voltage 3 | X |  |  |  | X | X | X
Alarm action: Remove from service | 28657 | 28658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Configuration - Flags - Busbar B over-voltage 3 |  | X
Alarm action: Remove from service | 28658 | 28659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Flags - Mains under-voltage 1 |  |  | X | X
Alarm action: Remove from service | 28658 | 28659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Configuration - Flags - Busbar under-voltage 1 | X |  |  |  | X | X | X
Alarm action: Remove from service | 28658 | 28659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Configuration - Flags - Busbar B under-voltage 1 |  | X
Alarm action: Remove from service | 28659 | 28660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Flags - Mains under-voltage 2 |  |  | X | X
Alarm action: Remove from service | 28659 | 28660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Configuration - Flags - Busbar under-voltage 2 | X |  |  |  | X | X | X
Alarm action: Remove from service | 28659 | 28660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Configuration - Flags - Busbar B under-voltage 2 |  | X
Alarm action: Remove from service | 28660 | 28661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Flags - Mains under-voltage 3 |  |  | X | X
Alarm action: Remove from service | 28660 | 28661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Configuration - Flags - Busbar under-voltage 3 | X |  |  |  | X | X | X
Alarm action: Remove from service | 28660 | 28661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Configuration - Flags - Busbar B under-voltage 3 |  | X
Alarm action: Remove from service | 28661 | 28662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Configuration - Flags - Mains under-voltage 4 |  |  | X | X
Alarm action: Remove from service | 28661 | 28662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Configuration - Flags - Busbar under-voltage 4 | X |  |  |  | X | X | X
Alarm action: Remove from service | 28661 | 28662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Configuration - Flags - Busbar B under-voltage 4 |  | X
Alarm action: Remove from service | 28662 | 28663 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Flags - Mains voltage unbalance |  |  | X | X
Alarm action: Remove from service | 28662 | 28663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Configuration - Flags - Busbar voltage unbalance | X |  |  |  | X | X | X
Alarm action: Remove from service | 28662 | 28663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Configuration - Flags - Busbar B voltage unbalance |  | X
Alarm action: Remove from service | 28663 | 28664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Flags - Mains over-frequency 1 |  |  | X | X
Alarm action: Remove from service | 28663 | 28664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Configuration - Flags - Busbar over-frequency 1 | X |  |  |  | X | X | X
Alarm action: Remove from service | 28663 | 28664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Configuration - Flags - Busbar B over-frequency 1 |  | X
Alarm action: Remove from service | 28664 | 28665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Flags - Mains over-frequency 2 |  |  | X | X
Alarm action: Remove from service | 28664 | 28665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Configuration - Flags - Busbar over-frequency 2 | X |  |  |  | X | X | X
Alarm action: Remove from service | 28664 | 28665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Configuration - Flags - Busbar B over-frequency 2 |  | X
Alarm action: Remove from service | 28665 | 28666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Flags - Mains over-frequency 3 |  |  | X | X
Alarm action: Remove from service | 28665 | 28666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Configuration - Flags - Busbar over-frequency 3 | X |  |  |  | X | X | X
Alarm action: Remove from service | 28665 | 28666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Configuration - Flags - Busbar B over-frequency 3 |  | X
Alarm action: Remove from service | 28666 | 28667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Flags - Mains under-frequency 1 |  |  | X | X
Alarm action: Remove from service | 28666 | 28667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Configuration - Flags - Busbar under-frequency 1 | X |  |  |  | X | X | X
Alarm action: Remove from service | 28666 | 28667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Configuration - Flags - Busbar B under-frequency 1 |  | X
Alarm action: Remove from service | 28667 | 28668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Flags - Mains under-frequency 2 |  |  | X | X
Alarm action: Remove from service | 28667 | 28668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Configuration - Flags - Busbar under-frequency 2 | X |  |  |  | X | X | X
Alarm action: Remove from service | 28667 | 28668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Configuration - Flags - Busbar B under-frequency 2 |  | X
Alarm action: Remove from service | 28668 | 28669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Flags - Mains under-frequency 3 |  |  | X | X
Alarm action: Remove from service | 28668 | 28669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Configuration - Flags - Busbar under-frequency 3 | X |  |  |  | X | X | X
Alarm action: Remove from service | 28668 | 28669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Configuration - Flags - Busbar B under-frequency 3 |  | X
Alarm action: Remove from service | 28669 | 28670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Configuration - Flags - Mains under-frequency 4 |  |  | X | X
Alarm action: Remove from service | 28669 | 28670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Configuration - Flags - Busbar under-frequency 4 | X |  |  |  | X | X | X
Alarm action: Remove from service | 28669 | 28670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Configuration - Flags - Busbar B under-frequency 4 |  | X
Alarm action: Remove from service | 28670 | 28671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Flags - Busbar negative sequence voltage |  |  | X | X
Alarm action: Remove from service | 28670 | 28671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Configuration - Flags - Busbar negative sequence voltage | X |  |  |  | X | X | X
Alarm action: Remove from service | 28670 | 28671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Configuration - Flags - Busbar B negative sequence voltage |  | X
Alarm action: Remove from service | 28671 | 28672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Flags - Busbar zero sequence voltage |  |  | X | X
Alarm action: Remove from service | 28671 | 28672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Configuration - Flags - Busbar zero sequence voltage | X |  |  |  | X | X | X
Alarm action: Remove from service | 28671 | 28672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Configuration - Flags - Busbar B zero sequence voltage |  | X
Alarm action: Remove from service | 28672 | 28673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Busbar positive sequence under-voltage |  |  | X | X
Alarm action: Remove from service | 28672 | 28673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Busbar positive sequence under-voltage | X |  |  |  | X | X | X
Alarm action: Remove from service | 28672 | 28673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Configuration - Flags - Busbar B positive sequence under-voltage |  | X
Alarm action: Remove from service | 28717 | 28718 | Parameters - Engine - Maintenance - Service timer - Configuration - Flags - Service timer 1 | X |  | X | X | X
Alarm action: Remove from service | 28718 | 28719 | Parameters - Engine - Maintenance - Service timer - Configuration - Flags - Service timer 2 | X |  | X | X | X
Alarm action: Remove from service | 28719 | 28720 | Parameters - Engine - Maintenance - Service timer - Configuration - Flags - Service timer 3 | X |  | X | X | X
Alarm action: Remove from service | 28720 | 28721 | Parameters - Engine - Maintenance - Service timer - Configuration - Flags - Service timer 4 | X |  | X | X | X
Alarm action: Remove from service | 28721 | 28722 | External MB open failure | X | X | X | X | X | X | X
Alarm action: Remove from service | 28722 | 28723 | Parameters - Power management rules - Ground relay - Ground relay general failure - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28723 | 28724 | Parameters - Power management rules - Ground relay - Ground relay open failure - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28724 | 28725 | Parameters - Power management rules - Ground relay - Ground relay close failure - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28725 | 28726 | Parameters - Power management rules - Ground relay - Ground relay position failure - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28726 | 28727 | Parameters - Breakers - Close before excitation - CBE rerun failure - Configuration - Flags | X |  | X | X | X
Alarm action: Remove from service | 28727 | 28728 | Parameters - Breakers - Close before excitation - CBE failure - Configuration - Flags - Close before excitation failure | X |  | X | X | X
Alarm action: Remove from service | 28728 | 28729 | Load too high | X | X | X | X | X | X | X
Alarm action: Remove from service | 28729 | 28730 | ID to run configuration failure | [5 empty] | X | X
Alarm action: Remove from service | 28731 | 28732 | Parameters - System - Monitoring - Missing any genset controller - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28732 | 28733 | Parameters - System - Monitoring - Missing any mains controller - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28733 | 28734 | Parameters - System - Monitoring - Missing any bustie controller - Configuration - Flags - Missing any bus tie controller | X | X | X | X | X | X | X
Alarm action: Remove from service | 28734 | 28735 | Can ID not available | X | X | X | X | X | X | X
Alarm action: Remove from service | 28735 | 28736 | Duplicated CAN IDs | X | X | X | X | X | X | X
Alarm action: Remove from service | 28736 | 28737 | Parameters - Local power management - Alarms - Busbar blocked - Configuration - Flags - Busbar blocked due to position failure | X |  | X | X | X | X | X
Alarm action: Remove from service | 28737 | 28738 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Configuration - Flags - Busbar A blocked due to position failure |  | X
Alarm action: Remove from service | 28738 | 28739 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Configuration - Flags - Busbar B blocked due to position failure |  | X
Alarm action: Remove from service | 28739 | 28740 | Parameters - System - Monitoring - BTB 33 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28740 | 28741 | Parameters - System - Monitoring - BTB 34 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28741 | 28742 | Parameters - System - Monitoring - BTB 35 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28742 | 28743 | Parameters - System - Monitoring - BTB 36 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28743 | 28744 | Parameters - System - Monitoring - BTB 37 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28744 | 28745 | Parameters - System - Monitoring - BTB 38 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28745 | 28746 | Parameters - System - Monitoring - BTB 39 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28746 | 28747 | Parameters - System - Monitoring - BTB 40 position failure - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28747 | 28748 | Primary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28748 | 28749 | Primary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28749 | 28750 | Primary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28750 | 28751 | Primary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28751 | 28752 | Primary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28752 | 28753 | Primary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28753 | 28754 | Primary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28754 | 28755 | Primary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28755 | 28756 | Primary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28756 | 28757 | Primary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28757 | 28758 | Primary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28758 | 28759 | Primary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28759 | 28760 | Primary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28760 | 28761 | Primary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28761 | 28762 | Primary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28762 | 28763 | Primary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28763 | 28764 | Primary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28764 | 28765 | Primary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28765 | 28766 | Primary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28766 | 28767 | Primary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28767 | 28768 | Primary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28768 | 28769 | Primary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28769 | 28770 | Primary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28770 | 28771 | Primary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28771 | 28772 | Primary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28772 | 28773 | Primary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28773 | 28774 | Primary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28774 | 28775 | Primary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28775 | 28776 | Primary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28776 | 28777 | Primary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28777 | 28778 | Primary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28778 | 28779 | Primary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28779 | 28780 | Primary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28780 | 28781 | Primary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28781 | 28782 | Primary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28782 | 28783 | Primary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28783 | 28784 | Primary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28784 | 28785 | Primary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28785 | 28786 | Primary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28786 | 28787 | Primary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28787 | 28788 | Secondary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28788 | 28789 | Secondary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28789 | 28790 | Secondary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28790 | 28791 | Secondary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28791 | 28792 | Secondary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28792 | 28793 | Secondary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28793 | 28794 | Secondary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28794 | 28795 | Secondary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28795 | 28796 | Secondary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28796 | 28797 | Secondary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28797 | 28798 | Secondary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28798 | 28799 | Secondary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28799 | 28800 | Secondary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28800 | 28801 | Secondary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28801 | 28802 | Secondary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28802 | 28803 | Secondary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28803 | 28804 | Secondary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28804 | 28805 | Secondary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28805 | 28806 | Secondary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28806 | 28807 | Secondary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28807 | 28808 | Secondary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28808 | 28809 | Secondary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28809 | 28810 | Secondary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28810 | 28811 | Secondary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28811 | 28812 | Secondary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28812 | 28813 | Secondary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28813 | 28814 | Secondary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28814 | 28815 | Secondary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28815 | 28816 | Secondary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28816 | 28817 | Secondary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28817 | 28818 | Secondary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28818 | 28819 | Secondary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28819 | 28820 | Secondary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28820 | 28821 | Secondary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28821 | 28822 | Secondary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28822 | 28823 | Secondary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28823 | 28824 | Secondary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28824 | 28825 | Secondary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28825 | 28826 | Secondary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28826 | 28827 | Secondary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm action: Remove from service | 28827 | 28828 | Priority error | X | X | X | X | X | X | X
Alarm action: Remove from service | 28828 | 28829 | Parameters - Non-essential load trip - Trip 1 - Over-current - Configuration - Flags - NEL 1 over-current | X |  | X | X | X | X | X
Alarm action: Remove from service | 28829 | 28830 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Configuration - Flags - NEL 1 under-frequency | X |  | X | X | X | X | X
Alarm action: Remove from service | 28830 | 28831 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Configuration - Flags - NEL 1 overload 1 | X |  | X | X | X | X | X
Alarm action: Remove from service | 28831 | 28832 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Configuration - Flags - NEL 1 overload 2 | X |  | X | X | X | X | X
Alarm action: Remove from service | 28832 | 28833 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Configuration - Flags - NEL 1 reactive overload | X |  | X | X | X | X | X
Alarm action: Remove from service | 28833 | 28834 | Parameters - Non-essential load trip - Trip 2 - Over-current - Configuration - Flags - NEL 2 over-current | X |  | X | X | X | X | X
Alarm action: Remove from service | 28834 | 28835 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Configuration - Flags - NEL 2 under-frequency | X |  | X | X | X | X | X
Alarm action: Remove from service | 28835 | 28836 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Configuration - Flags - NEL 2 overload 1 | X |  | X | X | X | X | X
Alarm action: Remove from service | 28836 | 28837 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Configuration - Flags - NEL 2 overload 2 | X |  | X | X | X | X | X
Alarm action: Remove from service | 28837 | 28838 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Configuration - Flags - NEL 2 reactive overload | X |  | X | X | X | X | X
Alarm action: Remove from service | 28838 | 28839 | Parameters - Non-essential load trip - Trip 3 - Over-current - Configuration - Flags - NEL 3 over-current | X |  | X | X | X | X | X
Alarm action: Remove from service | 28839 | 28840 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Configuration - Flags - NEL 3 under-frequency | X |  | X | X | X | X | X
Alarm action: Remove from service | 28840 | 28841 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Configuration - Flags - NEL 3 overload 1 | X |  | X | X | X | X | X
Alarm action: Remove from service | 28841 | 28842 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Configuration - Flags - NEL 3 overload 2 | X |  | X | X | X | X | X
Alarm action: Remove from service | 28842 | 28843 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Configuration - Flags - NEL 3 reactive overload | X |  | X | X | X | X | X
Alarm action: Remove from service | 28843 | 28844 | Parameters - System - Monitoring - Single-line hazard - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28844 | 28845 | ID not present | X | X | X | X | X | X | X
Alarm action: Remove from service | 28845 | 28846 | Unsupported application | X | X | X | X | X | X | X
Alarm action: Remove from service | 28846 | 28847 | Application internal CAN protocol conflict | X | X | X | X | X | X | X
Alarm action: Remove from service | 28847 | 28848 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Configuration - Flags - Section P> | X | X | X | X | X | X | X
Alarm action: Remove from service | 28848 | 28849 | Dry mode: Voltage level unexpected | X |  | X | X | X
Alarm action: Remove from service | 28849 | 28850 | Invalid DAVR configuration | X |  | X | X | X
Alarm action: Remove from service | 28850 | 28851 | Parameters - Communication - DEIF network - DEIF network fork detected - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28852 | 28853 | Parameters - Communication - DEIF network - DEIF network has only one connection - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28854 | 28855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Configuration - Flags - Breaker vector mismatch | X |  | X | X | X
Alarm action: Remove from service | 28854 | 28855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Configuration - Flags - Breaker vector mismatch |  | X
Alarm action: Remove from service | 28854 | 28855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Flags - Breaker vector mismatch | [5 empty] | X | X
Alarm action: Remove from service | 28855 | 28856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Flags - Breaker vector mismatch |  |  |  | X
Alarm action: Remove from service | 28855 | 28856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Configuration - Flags - Breaker vector mismatch | [6 empty] | X
Alarm action: Remove from service | 28857 | 28858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28858 | 28859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28859 | 28860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28860 | 28861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28861 | 28862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Configuration - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm action: Remove from service | 28862 | 28863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Configuration - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm action: Remove from service | 28863 | 28864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Configuration - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm action: Remove from service | 28864 | 28865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Configuration - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm action: Remove from service | 28865 | 28866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Configuration - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm action: Remove from service | 28866 | 28867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Configuration - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm action: Remove from service | 28867 | 28868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Configuration - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm action: Remove from service | 28868 | 28869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Configuration - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm action: Remove from service | 28869 | 28870 | AC protections not running | X | X | X | X | X | X | X
Alarm action: Remove from service | 28870 | 28871 | AC data is missing | X | X | X | X | X | X | X
Alarm action: Remove from service | 28871 | 28872 | AC protections not running | X | X | X | X | X | X | X
Alarm action: Remove from service | 28872 | 28873 | AC data is missing | X | X | X | X | X | X | X
Alarm action: Remove from service | 28873 | 28874 | AC protections not running | X | X | X | X | X | X | X
Alarm action: Remove from service | 28874 | 28875 | AC data is missing | X | X | X | X | X | X | X
Alarm action: Remove from service | 28875 | 28876 | AC protections not running | X | X | X | X | X | X | X
Alarm action: Remove from service | 28876 | 28877 | AC data is missing | X | X | X | X | X | X | X
Alarm action: Remove from service | 28877 | 28878 | Live voltage detected | X | X | X | X | X | X | X
Alarm action: Remove from service | 28878 | 28879 | Internal issue detected. A restart is required soon! | X | X | X | X | X | X | X
Alarm action: Remove from service | 28879 | 28880 | Parameters - System - Monitoring - Missing controllers - Configuration - Flags | X | X | X | X | X | X | X
Alarm action: Remove from service | 28880 | 28881 | Card issue detected | X | X | X | X | X | X | X
Alarm action: Remove from service | 28881 | 28882 | Card configuration failed | X | X | X | X | X | X | X
Alarm action: Remove from service | 28882 | 28883 | Unknown traffic on DEIF network | X | X | X | X | X | X | X
Alarm action: Remove from service | 28883 | 28884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Configuration - Flags - Fill failure | X |  | X | X | X
Alarm action: Remove from service | 28884 | 28885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Configuration - Flags - Fill failure | X |  | X | X | X
Alarm action: Remove from service | 28885 | 28886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Configuration - Flags - Fill failure | X |  | X | X | X
Alarm action: Remove from service | 28886 | 28887 | Local IO service error | X | X | X | X | X | X | X
Alarm action: Remove from service | 28887 | 28888 | App logging failure | X | X | X | X | X | X | X
Alarm action: Remove from service | 28888 | 28889 | Event logging failure | X | X | X | X | X | X | X
Alarm action: Remove from service | 28889 | 28890 | Licence error | X | X | X | X | X | X | X
Alarm action: Remove from service | 28890 | 28891 | Brightness is dimmed according to temperature | X | X | X | X | X | X | X
Alarm action: Remove from service | 28891 | 28892 | Parameters - Grid code - Mains sync inhibit - Configuration - Flags |  |  | X | X
Alarm action: Remove from service | 28892 | 28893 | Parameters - Grid code - Capability curve - Import protection - Configuration - Flags - Power import capability curve protection |  |  | X | X
Alarm action: Remove from service | 28893 | 28894 | Parameters - Grid code - Capability curve - Export protection - Configuration - Flags - Power export capability curve protection |  |  | X | X
Alarm action: Remove from service | 28894 | 28895 | Hardware is not compatible based on module versions | X | X | X | X | X | X | X
General parameter: Enable | 46015 | 46016 | Parameters - Engine - Idle run start - Idle run - Enable | X |  | X | X | X
General parameter: Enable | 46017 | 46018 | Parameters - Engine - Idle run start - Minimum - Use | X |  | X | X | X
General parameter: Enable | 46026 | 46027 | Parameters - Engine - Idle run stop - Minimum - Use | X |  | X | X | X
General parameter: Enable | 46042 | 46043 | Parameters - Engine - Running detection - Oil pressure running detection - Use oil pressure | X |  | X | X | X
General parameter: Enable | 46043 | 46044 | Parameters - Engine - Running detection - RPM running detection - Use engine speed | X |  | X | X | X
General parameter: Enable | 46273 | 46274 | Parameters - Engine - Power derate - Temperature - Derate 1 - Enable - Enable derate | X |  | X | X | X
General parameter: Enable | 46295 | 46296 | Parameters - Engine - Power derate - Temperature - Derate 2 - Enable - Enable derate | X |  | X | X | X
General parameter: Enable | 46317 | 46318 | Parameters - Engine - Power derate - Temperature - Derate 3 - Enable - Enable derate | X |  | X | X | X
General parameter: Enable | 46318 | 46319 | Parameters - Engine - Power derate - Percentage - Derate 1 - Enable - Enable derate | X |  | X | X | X
General parameter: Enable | 46627 | 46628 | Parameters - Local - Command sources - Active local sources - PICUS commands | X | X | X | X | X | X | X
General parameter: Enable | 46628 | 46629 | Parameters - Local - Command sources - Active local sources - Modbus commands | X | X | X | X | X | X | X
General parameter: Enable | 46629 | 46630 | Parameters - Local - Command sources - Active local sources - I/O commands | X | X | X | X | X | X | X
General parameter: Enable | 46630 | 46631 | Parameters - Local - Command sources - Active local sources - CustomLogic commands | X | X | X | X | X | X | X
General parameter: Enable | 46631 | 46632 | Parameters - Local - Command sources - Active local sources - CODESYS commands | X | X | X | X | X | X | X
General parameter: Enable | 46633 | 46634 | Parameters - Local - Command sources - Active remote sources - PICUS commands | X | X | X | X | X | X | X
General parameter: Enable | 46634 | 46635 | Parameters - Local - Command sources - Active remote sources - Modbus commands | X | X | X | X | X | X | X
General parameter: Enable | 46635 | 46636 | Parameters - Local - Command sources - Active remote sources - I/O commands | X | X | X | X | X | X | X
General parameter: Enable | 46636 | 46637 | Parameters - Local - Command sources - Active remote sources - CustomLogic commands | X | X | X | X | X | X | X
General parameter: Enable | 46637 | 46638 | Parameters - Local - Command sources - Active remote sources - CODESYS commands | X | X | X | X | X | X | X
General parameter: Enable | 46639 | 46640 | Parameters - Local - Alarm horn - Horn 1 - De-energise when all alarms are acknowledged | X | X | X | X | X | X | X
General parameter: Enable | 46640 | 46641 | Parameters - Local - Alarm horn - Horn 1 - Reset when new alarm | X | X | X | X | X | X | X
General parameter: Enable | 46643 | 46644 | Parameters - Local - Alarm horn - Horn 2 - De-energise when all alarms are acknowledged | X | X | X | X | X | X | X
General parameter: Enable | 46644 | 46645 | Parameters - Local - Alarm horn - Horn 2 - Reset when new alarm | X | X | X | X | X | X | X
General parameter: Enable | 46647 | 46648 | Parameters - Local - Alarm horn - Horn 3 - De-energise when all alarms are acknowledged | X | X | X | X | X | X | X
General parameter: Enable | 46648 | 46649 | Parameters - Local - Alarm horn - Horn 3 - Reset when new alarm | X | X | X | X | X | X | X
General parameter: Enable | 46653 | 46654 | Parameters - Local - CustomLogic - Configuration - Enable | X | X | X | X | X | X | X
General parameter: Enable | 47048 | 47049 | Parameters - Mains - AC setup - Supervision selector - Enable supervision |  |  | X | X |  | X | X
General parameter: Enable | 47069 | 47070 | Parameters - Test functions - Lamp test - Activate | X | X | X | X | X | X | X
General parameter: Enable | 47074 | 47075 | Parameters - CODESYS - Configuration - Enable | X | X | X | X | X | X | X
General parameter: Enable | 47077 | 47078 | Parameters - Engine - ECU - Controls - Speed control (TSC1 / Custom) - Enable | X |  | X | X | X
General parameter: Enable | 47079 | 47080 | Parameters - Engine - ECU - Controls - Generator control (GC1 / Custom) - Enable | X |  | X | X | X
General parameter: Enable | 47082 | 47083 | EIC derate | X |  | X | X | X
General parameter: Enable | 47083 | 47084 | Parameters - Engine - ECU - Controls - Speed control (TSC1 / Custom) - Use nominal RPM as reference | X |  | X | X | X
General parameter: Enable | 47084 | 47085 | Parameters - Engine - ECU - Controls - CAN controls - Enable | X |  | X | X | X
General parameter: Enable | 47085 | 47086 | Parameters - Engine - ECU - DPF controls - Controls - Aftertreatment Regeneration Inhibit Switch | X |  | X | X | X
General parameter: Enable | 47105 | 47106 | Parameters - Test functions - Emulation - Emulation active | X | X | X | X | X | X | X
General parameter: Enable | 47121 | 47122 | Parameters - Generator - Digital AVR - AC setup - Voltage transformer - Enable VT | X |  | X | X | X
General parameter: Enable | 47136 | 47137 | Parameters - Generator - Digital AVR - Settings - Controls - Write all settings | X |  | X | X | X
General parameter: Enable | 47138 | 47139 | Parameters - Generator - Digital AVR - Settings - Controls | X |  | X | X | X
General parameter: Enable | 47145 | 47146 | Parameters - Generator - Digital AVR - Settings - Controls - Reset all DVC alarms | X |  | X | X | X
General parameter: Enable | 47219 | 47220 | Parameters - Power management rules - Ground relay - Enable | X |  | X | X | X
General parameter: Enable | 47249 | 47250 | Parameters - Regulators - GOV - Regulation set points - Active power ramp configuration - Island ramping | X |  | X | X | X
General parameter: Enable | 47255 | 47256 | Parameters - Local power management - Mains configuration - Tie breaker configuration - TB de-load before GB | [5 empty] | X | X
General parameter: Enable | 47263 | 47264 | Internal CAN protocol | X | X | X | X | X | X | X
General parameter: Enable | 47289 | 47290 | Parameters - System power management - Bus tie breaker - Closed ring - Ring close allowed |  | X
General parameter: Enable | 47292 | 47293 | Parameters - System power management - Store common settings - Settings | X |  |  |  | X | X | X
General parameter: Enable | 47293 | 47294 | Parameters - Local power management - Mains configuration - Mains breaker configuration - Back synchronising | X |  | X | X | X | X | X
General parameter: Enable | 47294 | 47295 | Parameters - Local power management - Mains configuration - Mains breaker configuration - Synchronisation to mains | X |  | X | X | X | X | X
General parameter: Enable | 47295 | 47296 | Parallel |  | X
General parameter: Enable | 47295 | 47296 | Parameters - Local power management - Mains configuration - Mains breaker configuration - Parallel | [5 empty] | X | X
General parameter: Enable | 47296 | 47297 | No break transfer |  | X
General parameter: Enable | 47296 | 47297 | Parameters - Local power management - Mains configuration - Mains breaker configuration - No break transfer | [5 empty] | X | X
General parameter: Enable | 47300 | 47301 | Parameters - Local power management - Mains configuration - Controls - MB failure start | [5 empty] | X | X
General parameter: Enable | 47306 | 47307 | Parameters - Local power management - Mains configuration - Tie breaker configuration - Power capacity overrule enable | X | X | X | X | X | X | X
General parameter: Enable | 47307 | 47308 | Parameters - Local power management - Mains configuration - Controls - Exclude run all | [5 empty] | X | X
General parameter: Enable | 47345 | 47346 | Parameters - Non-essential load trip - Trip 1 - Settings - Trip when breaker trips | X |  | X | X | X | X | X
General parameter: Enable | 47346 | 47347 | Parameters - Non-essential load trip - Trip 2 - Settings - Trip when breaker trips | X |  | X | X | X | X | X
General parameter: Enable | 47347 | 47348 | Parameters - Non-essential load trip - Trip 3 - Settings - Trip when breaker trips | X |  | X | X | X | X | X
General parameter: Enable | 47368 | 47369 | Parameters - Power management rules - Load-dependent start/stop - Start 2 - Delay - Configuration | X | X | X | X | X | X | X
General parameter: Enable | 47373 | 47374 | Parameters - Power management rules - Load-dependent start/stop - Stop 2 - Delay - Configuration | X | X | X | X | X | X | X
General parameter: Enable | 47387 | 47388 | Parameters - Regulators - GOV - Regulation set points - Active power ramp configuration - Enter operation ramp enable | X |  | X | X | X
General parameter: Enable | 47388 | 47389 | Parameters - Regulators - GOV - Regulation set points - Active power ramp configuration - Deload ramp enable | X |  | X | X | X
General parameter: Enable | 47981 | 47982 | Parameters - Breakers - Close before excitation - Configuration - Enable | X |  | X | X | X | X | X
General parameter: Enable | 47982 | 47983 | Parameters - Regulators - GOV - Regulation set points - Base load | X |  | X | X | X
General parameter: Enable | 47984 | 47985 | Parameters - Power management rules - Asymmetric load sharing - Start when an asymmetric set point is exceeded - Enable | X | X | X | X | X
General parameter: Enable | 47991 | 47992 | Parameters - Power management rules - Load-dependent start/stop - Start 2 - Enable | X | X | X | X | X | X | X
General parameter: Enable | 47992 | 47993 | Parameters - Power management rules - Load-dependent start/stop - Stop 2 - Enable | X | X | X | X | X | X | X
General parameter: Enable | 47993 | 47994 | Parameters - Power management rules - Power reservation - Reserved power - Enable | X | X | X | X | X
General parameter: Enable | 47996 | 47997 | Parameters - Engine - ECU diagnostic - Enable | X |  | X | X | X
General parameter: Enable | 47997 | 47998 | Parameters - Engine - ECU diagnostic - Use timer | X |  | X | X | X
General parameter: Enable | 48015 | 48016 | Parameters - Grid code - Frequency offset - Frequency offset enable |  |  | X | X
General parameter: Enable | 48047 | 48048 | Parameters - Grid code - Feedforward - FeedForwardVolt_Ena |  |  | X | X
General parameter: Enable | 48049 | 48050 | Parameters - Grid code - Feedforward - FeedForwardFreq_Ena |  |  | X | X
General parameter: Enable | 48051 | 48052 | Parameters - Regulators - GOV - Regulation set points - Active power ramp configuration - Enable operation ramp 2 |  |  | X | X
General parameter: Enable | 48052 | 48053 | Parameters - Regulators - GOV - Regulation set points - Active power ramp configuration - Enable operation ramp 3 |  |  | X | X
General parameter: Enable | 48053 | 48054 | Parameters - Regulators - GOV - Regulation set points - Active power ramp configuration - Enable operation ramp 4 |  |  | X | X
General parameter: Enable | 48190 | 48191 | Parameters - Grid code - var(Q) regulation - Configuration - Limit Q under-excited |  |  | X | X
General parameter: Enable | 48191 | 48192 | Parameters - Grid code - var(Q) regulation - Configuration - Limit Q over-excited |  |  | X | X
General parameter: Enable | 48230 | 48231 | Parameters - Grid code - Droop curve 2 - Droop curve 2 enable |  |  | X | X

## Discrete input contact (02)
Discrete input contact (02)
Function group | Modbus address | PLC address | Controller function name | LC_GENSET_GB | LC_BUSTIE_BTB | LC_SINGLE_GENSET_GB | LC_SINGLE_GENSET_GB_MB | LC_SINGLE_GENSET_GB_NO_MAINS | LC_MAINS_MB | LC_MAINS_MB_TB
Status flag | 8000 | 108001 | Functions - Digital output functions - Engine - Controls - Run coil | X |  | X | X | X
Status flag | 8001 | 108002 | Functions - Digital output functions - Engine - Controls - Stop coil | X |  | X | X | X
Status flag | 8002 | 108003 | Functions - Digital output functions - Engine - Controls - Start prepare | X |  | X | X | X
Status flag | 8003 | 108004 | Functions - Digital output functions - Engine - Controls - Crank | X |  | X | X | X
Status flag | 8010 | 108011 | Functions - Digital output functions - Engine - State - Start prepare completed | X |  | X | X | X
Status flag | 8012 | 108013 | Functions - Digital output functions - Engine - State - Idling | X |  | X | X | X
Status flag | 8013 | 108014 | Functions - Digital output functions - Engine - Controls - Idle run | X |  | X | X | X
Status flag | 8014 | 108015 | Functions - Digital output functions - Engine - State - Running | X |  | X | X | X
Status flag | 8015 | 108016 | Functions - Digital output functions - Engine - State - Not running | X |  | X | X | X
Status flag | 8017 | 108018 | Fill failure 1 | X |  | X | X | X
Status flag | 8018 | 108019 | Functions - Digital output functions - Breakers - Generator breaker - Controls - GB open | X |  | X | X | X
Status flag | 8018 | 108019 | Functions - Digital output functions - Breakers - Bus tie breaker - Controls - BTB open |  | X
Status flag | 8018 | 108019 | Functions - Digital output functions - Breakers - Mains breaker - Controls - MB open | [5 empty] | X | X
Status flag | 8019 | 108020 | Functions - Digital output functions - Breakers - Generator breaker - Controls - GB close | X |  | X | X | X
Status flag | 8019 | 108020 | Functions - Digital output functions - Breakers - Bus tie breaker - Controls - BTB close |  | X
Status flag | 8019 | 108020 | Functions - Digital output functions - Breakers - Mains breaker - Controls - MB close | [5 empty] | X | X
Status flag | 8020 | 108021 | Functions - Digital output functions - Breakers - Generator breaker - State - GB is open | X |  | X | X | X
Status flag | 8020 | 108021 | Functions - Digital output functions - Breakers - Bus tie breaker - State - BTB is open |  | X
Status flag | 8020 | 108021 | Functions - Digital output functions - Breakers - Mains breaker - State - MB is open | [5 empty] | X | X
Status flag | 8021 | 108022 | Functions - Digital output functions - Breakers - Generator breaker - State - GB is closed | X |  | X | X | X
Status flag | 8021 | 108022 | Functions - Digital output functions - Breakers - Bus tie breaker - State - BTB is closed |  | X
Status flag | 8021 | 108022 | Functions - Digital output functions - Breakers - Mains breaker - State - MB is closed | [5 empty] | X | X
Status flag | 8022 | 108023 | Functions - Digital output functions - Breakers - Generator breaker - State - GB is synchronising | X |  | X | X | X
Status flag | 8022 | 108023 | Functions - Digital output functions - Breakers - Bus tie breaker - State - BTB is synchronising |  | X
Status flag | 8022 | 108023 | Functions - Digital output functions - Breakers - Mains breaker - State - MB is synchronising | [5 empty] | X | X
Status flag | 8023 | 108024 | Functions - Digital output functions - Breakers - Generator breaker - State - GB is de-loading | X |  | X | X | X
Status flag | 8023 | 108024 | Functions - Digital output functions - Breakers - Bus tie breaker - State - BTB is de-loading |  | X
Status flag | 8023 | 108024 | Functions - Digital output functions - Breakers - Mains breaker - State - MB is de-loading | [5 empty] | X | X
Status flag | 8024 | 108025 | Functions - Digital output functions - Breakers - Generator breaker - State - GB is preparing | X |  | X | X | X
Status flag | 8024 | 108025 | Functions - Digital output functions - Breakers - Bus tie breaker - State - BTB is preparing |  | X
Status flag | 8024 | 108025 | Functions - Digital output functions - Breakers - Mains breaker - State - MB is preparing | [5 empty] | X | X
Status flag | 8026 | 108027 | Functions - Digital output functions - Breakers - Mains breaker - Controls - MB open |  |  |  | X
Status flag | 8026 | 108027 | Functions - Digital output functions - Breakers - Tie breaker - Controls - TB open | [6 empty] | X
Status flag | 8027 | 108028 | Functions - Digital output functions - Breakers - Mains breaker - Controls - MB close |  |  |  | X
Status flag | 8027 | 108028 | Functions - Digital output functions - Breakers - Tie breaker - Controls - TB close | [6 empty] | X
Status flag | 8028 | 108029 | Functions - Digital output functions - Breakers - Mains breaker - State - MB is open |  |  |  | X
Status flag | 8028 | 108029 | Functions - Digital output functions - Breakers - Tie breaker - State - TB is open | [6 empty] | X
Status flag | 8029 | 108030 | Functions - Digital output functions - Breakers - Mains breaker - State - MB is closed |  |  |  | X
Status flag | 8029 | 108030 | Functions - Digital output functions - Breakers - Tie breaker - State - TB is closed | [6 empty] | X
Status flag | 8030 | 108031 | Functions - Digital output functions - Breakers - Mains breaker - State - MB is synchronising |  |  |  | X
Status flag | 8030 | 108031 | Functions - Digital output functions - Breakers - Tie breaker - State - TB is synchronising | [6 empty] | X
Status flag | 8031 | 108032 | Functions - Digital output functions - Breakers - Mains breaker - State - MB is de-loading |  |  |  | X
Status flag | 8031 | 108032 | Functions - Digital output functions - Breakers - Tie breaker - State - TB is de-loading | [6 empty] | X
Status flag | 8032 | 108033 | Functions - Digital output functions - Breakers - Mains breaker - State - MB is preparing |  |  |  | X
Status flag | 8032 | 108033 | Functions - Digital output functions - Breakers - Tie breaker - State - TB is preparing | [6 empty] | X
Status flag | 8034 | 108035 | Delta frequency above max. | X | X | X | X | X | X | X
Status flag | 8035 | 108036 | Delta frequency below min. | X | X | X | X | X | X | X
Status flag | 8036 | 108037 | Delta voltage above max. | X | X | X | X | X | X | X
Status flag | 8037 | 108038 | Delta voltage below min. | X | X | X | X | X | X | X
Status flag | 8038 | 108039 | Vector mismatch | X | X | X | X | X | X | X
Status flag | 8039 | 108040 | Phase angle outside window | X | X | X | X | X | X | X
Status flag | 8040 | 108041 | Inside window | X | X | X | X | X | X | X
Status flag | 8041 | 108042 | Synchronisation in progress | X | X | X | X | X | X | X
Status flag | 8042 | 108043 | Delta frequency above max. |  |  |  | X |  |  | X
Status flag | 8043 | 108044 | Delta frequency below min. |  |  |  | X |  |  | X
Status flag | 8044 | 108045 | Delta voltage above max. |  |  |  | X |  |  | X
Status flag | 8045 | 108046 | Delta voltage below min. |  |  |  | X |  |  | X
Status flag | 8046 | 108047 | Vector mismatch |  |  |  | X |  |  | X
Status flag | 8047 | 108048 | Phase angle outside window |  |  |  | X |  |  | X
Status flag | 8048 | 108049 | Inside window |  |  |  | X |  |  | X
Status flag | 8049 | 108050 | Synchronisation in progress |  |  |  | X |  |  | X
Status flag | 8050 | 108051 | Functions - Digital output functions - Local - Nominal settings - Controller nominal setting - Nominal settings 1 selected | X | X | X | X | X | X | X
Status flag | 8051 | 108052 | Functions - Digital output functions - Local - Nominal settings - Controller nominal setting - Nominal settings 2 selected | X | X | X | X | X | X | X
Status flag | 8052 | 108053 | Functions - Digital output functions - Local - Nominal settings - Controller nominal setting - Nominal settings 3 selected | X | X | X | X | X | X | X
Status flag | 8053 | 108054 | Functions - Digital output functions - Local - Nominal settings - Controller nominal setting - Nominal settings 4 selected | X | X | X | X | X | X | X
Status flag | 8054 | 108055 | Functions - Digital output functions - Generator - Production counters - Active energy export pulse | X |  | X | X | X
Status flag | 8054 | 108055 | Functions - Digital output functions - Busbar A - Production counters - Active energy export pulse |  | X
Status flag | 8054 | 108055 | Functions - Digital output functions - Mains - Production counters - Active energy export pulse | [5 empty] | X | X
Status flag | 8055 | 108056 | Functions - Digital output functions - Generator - Production counters - Reactive energy export pulse | X |  | X | X | X
Status flag | 8055 | 108056 | Functions - Digital output functions - Busbar A - Production counters - Reactive energy export pulse |  | X
Status flag | 8055 | 108056 | Functions - Digital output functions - Mains - Production counters - Reactive energy export pulse | [5 empty] | X | X
Status flag | 8056 | 108057 | Functions - Digital output functions - Busbar A - Production counters - Active energy import pulse |  | X
Status flag | 8056 | 108057 | Functions - Digital output functions - Mains - Production counters - Active energy import pulse | [5 empty] | X | X
Status flag | 8057 | 108058 | Functions - Digital output functions - Busbar A - Production counters - Reactive energy import pulse |  | X
Status flag | 8057 | 108058 | Functions - Digital output functions - Mains - Production counters - Reactive energy import pulse | [5 empty] | X | X
Status flag | 8058 | 108059 | Functions - Digital output functions - Busbar A - Production counters - Active energy difference pulse |  | X
Status flag | 8058 | 108059 | Functions - Digital output functions - Mains - Production counters - Active energy difference pulse | [5 empty] | X | X
Status flag | 8059 | 108060 | Functions - Digital output functions - Busbar A - Production counters - Reactive energy difference pulse |  | X
Status flag | 8059 | 108060 | Functions - Digital output functions - Mains - Production counters - Reactive energy difference pulse | [5 empty] | X | X
Status flag | 8060 | 108061 | Functions - Digital output functions - Mains - State - Voltage and frequency OK |  |  | X | X
Status flag | 8060 | 108061 | Functions - Digital output functions - Busbar - State - Voltage and frequency OK | X |  |  |  | X | X | X
Status flag | 8060 | 108061 | Functions - Digital output functions - Busbar B - State - Voltage and frequency OK |  | X
Status flag | 8061 | 108062 | Functions - Digital output functions - Mains - State - No voltage and frequency |  |  | X | X
Status flag | 8061 | 108062 | Functions - Digital output functions - Busbar - State - No voltage and frequency | X |  |  |  | X | X | X
Status flag | 8061 | 108062 | Functions - Digital output functions - Busbar B - State - No voltage and frequency |  | X
Status flag | 8062 | 108063 | Functions - Digital output functions - Generator - State - Voltage and frequency OK | X |  | X | X | X
Status flag | 8062 | 108063 | Functions - Digital output functions - Busbar A - State - Voltage and frequency OK |  | X
Status flag | 8062 | 108063 | Functions - Digital output functions - Mains - State - Voltage and frequency OK | [5 empty] | X | X
Status flag | 8063 | 108064 | Functions - Digital output functions - Generator - State - No voltage and frequency | X |  | X | X | X
Status flag | 8063 | 108064 | Functions - Digital output functions - Busbar A - State - No voltage and frequency |  | X
Status flag | 8063 | 108064 | Functions - Digital output functions - Mains - State - No voltage and frequency | [5 empty] | X | X
Status flag | 8064 | 108065 | Functions - Digital output functions - Local - Mode - Under local control | X | X | X | X | X | X | X
Status flag | 8065 | 108066 | Functions - Digital output functions - Local - Mode - Under remote control | X | X | X | X | X | X | X
Status flag | 8066 | 108067 | Functions - Digital output functions - Local - Alarm horn - Horn 1 | X | X | X | X | X | X | X
Status flag | 8067 | 108068 | Functions - Digital output functions - Local - Alarm horn - Horn 2 | X | X | X | X | X | X | X
Status flag | 8068 | 108069 | Functions - Digital output functions - Local - Alarm horn - Horn 3 | X | X | X | X | X | X | X
Status flag | 8069 | 108070 | Functions - Digital output functions - Local - System OK - Status OK | X | X | X | X | X | X | X
Status flag | 8070 | 108071 | Functions - Digital output functions - Local - Alive | X | X | X | X | X | X | X
Status flag | 8071 | 108072 | Functions - Digital output functions - Alarm system - State - Any warning alarm | X | X | X | X | X | X | X
Status flag | 8072 | 108073 | Functions - Digital output functions - Alarm system - State - Any block alarm | X | X | X | X | X | X | X
Status flag | 8073 | 108074 | Functions - Digital output functions - Alarm system - State - Any GB trip alarm | X |  | X | X | X
Status flag | 8074 | 108075 | Functions - Digital output functions - Alarm system - State - Any GB trip and stop alarm | X |  | X | X | X
Status flag | 8075 | 108076 | Functions - Digital output functions - Alarm system - State - Any GB trip and shutdown alarm | X |  | X | X | X
Status flag | 8076 | 108077 | Functions - Digital output functions - Alarm system - State - Any BTB trip alarm |  | X
Status flag | 8077 | 108078 | Functions - Digital output functions - Alarm system - State - Any alarm | X | X | X | X | X | X | X
Status flag | 8078 | 108079 | Functions - Digital output functions - Alarm system - State - Any unacknowledged alarm | X | X | X | X | X | X | X
Status flag | 8079 | 108080 | Functions - Digital output functions - Alarm system - State - Any latched alarm | X | X | X | X | X | X | X
Status flag | 8080 | 108081 | Functions - Digital output functions - Alarm system - State - Any shelved alarm | X | X | X | X | X | X | X
Status flag | 8081 | 108082 | Functions - Digital output functions - Alarm system - State - Any out of service alarm | X | X | X | X | X | X | X
Status flag | 8082 | 108083 | Functions - Digital output functions - Alarm system - State - Any MB trip alarm |  |  |  | X |  | X | X
Status flag | 8089 | 108090 | Functions - Digital output functions - Local - CustomLogic - State - Is enabled | X | X | X | X | X | X | X
Status flag | 8090 | 108091 | Functions - Digital output functions - Regulators - AVR - Controls - AVR increase | X |  | X | X | X
Status flag | 8091 | 108092 | Functions - Digital output functions - Regulators - AVR - Controls - AVR decrease | X |  | X | X | X
Status flag | 8092 | 108093 | Functions - Digital output functions - Regulators - GOV - Controls - GOV increase | X |  | X | X | X
Status flag | 8093 | 108094 | Functions - Digital output functions - Regulators - GOV - Controls - GOV decrease | X |  | X | X | X
Status flag | 8116 | 108117 | Functions - Digital output functions - Mains - Supervision - Mains error |  |  | X | X |  | X | X
Status flag | 8117 | 108118 | Functions - Digital output functions - Mains - Supervision - Mains recovery fast |  |  | X | X |  | X | X
Status flag | 8118 | 108119 | Functions - Digital output functions - Mains - Supervision - Mains recovery slow |  |  | X | X |  | X | X
Status flag | 8119 | 108120 | EIM3.1 1 relay 4 wire break detection | X | X | X | X | X | X | X
Status flag | 8120 | 108121 | EIM3.1 2 relay 4 wire break detection | X | X | X | X | X | X | X
Status flag | 8121 | 108122 | EIM3.1 3 relay 4 wire break detection | X | X | X | X | X | X | X
Status flag | 8122 | 108123 | EIM3.1 4 relay 4 wire break detection | X | X | X | X | X | X | X
Status flag | 8123 | 108124 | EIM3.1 5 relay 4 wire break detection | X | X | X | X | X | X | X
Status flag | 8137 | 108138 | Texts - Pop-up active | X | X | X | X | X | X | X
Status flag | 8138 | 108139 | Functions - Digital output functions - Local - CODESYS - State - CODESYS application OK | X | X | X | X | X | X | X
Status flag | 8139 | 108140 | Functions - Digital output functions - Alarm system - State - Any TB trip alarm | [6 empty] | X
Status flag | 8142 | 108143 | Functions - Digital output functions - Alarm system - Severity - Any high severity alarm | X | X | X | X | X | X | X
Status flag | 8143 | 108144 | Functions - Digital output functions - Alarm system - Severity - Any medium severity alarm | X | X | X | X | X | X | X
Status flag | 8144 | 108145 | Functions - Digital output functions - Alarm system - Severity - Any low severity alarm | X | X | X | X | X | X | X
Status flag | 8145 | 108146 | Functions - Digital output functions - Auxiliary - Ground relay - Ground relay A | X |  | X | X | X
Status flag | 8146 | 108147 | Functions - Digital output functions - Auxiliary - Ground relay - Ground relay B | X |  | X | X | X
Status flag | 8147 | 108148 | Functions - Digital output functions - Auxiliary - Close before excitation - CBE AVR relay | X |  | X | X | X
Status flag | 8148 | 108149 | Functions - Digital output functions - Local - Mode - In MANUAL | X | X | X | X | X | X | X
Status flag | 8149 | 108150 | Functions - Digital output functions - Alarm system - State - Any PMS-controlled stop alarm | X |  | X | X | X
Status flag | 8150 | 108151 | Functions - Digital output functions - Alarm system - State - Any controlled stop alarm | X |  | X | X | X
Status flag | 8151 | 108152 | External power set point is selected | X |  | X | X |  | X | X
Status flag | 8152 | 108153 | Functions - Digital output functions - Non-essential load trip - Non-essential load trip 1 | X |  | X | X | X | X | X
Status flag | 8153 | 108154 | Functions - Digital output functions - Non-essential load trip - Non-essential load trip 2 | X |  | X | X | X | X | X
Status flag | 8154 | 108155 | Functions - Digital output functions - Non-essential load trip - Non-essential load trip 3 | X |  | X | X | X | X | X
Status flag | 8155 | 108156 | Functions - Digital output functions - Regulators - GOV - State - Enter operation ramp active | X |  | X | X | X
Status flag | 8156 | 108157 | Functions - Digital output functions - Regulators - GOV - State - Operation ramp 1 active | X |  | X | X | X
Status flag | 8157 | 108158 | Functions - Digital output functions - Regulators - GOV - State - Deload ramp active | X |  | X | X | X
Status flag | 8158 | 108159 | Functions - Digital output functions - Local - Nominal settings - Transducer 1 nominal setting - Nominal settings 1 selected | X | X | X | X | X | X | X
Status flag | 8159 | 108160 | Functions - Digital output functions - Local - Nominal settings - Transducer 1 nominal setting - Nominal settings 2 selected | X | X | X | X | X | X | X
Status flag | 8160 | 108161 | Functions - Digital output functions - Local - Nominal settings - Transducer 1 nominal setting - Nominal settings 3 selected | X | X | X | X | X | X | X
Status flag | 8161 | 108162 | Functions - Digital output functions - Local - Nominal settings - Transducer 1 nominal setting - Nominal settings 4 selected | X | X | X | X | X | X | X
Status flag | 8162 | 108163 | Functions - Digital output functions - Local - Nominal settings - Transducer 2 nominal setting - Nominal settings 1 selected | X | X | X | X | X | X | X
Status flag | 8163 | 108164 | Functions - Digital output functions - Local - Nominal settings - Transducer 2 nominal setting - Nominal settings 2 selected | X | X | X | X | X | X | X
Status flag | 8164 | 108165 | Functions - Digital output functions - Local - Nominal settings - Transducer 2 nominal setting - Nominal settings 3 selected | X | X | X | X | X | X | X
Status flag | 8165 | 108166 | Functions - Digital output functions - Local - Nominal settings - Transducer 2 nominal setting - Nominal settings 4 selected | X | X | X | X | X | X | X
Status flag | 8166 | 108167 | Functions - Digital output functions - Local - Nominal settings - Transducer 3 nominal setting - Nominal settings 1 selected | X | X | X | X | X | X | X
Status flag | 8167 | 108168 | Functions - Digital output functions - Local - Nominal settings - Transducer 3 nominal setting - Nominal settings 2 selected | X | X | X | X | X | X | X
Status flag | 8168 | 108169 | Functions - Digital output functions - Local - Nominal settings - Transducer 3 nominal setting - Nominal settings 3 selected | X | X | X | X | X | X | X
Status flag | 8169 | 108170 | Functions - Digital output functions - Local - Nominal settings - Transducer 3 nominal setting - Nominal settings 4 selected | X | X | X | X | X | X | X
Status flag | 8170 | 108171 | Functions - Digital output functions - Local - Nominal settings - Transducer 4 nominal setting - Nominal settings 1 selected | X | X | X | X | X | X | X
Status flag | 8171 | 108172 | Functions - Digital output functions - Local - Nominal settings - Transducer 4 nominal setting - Nominal settings 2 selected | X | X | X | X | X | X | X
Status flag | 8172 | 108173 | Functions - Digital output functions - Local - Nominal settings - Transducer 4 nominal setting - Nominal settings 3 selected | X | X | X | X | X | X | X
Status flag | 8173 | 108174 | Functions - Digital output functions - Local - Nominal settings - Transducer 4 nominal setting - Nominal settings 4 selected | X | X | X | X | X | X | X
Status flag | 8174 | 108175 | Functions - Digital output functions - Transducers - Transducer 1 - Reference A - Production counters - Active energy export pulse | X | X | X | X | X | X | X
Status flag | 8175 | 108176 | Functions - Digital output functions - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy export pulse | X | X | X | X | X | X | X
Status flag | 8176 | 108177 | Functions - Digital output functions - Transducers - Transducer 1 - Reference A - Production counters - Active energy import pulse | X | X | X | X | X | X | X
Status flag | 8177 | 108178 | Functions - Digital output functions - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy import pulse | X | X | X | X | X | X | X
Status flag | 8178 | 108179 | Functions - Digital output functions - Transducers - Transducer 1 - Reference A - Production counters - Active energy difference pulse | X | X | X | X | X | X | X
Status flag | 8179 | 108180 | Functions - Digital output functions - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy difference pulse | X | X | X | X | X | X | X
Status flag | 8180 | 108181 | Functions - Digital output functions - Transducers - Transducer 2 - Reference A - Production counters - Active energy export pulse | X | X | X | X | X | X | X
Status flag | 8181 | 108182 | Functions - Digital output functions - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy export pulse | X | X | X | X | X | X | X
Status flag | 8182 | 108183 | Functions - Digital output functions - Transducers - Transducer 2 - Reference A - Production counters - Active energy import pulse | X | X | X | X | X | X | X
Status flag | 8183 | 108184 | Functions - Digital output functions - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy import pulse | X | X | X | X | X | X | X
Status flag | 8184 | 108185 | Functions - Digital output functions - Transducers - Transducer 2 - Reference A - Production counters - Active energy difference pulse | X | X | X | X | X | X | X
Status flag | 8185 | 108186 | Functions - Digital output functions - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy difference pulse | X | X | X | X | X | X | X
Status flag | 8186 | 108187 | Functions - Digital output functions - Transducers - Transducer 3 - Reference A - Production counters - Active energy export pulse | X | X | X | X | X | X | X
Status flag | 8187 | 108188 | Functions - Digital output functions - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy export pulse | X | X | X | X | X | X | X
Status flag | 8188 | 108189 | Functions - Digital output functions - Transducers - Transducer 3 - Reference A - Production counters - Active energy import pulse | X | X | X | X | X | X | X
Status flag | 8189 | 108190 | Functions - Digital output functions - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy import pulse | X | X | X | X | X | X | X
Status flag | 8190 | 108191 | Functions - Digital output functions - Transducers - Transducer 3 - Reference A - Production counters - Active energy difference pulse | X | X | X | X | X | X | X
Status flag | 8191 | 108192 | Functions - Digital output functions - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy difference pulse | X | X | X | X | X | X | X
Status flag | 8192 | 108193 | Functions - Digital output functions - Transducers - Transducer 4 - Reference A - Production counters - Active energy export pulse | X | X | X | X | X | X | X
Status flag | 8193 | 108194 | Functions - Digital output functions - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy export pulse | X | X | X | X | X | X | X
Status flag | 8194 | 108195 | Functions - Digital output functions - Transducers - Transducer 4 - Reference A - Production counters - Active energy import pulse | X | X | X | X | X | X | X
Status flag | 8195 | 108196 | Functions - Digital output functions - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy import pulse | X | X | X | X | X | X | X
Status flag | 8196 | 108197 | Functions - Digital output functions - Transducers - Transducer 4 - Reference A - Production counters - Active energy difference pulse | X | X | X | X | X | X | X
Status flag | 8197 | 108198 | Functions - Digital output functions - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy difference pulse | X | X | X | X | X | X | X
Status flag | 8198 | 108199 | Functions - Digital output functions - Transducers - Transducer 1 - Reference B - State - Voltage and frequency OK | X | X | X | X | X | X | X
Status flag | 8199 | 108200 | Functions - Digital output functions - Transducers - Transducer 1 - Reference B - State - No voltage and frequency | X | X | X | X | X | X | X
Status flag | 8200 | 108201 | Functions - Digital output functions - Transducers - Transducer 2 - Reference B - State - Voltage and frequency OK | X | X | X | X | X | X | X
Status flag | 8201 | 108202 | Functions - Digital output functions - Transducers - Transducer 2 - Reference B - State - No voltage and frequency | X | X | X | X | X | X | X
Status flag | 8202 | 108203 | Functions - Digital output functions - Transducers - Transducer 3 - Reference B - State - Voltage and frequency OK | X | X | X | X | X | X | X
Status flag | 8203 | 108204 | Functions - Digital output functions - Transducers - Transducer 3 - Reference B - State - No voltage and frequency | X | X | X | X | X | X | X
Status flag | 8204 | 108205 | Functions - Digital output functions - Transducers - Transducer 4 - Reference B - State - Voltage and frequency OK | X | X | X | X | X | X | X
Status flag | 8205 | 108206 | Functions - Digital output functions - Transducers - Transducer 4 - Reference B - State - No voltage and frequency | X | X | X | X | X | X | X
Status flag | 8206 | 108207 | Functions - Digital output functions - Transducers - Transducer 1 - Reference A - State - Voltage and frequency OK | X | X | X | X | X | X | X
Status flag | 8207 | 108208 | Functions - Digital output functions - Transducers - Transducer 1 - Reference A - State - No voltage and frequency | X | X | X | X | X | X | X
Status flag | 8208 | 108209 | Functions - Digital output functions - Transducers - Transducer 2 - Reference A - State - Voltage and frequency OK | X | X | X | X | X | X | X
Status flag | 8209 | 108210 | Functions - Digital output functions - Transducers - Transducer 2 - Reference A - State - No voltage and frequency | X | X | X | X | X | X | X
Status flag | 8210 | 108211 | Functions - Digital output functions - Transducers - Transducer 3 - Reference A - State - Voltage and frequency OK | X | X | X | X | X | X | X
Status flag | 8211 | 108212 | Functions - Digital output functions - Transducers - Transducer 3 - Reference A - State - No voltage and frequency | X | X | X | X | X | X | X
Status flag | 8212 | 108213 | Functions - Digital output functions - Transducers - Transducer 4 - Reference A - State - Voltage and frequency OK | X | X | X | X | X | X | X
Status flag | 8213 | 108214 | Functions - Digital output functions - Transducers - Transducer 4 - Reference A - State - No voltage and frequency | X | X | X | X | X | X | X
Status flag | 8223 | 108224 | Functions - Digital output functions - Auxiliary - Pump logic - Activate pump 1 | X |  | X | X | X
Status flag | 8224 | 108225 | Functions - Digital output functions - Auxiliary - Pump logic - Activate pump 2 | X |  | X | X | X
Status flag | 8225 | 108226 | Functions - Digital output functions - Auxiliary - Pump logic - Activate pump 3 | X |  | X | X | X
Status flag | 8230 | 108231 | Functions - Digital output functions - Regulators - GOV - State - Operation ramp 2 active |  |  | X | X
Status flag | 8231 | 108232 | Functions - Digital output functions - Regulators - GOV - State - Operation ramp 3 active |  |  | X | X
Status flag | 8232 | 108233 | Functions - Digital output functions - Regulators - GOV - State - Operation ramp 4 active |  |  | X | X
Status flag | 8233 | 108234 | Functions - Digital output functions - Grid code - RRCR - RRCR output 1 |  |  | X | X
Status flag | 8234 | 108235 | Functions - Digital output functions - Grid code - RRCR - RRCR output 2 |  |  | X | X
Status flag | 8235 | 108236 | Functions - Digital output functions - Grid code - RRCR - RRCR output 3 |  |  | X | X
Status flag | 8236 | 108237 | Functions - Digital output functions - Grid code - RRCR - RRCR output 4 |  |  | X | X
Status flag | 8237 | 108238 | Functions - Digital output functions - Grid code - Mains sync inhibit - Recovery delay 1 |  |  | X | X
Status flag | 8238 | 108239 | Functions - Digital output functions - Grid code - Mains sync inhibit - Recovery delay 2 |  |  | X | X
CustomLogic: Modbus signal | 12000 | 112001 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 1 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12001 | 112002 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 2 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12002 | 112003 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 3 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12003 | 112004 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 4 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12004 | 112005 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 5 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12005 | 112006 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 6 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12006 | 112007 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 7 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12007 | 112008 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 8 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12008 | 112009 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 9 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12009 | 112010 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 10 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12010 | 112011 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 11 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12011 | 112012 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 12 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12012 | 112013 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 13 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12013 | 112014 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 14 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12014 | 112015 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 15 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12015 | 112016 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 16 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12016 | 112017 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 17 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12017 | 112018 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 18 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12018 | 112019 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 19 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12019 | 112020 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 20 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12020 | 112021 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 21 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12021 | 112022 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 22 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12022 | 112023 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 23 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12023 | 112024 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 24 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12024 | 112025 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 25 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12025 | 112026 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 26 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12026 | 112027 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 27 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12027 | 112028 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 28 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12028 | 112029 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 29 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12029 | 112030 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 30 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12030 | 112031 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 31 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12031 | 112032 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 32 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12032 | 112033 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 33 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12033 | 112034 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 34 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12034 | 112035 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 35 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12035 | 112036 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 36 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12036 | 112037 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 37 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12037 | 112038 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 38 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12038 | 112039 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 39 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12039 | 112040 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 40 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12040 | 112041 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 41 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12041 | 112042 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 42 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12042 | 112043 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 43 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12043 | 112044 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 44 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12044 | 112045 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 45 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12045 | 112046 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 46 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12046 | 112047 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 47 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12047 | 112048 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 48 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12048 | 112049 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 49 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12049 | 112050 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 50 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12050 | 112051 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 51 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12051 | 112052 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 52 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12052 | 112053 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 53 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12053 | 112054 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 54 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12054 | 112055 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 55 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12055 | 112056 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 56 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12056 | 112057 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 57 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12057 | 112058 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 58 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12058 | 112059 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 59 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12059 | 112060 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 60 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12060 | 112061 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 61 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12061 | 112062 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 62 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12062 | 112063 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 63 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12063 | 112064 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 64 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12064 | 112065 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 65 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12065 | 112066 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 66 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12066 | 112067 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 67 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12067 | 112068 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 68 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12068 | 112069 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 69 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12069 | 112070 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 70 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12070 | 112071 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 71 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12071 | 112072 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 72 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12072 | 112073 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 73 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12073 | 112074 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 74 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12074 | 112075 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 75 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12075 | 112076 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 76 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12076 | 112077 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 77 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12077 | 112078 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 78 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12078 | 112079 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 79 | X | X | X | X | X | X | X
CustomLogic: Modbus signal | 12079 | 112080 | Functions - Digital output functions - Local - CustomLogic - Signals - Signal 80 | X | X | X | X | X | X | X
Custom logic: digital output | 12200 | 112201 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12201 | 112202 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12202 | 112203 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12203 | 112204 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12204 | 112205 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12205 | 112206 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12206 | 112207 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12207 | 112208 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12208 | 112209 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12209 | 112210 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12210 | 112211 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12211 | 112212 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12212 | 112213 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12213 | 112214 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12214 | 112215 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12215 | 112216 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12216 | 112217 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12217 | 112218 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12218 | 112219 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12219 | 112220 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12220 | 112221 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12221 | 112222 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12222 | 112223 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12223 | 112224 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12224 | 112225 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12225 | 112226 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12226 | 112227 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12227 | 112228 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12228 | 112229 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12229 | 112230 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12230 | 112231 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12231 | 112232 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12232 | 112233 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12233 | 112234 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12234 | 112235 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12235 | 112236 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12236 | 112237 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12237 | 112238 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12238 | 112239 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12239 | 112240 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12240 | 112241 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12241 | 112242 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12242 | 112243 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12243 | 112244 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12244 | 112245 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12245 | 112246 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12246 | 112247 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12247 | 112248 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12248 | 112249 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12249 | 112250 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12250 | 112251 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12251 | 112252 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12252 | 112253 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12253 | 112254 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12254 | 112255 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12255 | 112256 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12256 | 112257 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12257 | 112258 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12258 | 112259 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12259 | 112260 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12260 | 112261 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12261 | 112262 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12262 | 112263 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12263 | 112264 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12264 | 112265 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12265 | 112266 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12266 | 112267 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12267 | 112268 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12268 | 112269 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12269 | 112270 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12270 | 112271 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12271 | 112272 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12272 | 112273 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12273 | 112274 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12274 | 112275 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12275 | 112276 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12276 | 112277 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12277 | 112278 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12278 | 112279 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
Custom logic: digital output | 12279 | 112280 | Functions - Digital output functions - Local - CustomLogic - Outputs - Custom digital output | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14400 | 114401 | Inter-controller communication - Inputs - 1 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14401 | 114402 | Inter-controller communication - Inputs - 2 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14402 | 114403 | Inter-controller communication - Inputs - 3 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14403 | 114404 | Inter-controller communication - Inputs - 4 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14404 | 114405 | Inter-controller communication - Inputs - 5 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14405 | 114406 | Inter-controller communication - Inputs - 6 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14406 | 114407 | Inter-controller communication - Inputs - 7 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14407 | 114408 | Inter-controller communication - Inputs - 8 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14408 | 114409 | Inter-controller communication - Inputs - 9 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14409 | 114410 | Inter-controller communication - Inputs - 10 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14410 | 114411 | Inter-controller communication - Inputs - 11 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14411 | 114412 | Inter-controller communication - Inputs - 12 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14412 | 114413 | Inter-controller communication - Inputs - 13 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14413 | 114414 | Inter-controller communication - Inputs - 14 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14414 | 114415 | Inter-controller communication - Inputs - 15 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14415 | 114416 | Inter-controller communication - Inputs - 16 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14416 | 114417 | Inter-controller communication - Inputs - 17 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14417 | 114418 | Inter-controller communication - Inputs - 18 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14418 | 114419 | Inter-controller communication - Inputs - 19 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14419 | 114420 | Inter-controller communication - Inputs - 20 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14420 | 114421 | Inter-controller communication - Inputs - 21 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14421 | 114422 | Inter-controller communication - Inputs - 22 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14422 | 114423 | Inter-controller communication - Inputs - 23 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14423 | 114424 | Inter-controller communication - Inputs - 24 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14424 | 114425 | Inter-controller communication - Inputs - 25 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14425 | 114426 | Inter-controller communication - Inputs - 26 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14426 | 114427 | Inter-controller communication - Inputs - 27 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14427 | 114428 | Inter-controller communication - Inputs - 28 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14428 | 114429 | Inter-controller communication - Inputs - 29 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14429 | 114430 | Inter-controller communication - Inputs - 30 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14430 | 114431 | Inter-controller communication - Inputs - 31 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14431 | 114432 | Inter-controller communication - Inputs - 32 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14432 | 114433 | Inter-controller communication - Inputs - 33 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14433 | 114434 | Inter-controller communication - Inputs - 34 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14434 | 114435 | Inter-controller communication - Inputs - 35 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14435 | 114436 | Inter-controller communication - Inputs - 36 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14436 | 114437 | Inter-controller communication - Inputs - 37 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14437 | 114438 | Inter-controller communication - Inputs - 38 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14438 | 114439 | Inter-controller communication - Inputs - 39 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14439 | 114440 | Inter-controller communication - Inputs - 40 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14440 | 114441 | Inter-controller communication - Inputs - 41 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14441 | 114442 | Inter-controller communication - Inputs - 42 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14442 | 114443 | Inter-controller communication - Inputs - 43 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14443 | 114444 | Inter-controller communication - Inputs - 44 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14444 | 114445 | Inter-controller communication - Inputs - 45 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14445 | 114446 | Inter-controller communication - Inputs - 46 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14446 | 114447 | Inter-controller communication - Inputs - 47 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14447 | 114448 | Inter-controller communication - Inputs - 48 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14448 | 114449 | Inter-controller communication - Inputs - 49 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14449 | 114450 | Inter-controller communication - Inputs - 50 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14450 | 114451 | Inter-controller communication - Inputs - 51 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14451 | 114452 | Inter-controller communication - Inputs - 52 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14452 | 114453 | Inter-controller communication - Inputs - 53 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14453 | 114454 | Inter-controller communication - Inputs - 54 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14454 | 114455 | Inter-controller communication - Inputs - 55 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14455 | 114456 | Inter-controller communication - Inputs - 56 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14456 | 114457 | Inter-controller communication - Inputs - 57 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14457 | 114458 | Inter-controller communication - Inputs - 58 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14458 | 114459 | Inter-controller communication - Inputs - 59 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14459 | 114460 | Inter-controller communication - Inputs - 60 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14460 | 114461 | Inter-controller communication - Inputs - 61 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14461 | 114462 | Inter-controller communication - Inputs - 62 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14462 | 114463 | Inter-controller communication - Inputs - 63 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14463 | 114464 | Inter-controller communication - Inputs - 64 - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14464 | 114465 | Inter-controller communication - Inputs - 1 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14465 | 114466 | Inter-controller communication - Inputs - 2 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14466 | 114467 | Inter-controller communication - Inputs - 3 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14467 | 114468 | Inter-controller communication - Inputs - 4 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14468 | 114469 | Inter-controller communication - Inputs - 5 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14469 | 114470 | Inter-controller communication - Inputs - 6 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14470 | 114471 | Inter-controller communication - Inputs - 7 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14471 | 114472 | Inter-controller communication - Inputs - 8 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14472 | 114473 | Inter-controller communication - Inputs - 9 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14473 | 114474 | Inter-controller communication - Inputs - 10 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14474 | 114475 | Inter-controller communication - Inputs - 11 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14475 | 114476 | Inter-controller communication - Inputs - 12 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14476 | 114477 | Inter-controller communication - Inputs - 13 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14477 | 114478 | Inter-controller communication - Inputs - 14 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14478 | 114479 | Inter-controller communication - Inputs - 15 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14479 | 114480 | Inter-controller communication - Inputs - 16 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14480 | 114481 | Inter-controller communication - Inputs - 17 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14481 | 114482 | Inter-controller communication - Inputs - 18 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14482 | 114483 | Inter-controller communication - Inputs - 19 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14483 | 114484 | Inter-controller communication - Inputs - 20 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14484 | 114485 | Inter-controller communication - Inputs - 21 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14485 | 114486 | Inter-controller communication - Inputs - 22 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14486 | 114487 | Inter-controller communication - Inputs - 23 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14487 | 114488 | Inter-controller communication - Inputs - 24 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14488 | 114489 | Inter-controller communication - Inputs - 25 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14489 | 114490 | Inter-controller communication - Inputs - 26 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14490 | 114491 | Inter-controller communication - Inputs - 27 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14491 | 114492 | Inter-controller communication - Inputs - 28 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14492 | 114493 | Inter-controller communication - Inputs - 29 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14493 | 114494 | Inter-controller communication - Inputs - 30 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14494 | 114495 | Inter-controller communication - Inputs - 31 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14495 | 114496 | Inter-controller communication - Inputs - 32 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14496 | 114497 | Inter-controller communication - Inputs - 33 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14497 | 114498 | Inter-controller communication - Inputs - 34 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14498 | 114499 | Inter-controller communication - Inputs - 35 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14499 | 114500 | Inter-controller communication - Inputs - 36 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14500 | 114501 | Inter-controller communication - Inputs - 37 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14501 | 114502 | Inter-controller communication - Inputs - 38 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14502 | 114503 | Inter-controller communication - Inputs - 39 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14503 | 114504 | Inter-controller communication - Inputs - 40 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14504 | 114505 | Inter-controller communication - Inputs - 41 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14505 | 114506 | Inter-controller communication - Inputs - 42 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14506 | 114507 | Inter-controller communication - Inputs - 43 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14507 | 114508 | Inter-controller communication - Inputs - 44 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14508 | 114509 | Inter-controller communication - Inputs - 45 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14509 | 114510 | Inter-controller communication - Inputs - 46 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14510 | 114511 | Inter-controller communication - Inputs - 47 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14511 | 114512 | Inter-controller communication - Inputs - 48 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14512 | 114513 | Inter-controller communication - Inputs - 49 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14513 | 114514 | Inter-controller communication - Inputs - 50 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14514 | 114515 | Inter-controller communication - Inputs - 51 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14515 | 114516 | Inter-controller communication - Inputs - 52 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14516 | 114517 | Inter-controller communication - Inputs - 53 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14517 | 114518 | Inter-controller communication - Inputs - 54 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14518 | 114519 | Inter-controller communication - Inputs - 55 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14519 | 114520 | Inter-controller communication - Inputs - 56 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14520 | 114521 | Inter-controller communication - Inputs - 57 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14521 | 114522 | Inter-controller communication - Inputs - 58 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14522 | 114523 | Inter-controller communication - Inputs - 59 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14523 | 114524 | Inter-controller communication - Inputs - 60 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14524 | 114525 | Inter-controller communication - Inputs - 61 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14525 | 114526 | Inter-controller communication - Inputs - 62 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14526 | 114527 | Inter-controller communication - Inputs - 63 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14527 | 114528 | Inter-controller communication - Inputs - 64 - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14528 | 114529 | Inter-controller communication - Inputs - 1 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14529 | 114530 | Inter-controller communication - Inputs - 2 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14530 | 114531 | Inter-controller communication - Inputs - 3 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14531 | 114532 | Inter-controller communication - Inputs - 4 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14532 | 114533 | Inter-controller communication - Inputs - 5 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14533 | 114534 | Inter-controller communication - Inputs - 6 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14534 | 114535 | Inter-controller communication - Inputs - 7 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14535 | 114536 | Inter-controller communication - Inputs - 8 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14536 | 114537 | Inter-controller communication - Inputs - 9 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14537 | 114538 | Inter-controller communication - Inputs - 10 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14538 | 114539 | Inter-controller communication - Inputs - 11 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14539 | 114540 | Inter-controller communication - Inputs - 12 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14540 | 114541 | Inter-controller communication - Inputs - 13 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14541 | 114542 | Inter-controller communication - Inputs - 14 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14542 | 114543 | Inter-controller communication - Inputs - 15 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14543 | 114544 | Inter-controller communication - Inputs - 16 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14544 | 114545 | Inter-controller communication - Inputs - 17 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14545 | 114546 | Inter-controller communication - Inputs - 18 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14546 | 114547 | Inter-controller communication - Inputs - 19 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14547 | 114548 | Inter-controller communication - Inputs - 20 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14548 | 114549 | Inter-controller communication - Inputs - 21 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14549 | 114550 | Inter-controller communication - Inputs - 22 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14550 | 114551 | Inter-controller communication - Inputs - 23 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14551 | 114552 | Inter-controller communication - Inputs - 24 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14552 | 114553 | Inter-controller communication - Inputs - 25 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14553 | 114554 | Inter-controller communication - Inputs - 26 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14554 | 114555 | Inter-controller communication - Inputs - 27 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14555 | 114556 | Inter-controller communication - Inputs - 28 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14556 | 114557 | Inter-controller communication - Inputs - 29 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14557 | 114558 | Inter-controller communication - Inputs - 30 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14558 | 114559 | Inter-controller communication - Inputs - 31 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14559 | 114560 | Inter-controller communication - Inputs - 32 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14560 | 114561 | Inter-controller communication - Inputs - 33 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14561 | 114562 | Inter-controller communication - Inputs - 34 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14562 | 114563 | Inter-controller communication - Inputs - 35 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14563 | 114564 | Inter-controller communication - Inputs - 36 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14564 | 114565 | Inter-controller communication - Inputs - 37 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14565 | 114566 | Inter-controller communication - Inputs - 38 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14566 | 114567 | Inter-controller communication - Inputs - 39 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14567 | 114568 | Inter-controller communication - Inputs - 40 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14568 | 114569 | Inter-controller communication - Inputs - 41 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14569 | 114570 | Inter-controller communication - Inputs - 42 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14570 | 114571 | Inter-controller communication - Inputs - 43 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14571 | 114572 | Inter-controller communication - Inputs - 44 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14572 | 114573 | Inter-controller communication - Inputs - 45 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14573 | 114574 | Inter-controller communication - Inputs - 46 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14574 | 114575 | Inter-controller communication - Inputs - 47 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14575 | 114576 | Inter-controller communication - Inputs - 48 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14576 | 114577 | Inter-controller communication - Inputs - 49 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14577 | 114578 | Inter-controller communication - Inputs - 50 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14578 | 114579 | Inter-controller communication - Inputs - 51 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14579 | 114580 | Inter-controller communication - Inputs - 52 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14580 | 114581 | Inter-controller communication - Inputs - 53 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14581 | 114582 | Inter-controller communication - Inputs - 54 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14582 | 114583 | Inter-controller communication - Inputs - 55 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14583 | 114584 | Inter-controller communication - Inputs - 56 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14584 | 114585 | Inter-controller communication - Inputs - 57 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14585 | 114586 | Inter-controller communication - Inputs - 58 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14586 | 114587 | Inter-controller communication - Inputs - 59 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14587 | 114588 | Inter-controller communication - Inputs - 60 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14588 | 114589 | Inter-controller communication - Inputs - 61 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14589 | 114590 | Inter-controller communication - Inputs - 62 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14590 | 114591 | Inter-controller communication - Inputs - 63 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14591 | 114592 | Inter-controller communication - Inputs - 64 - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14592 | 114593 | Inter-controller communication - Inputs - 1 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14593 | 114594 | Inter-controller communication - Inputs - 2 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14594 | 114595 | Inter-controller communication - Inputs - 3 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14595 | 114596 | Inter-controller communication - Inputs - 4 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14596 | 114597 | Inter-controller communication - Inputs - 5 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14597 | 114598 | Inter-controller communication - Inputs - 6 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14598 | 114599 | Inter-controller communication - Inputs - 7 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14599 | 114600 | Inter-controller communication - Inputs - 8 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14600 | 114601 | Inter-controller communication - Inputs - 9 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14601 | 114602 | Inter-controller communication - Inputs - 10 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14602 | 114603 | Inter-controller communication - Inputs - 11 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14603 | 114604 | Inter-controller communication - Inputs - 12 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14604 | 114605 | Inter-controller communication - Inputs - 13 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14605 | 114606 | Inter-controller communication - Inputs - 14 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14606 | 114607 | Inter-controller communication - Inputs - 15 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14607 | 114608 | Inter-controller communication - Inputs - 16 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14608 | 114609 | Inter-controller communication - Inputs - 17 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14609 | 114610 | Inter-controller communication - Inputs - 18 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14610 | 114611 | Inter-controller communication - Inputs - 19 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14611 | 114612 | Inter-controller communication - Inputs - 20 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14612 | 114613 | Inter-controller communication - Inputs - 21 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14613 | 114614 | Inter-controller communication - Inputs - 22 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14614 | 114615 | Inter-controller communication - Inputs - 23 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14615 | 114616 | Inter-controller communication - Inputs - 24 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14616 | 114617 | Inter-controller communication - Inputs - 25 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14617 | 114618 | Inter-controller communication - Inputs - 26 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14618 | 114619 | Inter-controller communication - Inputs - 27 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14619 | 114620 | Inter-controller communication - Inputs - 28 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14620 | 114621 | Inter-controller communication - Inputs - 29 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14621 | 114622 | Inter-controller communication - Inputs - 30 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14622 | 114623 | Inter-controller communication - Inputs - 31 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14623 | 114624 | Inter-controller communication - Inputs - 32 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14624 | 114625 | Inter-controller communication - Inputs - 33 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14625 | 114626 | Inter-controller communication - Inputs - 34 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14626 | 114627 | Inter-controller communication - Inputs - 35 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14627 | 114628 | Inter-controller communication - Inputs - 36 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14628 | 114629 | Inter-controller communication - Inputs - 37 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14629 | 114630 | Inter-controller communication - Inputs - 38 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14630 | 114631 | Inter-controller communication - Inputs - 39 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14631 | 114632 | Inter-controller communication - Inputs - 40 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14632 | 114633 | Inter-controller communication - Inputs - 41 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14633 | 114634 | Inter-controller communication - Inputs - 42 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14634 | 114635 | Inter-controller communication - Inputs - 43 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14635 | 114636 | Inter-controller communication - Inputs - 44 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14636 | 114637 | Inter-controller communication - Inputs - 45 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14637 | 114638 | Inter-controller communication - Inputs - 46 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14638 | 114639 | Inter-controller communication - Inputs - 47 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14639 | 114640 | Inter-controller communication - Inputs - 48 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14640 | 114641 | Inter-controller communication - Inputs - 49 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14641 | 114642 | Inter-controller communication - Inputs - 50 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14642 | 114643 | Inter-controller communication - Inputs - 51 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14643 | 114644 | Inter-controller communication - Inputs - 52 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14644 | 114645 | Inter-controller communication - Inputs - 53 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14645 | 114646 | Inter-controller communication - Inputs - 54 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14646 | 114647 | Inter-controller communication - Inputs - 55 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14647 | 114648 | Inter-controller communication - Inputs - 56 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14648 | 114649 | Inter-controller communication - Inputs - 57 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14649 | 114650 | Inter-controller communication - Inputs - 58 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14650 | 114651 | Inter-controller communication - Inputs - 59 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14651 | 114652 | Inter-controller communication - Inputs - 60 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14652 | 114653 | Inter-controller communication - Inputs - 61 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14653 | 114654 | Inter-controller communication - Inputs - 62 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14654 | 114655 | Inter-controller communication - Inputs - 63 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14655 | 114656 | Inter-controller communication - Inputs - 64 - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14656 | 114657 | Inter-controller communication - Inputs - 1 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14657 | 114658 | Inter-controller communication - Inputs - 2 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14658 | 114659 | Inter-controller communication - Inputs - 3 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14659 | 114660 | Inter-controller communication - Inputs - 4 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14660 | 114661 | Inter-controller communication - Inputs - 5 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14661 | 114662 | Inter-controller communication - Inputs - 6 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14662 | 114663 | Inter-controller communication - Inputs - 7 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14663 | 114664 | Inter-controller communication - Inputs - 8 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14664 | 114665 | Inter-controller communication - Inputs - 9 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14665 | 114666 | Inter-controller communication - Inputs - 10 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14666 | 114667 | Inter-controller communication - Inputs - 11 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14667 | 114668 | Inter-controller communication - Inputs - 12 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14668 | 114669 | Inter-controller communication - Inputs - 13 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14669 | 114670 | Inter-controller communication - Inputs - 14 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14670 | 114671 | Inter-controller communication - Inputs - 15 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14671 | 114672 | Inter-controller communication - Inputs - 16 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14672 | 114673 | Inter-controller communication - Inputs - 17 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14673 | 114674 | Inter-controller communication - Inputs - 18 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14674 | 114675 | Inter-controller communication - Inputs - 19 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14675 | 114676 | Inter-controller communication - Inputs - 20 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14676 | 114677 | Inter-controller communication - Inputs - 21 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14677 | 114678 | Inter-controller communication - Inputs - 22 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14678 | 114679 | Inter-controller communication - Inputs - 23 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14679 | 114680 | Inter-controller communication - Inputs - 24 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14680 | 114681 | Inter-controller communication - Inputs - 25 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14681 | 114682 | Inter-controller communication - Inputs - 26 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14682 | 114683 | Inter-controller communication - Inputs - 27 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14683 | 114684 | Inter-controller communication - Inputs - 28 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14684 | 114685 | Inter-controller communication - Inputs - 29 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14685 | 114686 | Inter-controller communication - Inputs - 30 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14686 | 114687 | Inter-controller communication - Inputs - 31 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14687 | 114688 | Inter-controller communication - Inputs - 32 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14688 | 114689 | Inter-controller communication - Inputs - 33 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14689 | 114690 | Inter-controller communication - Inputs - 34 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14690 | 114691 | Inter-controller communication - Inputs - 35 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14691 | 114692 | Inter-controller communication - Inputs - 36 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14692 | 114693 | Inter-controller communication - Inputs - 37 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14693 | 114694 | Inter-controller communication - Inputs - 38 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14694 | 114695 | Inter-controller communication - Inputs - 39 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14695 | 114696 | Inter-controller communication - Inputs - 40 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14696 | 114697 | Inter-controller communication - Inputs - 41 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14697 | 114698 | Inter-controller communication - Inputs - 42 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14698 | 114699 | Inter-controller communication - Inputs - 43 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14699 | 114700 | Inter-controller communication - Inputs - 44 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14700 | 114701 | Inter-controller communication - Inputs - 45 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14701 | 114702 | Inter-controller communication - Inputs - 46 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14702 | 114703 | Inter-controller communication - Inputs - 47 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14703 | 114704 | Inter-controller communication - Inputs - 48 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14704 | 114705 | Inter-controller communication - Inputs - 49 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14705 | 114706 | Inter-controller communication - Inputs - 50 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14706 | 114707 | Inter-controller communication - Inputs - 51 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14707 | 114708 | Inter-controller communication - Inputs - 52 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14708 | 114709 | Inter-controller communication - Inputs - 53 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14709 | 114710 | Inter-controller communication - Inputs - 54 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14710 | 114711 | Inter-controller communication - Inputs - 55 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14711 | 114712 | Inter-controller communication - Inputs - 56 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14712 | 114713 | Inter-controller communication - Inputs - 57 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14713 | 114714 | Inter-controller communication - Inputs - 58 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14714 | 114715 | Inter-controller communication - Inputs - 59 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14715 | 114716 | Inter-controller communication - Inputs - 60 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14716 | 114717 | Inter-controller communication - Inputs - 61 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14717 | 114718 | Inter-controller communication - Inputs - 62 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14718 | 114719 | Inter-controller communication - Inputs - 63 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14719 | 114720 | Inter-controller communication - Inputs - 64 - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14720 | 114721 | Inter-controller communication - Inputs - 1 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14721 | 114722 | Inter-controller communication - Inputs - 2 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14722 | 114723 | Inter-controller communication - Inputs - 3 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14723 | 114724 | Inter-controller communication - Inputs - 4 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14724 | 114725 | Inter-controller communication - Inputs - 5 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14725 | 114726 | Inter-controller communication - Inputs - 6 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14726 | 114727 | Inter-controller communication - Inputs - 7 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14727 | 114728 | Inter-controller communication - Inputs - 8 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14728 | 114729 | Inter-controller communication - Inputs - 9 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14729 | 114730 | Inter-controller communication - Inputs - 10 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14730 | 114731 | Inter-controller communication - Inputs - 11 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14731 | 114732 | Inter-controller communication - Inputs - 12 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14732 | 114733 | Inter-controller communication - Inputs - 13 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14733 | 114734 | Inter-controller communication - Inputs - 14 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14734 | 114735 | Inter-controller communication - Inputs - 15 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14735 | 114736 | Inter-controller communication - Inputs - 16 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14736 | 114737 | Inter-controller communication - Inputs - 17 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14737 | 114738 | Inter-controller communication - Inputs - 18 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14738 | 114739 | Inter-controller communication - Inputs - 19 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14739 | 114740 | Inter-controller communication - Inputs - 20 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14740 | 114741 | Inter-controller communication - Inputs - 21 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14741 | 114742 | Inter-controller communication - Inputs - 22 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14742 | 114743 | Inter-controller communication - Inputs - 23 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14743 | 114744 | Inter-controller communication - Inputs - 24 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14744 | 114745 | Inter-controller communication - Inputs - 25 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14745 | 114746 | Inter-controller communication - Inputs - 26 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14746 | 114747 | Inter-controller communication - Inputs - 27 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14747 | 114748 | Inter-controller communication - Inputs - 28 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14748 | 114749 | Inter-controller communication - Inputs - 29 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14749 | 114750 | Inter-controller communication - Inputs - 30 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14750 | 114751 | Inter-controller communication - Inputs - 31 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14751 | 114752 | Inter-controller communication - Inputs - 32 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14752 | 114753 | Inter-controller communication - Inputs - 33 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14753 | 114754 | Inter-controller communication - Inputs - 34 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14754 | 114755 | Inter-controller communication - Inputs - 35 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14755 | 114756 | Inter-controller communication - Inputs - 36 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14756 | 114757 | Inter-controller communication - Inputs - 37 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14757 | 114758 | Inter-controller communication - Inputs - 38 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14758 | 114759 | Inter-controller communication - Inputs - 39 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14759 | 114760 | Inter-controller communication - Inputs - 40 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14760 | 114761 | Inter-controller communication - Inputs - 41 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14761 | 114762 | Inter-controller communication - Inputs - 42 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14762 | 114763 | Inter-controller communication - Inputs - 43 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14763 | 114764 | Inter-controller communication - Inputs - 44 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14764 | 114765 | Inter-controller communication - Inputs - 45 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14765 | 114766 | Inter-controller communication - Inputs - 46 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14766 | 114767 | Inter-controller communication - Inputs - 47 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14767 | 114768 | Inter-controller communication - Inputs - 48 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14768 | 114769 | Inter-controller communication - Inputs - 49 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14769 | 114770 | Inter-controller communication - Inputs - 50 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14770 | 114771 | Inter-controller communication - Inputs - 51 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14771 | 114772 | Inter-controller communication - Inputs - 52 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14772 | 114773 | Inter-controller communication - Inputs - 53 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14773 | 114774 | Inter-controller communication - Inputs - 54 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14774 | 114775 | Inter-controller communication - Inputs - 55 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14775 | 114776 | Inter-controller communication - Inputs - 56 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14776 | 114777 | Inter-controller communication - Inputs - 57 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14777 | 114778 | Inter-controller communication - Inputs - 58 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14778 | 114779 | Inter-controller communication - Inputs - 59 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14779 | 114780 | Inter-controller communication - Inputs - 60 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14780 | 114781 | Inter-controller communication - Inputs - 61 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14781 | 114782 | Inter-controller communication - Inputs - 62 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14782 | 114783 | Inter-controller communication - Inputs - 63 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14783 | 114784 | Inter-controller communication - Inputs - 64 - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14784 | 114785 | Inter-controller communication - Inputs - 1 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14785 | 114786 | Inter-controller communication - Inputs - 2 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14786 | 114787 | Inter-controller communication - Inputs - 3 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14787 | 114788 | Inter-controller communication - Inputs - 4 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14788 | 114789 | Inter-controller communication - Inputs - 5 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14789 | 114790 | Inter-controller communication - Inputs - 6 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14790 | 114791 | Inter-controller communication - Inputs - 7 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14791 | 114792 | Inter-controller communication - Inputs - 8 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14792 | 114793 | Inter-controller communication - Inputs - 9 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14793 | 114794 | Inter-controller communication - Inputs - 10 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14794 | 114795 | Inter-controller communication - Inputs - 11 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14795 | 114796 | Inter-controller communication - Inputs - 12 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14796 | 114797 | Inter-controller communication - Inputs - 13 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14797 | 114798 | Inter-controller communication - Inputs - 14 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14798 | 114799 | Inter-controller communication - Inputs - 15 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14799 | 114800 | Inter-controller communication - Inputs - 16 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14800 | 114801 | Inter-controller communication - Inputs - 17 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14801 | 114802 | Inter-controller communication - Inputs - 18 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14802 | 114803 | Inter-controller communication - Inputs - 19 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14803 | 114804 | Inter-controller communication - Inputs - 20 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14804 | 114805 | Inter-controller communication - Inputs - 21 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14805 | 114806 | Inter-controller communication - Inputs - 22 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14806 | 114807 | Inter-controller communication - Inputs - 23 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14807 | 114808 | Inter-controller communication - Inputs - 24 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14808 | 114809 | Inter-controller communication - Inputs - 25 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14809 | 114810 | Inter-controller communication - Inputs - 26 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14810 | 114811 | Inter-controller communication - Inputs - 27 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14811 | 114812 | Inter-controller communication - Inputs - 28 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14812 | 114813 | Inter-controller communication - Inputs - 29 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14813 | 114814 | Inter-controller communication - Inputs - 30 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14814 | 114815 | Inter-controller communication - Inputs - 31 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14815 | 114816 | Inter-controller communication - Inputs - 32 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14816 | 114817 | Inter-controller communication - Inputs - 33 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14817 | 114818 | Inter-controller communication - Inputs - 34 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14818 | 114819 | Inter-controller communication - Inputs - 35 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14819 | 114820 | Inter-controller communication - Inputs - 36 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14820 | 114821 | Inter-controller communication - Inputs - 37 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14821 | 114822 | Inter-controller communication - Inputs - 38 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14822 | 114823 | Inter-controller communication - Inputs - 39 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14823 | 114824 | Inter-controller communication - Inputs - 40 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14824 | 114825 | Inter-controller communication - Inputs - 41 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14825 | 114826 | Inter-controller communication - Inputs - 42 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14826 | 114827 | Inter-controller communication - Inputs - 43 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14827 | 114828 | Inter-controller communication - Inputs - 44 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14828 | 114829 | Inter-controller communication - Inputs - 45 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14829 | 114830 | Inter-controller communication - Inputs - 46 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14830 | 114831 | Inter-controller communication - Inputs - 47 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14831 | 114832 | Inter-controller communication - Inputs - 48 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14832 | 114833 | Inter-controller communication - Inputs - 49 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14833 | 114834 | Inter-controller communication - Inputs - 50 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14834 | 114835 | Inter-controller communication - Inputs - 51 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14835 | 114836 | Inter-controller communication - Inputs - 52 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14836 | 114837 | Inter-controller communication - Inputs - 53 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14837 | 114838 | Inter-controller communication - Inputs - 54 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14838 | 114839 | Inter-controller communication - Inputs - 55 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14839 | 114840 | Inter-controller communication - Inputs - 56 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14840 | 114841 | Inter-controller communication - Inputs - 57 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14841 | 114842 | Inter-controller communication - Inputs - 58 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14842 | 114843 | Inter-controller communication - Inputs - 59 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14843 | 114844 | Inter-controller communication - Inputs - 60 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14844 | 114845 | Inter-controller communication - Inputs - 61 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14845 | 114846 | Inter-controller communication - Inputs - 62 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14846 | 114847 | Inter-controller communication - Inputs - 63 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14847 | 114848 | Inter-controller communication - Inputs - 64 - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14848 | 114849 | Inter-controller communication - Inputs - 1 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14849 | 114850 | Inter-controller communication - Inputs - 2 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14850 | 114851 | Inter-controller communication - Inputs - 3 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14851 | 114852 | Inter-controller communication - Inputs - 4 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14852 | 114853 | Inter-controller communication - Inputs - 5 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14853 | 114854 | Inter-controller communication - Inputs - 6 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14854 | 114855 | Inter-controller communication - Inputs - 7 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14855 | 114856 | Inter-controller communication - Inputs - 8 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14856 | 114857 | Inter-controller communication - Inputs - 9 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14857 | 114858 | Inter-controller communication - Inputs - 10 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14858 | 114859 | Inter-controller communication - Inputs - 11 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14859 | 114860 | Inter-controller communication - Inputs - 12 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14860 | 114861 | Inter-controller communication - Inputs - 13 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14861 | 114862 | Inter-controller communication - Inputs - 14 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14862 | 114863 | Inter-controller communication - Inputs - 15 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14863 | 114864 | Inter-controller communication - Inputs - 16 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14864 | 114865 | Inter-controller communication - Inputs - 17 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14865 | 114866 | Inter-controller communication - Inputs - 18 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14866 | 114867 | Inter-controller communication - Inputs - 19 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14867 | 114868 | Inter-controller communication - Inputs - 20 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14868 | 114869 | Inter-controller communication - Inputs - 21 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14869 | 114870 | Inter-controller communication - Inputs - 22 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14870 | 114871 | Inter-controller communication - Inputs - 23 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14871 | 114872 | Inter-controller communication - Inputs - 24 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14872 | 114873 | Inter-controller communication - Inputs - 25 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14873 | 114874 | Inter-controller communication - Inputs - 26 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14874 | 114875 | Inter-controller communication - Inputs - 27 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14875 | 114876 | Inter-controller communication - Inputs - 28 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14876 | 114877 | Inter-controller communication - Inputs - 29 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14877 | 114878 | Inter-controller communication - Inputs - 30 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14878 | 114879 | Inter-controller communication - Inputs - 31 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14879 | 114880 | Inter-controller communication - Inputs - 32 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14880 | 114881 | Inter-controller communication - Inputs - 33 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14881 | 114882 | Inter-controller communication - Inputs - 34 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14882 | 114883 | Inter-controller communication - Inputs - 35 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14883 | 114884 | Inter-controller communication - Inputs - 36 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14884 | 114885 | Inter-controller communication - Inputs - 37 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14885 | 114886 | Inter-controller communication - Inputs - 38 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14886 | 114887 | Inter-controller communication - Inputs - 39 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14887 | 114888 | Inter-controller communication - Inputs - 40 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14888 | 114889 | Inter-controller communication - Inputs - 41 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14889 | 114890 | Inter-controller communication - Inputs - 42 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14890 | 114891 | Inter-controller communication - Inputs - 43 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14891 | 114892 | Inter-controller communication - Inputs - 44 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14892 | 114893 | Inter-controller communication - Inputs - 45 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14893 | 114894 | Inter-controller communication - Inputs - 46 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14894 | 114895 | Inter-controller communication - Inputs - 47 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14895 | 114896 | Inter-controller communication - Inputs - 48 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14896 | 114897 | Inter-controller communication - Inputs - 49 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14897 | 114898 | Inter-controller communication - Inputs - 50 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14898 | 114899 | Inter-controller communication - Inputs - 51 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14899 | 114900 | Inter-controller communication - Inputs - 52 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14900 | 114901 | Inter-controller communication - Inputs - 53 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14901 | 114902 | Inter-controller communication - Inputs - 54 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14902 | 114903 | Inter-controller communication - Inputs - 55 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14903 | 114904 | Inter-controller communication - Inputs - 56 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14904 | 114905 | Inter-controller communication - Inputs - 57 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14905 | 114906 | Inter-controller communication - Inputs - 58 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14906 | 114907 | Inter-controller communication - Inputs - 59 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14907 | 114908 | Inter-controller communication - Inputs - 60 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14908 | 114909 | Inter-controller communication - Inputs - 61 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14909 | 114910 | Inter-controller communication - Inputs - 62 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14910 | 114911 | Inter-controller communication - Inputs - 63 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14911 | 114912 | Inter-controller communication - Inputs - 64 - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14912 | 114913 | Inter-controller communication - Inputs - 1 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14913 | 114914 | Inter-controller communication - Inputs - 2 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14914 | 114915 | Inter-controller communication - Inputs - 3 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14915 | 114916 | Inter-controller communication - Inputs - 4 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14916 | 114917 | Inter-controller communication - Inputs - 5 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14917 | 114918 | Inter-controller communication - Inputs - 6 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14918 | 114919 | Inter-controller communication - Inputs - 7 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14919 | 114920 | Inter-controller communication - Inputs - 8 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14920 | 114921 | Inter-controller communication - Inputs - 9 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14921 | 114922 | Inter-controller communication - Inputs - 10 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14922 | 114923 | Inter-controller communication - Inputs - 11 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14923 | 114924 | Inter-controller communication - Inputs - 12 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14924 | 114925 | Inter-controller communication - Inputs - 13 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14925 | 114926 | Inter-controller communication - Inputs - 14 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14926 | 114927 | Inter-controller communication - Inputs - 15 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14927 | 114928 | Inter-controller communication - Inputs - 16 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14928 | 114929 | Inter-controller communication - Inputs - 17 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14929 | 114930 | Inter-controller communication - Inputs - 18 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14930 | 114931 | Inter-controller communication - Inputs - 19 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14931 | 114932 | Inter-controller communication - Inputs - 20 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14932 | 114933 | Inter-controller communication - Inputs - 21 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14933 | 114934 | Inter-controller communication - Inputs - 22 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14934 | 114935 | Inter-controller communication - Inputs - 23 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14935 | 114936 | Inter-controller communication - Inputs - 24 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14936 | 114937 | Inter-controller communication - Inputs - 25 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14937 | 114938 | Inter-controller communication - Inputs - 26 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14938 | 114939 | Inter-controller communication - Inputs - 27 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14939 | 114940 | Inter-controller communication - Inputs - 28 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14940 | 114941 | Inter-controller communication - Inputs - 29 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14941 | 114942 | Inter-controller communication - Inputs - 30 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14942 | 114943 | Inter-controller communication - Inputs - 31 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14943 | 114944 | Inter-controller communication - Inputs - 32 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14944 | 114945 | Inter-controller communication - Inputs - 33 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14945 | 114946 | Inter-controller communication - Inputs - 34 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14946 | 114947 | Inter-controller communication - Inputs - 35 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14947 | 114948 | Inter-controller communication - Inputs - 36 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14948 | 114949 | Inter-controller communication - Inputs - 37 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14949 | 114950 | Inter-controller communication - Inputs - 38 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14950 | 114951 | Inter-controller communication - Inputs - 39 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14951 | 114952 | Inter-controller communication - Inputs - 40 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14952 | 114953 | Inter-controller communication - Inputs - 41 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14953 | 114954 | Inter-controller communication - Inputs - 42 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14954 | 114955 | Inter-controller communication - Inputs - 43 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14955 | 114956 | Inter-controller communication - Inputs - 44 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14956 | 114957 | Inter-controller communication - Inputs - 45 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14957 | 114958 | Inter-controller communication - Inputs - 46 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14958 | 114959 | Inter-controller communication - Inputs - 47 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14959 | 114960 | Inter-controller communication - Inputs - 48 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14960 | 114961 | Inter-controller communication - Inputs - 49 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14961 | 114962 | Inter-controller communication - Inputs - 50 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14962 | 114963 | Inter-controller communication - Inputs - 51 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14963 | 114964 | Inter-controller communication - Inputs - 52 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14964 | 114965 | Inter-controller communication - Inputs - 53 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14965 | 114966 | Inter-controller communication - Inputs - 54 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14966 | 114967 | Inter-controller communication - Inputs - 55 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14967 | 114968 | Inter-controller communication - Inputs - 56 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14968 | 114969 | Inter-controller communication - Inputs - 57 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14969 | 114970 | Inter-controller communication - Inputs - 58 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14970 | 114971 | Inter-controller communication - Inputs - 59 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14971 | 114972 | Inter-controller communication - Inputs - 60 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14972 | 114973 | Inter-controller communication - Inputs - 61 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14973 | 114974 | Inter-controller communication - Inputs - 62 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14974 | 114975 | Inter-controller communication - Inputs - 63 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14975 | 114976 | Inter-controller communication - Inputs - 64 - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14976 | 114977 | Inter-controller communication - Inputs - 1 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14977 | 114978 | Inter-controller communication - Inputs - 2 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14978 | 114979 | Inter-controller communication - Inputs - 3 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14979 | 114980 | Inter-controller communication - Inputs - 4 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14980 | 114981 | Inter-controller communication - Inputs - 5 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14981 | 114982 | Inter-controller communication - Inputs - 6 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14982 | 114983 | Inter-controller communication - Inputs - 7 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14983 | 114984 | Inter-controller communication - Inputs - 8 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14984 | 114985 | Inter-controller communication - Inputs - 9 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14985 | 114986 | Inter-controller communication - Inputs - 10 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14986 | 114987 | Inter-controller communication - Inputs - 11 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14987 | 114988 | Inter-controller communication - Inputs - 12 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14988 | 114989 | Inter-controller communication - Inputs - 13 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14989 | 114990 | Inter-controller communication - Inputs - 14 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14990 | 114991 | Inter-controller communication - Inputs - 15 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14991 | 114992 | Inter-controller communication - Inputs - 16 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14992 | 114993 | Inter-controller communication - Inputs - 17 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14993 | 114994 | Inter-controller communication - Inputs - 18 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14994 | 114995 | Inter-controller communication - Inputs - 19 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14995 | 114996 | Inter-controller communication - Inputs - 20 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14996 | 114997 | Inter-controller communication - Inputs - 21 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14997 | 114998 | Inter-controller communication - Inputs - 22 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14998 | 114999 | Inter-controller communication - Inputs - 23 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 14999 | 115000 | Inter-controller communication - Inputs - 24 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15000 | 115001 | Inter-controller communication - Inputs - 25 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15001 | 115002 | Inter-controller communication - Inputs - 26 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15002 | 115003 | Inter-controller communication - Inputs - 27 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15003 | 115004 | Inter-controller communication - Inputs - 28 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15004 | 115005 | Inter-controller communication - Inputs - 29 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15005 | 115006 | Inter-controller communication - Inputs - 30 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15006 | 115007 | Inter-controller communication - Inputs - 31 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15007 | 115008 | Inter-controller communication - Inputs - 32 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15008 | 115009 | Inter-controller communication - Inputs - 33 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15009 | 115010 | Inter-controller communication - Inputs - 34 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15010 | 115011 | Inter-controller communication - Inputs - 35 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15011 | 115012 | Inter-controller communication - Inputs - 36 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15012 | 115013 | Inter-controller communication - Inputs - 37 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15013 | 115014 | Inter-controller communication - Inputs - 38 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15014 | 115015 | Inter-controller communication - Inputs - 39 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15015 | 115016 | Inter-controller communication - Inputs - 40 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15016 | 115017 | Inter-controller communication - Inputs - 41 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15017 | 115018 | Inter-controller communication - Inputs - 42 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15018 | 115019 | Inter-controller communication - Inputs - 43 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15019 | 115020 | Inter-controller communication - Inputs - 44 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15020 | 115021 | Inter-controller communication - Inputs - 45 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15021 | 115022 | Inter-controller communication - Inputs - 46 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15022 | 115023 | Inter-controller communication - Inputs - 47 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15023 | 115024 | Inter-controller communication - Inputs - 48 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15024 | 115025 | Inter-controller communication - Inputs - 49 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15025 | 115026 | Inter-controller communication - Inputs - 50 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15026 | 115027 | Inter-controller communication - Inputs - 51 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15027 | 115028 | Inter-controller communication - Inputs - 52 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15028 | 115029 | Inter-controller communication - Inputs - 53 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15029 | 115030 | Inter-controller communication - Inputs - 54 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15030 | 115031 | Inter-controller communication - Inputs - 55 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15031 | 115032 | Inter-controller communication - Inputs - 56 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15032 | 115033 | Inter-controller communication - Inputs - 57 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15033 | 115034 | Inter-controller communication - Inputs - 58 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15034 | 115035 | Inter-controller communication - Inputs - 59 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15035 | 115036 | Inter-controller communication - Inputs - 60 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15036 | 115037 | Inter-controller communication - Inputs - 61 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15037 | 115038 | Inter-controller communication - Inputs - 62 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15038 | 115039 | Inter-controller communication - Inputs - 63 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15039 | 115040 | Inter-controller communication - Inputs - 64 - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15040 | 115041 | Inter-controller communication - Inputs - 1 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15041 | 115042 | Inter-controller communication - Inputs - 2 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15042 | 115043 | Inter-controller communication - Inputs - 3 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15043 | 115044 | Inter-controller communication - Inputs - 4 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15044 | 115045 | Inter-controller communication - Inputs - 5 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15045 | 115046 | Inter-controller communication - Inputs - 6 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15046 | 115047 | Inter-controller communication - Inputs - 7 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15047 | 115048 | Inter-controller communication - Inputs - 8 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15048 | 115049 | Inter-controller communication - Inputs - 9 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15049 | 115050 | Inter-controller communication - Inputs - 10 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15050 | 115051 | Inter-controller communication - Inputs - 11 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15051 | 115052 | Inter-controller communication - Inputs - 12 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15052 | 115053 | Inter-controller communication - Inputs - 13 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15053 | 115054 | Inter-controller communication - Inputs - 14 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15054 | 115055 | Inter-controller communication - Inputs - 15 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15055 | 115056 | Inter-controller communication - Inputs - 16 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15056 | 115057 | Inter-controller communication - Inputs - 17 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15057 | 115058 | Inter-controller communication - Inputs - 18 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15058 | 115059 | Inter-controller communication - Inputs - 19 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15059 | 115060 | Inter-controller communication - Inputs - 20 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15060 | 115061 | Inter-controller communication - Inputs - 21 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15061 | 115062 | Inter-controller communication - Inputs - 22 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15062 | 115063 | Inter-controller communication - Inputs - 23 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15063 | 115064 | Inter-controller communication - Inputs - 24 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15064 | 115065 | Inter-controller communication - Inputs - 25 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15065 | 115066 | Inter-controller communication - Inputs - 26 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15066 | 115067 | Inter-controller communication - Inputs - 27 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15067 | 115068 | Inter-controller communication - Inputs - 28 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15068 | 115069 | Inter-controller communication - Inputs - 29 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15069 | 115070 | Inter-controller communication - Inputs - 30 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15070 | 115071 | Inter-controller communication - Inputs - 31 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15071 | 115072 | Inter-controller communication - Inputs - 32 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15072 | 115073 | Inter-controller communication - Inputs - 33 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15073 | 115074 | Inter-controller communication - Inputs - 34 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15074 | 115075 | Inter-controller communication - Inputs - 35 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15075 | 115076 | Inter-controller communication - Inputs - 36 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15076 | 115077 | Inter-controller communication - Inputs - 37 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15077 | 115078 | Inter-controller communication - Inputs - 38 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15078 | 115079 | Inter-controller communication - Inputs - 39 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15079 | 115080 | Inter-controller communication - Inputs - 40 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15080 | 115081 | Inter-controller communication - Inputs - 41 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15081 | 115082 | Inter-controller communication - Inputs - 42 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15082 | 115083 | Inter-controller communication - Inputs - 43 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15083 | 115084 | Inter-controller communication - Inputs - 44 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15084 | 115085 | Inter-controller communication - Inputs - 45 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15085 | 115086 | Inter-controller communication - Inputs - 46 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15086 | 115087 | Inter-controller communication - Inputs - 47 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15087 | 115088 | Inter-controller communication - Inputs - 48 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15088 | 115089 | Inter-controller communication - Inputs - 49 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15089 | 115090 | Inter-controller communication - Inputs - 50 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15090 | 115091 | Inter-controller communication - Inputs - 51 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15091 | 115092 | Inter-controller communication - Inputs - 52 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15092 | 115093 | Inter-controller communication - Inputs - 53 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15093 | 115094 | Inter-controller communication - Inputs - 54 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15094 | 115095 | Inter-controller communication - Inputs - 55 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15095 | 115096 | Inter-controller communication - Inputs - 56 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15096 | 115097 | Inter-controller communication - Inputs - 57 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15097 | 115098 | Inter-controller communication - Inputs - 58 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15098 | 115099 | Inter-controller communication - Inputs - 59 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15099 | 115100 | Inter-controller communication - Inputs - 60 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15100 | 115101 | Inter-controller communication - Inputs - 61 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15101 | 115102 | Inter-controller communication - Inputs - 62 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15102 | 115103 | Inter-controller communication - Inputs - 63 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15103 | 115104 | Inter-controller communication - Inputs - 64 - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15104 | 115105 | Inter-controller communication - Inputs - 1 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15105 | 115106 | Inter-controller communication - Inputs - 2 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15106 | 115107 | Inter-controller communication - Inputs - 3 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15107 | 115108 | Inter-controller communication - Inputs - 4 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15108 | 115109 | Inter-controller communication - Inputs - 5 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15109 | 115110 | Inter-controller communication - Inputs - 6 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15110 | 115111 | Inter-controller communication - Inputs - 7 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15111 | 115112 | Inter-controller communication - Inputs - 8 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15112 | 115113 | Inter-controller communication - Inputs - 9 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15113 | 115114 | Inter-controller communication - Inputs - 10 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15114 | 115115 | Inter-controller communication - Inputs - 11 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15115 | 115116 | Inter-controller communication - Inputs - 12 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15116 | 115117 | Inter-controller communication - Inputs - 13 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15117 | 115118 | Inter-controller communication - Inputs - 14 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15118 | 115119 | Inter-controller communication - Inputs - 15 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15119 | 115120 | Inter-controller communication - Inputs - 16 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15120 | 115121 | Inter-controller communication - Inputs - 17 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15121 | 115122 | Inter-controller communication - Inputs - 18 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15122 | 115123 | Inter-controller communication - Inputs - 19 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15123 | 115124 | Inter-controller communication - Inputs - 20 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15124 | 115125 | Inter-controller communication - Inputs - 21 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15125 | 115126 | Inter-controller communication - Inputs - 22 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15126 | 115127 | Inter-controller communication - Inputs - 23 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15127 | 115128 | Inter-controller communication - Inputs - 24 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15128 | 115129 | Inter-controller communication - Inputs - 25 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15129 | 115130 | Inter-controller communication - Inputs - 26 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15130 | 115131 | Inter-controller communication - Inputs - 27 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15131 | 115132 | Inter-controller communication - Inputs - 28 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15132 | 115133 | Inter-controller communication - Inputs - 29 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15133 | 115134 | Inter-controller communication - Inputs - 30 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15134 | 115135 | Inter-controller communication - Inputs - 31 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15135 | 115136 | Inter-controller communication - Inputs - 32 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15136 | 115137 | Inter-controller communication - Inputs - 33 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15137 | 115138 | Inter-controller communication - Inputs - 34 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15138 | 115139 | Inter-controller communication - Inputs - 35 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15139 | 115140 | Inter-controller communication - Inputs - 36 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15140 | 115141 | Inter-controller communication - Inputs - 37 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15141 | 115142 | Inter-controller communication - Inputs - 38 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15142 | 115143 | Inter-controller communication - Inputs - 39 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15143 | 115144 | Inter-controller communication - Inputs - 40 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15144 | 115145 | Inter-controller communication - Inputs - 41 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15145 | 115146 | Inter-controller communication - Inputs - 42 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15146 | 115147 | Inter-controller communication - Inputs - 43 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15147 | 115148 | Inter-controller communication - Inputs - 44 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15148 | 115149 | Inter-controller communication - Inputs - 45 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15149 | 115150 | Inter-controller communication - Inputs - 46 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15150 | 115151 | Inter-controller communication - Inputs - 47 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15151 | 115152 | Inter-controller communication - Inputs - 48 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15152 | 115153 | Inter-controller communication - Inputs - 49 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15153 | 115154 | Inter-controller communication - Inputs - 50 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15154 | 115155 | Inter-controller communication - Inputs - 51 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15155 | 115156 | Inter-controller communication - Inputs - 52 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15156 | 115157 | Inter-controller communication - Inputs - 53 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15157 | 115158 | Inter-controller communication - Inputs - 54 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15158 | 115159 | Inter-controller communication - Inputs - 55 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15159 | 115160 | Inter-controller communication - Inputs - 56 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15160 | 115161 | Inter-controller communication - Inputs - 57 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15161 | 115162 | Inter-controller communication - Inputs - 58 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15162 | 115163 | Inter-controller communication - Inputs - 59 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15163 | 115164 | Inter-controller communication - Inputs - 60 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15164 | 115165 | Inter-controller communication - Inputs - 61 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15165 | 115166 | Inter-controller communication - Inputs - 62 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15166 | 115167 | Inter-controller communication - Inputs - 63 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15167 | 115168 | Inter-controller communication - Inputs - 64 - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15168 | 115169 | Inter-controller communication - Inputs - 1 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15169 | 115170 | Inter-controller communication - Inputs - 2 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15170 | 115171 | Inter-controller communication - Inputs - 3 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15171 | 115172 | Inter-controller communication - Inputs - 4 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15172 | 115173 | Inter-controller communication - Inputs - 5 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15173 | 115174 | Inter-controller communication - Inputs - 6 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15174 | 115175 | Inter-controller communication - Inputs - 7 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15175 | 115176 | Inter-controller communication - Inputs - 8 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15176 | 115177 | Inter-controller communication - Inputs - 9 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15177 | 115178 | Inter-controller communication - Inputs - 10 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15178 | 115179 | Inter-controller communication - Inputs - 11 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15179 | 115180 | Inter-controller communication - Inputs - 12 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15180 | 115181 | Inter-controller communication - Inputs - 13 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15181 | 115182 | Inter-controller communication - Inputs - 14 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15182 | 115183 | Inter-controller communication - Inputs - 15 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15183 | 115184 | Inter-controller communication - Inputs - 16 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15184 | 115185 | Inter-controller communication - Inputs - 17 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15185 | 115186 | Inter-controller communication - Inputs - 18 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15186 | 115187 | Inter-controller communication - Inputs - 19 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15187 | 115188 | Inter-controller communication - Inputs - 20 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15188 | 115189 | Inter-controller communication - Inputs - 21 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15189 | 115190 | Inter-controller communication - Inputs - 22 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15190 | 115191 | Inter-controller communication - Inputs - 23 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15191 | 115192 | Inter-controller communication - Inputs - 24 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15192 | 115193 | Inter-controller communication - Inputs - 25 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15193 | 115194 | Inter-controller communication - Inputs - 26 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15194 | 115195 | Inter-controller communication - Inputs - 27 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15195 | 115196 | Inter-controller communication - Inputs - 28 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15196 | 115197 | Inter-controller communication - Inputs - 29 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15197 | 115198 | Inter-controller communication - Inputs - 30 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15198 | 115199 | Inter-controller communication - Inputs - 31 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15199 | 115200 | Inter-controller communication - Inputs - 32 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15200 | 115201 | Inter-controller communication - Inputs - 33 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15201 | 115202 | Inter-controller communication - Inputs - 34 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15202 | 115203 | Inter-controller communication - Inputs - 35 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15203 | 115204 | Inter-controller communication - Inputs - 36 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15204 | 115205 | Inter-controller communication - Inputs - 37 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15205 | 115206 | Inter-controller communication - Inputs - 38 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15206 | 115207 | Inter-controller communication - Inputs - 39 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15207 | 115208 | Inter-controller communication - Inputs - 40 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15208 | 115209 | Inter-controller communication - Inputs - 41 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15209 | 115210 | Inter-controller communication - Inputs - 42 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15210 | 115211 | Inter-controller communication - Inputs - 43 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15211 | 115212 | Inter-controller communication - Inputs - 44 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15212 | 115213 | Inter-controller communication - Inputs - 45 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15213 | 115214 | Inter-controller communication - Inputs - 46 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15214 | 115215 | Inter-controller communication - Inputs - 47 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15215 | 115216 | Inter-controller communication - Inputs - 48 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15216 | 115217 | Inter-controller communication - Inputs - 49 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15217 | 115218 | Inter-controller communication - Inputs - 50 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15218 | 115219 | Inter-controller communication - Inputs - 51 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15219 | 115220 | Inter-controller communication - Inputs - 52 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15220 | 115221 | Inter-controller communication - Inputs - 53 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15221 | 115222 | Inter-controller communication - Inputs - 54 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15222 | 115223 | Inter-controller communication - Inputs - 55 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15223 | 115224 | Inter-controller communication - Inputs - 56 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15224 | 115225 | Inter-controller communication - Inputs - 57 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15225 | 115226 | Inter-controller communication - Inputs - 58 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15226 | 115227 | Inter-controller communication - Inputs - 59 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15227 | 115228 | Inter-controller communication - Inputs - 60 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15228 | 115229 | Inter-controller communication - Inputs - 61 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15229 | 115230 | Inter-controller communication - Inputs - 62 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15230 | 115231 | Inter-controller communication - Inputs - 63 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15231 | 115232 | Inter-controller communication - Inputs - 64 - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15232 | 115233 | Inter-controller communication - Inputs - 1 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15233 | 115234 | Inter-controller communication - Inputs - 2 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15234 | 115235 | Inter-controller communication - Inputs - 3 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15235 | 115236 | Inter-controller communication - Inputs - 4 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15236 | 115237 | Inter-controller communication - Inputs - 5 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15237 | 115238 | Inter-controller communication - Inputs - 6 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15238 | 115239 | Inter-controller communication - Inputs - 7 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15239 | 115240 | Inter-controller communication - Inputs - 8 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15240 | 115241 | Inter-controller communication - Inputs - 9 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15241 | 115242 | Inter-controller communication - Inputs - 10 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15242 | 115243 | Inter-controller communication - Inputs - 11 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15243 | 115244 | Inter-controller communication - Inputs - 12 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15244 | 115245 | Inter-controller communication - Inputs - 13 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15245 | 115246 | Inter-controller communication - Inputs - 14 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15246 | 115247 | Inter-controller communication - Inputs - 15 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15247 | 115248 | Inter-controller communication - Inputs - 16 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15248 | 115249 | Inter-controller communication - Inputs - 17 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15249 | 115250 | Inter-controller communication - Inputs - 18 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15250 | 115251 | Inter-controller communication - Inputs - 19 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15251 | 115252 | Inter-controller communication - Inputs - 20 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15252 | 115253 | Inter-controller communication - Inputs - 21 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15253 | 115254 | Inter-controller communication - Inputs - 22 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15254 | 115255 | Inter-controller communication - Inputs - 23 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15255 | 115256 | Inter-controller communication - Inputs - 24 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15256 | 115257 | Inter-controller communication - Inputs - 25 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15257 | 115258 | Inter-controller communication - Inputs - 26 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15258 | 115259 | Inter-controller communication - Inputs - 27 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15259 | 115260 | Inter-controller communication - Inputs - 28 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15260 | 115261 | Inter-controller communication - Inputs - 29 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15261 | 115262 | Inter-controller communication - Inputs - 30 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15262 | 115263 | Inter-controller communication - Inputs - 31 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15263 | 115264 | Inter-controller communication - Inputs - 32 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15264 | 115265 | Inter-controller communication - Inputs - 33 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15265 | 115266 | Inter-controller communication - Inputs - 34 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15266 | 115267 | Inter-controller communication - Inputs - 35 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15267 | 115268 | Inter-controller communication - Inputs - 36 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15268 | 115269 | Inter-controller communication - Inputs - 37 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15269 | 115270 | Inter-controller communication - Inputs - 38 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15270 | 115271 | Inter-controller communication - Inputs - 39 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15271 | 115272 | Inter-controller communication - Inputs - 40 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15272 | 115273 | Inter-controller communication - Inputs - 41 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15273 | 115274 | Inter-controller communication - Inputs - 42 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15274 | 115275 | Inter-controller communication - Inputs - 43 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15275 | 115276 | Inter-controller communication - Inputs - 44 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15276 | 115277 | Inter-controller communication - Inputs - 45 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15277 | 115278 | Inter-controller communication - Inputs - 46 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15278 | 115279 | Inter-controller communication - Inputs - 47 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15279 | 115280 | Inter-controller communication - Inputs - 48 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15280 | 115281 | Inter-controller communication - Inputs - 49 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15281 | 115282 | Inter-controller communication - Inputs - 50 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15282 | 115283 | Inter-controller communication - Inputs - 51 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15283 | 115284 | Inter-controller communication - Inputs - 52 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15284 | 115285 | Inter-controller communication - Inputs - 53 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15285 | 115286 | Inter-controller communication - Inputs - 54 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15286 | 115287 | Inter-controller communication - Inputs - 55 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15287 | 115288 | Inter-controller communication - Inputs - 56 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15288 | 115289 | Inter-controller communication - Inputs - 57 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15289 | 115290 | Inter-controller communication - Inputs - 58 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15290 | 115291 | Inter-controller communication - Inputs - 59 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15291 | 115292 | Inter-controller communication - Inputs - 60 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15292 | 115293 | Inter-controller communication - Inputs - 61 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15293 | 115294 | Inter-controller communication - Inputs - 62 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15294 | 115295 | Inter-controller communication - Inputs - 63 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15295 | 115296 | Inter-controller communication - Inputs - 64 - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15296 | 115297 | Inter-controller communication - Inputs - 1 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15297 | 115298 | Inter-controller communication - Inputs - 2 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15298 | 115299 | Inter-controller communication - Inputs - 3 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15299 | 115300 | Inter-controller communication - Inputs - 4 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15300 | 115301 | Inter-controller communication - Inputs - 5 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15301 | 115302 | Inter-controller communication - Inputs - 6 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15302 | 115303 | Inter-controller communication - Inputs - 7 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15303 | 115304 | Inter-controller communication - Inputs - 8 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15304 | 115305 | Inter-controller communication - Inputs - 9 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15305 | 115306 | Inter-controller communication - Inputs - 10 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15306 | 115307 | Inter-controller communication - Inputs - 11 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15307 | 115308 | Inter-controller communication - Inputs - 12 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15308 | 115309 | Inter-controller communication - Inputs - 13 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15309 | 115310 | Inter-controller communication - Inputs - 14 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15310 | 115311 | Inter-controller communication - Inputs - 15 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15311 | 115312 | Inter-controller communication - Inputs - 16 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15312 | 115313 | Inter-controller communication - Inputs - 17 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15313 | 115314 | Inter-controller communication - Inputs - 18 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15314 | 115315 | Inter-controller communication - Inputs - 19 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15315 | 115316 | Inter-controller communication - Inputs - 20 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15316 | 115317 | Inter-controller communication - Inputs - 21 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15317 | 115318 | Inter-controller communication - Inputs - 22 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15318 | 115319 | Inter-controller communication - Inputs - 23 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15319 | 115320 | Inter-controller communication - Inputs - 24 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15320 | 115321 | Inter-controller communication - Inputs - 25 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15321 | 115322 | Inter-controller communication - Inputs - 26 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15322 | 115323 | Inter-controller communication - Inputs - 27 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15323 | 115324 | Inter-controller communication - Inputs - 28 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15324 | 115325 | Inter-controller communication - Inputs - 29 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15325 | 115326 | Inter-controller communication - Inputs - 30 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15326 | 115327 | Inter-controller communication - Inputs - 31 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15327 | 115328 | Inter-controller communication - Inputs - 32 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15328 | 115329 | Inter-controller communication - Inputs - 33 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15329 | 115330 | Inter-controller communication - Inputs - 34 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15330 | 115331 | Inter-controller communication - Inputs - 35 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15331 | 115332 | Inter-controller communication - Inputs - 36 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15332 | 115333 | Inter-controller communication - Inputs - 37 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15333 | 115334 | Inter-controller communication - Inputs - 38 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15334 | 115335 | Inter-controller communication - Inputs - 39 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15335 | 115336 | Inter-controller communication - Inputs - 40 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15336 | 115337 | Inter-controller communication - Inputs - 41 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15337 | 115338 | Inter-controller communication - Inputs - 42 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15338 | 115339 | Inter-controller communication - Inputs - 43 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15339 | 115340 | Inter-controller communication - Inputs - 44 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15340 | 115341 | Inter-controller communication - Inputs - 45 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15341 | 115342 | Inter-controller communication - Inputs - 46 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15342 | 115343 | Inter-controller communication - Inputs - 47 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15343 | 115344 | Inter-controller communication - Inputs - 48 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15344 | 115345 | Inter-controller communication - Inputs - 49 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15345 | 115346 | Inter-controller communication - Inputs - 50 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15346 | 115347 | Inter-controller communication - Inputs - 51 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15347 | 115348 | Inter-controller communication - Inputs - 52 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15348 | 115349 | Inter-controller communication - Inputs - 53 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15349 | 115350 | Inter-controller communication - Inputs - 54 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15350 | 115351 | Inter-controller communication - Inputs - 55 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15351 | 115352 | Inter-controller communication - Inputs - 56 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15352 | 115353 | Inter-controller communication - Inputs - 57 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15353 | 115354 | Inter-controller communication - Inputs - 58 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15354 | 115355 | Inter-controller communication - Inputs - 59 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15355 | 115356 | Inter-controller communication - Inputs - 60 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15356 | 115357 | Inter-controller communication - Inputs - 61 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15357 | 115358 | Inter-controller communication - Inputs - 62 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15358 | 115359 | Inter-controller communication - Inputs - 63 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15359 | 115360 | Inter-controller communication - Inputs - 64 - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15360 | 115361 | Inter-controller communication - Inputs - 1 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15361 | 115362 | Inter-controller communication - Inputs - 2 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15362 | 115363 | Inter-controller communication - Inputs - 3 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15363 | 115364 | Inter-controller communication - Inputs - 4 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15364 | 115365 | Inter-controller communication - Inputs - 5 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15365 | 115366 | Inter-controller communication - Inputs - 6 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15366 | 115367 | Inter-controller communication - Inputs - 7 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15367 | 115368 | Inter-controller communication - Inputs - 8 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15368 | 115369 | Inter-controller communication - Inputs - 9 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15369 | 115370 | Inter-controller communication - Inputs - 10 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15370 | 115371 | Inter-controller communication - Inputs - 11 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15371 | 115372 | Inter-controller communication - Inputs - 12 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15372 | 115373 | Inter-controller communication - Inputs - 13 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15373 | 115374 | Inter-controller communication - Inputs - 14 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15374 | 115375 | Inter-controller communication - Inputs - 15 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15375 | 115376 | Inter-controller communication - Inputs - 16 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15376 | 115377 | Inter-controller communication - Inputs - 17 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15377 | 115378 | Inter-controller communication - Inputs - 18 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15378 | 115379 | Inter-controller communication - Inputs - 19 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15379 | 115380 | Inter-controller communication - Inputs - 20 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15380 | 115381 | Inter-controller communication - Inputs - 21 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15381 | 115382 | Inter-controller communication - Inputs - 22 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15382 | 115383 | Inter-controller communication - Inputs - 23 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15383 | 115384 | Inter-controller communication - Inputs - 24 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15384 | 115385 | Inter-controller communication - Inputs - 25 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15385 | 115386 | Inter-controller communication - Inputs - 26 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15386 | 115387 | Inter-controller communication - Inputs - 27 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15387 | 115388 | Inter-controller communication - Inputs - 28 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15388 | 115389 | Inter-controller communication - Inputs - 29 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15389 | 115390 | Inter-controller communication - Inputs - 30 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15390 | 115391 | Inter-controller communication - Inputs - 31 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15391 | 115392 | Inter-controller communication - Inputs - 32 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15392 | 115393 | Inter-controller communication - Inputs - 33 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15393 | 115394 | Inter-controller communication - Inputs - 34 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15394 | 115395 | Inter-controller communication - Inputs - 35 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15395 | 115396 | Inter-controller communication - Inputs - 36 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15396 | 115397 | Inter-controller communication - Inputs - 37 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15397 | 115398 | Inter-controller communication - Inputs - 38 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15398 | 115399 | Inter-controller communication - Inputs - 39 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15399 | 115400 | Inter-controller communication - Inputs - 40 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15400 | 115401 | Inter-controller communication - Inputs - 41 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15401 | 115402 | Inter-controller communication - Inputs - 42 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15402 | 115403 | Inter-controller communication - Inputs - 43 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15403 | 115404 | Inter-controller communication - Inputs - 44 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15404 | 115405 | Inter-controller communication - Inputs - 45 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15405 | 115406 | Inter-controller communication - Inputs - 46 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15406 | 115407 | Inter-controller communication - Inputs - 47 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15407 | 115408 | Inter-controller communication - Inputs - 48 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15408 | 115409 | Inter-controller communication - Inputs - 49 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15409 | 115410 | Inter-controller communication - Inputs - 50 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15410 | 115411 | Inter-controller communication - Inputs - 51 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15411 | 115412 | Inter-controller communication - Inputs - 52 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15412 | 115413 | Inter-controller communication - Inputs - 53 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15413 | 115414 | Inter-controller communication - Inputs - 54 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15414 | 115415 | Inter-controller communication - Inputs - 55 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15415 | 115416 | Inter-controller communication - Inputs - 56 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15416 | 115417 | Inter-controller communication - Inputs - 57 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15417 | 115418 | Inter-controller communication - Inputs - 58 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15418 | 115419 | Inter-controller communication - Inputs - 59 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15419 | 115420 | Inter-controller communication - Inputs - 60 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15420 | 115421 | Inter-controller communication - Inputs - 61 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15421 | 115422 | Inter-controller communication - Inputs - 62 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15422 | 115423 | Inter-controller communication - Inputs - 63 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in | 15423 | 115424 | Inter-controller communication - Inputs - 64 - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15450 | 115451 | Inter-controller communication - Outputs - ICC output 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15451 | 115452 | Inter-controller communication - Outputs - ICC output 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15452 | 115453 | Inter-controller communication - Outputs - ICC output 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15453 | 115454 | Inter-controller communication - Outputs - ICC output 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15454 | 115455 | Inter-controller communication - Outputs - ICC output 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15455 | 115456 | Inter-controller communication - Outputs - ICC output 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15456 | 115457 | Inter-controller communication - Outputs - ICC output 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15457 | 115458 | Inter-controller communication - Outputs - ICC output 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15458 | 115459 | Inter-controller communication - Outputs - ICC output 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15459 | 115460 | Inter-controller communication - Outputs - ICC output 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15460 | 115461 | Inter-controller communication - Outputs - ICC output 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15461 | 115462 | Inter-controller communication - Outputs - ICC output 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15462 | 115463 | Inter-controller communication - Outputs - ICC output 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15463 | 115464 | Inter-controller communication - Outputs - ICC output 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15464 | 115465 | Inter-controller communication - Outputs - ICC output 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15465 | 115466 | Inter-controller communication - Outputs - ICC output 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15466 | 115467 | Inter-controller communication - Outputs - ICC output 17 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15467 | 115468 | Inter-controller communication - Outputs - ICC output 18 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15468 | 115469 | Inter-controller communication - Outputs - ICC output 19 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15469 | 115470 | Inter-controller communication - Outputs - ICC output 20 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15470 | 115471 | Inter-controller communication - Outputs - ICC output 21 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15471 | 115472 | Inter-controller communication - Outputs - ICC output 22 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15472 | 115473 | Inter-controller communication - Outputs - ICC output 23 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15473 | 115474 | Inter-controller communication - Outputs - ICC output 24 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15474 | 115475 | Inter-controller communication - Outputs - ICC output 25 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15475 | 115476 | Inter-controller communication - Outputs - ICC output 26 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15476 | 115477 | Inter-controller communication - Outputs - ICC output 27 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15477 | 115478 | Inter-controller communication - Outputs - ICC output 28 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15478 | 115479 | Inter-controller communication - Outputs - ICC output 29 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15479 | 115480 | Inter-controller communication - Outputs - ICC output 30 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15480 | 115481 | Inter-controller communication - Outputs - ICC output 31 | X | X | X | X | X | X | X
CustomLogic: ICC flag out | 15481 | 115482 | Inter-controller communication - Outputs - ICC output 32 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15600 | 115601 | Inter-controller communication - Inputs - Any - ICC input 1 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15601 | 115602 | Inter-controller communication - Inputs - Any - ICC input 2 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15602 | 115603 | Inter-controller communication - Inputs - Any - ICC input 3 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15603 | 115604 | Inter-controller communication - Inputs - Any - ICC input 4 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15604 | 115605 | Inter-controller communication - Inputs - Any - ICC input 5 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15605 | 115606 | Inter-controller communication - Inputs - Any - ICC input 6 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15606 | 115607 | Inter-controller communication - Inputs - Any - ICC input 7 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15607 | 115608 | Inter-controller communication - Inputs - Any - ICC input 8 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15608 | 115609 | Inter-controller communication - Inputs - Any - ICC input 9 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15609 | 115610 | Inter-controller communication - Inputs - Any - ICC input 10 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15610 | 115611 | Inter-controller communication - Inputs - Any - ICC input 11 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15611 | 115612 | Inter-controller communication - Inputs - Any - ICC input 12 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15612 | 115613 | Inter-controller communication - Inputs - Any - ICC input 13 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15613 | 115614 | Inter-controller communication - Inputs - Any - ICC input 14 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15614 | 115615 | Inter-controller communication - Inputs - Any - ICC input 15 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15615 | 115616 | Inter-controller communication - Inputs - Any - ICC input 16 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15616 | 115617 | Inter-controller communication - Inputs - Any - ICC input 17 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15617 | 115618 | Inter-controller communication - Inputs - Any - ICC input 18 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15618 | 115619 | Inter-controller communication - Inputs - Any - ICC input 19 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15619 | 115620 | Inter-controller communication - Inputs - Any - ICC input 20 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15620 | 115621 | Inter-controller communication - Inputs - Any - ICC input 21 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15621 | 115622 | Inter-controller communication - Inputs - Any - ICC input 22 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15622 | 115623 | Inter-controller communication - Inputs - Any - ICC input 23 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15623 | 115624 | Inter-controller communication - Inputs - Any - ICC input 24 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15624 | 115625 | Inter-controller communication - Inputs - Any - ICC input 25 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15625 | 115626 | Inter-controller communication - Inputs - Any - ICC input 26 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15626 | 115627 | Inter-controller communication - Inputs - Any - ICC input 27 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15627 | 115628 | Inter-controller communication - Inputs - Any - ICC input 28 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15628 | 115629 | Inter-controller communication - Inputs - Any - ICC input 29 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15629 | 115630 | Inter-controller communication - Inputs - Any - ICC input 30 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15630 | 115631 | Inter-controller communication - Inputs - Any - ICC input 31 | X | X | X | X | X | X | X
CustomLogic: ICC flag in any | 15631 | 115632 | Inter-controller communication - Inputs - Any - ICC input 32 | X | X | X | X | X | X | X
Codesys digital outputs | 16000 | 116001 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16001 | 116002 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16002 | 116003 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16003 | 116004 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16004 | 116005 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16005 | 116006 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16006 | 116007 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16007 | 116008 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16008 | 116009 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16009 | 116010 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16010 | 116011 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16011 | 116012 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16012 | 116013 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16013 | 116014 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16014 | 116015 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16015 | 116016 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16016 | 116017 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16017 | 116018 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16018 | 116019 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16019 | 116020 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16020 | 116021 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16021 | 116022 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16022 | 116023 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16023 | 116024 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16024 | 116025 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16025 | 116026 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16026 | 116027 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16027 | 116028 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16028 | 116029 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16029 | 116030 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16030 | 116031 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16031 | 116032 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16032 | 116033 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16033 | 116034 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16034 | 116035 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16035 | 116036 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16036 | 116037 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16037 | 116038 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16038 | 116039 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16039 | 116040 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16040 | 116041 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16041 | 116042 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16042 | 116043 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16043 | 116044 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16044 | 116045 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16045 | 116046 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16046 | 116047 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16047 | 116048 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16048 | 116049 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16049 | 116050 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16050 | 116051 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16051 | 116052 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16052 | 116053 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16053 | 116054 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16054 | 116055 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16055 | 116056 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16056 | 116057 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16057 | 116058 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16058 | 116059 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16059 | 116060 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16060 | 116061 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16061 | 116062 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16062 | 116063 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16063 | 116064 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16064 | 116065 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16065 | 116066 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16066 | 116067 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16067 | 116068 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16068 | 116069 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16069 | 116070 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16070 | 116071 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16071 | 116072 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16072 | 116073 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16073 | 116074 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16074 | 116075 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16075 | 116076 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16076 | 116077 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16077 | 116078 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16078 | 116079 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16079 | 116080 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16080 | 116081 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16081 | 116082 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16082 | 116083 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16083 | 116084 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16084 | 116085 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16085 | 116086 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16086 | 116087 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16087 | 116088 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16088 | 116089 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16089 | 116090 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16090 | 116091 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16091 | 116092 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16092 | 116093 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16093 | 116094 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16094 | 116095 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16095 | 116096 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16096 | 116097 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16097 | 116098 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16098 | 116099 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Codesys digital outputs | 16099 | 116100 | Functions - Digital output functions - Local - CODESYS - Outputs - Custom digital output | X | X | X | X | X | X | X
Alarm status: Active | 20000 | 120001 | Application initialisation error | X | X | X | X | X | X | X
Alarm status: Active | 20001 | 120002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm status: Active | 20002 | 120003 | Preliminary software | X | X | X | X | X | X | X
Alarm status: Active | 20003 | 120004 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | X |  | X | X | X
Alarm status: Active | 20004 | 120005 | Parameters - Engine - Start sequence - Start failure - Information - Flags | X |  | X | X | X
Alarm status: Active | 20005 | 120006 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | X |  | X | X | X
Alarm status: Active | 20006 | 120007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20007 | 120008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20008 | 120009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20009 | 120010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20010 | 120011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | X |  | X | X | X
Alarm status: Active | 20011 | 120012 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | X |  | X | X | X
Alarm status: Active | 20013 | 120014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20014 | 120015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20015 | 120016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20016 | 120017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20017 | 120018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20018 | 120019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20019 | 120020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20020 | 120021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20021 | 120022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20022 | 120023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20027 | 120028 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | X |  | X | X | X
Alarm status: Active | 20041 | 120042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | X |  | X | X | X
Alarm status: Active | 20041 | 120042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure |  | X
Alarm status: Active | 20041 | 120042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | [5 empty] | X | X
Alarm status: Active | 20042 | 120043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | X |  | X | X | X
Alarm status: Active | 20042 | 120043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure |  | X
Alarm status: Active | 20042 | 120043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | [5 empty] | X | X
Alarm status: Active | 20043 | 120044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | X |  | X | X | X
Alarm status: Active | 20043 | 120044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure |  | X
Alarm status: Active | 20043 | 120044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | [5 empty] | X | X
Alarm status: Active | 20044 | 120045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | X |  | X | X | X
Alarm status: Active | 20044 | 120045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure |  | X
Alarm status: Active | 20044 | 120045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | [5 empty] | X | X
Alarm status: Active | 20045 | 120046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | X |  | X | X | X
Alarm status: Active | 20045 | 120046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure |  | X
Alarm status: Active | 20045 | 120046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | [5 empty] | X | X
Alarm status: Active | 20046 | 120047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | X |  | X | X | X
Alarm status: Active | 20046 | 120047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure |  | X
Alarm status: Active | 20046 | 120047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | [5 empty] | X | X
Alarm status: Active | 20047 | 120048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | X |  | X | X | X
Alarm status: Active | 20047 | 120048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) |  | X
Alarm status: Active | 20047 | 120048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | [5 empty] | X | X
Alarm status: Active | 20048 | 120049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | X |  | X | X | X
Alarm status: Active | 20048 | 120049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit |  | X
Alarm status: Active | 20048 | 120049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | [5 empty] | X | X
Alarm status: Active | 20049 | 120050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure |  |  |  | X
Alarm status: Active | 20049 | 120050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | [6 empty] | X
Alarm status: Active | 20050 | 120051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure |  |  |  | X
Alarm status: Active | 20050 | 120051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | [6 empty] | X
Alarm status: Active | 20051 | 120052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure |  |  |  | X
Alarm status: Active | 20051 | 120052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | [6 empty] | X
Alarm status: Active | 20052 | 120053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure |  |  |  | X
Alarm status: Active | 20052 | 120053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | [6 empty] | X
Alarm status: Active | 20053 | 120054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure |  |  |  | X
Alarm status: Active | 20053 | 120054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | [6 empty] | X
Alarm status: Active | 20054 | 120055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure |  |  |  | X
Alarm status: Active | 20054 | 120055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | [6 empty] | X
Alarm status: Active | 20055 | 120056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) |  |  |  | X
Alarm status: Active | 20055 | 120056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | [6 empty] | X
Alarm status: Active | 20056 | 120057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit |  |  |  | X
Alarm status: Active | 20056 | 120057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | [6 empty] | X
Alarm status: Active | 20060 | 120061 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error |  |  | X | X
Alarm status: Active | 20060 | 120061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | X |  |  |  | X | X | X
Alarm status: Active | 20060 | 120061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error |  | X
Alarm status: Active | 20061 | 120062 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | X |  | X | X | X
Alarm status: Active | 20061 | 120062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error |  | X
Alarm status: Active | 20061 | 120062 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | [5 empty] | X | X
Alarm status: Active | 20062 | 120063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | X |  | X | X | X
Alarm status: Active | 20103 | 120104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information - Flags |  |  | X | X
Alarm status: Active | 20103 | 120104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information - Flags | X |  |  |  | X | X | X
Alarm status: Active | 20103 | 120104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information - Flags |  | X
Alarm status: Active | 20104 | 120105 | Parameters - Mains - Additional protections - Vector shift - Information - Flags |  |  | X | X
Alarm status: Active | 20104 | 120105 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | X |  |  |  | X | X | X
Alarm status: Active | 20104 | 120105 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags |  | X
Alarm status: Active | 20105 | 120106 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | X |  | X | X | X
Alarm status: Active | 20105 | 120106 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags |  | X
Alarm status: Active | 20105 | 120106 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20106 | 120107 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20107 | 120108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20108 | 120109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20108 | 120109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags |  | X
Alarm status: Active | 20108 | 120109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20109 | 120110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20109 | 120110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags |  | X
Alarm status: Active | 20109 | 120110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20110 | 120111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20110 | 120111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags |  | X
Alarm status: Active | 20110 | 120111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20111 | 120112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20111 | 120112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags |  | X
Alarm status: Active | 20111 | 120112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20115 | 120116 | Protection set point out of range | X | X | X | X | X | X | X
Alarm status: Active | 20116 | 120117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | X |  | X | X | X
Alarm status: Active | 20117 | 120118 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | X |  | X | X | X
Alarm status: Active | 20118 | 120119 | Protection set point out of range (differential current) | X |  | X | X | X
Alarm status: Active | 20119 | 120120 | Parameters - Local - Mode - Not under remote control - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20121 | 120122 | Parameters - Local - Monitoring - System not OK - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20122 | 120123 | Configuration update delayed | X | X | X | X | X | X | X
Alarm status: Active | 20123 | 120124 | Critical process error | X | X | X | X | X | X | X
Alarm status: Active | 20124 | 120125 | Restore error | X | X | X | X | X | X | X
Alarm status: Active | 20125 | 120126 | SD-card format error | X | X | X | X | X | X | X
Alarm status: Active | 20126 | 120127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm status: Active | 20127 | 120128 | Fieldbus configuration exceeded maximum I/O configuration | X | X | X | X | X | X | X
Alarm status: Active | 20128 | 120129 | Parameters - Custom alarm - Custom alarm 0 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20129 | 120130 | Parameters - Custom alarm - Custom alarm 1 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20130 | 120131 | Parameters - Custom alarm - Custom alarm 2 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20131 | 120132 | Parameters - Custom alarm - Custom alarm 3 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20132 | 120133 | Parameters - Custom alarm - Custom alarm 4 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20133 | 120134 | Parameters - Custom alarm - Custom alarm 5 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20134 | 120135 | Parameters - Custom alarm - Custom alarm 6 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20135 | 120136 | Parameters - Custom alarm - Custom alarm 7 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20136 | 120137 | Parameters - Custom alarm - Custom alarm 8 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20137 | 120138 | Parameters - Custom alarm - Custom alarm 9 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20138 | 120139 | Parameters - Custom alarm - Custom alarm 10 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20139 | 120140 | Parameters - Custom alarm - Custom alarm 11 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20140 | 120141 | Parameters - Custom alarm - Custom alarm 12 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20141 | 120142 | Parameters - Custom alarm - Custom alarm 13 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20142 | 120143 | Parameters - Custom alarm - Custom alarm 14 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20143 | 120144 | Parameters - Custom alarm - Custom alarm 15 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20144 | 120145 | Parameters - Custom alarm - Custom alarm 16 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20145 | 120146 | Parameters - Custom alarm - Custom alarm 17 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20146 | 120147 | Parameters - Custom alarm - Custom alarm 18 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20147 | 120148 | Parameters - Custom alarm - Custom alarm 19 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20148 | 120149 | Parameters - Custom alarm - Custom alarm 20 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20149 | 120150 | Parameters - Custom alarm - Custom alarm 21 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20150 | 120151 | Parameters - Custom alarm - Custom alarm 22 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20151 | 120152 | Parameters - Custom alarm - Custom alarm 23 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20152 | 120153 | Parameters - Custom alarm - Custom alarm 24 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Active | 20153 | 120154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | X |  | X | X | X
Alarm status: Active | 20154 | 120155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | X |  | X | X | X
Alarm status: Active | 20163 | 120164 | Required hardware card(s) not found | X | X | X | X | X | X | X
Alarm status: Active | 20164 | 120165 | Software mismatch on hardware module(s) | X | X | X | X | X | X | X
Alarm status: Active | 20165 | 120166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break |  |  | X
Alarm status: Active | 20165 | 120166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | X |  |  |  | X | X
Alarm status: Active | 20165 | 120166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break |  | X
Alarm status: Active | 20166 | 120167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | X |  | X |  | X
Alarm status: Active | 20166 | 120167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break |  | X
Alarm status: Active | 20166 | 120167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | [5 empty] | X
Alarm status: Active | 20167 | 120168 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break |  |  | X
Alarm status: Active | 20167 | 120168 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | X |  |  |  | X | X
Alarm status: Active | 20167 | 120168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break |  | X
Alarm status: Active | 20168 | 120169 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break |  |  | X
Alarm status: Active | 20168 | 120169 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | X |  |  |  | X | X
Alarm status: Active | 20168 | 120169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break |  | X
Alarm status: Active | 20169 | 120170 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break |  |  | X
Alarm status: Active | 20169 | 120170 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | X |  |  |  | X | X
Alarm status: Active | 20169 | 120170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break |  | X
Alarm status: Active | 20170 | 120171 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | X |  | X |  | X
Alarm status: Active | 20170 | 120171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break |  | X
Alarm status: Active | 20170 | 120171 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | [5 empty] | X
Alarm status: Active | 20171 | 120172 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | X |  | X |  | X
Alarm status: Active | 20171 | 120172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break |  | X
Alarm status: Active | 20171 | 120172 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | [5 empty] | X
Alarm status: Active | 20172 | 120173 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | X |  | X |  | X
Alarm status: Active | 20172 | 120173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break |  | X
Alarm status: Active | 20172 | 120173 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | [5 empty] | X
Alarm status: Active | 20178 | 120179 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm |  |  | X | X |  | X | X
Alarm status: Active | 20179 | 120180 | Parameters - Engine - Emergency stop - Information - Flags | X |  | X | X | X
Alarm status: Active | 20179 | 120180 | Parameters - Busbar A - Emergency stop - Information - Flags |  | X
Alarm status: Active | 20179 | 120180 | Parameters - Mains - Emergency stop - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20180 | 120181 | Clock battery failure | X | X | X | X | X | X | X
Alarm status: Active | 20181 | 120182 | Controller temperature too high | X | X | X | X | X | X | X
Alarm status: Active | 20182 | 120183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20183 | 120184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | X | X | X | X | X | X | X
Alarm status: Active | 20184 | 120185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20185 | 120186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | X | X | X | X | X | X | X
Alarm status: Active | 20186 | 120187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20187 | 120188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | X | X | X | X | X | X | X
Alarm status: Active | 20188 | 120189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20189 | 120190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | X | X | X | X | X | X | X
Alarm status: Active | 20190 | 120191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20191 | 120192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Active | 20192 | 120193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20193 | 120194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Active | 20194 | 120195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20195 | 120196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Active | 20196 | 120197 | EIM3.1 4 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20197 | 120198 | EIM3.1 4 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Active | 20198 | 120199 | EIM3.1 5 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20199 | 120200 | EIM3.1 5 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Active | 20200 | 120201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Active | 20201 | 120202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Active | 20202 | 120203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Active | 20203 | 120204 | EIM3.1 4 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Active | 20204 | 120205 | EIM3.1 5 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Active | 20205 | 120206 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Active | 20206 | 120207 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Active | 20207 | 120208 | AC protections not running (differential current) | X |  | X | X | X
Alarm status: Active | 20208 | 120209 | AC data is missing (differential current) | X |  | X | X | X
Alarm status: Active | 20209 | 120210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20210 | 120211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Active | 20211 | 120212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20212 | 120213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Active | 20213 | 120214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20214 | 120215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Active | 20215 | 120216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20216 | 120217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | X | X | X | X | X | X | X
Alarm status: Active | 20217 | 120218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20218 | 120219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | X | X | X | X | X | X | X
Alarm status: Active | 20219 | 120220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20220 | 120221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | X | X | X | X | X | X | X
Alarm status: Active | 20221 | 120222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20222 | 120223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | X | X | X | X | X | X | X
Alarm status: Active | 20223 | 120224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20224 | 120225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | X | X | X | X | X | X | X
Alarm status: Active | 20225 | 120226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | X | X | X | X | X | X | X
Alarm status: Active | 20226 | 120227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | X | X | X | X | X | X | X
Alarm status: Active | 20228 | 120229 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20229 | 120230 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20231 | 120232 | Controller ID not configured | X | X | X | X | X | X | X
Alarm status: Active | 20236 | 120237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20237 | 120238 | Blackout detection mismatch | X |  | X | X | X
Alarm status: Active | 20240 | 120241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | X | X | X | X | X | X | X
Alarm status: Active | 20241 | 120242 | Parameters - Communication - NTP - NTP server 1 no response - Information - Flags - NTP server 1 is not responding | X | X | X | X | X | X | X
Alarm status: Active | 20242 | 120243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | X | X | X | X | X | X | X
Alarm status: Active | 20243 | 120244 | Parameters - Communication - NTP - NTP server 2 no response - Information - Flags - NTP server 2 is not responding | X | X | X | X | X | X | X
Alarm status: Active | 20244 | 120245 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20245 | 120246 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20246 | 120247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20247 | 120248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20296 | 120297 | Controller not part of system | X | X | X | X | X | X | X
Alarm status: Active | 20297 | 120298 | Different single-line configurations | X | X | X | X | X | X | X
Alarm status: Active | 20298 | 120299 | Single-line missing/none active | X | X | X | X | X | X | X
Alarm status: Active | 20299 | 120300 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20300 | 120301 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | X | X | X | X | X | X | X
Alarm status: Active | 20301 | 120302 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | X | X | X | X | X | X | X
Alarm status: Active | 20302 | 120303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | X |  | X | X | X
Alarm status: Active | 20303 | 120304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | X |  | X | X | X
Alarm status: Active | 20304 | 120305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | X |  | X | X | X
Alarm status: Active | 20305 | 120306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | X |  | X | X | X
Alarm status: Active | 20306 | 120307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | X |  | X | X | X
Alarm status: Active | 20307 | 120308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Active | 20308 | 120309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Active | 20309 | 120310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Active | 20310 | 120311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Active | 20311 | 120312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20312 | 120313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20313 | 120314 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20314 | 120315 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20315 | 120316 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20316 | 120317 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20317 | 120318 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20318 | 120319 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20319 | 120320 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20320 | 120321 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20321 | 120322 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20322 | 120323 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20323 | 120324 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20324 | 120325 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20325 | 120326 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20326 | 120327 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20327 | 120328 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20328 | 120329 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20329 | 120330 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20330 | 120331 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20331 | 120332 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20332 | 120333 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20333 | 120334 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20334 | 120335 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20335 | 120336 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20336 | 120337 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20337 | 120338 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20338 | 120339 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20339 | 120340 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20340 | 120341 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20341 | 120342 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20342 | 120343 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20343 | 120344 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20344 | 120345 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20345 | 120346 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20346 | 120347 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20347 | 120348 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20348 | 120349 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20349 | 120350 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20350 | 120351 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20351 | 120352 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20352 | 120353 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20353 | 120354 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20354 | 120355 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20355 | 120356 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20356 | 120357 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20357 | 120358 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20358 | 120359 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20359 | 120360 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20360 | 120361 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20361 | 120362 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20362 | 120363 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20363 | 120364 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20364 | 120365 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20365 | 120366 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20366 | 120367 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20367 | 120368 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20368 | 120369 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20369 | 120370 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20370 | 120371 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20371 | 120372 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20372 | 120373 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20373 | 120374 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20374 | 120375 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20375 | 120376 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20376 | 120377 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20377 | 120378 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20378 | 120379 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20379 | 120380 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20380 | 120381 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20381 | 120382 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20382 | 120383 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20383 | 120384 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20384 | 120385 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20385 | 120386 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20386 | 120387 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20387 | 120388 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20388 | 120389 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20389 | 120390 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20390 | 120391 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20391 | 120392 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20392 | 120393 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20393 | 120394 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20394 | 120395 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20395 | 120396 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20396 | 120397 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20397 | 120398 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20398 | 120399 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20399 | 120400 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20400 | 120401 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20401 | 120402 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20402 | 120403 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20403 | 120404 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20404 | 120405 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20405 | 120406 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20406 | 120407 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20407 | 120408 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20408 | 120409 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20409 | 120410 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20410 | 120411 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20411 | 120412 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20412 | 120413 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20413 | 120414 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20414 | 120415 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20415 | 120416 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20416 | 120417 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20417 | 120418 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20418 | 120419 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20419 | 120420 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20420 | 120421 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20421 | 120422 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20422 | 120423 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20423 | 120424 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20424 | 120425 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20425 | 120426 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20426 | 120427 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20427 | 120428 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20428 | 120429 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20429 | 120430 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20430 | 120431 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20431 | 120432 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20432 | 120433 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20433 | 120434 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20434 | 120435 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20435 | 120436 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20436 | 120437 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20437 | 120438 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20438 | 120439 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20439 | 120440 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20440 | 120441 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20441 | 120442 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20442 | 120443 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20443 | 120444 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20444 | 120445 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20445 | 120446 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20446 | 120447 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20447 | 120448 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20448 | 120449 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20449 | 120450 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20450 | 120451 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20451 | 120452 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20452 | 120453 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20453 | 120454 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20454 | 120455 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20455 | 120456 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20456 | 120457 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20457 | 120458 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20458 | 120459 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20459 | 120460 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20460 | 120461 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20461 | 120462 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20462 | 120463 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20463 | 120464 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20464 | 120465 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20465 | 120466 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20466 | 120467 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20467 | 120468 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20468 | 120469 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20469 | 120470 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20470 | 120471 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20471 | 120472 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20472 | 120473 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20473 | 120474 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20474 | 120475 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20475 | 120476 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20476 | 120477 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20477 | 120478 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20478 | 120479 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20479 | 120480 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20480 | 120481 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20481 | 120482 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20482 | 120483 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20483 | 120484 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20484 | 120485 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20485 | 120486 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20486 | 120487 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20487 | 120488 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20488 | 120489 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20489 | 120490 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20490 | 120491 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20491 | 120492 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20492 | 120493 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20493 | 120494 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20494 | 120495 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20495 | 120496 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20496 | 120497 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20497 | 120498 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20498 | 120499 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20499 | 120500 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20500 | 120501 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20501 | 120502 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20502 | 120503 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20503 | 120504 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20504 | 120505 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20505 | 120506 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20506 | 120507 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20507 | 120508 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20508 | 120509 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20509 | 120510 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20510 | 120511 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20511 | 120512 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20512 | 120513 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20513 | 120514 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20514 | 120515 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20515 | 120516 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20516 | 120517 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20517 | 120518 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20518 | 120519 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20519 | 120520 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20520 | 120521 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20521 | 120522 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20522 | 120523 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20523 | 120524 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20524 | 120525 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20525 | 120526 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20526 | 120527 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20527 | 120528 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20528 | 120529 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20529 | 120530 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20530 | 120531 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20531 | 120532 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20532 | 120533 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20533 | 120534 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20534 | 120535 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20535 | 120536 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20536 | 120537 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20537 | 120538 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20538 | 120539 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20539 | 120540 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20540 | 120541 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20541 | 120542 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20542 | 120543 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20543 | 120544 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20544 | 120545 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20545 | 120546 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20546 | 120547 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20547 | 120548 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20548 | 120549 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20549 | 120550 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20550 | 120551 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20551 | 120552 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20552 | 120553 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20553 | 120554 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20554 | 120555 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20555 | 120556 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20556 | 120557 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20557 | 120558 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20558 | 120559 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20559 | 120560 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20560 | 120561 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20561 | 120562 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20562 | 120563 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Active | 20565 | 120566 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | X | X | X | X | X | X | X
Alarm status: Active | 20566 | 120567 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | X |  | X | X | X
Alarm status: Active | 20567 | 120568 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | X |  | X | X | X
Alarm status: Active | 20568 | 120569 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | X |  | X | X | X
Alarm status: Active | 20569 | 120570 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | X |  | X | X | X
Alarm status: Active | 20570 | 120571 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | X |  | X | X | X
Alarm status: Active | 20571 | 120572 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | X |  | X | X | X
Alarm status: Active | 20572 | 120573 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | X |  | X | X | X
Alarm status: Active | 20573 | 120574 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | X |  | X | X | X
Alarm status: Active | 20574 | 120575 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | X |  | X | X | X
Alarm status: Active | 20575 | 120576 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | X |  | X | X | X
Alarm status: Active | 20576 | 120577 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | X |  | X | X | X
Alarm status: Active | 20577 | 120578 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | X |  | X | X | X
Alarm status: Active | 20578 | 120579 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | X |  | X | X | X
Alarm status: Active | 20579 | 120580 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | X |  | X | X | X
Alarm status: Active | 20580 | 120581 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | X |  | X | X | X
Alarm status: Active | 20581 | 120582 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | X |  | X | X | X
Alarm status: Active | 20582 | 120583 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | X |  | X | X | X
Alarm status: Active | 20583 | 120584 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | X |  | X | X | X
Alarm status: Active | 20584 | 120585 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | X |  | X | X | X
Alarm status: Active | 20585 | 120586 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | X |  | X | X | X
Alarm status: Active | 20586 | 120587 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | X |  | X | X | X
Alarm status: Active | 20587 | 120588 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | X |  | X | X | X
Alarm status: Active | 20588 | 120589 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | X |  | X | X | X
Alarm status: Active | 20589 | 120590 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | X |  | X | X | X
Alarm status: Active | 20590 | 120591 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | X |  | X | X | X
Alarm status: Active | 20591 | 120592 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | X |  | X | X | X
Alarm status: Active | 20592 | 120593 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | X |  | X | X | X
Alarm status: Active | 20593 | 120594 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | X |  | X | X | X
Alarm status: Active | 20594 | 120595 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | X |  | X | X | X
Alarm status: Active | 20595 | 120596 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | X |  | X | X | X
Alarm status: Active | 20596 | 120597 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | X |  | X | X | X
Alarm status: Active | 20597 | 120598 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | X |  | X | X | X
Alarm status: Active | 20598 | 120599 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | X |  | X | X | X
Alarm status: Active | 20599 | 120600 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Active | 20600 | 120601 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Active | 20601 | 120602 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Active | 20602 | 120603 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Active | 20603 | 120604 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Active | 20604 | 120605 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Active | 20605 | 120606 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Active | 20606 | 120607 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Active | 20607 | 120608 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Active | 20608 | 120609 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Active | 20609 | 120610 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Active | 20610 | 120611 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Active | 20611 | 120612 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Active | 20612 | 120613 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | X |  | X | X | X
Alarm status: Active | 20613 | 120614 | DAVR unsupported AC configuration | X |  | X | X | X
Alarm status: Active | 20614 | 120615 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | X |  | X | X | X
Alarm status: Active | 20615 | 120616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | X |  | X | X | X
Alarm status: Active | 20615 | 120616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 |  | X
Alarm status: Active | 20615 | 120616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | [5 empty] | X | X
Alarm status: Active | 20616 | 120617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | X |  | X | X | X
Alarm status: Active | 20616 | 120617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 |  | X
Alarm status: Active | 20616 | 120617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | [5 empty] | X | X
Alarm status: Active | 20617 | 120618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | X |  | X | X | X
Alarm status: Active | 20617 | 120618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 |  | X
Alarm status: Active | 20617 | 120618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | [5 empty] | X | X
Alarm status: Active | 20618 | 120619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | X |  | X | X | X
Alarm status: Active | 20618 | 120619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 |  | X
Alarm status: Active | 20618 | 120619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | [5 empty] | X | X
Alarm status: Active | 20619 | 120620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | X |  | X | X | X
Alarm status: Active | 20619 | 120620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 |  | X
Alarm status: Active | 20619 | 120620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | [5 empty] | X | X
Alarm status: Active | 20620 | 120621 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | X |  | X | X | X
Alarm status: Active | 20620 | 120621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance |  | X
Alarm status: Active | 20620 | 120621 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | [5 empty] | X | X
Alarm status: Active | 20621 | 120622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | X |  | X | X | X
Alarm status: Active | 20621 | 120622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage |  | X
Alarm status: Active | 20621 | 120622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | [5 empty] | X | X
Alarm status: Active | 20622 | 120623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | X |  | X | X | X
Alarm status: Active | 20622 | 120623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage |  | X
Alarm status: Active | 20622 | 120623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | [5 empty] | X | X
Alarm status: Active | 20623 | 120624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | X |  | X | X | X
Alarm status: Active | 20623 | 120624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage |  | X
Alarm status: Active | 20623 | 120624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | [5 empty] | X | X
Alarm status: Active | 20624 | 120625 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20624 | 120625 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags |  | X
Alarm status: Active | 20624 | 120625 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20625 | 120626 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20625 | 120626 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags |  | X
Alarm status: Active | 20625 | 120626 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20626 | 120627 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20626 | 120627 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags |  | X
Alarm status: Active | 20626 | 120627 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20627 | 120628 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20627 | 120628 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags |  | X
Alarm status: Active | 20627 | 120628 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20628 | 120629 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20628 | 120629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags |  | X
Alarm status: Active | 20628 | 120629 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20629 | 120630 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20629 | 120630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags |  | X
Alarm status: Active | 20629 | 120630 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20630 | 120631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | X |  | X | X | X
Alarm status: Active | 20630 | 120631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags |  | X
Alarm status: Active | 20630 | 120631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20631 | 120632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | X |  | X | X | X
Alarm status: Active | 20631 | 120632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags |  | X
Alarm status: Active | 20631 | 120632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20632 | 120633 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20632 | 120633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags |  | X
Alarm status: Active | 20632 | 120633 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20633 | 120634 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20633 | 120634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags |  | X
Alarm status: Active | 20633 | 120634 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20634 | 120635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags |  | X
Alarm status: Active | 20635 | 120636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags |  | X
Alarm status: Active | 20636 | 120637 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | X |  | X | X | X
Alarm status: Active | 20636 | 120637 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags |  | X
Alarm status: Active | 20636 | 120637 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20637 | 120638 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | X |  | X | X | X
Alarm status: Active | 20637 | 120638 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags |  | X
Alarm status: Active | 20637 | 120638 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20638 | 120639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | X |  | X | X | X
Alarm status: Active | 20638 | 120639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 |  | X
Alarm status: Active | 20638 | 120639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | [5 empty] | X | X
Alarm status: Active | 20639 | 120640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | X |  | X | X | X
Alarm status: Active | 20639 | 120640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 |  | X
Alarm status: Active | 20639 | 120640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | [5 empty] | X | X
Alarm status: Active | 20640 | 120641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | X |  | X | X | X
Alarm status: Active | 20640 | 120641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 |  | X
Alarm status: Active | 20640 | 120641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | [5 empty] | X | X
Alarm status: Active | 20641 | 120642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | X |  | X | X | X
Alarm status: Active | 20641 | 120642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 |  | X
Alarm status: Active | 20641 | 120642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | [5 empty] | X | X
Alarm status: Active | 20642 | 120643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | X |  | X | X | X
Alarm status: Active | 20642 | 120643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 |  | X
Alarm status: Active | 20642 | 120643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | [5 empty] | X | X
Alarm status: Active | 20643 | 120644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | X |  | X | X | X
Alarm status: Active | 20643 | 120644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 |  | X
Alarm status: Active | 20643 | 120644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | [5 empty] | X | X
Alarm status: Active | 20644 | 120645 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20644 | 120645 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags |  | X
Alarm status: Active | 20644 | 120645 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20645 | 120646 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20645 | 120646 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags |  | X
Alarm status: Active | 20645 | 120646 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20646 | 120647 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20646 | 120647 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags |  | X
Alarm status: Active | 20646 | 120647 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20647 | 120648 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20647 | 120648 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags |  | X
Alarm status: Active | 20647 | 120648 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20648 | 120649 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20648 | 120649 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags |  | X
Alarm status: Active | 20648 | 120649 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20649 | 120650 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20649 | 120650 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags |  | X
Alarm status: Active | 20649 | 120650 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20650 | 120651 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20650 | 120651 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags |  | X
Alarm status: Active | 20650 | 120651 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20651 | 120652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20651 | 120652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags |  | X
Alarm status: Active | 20651 | 120652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20652 | 120653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20652 | 120653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags |  | X
Alarm status: Active | 20652 | 120653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20653 | 120654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20653 | 120654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags |  | X
Alarm status: Active | 20653 | 120654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20654 | 120655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | X |  | X | X | X
Alarm status: Active | 20654 | 120655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags |  | X
Alarm status: Active | 20654 | 120655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | [5 empty] | X | X
Alarm status: Active | 20655 | 120656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 |  |  | X | X
Alarm status: Active | 20655 | 120656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | X |  |  |  | X | X | X
Alarm status: Active | 20655 | 120656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 |  | X
Alarm status: Active | 20656 | 120657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 |  |  | X | X
Alarm status: Active | 20656 | 120657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | X |  |  |  | X | X | X
Alarm status: Active | 20656 | 120657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 |  | X
Alarm status: Active | 20657 | 120658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 |  |  | X | X
Alarm status: Active | 20657 | 120658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | X |  |  |  | X | X | X
Alarm status: Active | 20657 | 120658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 |  | X
Alarm status: Active | 20658 | 120659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 |  |  | X | X
Alarm status: Active | 20658 | 120659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | X |  |  |  | X | X | X
Alarm status: Active | 20658 | 120659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 |  | X
Alarm status: Active | 20659 | 120660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 |  |  | X | X
Alarm status: Active | 20659 | 120660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | X |  |  |  | X | X | X
Alarm status: Active | 20659 | 120660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 |  | X
Alarm status: Active | 20660 | 120661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 |  |  | X | X
Alarm status: Active | 20660 | 120661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | X |  |  |  | X | X | X
Alarm status: Active | 20660 | 120661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 |  | X
Alarm status: Active | 20661 | 120662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 |  |  | X | X
Alarm status: Active | 20661 | 120662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | X |  |  |  | X | X | X
Alarm status: Active | 20661 | 120662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 |  | X
Alarm status: Active | 20662 | 120663 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance |  |  | X | X
Alarm status: Active | 20662 | 120663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | X |  |  |  | X | X | X
Alarm status: Active | 20662 | 120663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance |  | X
Alarm status: Active | 20663 | 120664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 |  |  | X | X
Alarm status: Active | 20663 | 120664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | X |  |  |  | X | X | X
Alarm status: Active | 20663 | 120664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 |  | X
Alarm status: Active | 20664 | 120665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 |  |  | X | X
Alarm status: Active | 20664 | 120665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | X |  |  |  | X | X | X
Alarm status: Active | 20664 | 120665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 |  | X
Alarm status: Active | 20665 | 120666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 |  |  | X | X
Alarm status: Active | 20665 | 120666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | X |  |  |  | X | X | X
Alarm status: Active | 20665 | 120666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 |  | X
Alarm status: Active | 20666 | 120667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 |  |  | X | X
Alarm status: Active | 20666 | 120667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | X |  |  |  | X | X | X
Alarm status: Active | 20666 | 120667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 |  | X
Alarm status: Active | 20667 | 120668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 |  |  | X | X
Alarm status: Active | 20667 | 120668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | X |  |  |  | X | X | X
Alarm status: Active | 20667 | 120668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 |  | X
Alarm status: Active | 20668 | 120669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 |  |  | X | X
Alarm status: Active | 20668 | 120669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | X |  |  |  | X | X | X
Alarm status: Active | 20668 | 120669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 |  | X
Alarm status: Active | 20669 | 120670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 |  |  | X | X
Alarm status: Active | 20669 | 120670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | X |  |  |  | X | X | X
Alarm status: Active | 20669 | 120670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 |  | X
Alarm status: Active | 20670 | 120671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage |  |  | X | X
Alarm status: Active | 20670 | 120671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | X |  |  |  | X | X | X
Alarm status: Active | 20670 | 120671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage |  | X
Alarm status: Active | 20671 | 120672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage |  |  | X | X
Alarm status: Active | 20671 | 120672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | X |  |  |  | X | X | X
Alarm status: Active | 20671 | 120672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage |  | X
Alarm status: Active | 20672 | 120673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage |  |  | X | X
Alarm status: Active | 20672 | 120673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | X |  |  |  | X | X | X
Alarm status: Active | 20672 | 120673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage |  | X
Alarm status: Active | 20717 | 120718 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 1 | X |  | X | X | X
Alarm status: Active | 20718 | 120719 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 2 | X |  | X | X | X
Alarm status: Active | 20719 | 120720 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 3 | X |  | X | X | X
Alarm status: Active | 20720 | 120721 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 4 | X |  | X | X | X
Alarm status: Active | 20721 | 120722 | External MB open failure | X | X | X | X | X | X | X
Alarm status: Active | 20722 | 120723 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - Flags | X |  | X | X | X
Alarm status: Active | 20723 | 120724 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - Flags | X |  | X | X | X
Alarm status: Active | 20724 | 120725 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - Flags | X |  | X | X | X
Alarm status: Active | 20725 | 120726 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - Flags | X |  | X | X | X
Alarm status: Active | 20726 | 120727 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - Flags | X |  | X | X | X
Alarm status: Active | 20727 | 120728 | Parameters - Breakers - Close before excitation - CBE failure - Information - Flags - Close before excitation failure | X |  | X | X | X
Alarm status: Active | 20728 | 120729 | Load too high | X | X | X | X | X | X | X
Alarm status: Active | 20729 | 120730 | ID to run configuration failure | [5 empty] | X | X
Alarm status: Active | 20731 | 120732 | Parameters - System - Monitoring - Missing any genset controller - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20732 | 120733 | Parameters - System - Monitoring - Missing any mains controller - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20733 | 120734 | Parameters - System - Monitoring - Missing any bustie controller - Information - Flags - Missing any bus tie controller | X | X | X | X | X | X | X
Alarm status: Active | 20734 | 120735 | Can ID not available | X | X | X | X | X | X | X
Alarm status: Active | 20735 | 120736 | Duplicated CAN IDs | X | X | X | X | X | X | X
Alarm status: Active | 20736 | 120737 | Parameters - Local power management - Alarms - Busbar blocked - Information - Flags - Busbar blocked due to position failure | X |  | X | X | X | X | X
Alarm status: Active | 20737 | 120738 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Flags - Busbar A blocked due to position failure |  | X
Alarm status: Active | 20738 | 120739 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Flags - Busbar B blocked due to position failure |  | X
Alarm status: Active | 20739 | 120740 | Parameters - System - Monitoring - BTB 33 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20740 | 120741 | Parameters - System - Monitoring - BTB 34 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20741 | 120742 | Parameters - System - Monitoring - BTB 35 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20742 | 120743 | Parameters - System - Monitoring - BTB 36 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20743 | 120744 | Parameters - System - Monitoring - BTB 37 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20744 | 120745 | Parameters - System - Monitoring - BTB 38 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20745 | 120746 | Parameters - System - Monitoring - BTB 39 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20746 | 120747 | Parameters - System - Monitoring - BTB 40 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20747 | 120748 | Primary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm status: Active | 20748 | 120749 | Primary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm status: Active | 20749 | 120750 | Primary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm status: Active | 20750 | 120751 | Primary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm status: Active | 20751 | 120752 | Primary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm status: Active | 20752 | 120753 | Primary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm status: Active | 20753 | 120754 | Primary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm status: Active | 20754 | 120755 | Primary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm status: Active | 20755 | 120756 | Primary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm status: Active | 20756 | 120757 | Primary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm status: Active | 20757 | 120758 | Primary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm status: Active | 20758 | 120759 | Primary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm status: Active | 20759 | 120760 | Primary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm status: Active | 20760 | 120761 | Primary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm status: Active | 20761 | 120762 | Primary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm status: Active | 20762 | 120763 | Primary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm status: Active | 20763 | 120764 | Primary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm status: Active | 20764 | 120765 | Primary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm status: Active | 20765 | 120766 | Primary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm status: Active | 20766 | 120767 | Primary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm status: Active | 20767 | 120768 | Primary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm status: Active | 20768 | 120769 | Primary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm status: Active | 20769 | 120770 | Primary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm status: Active | 20770 | 120771 | Primary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm status: Active | 20771 | 120772 | Primary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm status: Active | 20772 | 120773 | Primary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm status: Active | 20773 | 120774 | Primary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm status: Active | 20774 | 120775 | Primary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm status: Active | 20775 | 120776 | Primary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm status: Active | 20776 | 120777 | Primary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm status: Active | 20777 | 120778 | Primary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm status: Active | 20778 | 120779 | Primary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm status: Active | 20779 | 120780 | Primary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm status: Active | 20780 | 120781 | Primary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm status: Active | 20781 | 120782 | Primary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm status: Active | 20782 | 120783 | Primary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm status: Active | 20783 | 120784 | Primary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm status: Active | 20784 | 120785 | Primary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm status: Active | 20785 | 120786 | Primary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm status: Active | 20786 | 120787 | Primary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm status: Active | 20787 | 120788 | Secondary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm status: Active | 20788 | 120789 | Secondary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm status: Active | 20789 | 120790 | Secondary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm status: Active | 20790 | 120791 | Secondary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm status: Active | 20791 | 120792 | Secondary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm status: Active | 20792 | 120793 | Secondary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm status: Active | 20793 | 120794 | Secondary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm status: Active | 20794 | 120795 | Secondary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm status: Active | 20795 | 120796 | Secondary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm status: Active | 20796 | 120797 | Secondary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm status: Active | 20797 | 120798 | Secondary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm status: Active | 20798 | 120799 | Secondary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm status: Active | 20799 | 120800 | Secondary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm status: Active | 20800 | 120801 | Secondary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm status: Active | 20801 | 120802 | Secondary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm status: Active | 20802 | 120803 | Secondary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm status: Active | 20803 | 120804 | Secondary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm status: Active | 20804 | 120805 | Secondary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm status: Active | 20805 | 120806 | Secondary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm status: Active | 20806 | 120807 | Secondary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm status: Active | 20807 | 120808 | Secondary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm status: Active | 20808 | 120809 | Secondary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm status: Active | 20809 | 120810 | Secondary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm status: Active | 20810 | 120811 | Secondary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm status: Active | 20811 | 120812 | Secondary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm status: Active | 20812 | 120813 | Secondary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm status: Active | 20813 | 120814 | Secondary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm status: Active | 20814 | 120815 | Secondary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm status: Active | 20815 | 120816 | Secondary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm status: Active | 20816 | 120817 | Secondary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm status: Active | 20817 | 120818 | Secondary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm status: Active | 20818 | 120819 | Secondary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm status: Active | 20819 | 120820 | Secondary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm status: Active | 20820 | 120821 | Secondary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm status: Active | 20821 | 120822 | Secondary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm status: Active | 20822 | 120823 | Secondary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm status: Active | 20823 | 120824 | Secondary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm status: Active | 20824 | 120825 | Secondary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm status: Active | 20825 | 120826 | Secondary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm status: Active | 20826 | 120827 | Secondary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm status: Active | 20827 | 120828 | Priority error | X | X | X | X | X | X | X
Alarm status: Active | 20828 | 120829 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - Flags - NEL 1 over-current | X |  | X | X | X | X | X
Alarm status: Active | 20829 | 120830 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - Flags - NEL 1 under-frequency | X |  | X | X | X | X | X
Alarm status: Active | 20830 | 120831 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - Flags - NEL 1 overload 1 | X |  | X | X | X | X | X
Alarm status: Active | 20831 | 120832 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - Flags - NEL 1 overload 2 | X |  | X | X | X | X | X
Alarm status: Active | 20832 | 120833 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - Flags - NEL 1 reactive overload | X |  | X | X | X | X | X
Alarm status: Active | 20833 | 120834 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - Flags - NEL 2 over-current | X |  | X | X | X | X | X
Alarm status: Active | 20834 | 120835 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - Flags - NEL 2 under-frequency | X |  | X | X | X | X | X
Alarm status: Active | 20835 | 120836 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - Flags - NEL 2 overload 1 | X |  | X | X | X | X | X
Alarm status: Active | 20836 | 120837 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - Flags - NEL 2 overload 2 | X |  | X | X | X | X | X
Alarm status: Active | 20837 | 120838 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - Flags - NEL 2 reactive overload | X |  | X | X | X | X | X
Alarm status: Active | 20838 | 120839 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - Flags - NEL 3 over-current | X |  | X | X | X | X | X
Alarm status: Active | 20839 | 120840 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - Flags - NEL 3 under-frequency | X |  | X | X | X | X | X
Alarm status: Active | 20840 | 120841 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - Flags - NEL 3 overload 1 | X |  | X | X | X | X | X
Alarm status: Active | 20841 | 120842 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - Flags - NEL 3 overload 2 | X |  | X | X | X | X | X
Alarm status: Active | 20842 | 120843 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - Flags - NEL 3 reactive overload | X |  | X | X | X | X | X
Alarm status: Active | 20843 | 120844 | Parameters - System - Monitoring - Single-line hazard - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20844 | 120845 | ID not present | X | X | X | X | X | X | X
Alarm status: Active | 20845 | 120846 | Unsupported application | X | X | X | X | X | X | X
Alarm status: Active | 20846 | 120847 | Application internal CAN protocol conflict | X | X | X | X | X | X | X
Alarm status: Active | 20847 | 120848 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Flags - Section P> | X | X | X | X | X | X | X
Alarm status: Active | 20848 | 120849 | Dry mode: Voltage level unexpected | X |  | X | X | X
Alarm status: Active | 20849 | 120850 | Invalid DAVR configuration | X |  | X | X | X
Alarm status: Active | 20850 | 120851 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20852 | 120853 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20854 | 120855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | X |  | X | X | X
Alarm status: Active | 20854 | 120855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch |  | X
Alarm status: Active | 20854 | 120855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | [5 empty] | X | X
Alarm status: Active | 20855 | 120856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch |  |  |  | X
Alarm status: Active | 20855 | 120856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | [6 empty] | X
Alarm status: Active | 20857 | 120858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20858 | 120859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20859 | 120860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20860 | 120861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20861 | 120862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Active | 20862 | 120863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Active | 20863 | 120864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Active | 20864 | 120865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Active | 20865 | 120866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Active | 20866 | 120867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Active | 20867 | 120868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Active | 20868 | 120869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Active | 20869 | 120870 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Active | 20870 | 120871 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Active | 20871 | 120872 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Active | 20872 | 120873 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Active | 20873 | 120874 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Active | 20874 | 120875 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Active | 20875 | 120876 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Active | 20876 | 120877 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Active | 20877 | 120878 | Live voltage detected | X | X | X | X | X | X | X
Alarm status: Active | 20878 | 120879 | Internal issue detected. A restart is required soon! | X | X | X | X | X | X | X
Alarm status: Active | 20879 | 120880 | Parameters - System - Monitoring - Missing controllers - Information - Flags | X | X | X | X | X | X | X
Alarm status: Active | 20880 | 120881 | Card issue detected | X | X | X | X | X | X | X
Alarm status: Active | 20881 | 120882 | Card configuration failed | X | X | X | X | X | X | X
Alarm status: Active | 20882 | 120883 | Unknown traffic on DEIF network | X | X | X | X | X | X | X
Alarm status: Active | 20883 | 120884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Active | 20884 | 120885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Active | 20885 | 120886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Active | 20886 | 120887 | Local IO service error | X | X | X | X | X | X | X
Alarm status: Active | 20887 | 120888 | App logging failure | X | X | X | X | X | X | X
Alarm status: Active | 20888 | 120889 | Event logging failure | X | X | X | X | X | X | X
Alarm status: Active | 20889 | 120890 | Licence error | X | X | X | X | X | X | X
Alarm status: Active | 20890 | 120891 | Brightness is dimmed according to temperature | X | X | X | X | X | X | X
Alarm status: Active | 20891 | 120892 | Parameters - Grid code - Mains sync inhibit - Information - Flags |  |  | X | X
Alarm status: Active | 20892 | 120893 | Parameters - Grid code - Capability curve - Import protection - Information - Flags - Power import capability curve protection |  |  | X | X
Alarm status: Active | 20893 | 120894 | Parameters - Grid code - Capability curve - Export protection - Information - Flags - Power export capability curve protection |  |  | X | X
Alarm status: Active | 20894 | 120895 | Hardware is not compatible based on module versions | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22000 | 122001 | Application initialisation error | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22001 | 122002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22002 | 122003 | Preliminary software | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22003 | 122004 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22004 | 122005 | Parameters - Engine - Start sequence - Start failure - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22005 | 122006 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22006 | 122007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22007 | 122008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22008 | 122009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22009 | 122010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22010 | 122011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | X |  | X | X | X
Alarm status: Acknowledged | 22011 | 122012 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22013 | 122014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22014 | 122015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22015 | 122016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22016 | 122017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22017 | 122018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22018 | 122019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22019 | 122020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22020 | 122021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22021 | 122022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22022 | 122023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22027 | 122028 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22041 | 122042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | X |  | X | X | X
Alarm status: Acknowledged | 22041 | 122042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure |  | X
Alarm status: Acknowledged | 22041 | 122042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | [5 empty] | X | X
Alarm status: Acknowledged | 22042 | 122043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | X |  | X | X | X
Alarm status: Acknowledged | 22042 | 122043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure |  | X
Alarm status: Acknowledged | 22042 | 122043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | [5 empty] | X | X
Alarm status: Acknowledged | 22043 | 122044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | X |  | X | X | X
Alarm status: Acknowledged | 22043 | 122044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure |  | X
Alarm status: Acknowledged | 22043 | 122044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | [5 empty] | X | X
Alarm status: Acknowledged | 22044 | 122045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | X |  | X | X | X
Alarm status: Acknowledged | 22044 | 122045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure |  | X
Alarm status: Acknowledged | 22044 | 122045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | [5 empty] | X | X
Alarm status: Acknowledged | 22045 | 122046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | X |  | X | X | X
Alarm status: Acknowledged | 22045 | 122046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure |  | X
Alarm status: Acknowledged | 22045 | 122046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | [5 empty] | X | X
Alarm status: Acknowledged | 22046 | 122047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | X |  | X | X | X
Alarm status: Acknowledged | 22046 | 122047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure |  | X
Alarm status: Acknowledged | 22046 | 122047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | [5 empty] | X | X
Alarm status: Acknowledged | 22047 | 122048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | X |  | X | X | X
Alarm status: Acknowledged | 22047 | 122048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) |  | X
Alarm status: Acknowledged | 22047 | 122048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | [5 empty] | X | X
Alarm status: Acknowledged | 22048 | 122049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | X |  | X | X | X
Alarm status: Acknowledged | 22048 | 122049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit |  | X
Alarm status: Acknowledged | 22048 | 122049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | [5 empty] | X | X
Alarm status: Acknowledged | 22049 | 122050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure |  |  |  | X
Alarm status: Acknowledged | 22049 | 122050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | [6 empty] | X
Alarm status: Acknowledged | 22050 | 122051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure |  |  |  | X
Alarm status: Acknowledged | 22050 | 122051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | [6 empty] | X
Alarm status: Acknowledged | 22051 | 122052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure |  |  |  | X
Alarm status: Acknowledged | 22051 | 122052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | [6 empty] | X
Alarm status: Acknowledged | 22052 | 122053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure |  |  |  | X
Alarm status: Acknowledged | 22052 | 122053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | [6 empty] | X
Alarm status: Acknowledged | 22053 | 122054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure |  |  |  | X
Alarm status: Acknowledged | 22053 | 122054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | [6 empty] | X
Alarm status: Acknowledged | 22054 | 122055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure |  |  |  | X
Alarm status: Acknowledged | 22054 | 122055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | [6 empty] | X
Alarm status: Acknowledged | 22055 | 122056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) |  |  |  | X
Alarm status: Acknowledged | 22055 | 122056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | [6 empty] | X
Alarm status: Acknowledged | 22056 | 122057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit |  |  |  | X
Alarm status: Acknowledged | 22056 | 122057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | [6 empty] | X
Alarm status: Acknowledged | 22060 | 122061 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error |  |  | X | X
Alarm status: Acknowledged | 22060 | 122061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22060 | 122061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error |  | X
Alarm status: Acknowledged | 22061 | 122062 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | X |  | X | X | X
Alarm status: Acknowledged | 22061 | 122062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error |  | X
Alarm status: Acknowledged | 22061 | 122062 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | [5 empty] | X | X
Alarm status: Acknowledged | 22062 | 122063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22103 | 122104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information - Flags |  |  | X | X
Alarm status: Acknowledged | 22103 | 122104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information - Flags | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22103 | 122104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information - Flags |  | X
Alarm status: Acknowledged | 22104 | 122105 | Parameters - Mains - Additional protections - Vector shift - Information - Flags |  |  | X | X
Alarm status: Acknowledged | 22104 | 122105 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22104 | 122105 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags |  | X
Alarm status: Acknowledged | 22105 | 122106 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22105 | 122106 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags |  | X
Alarm status: Acknowledged | 22105 | 122106 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22106 | 122107 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22107 | 122108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22108 | 122109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22108 | 122109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags |  | X
Alarm status: Acknowledged | 22108 | 122109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22109 | 122110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22109 | 122110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags |  | X
Alarm status: Acknowledged | 22109 | 122110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22110 | 122111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22110 | 122111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags |  | X
Alarm status: Acknowledged | 22110 | 122111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22111 | 122112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22111 | 122112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags |  | X
Alarm status: Acknowledged | 22111 | 122112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22115 | 122116 | Protection set point out of range | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22116 | 122117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | X |  | X | X | X
Alarm status: Acknowledged | 22117 | 122118 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | X |  | X | X | X
Alarm status: Acknowledged | 22118 | 122119 | Protection set point out of range (differential current) | X |  | X | X | X
Alarm status: Acknowledged | 22119 | 122120 | Parameters - Local - Mode - Not under remote control - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22121 | 122122 | Parameters - Local - Monitoring - System not OK - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22122 | 122123 | Configuration update delayed | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22123 | 122124 | Critical process error | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22124 | 122125 | Restore error | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22125 | 122126 | SD-card format error | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22126 | 122127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22127 | 122128 | Fieldbus configuration exceeded maximum I/O configuration | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22128 | 122129 | Parameters - Custom alarm - Custom alarm 0 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22129 | 122130 | Parameters - Custom alarm - Custom alarm 1 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22130 | 122131 | Parameters - Custom alarm - Custom alarm 2 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22131 | 122132 | Parameters - Custom alarm - Custom alarm 3 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22132 | 122133 | Parameters - Custom alarm - Custom alarm 4 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22133 | 122134 | Parameters - Custom alarm - Custom alarm 5 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22134 | 122135 | Parameters - Custom alarm - Custom alarm 6 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22135 | 122136 | Parameters - Custom alarm - Custom alarm 7 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22136 | 122137 | Parameters - Custom alarm - Custom alarm 8 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22137 | 122138 | Parameters - Custom alarm - Custom alarm 9 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22138 | 122139 | Parameters - Custom alarm - Custom alarm 10 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22139 | 122140 | Parameters - Custom alarm - Custom alarm 11 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22140 | 122141 | Parameters - Custom alarm - Custom alarm 12 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22141 | 122142 | Parameters - Custom alarm - Custom alarm 13 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22142 | 122143 | Parameters - Custom alarm - Custom alarm 14 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22143 | 122144 | Parameters - Custom alarm - Custom alarm 15 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22144 | 122145 | Parameters - Custom alarm - Custom alarm 16 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22145 | 122146 | Parameters - Custom alarm - Custom alarm 17 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22146 | 122147 | Parameters - Custom alarm - Custom alarm 18 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22147 | 122148 | Parameters - Custom alarm - Custom alarm 19 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22148 | 122149 | Parameters - Custom alarm - Custom alarm 20 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22149 | 122150 | Parameters - Custom alarm - Custom alarm 21 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22150 | 122151 | Parameters - Custom alarm - Custom alarm 22 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22151 | 122152 | Parameters - Custom alarm - Custom alarm 23 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22152 | 122153 | Parameters - Custom alarm - Custom alarm 24 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22153 | 122154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | X |  | X | X | X
Alarm status: Acknowledged | 22154 | 122155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | X |  | X | X | X
Alarm status: Acknowledged | 22163 | 122164 | Required hardware card(s) not found | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22164 | 122165 | Software mismatch on hardware module(s) | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22165 | 122166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break |  |  | X
Alarm status: Acknowledged | 22165 | 122166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | X |  |  |  | X | X
Alarm status: Acknowledged | 22165 | 122166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break |  | X
Alarm status: Acknowledged | 22166 | 122167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | X |  | X |  | X
Alarm status: Acknowledged | 22166 | 122167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break |  | X
Alarm status: Acknowledged | 22166 | 122167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | [5 empty] | X
Alarm status: Acknowledged | 22167 | 122168 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break |  |  | X
Alarm status: Acknowledged | 22167 | 122168 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | X |  |  |  | X | X
Alarm status: Acknowledged | 22167 | 122168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break |  | X
Alarm status: Acknowledged | 22168 | 122169 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break |  |  | X
Alarm status: Acknowledged | 22168 | 122169 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | X |  |  |  | X | X
Alarm status: Acknowledged | 22168 | 122169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break |  | X
Alarm status: Acknowledged | 22169 | 122170 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break |  |  | X
Alarm status: Acknowledged | 22169 | 122170 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | X |  |  |  | X | X
Alarm status: Acknowledged | 22169 | 122170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break |  | X
Alarm status: Acknowledged | 22170 | 122171 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | X |  | X |  | X
Alarm status: Acknowledged | 22170 | 122171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break |  | X
Alarm status: Acknowledged | 22170 | 122171 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | [5 empty] | X
Alarm status: Acknowledged | 22171 | 122172 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | X |  | X |  | X
Alarm status: Acknowledged | 22171 | 122172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break |  | X
Alarm status: Acknowledged | 22171 | 122172 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | [5 empty] | X
Alarm status: Acknowledged | 22172 | 122173 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | X |  | X |  | X
Alarm status: Acknowledged | 22172 | 122173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break |  | X
Alarm status: Acknowledged | 22172 | 122173 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | [5 empty] | X
Alarm status: Acknowledged | 22178 | 122179 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm |  |  | X | X |  | X | X
Alarm status: Acknowledged | 22179 | 122180 | Parameters - Engine - Emergency stop - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22179 | 122180 | Parameters - Busbar A - Emergency stop - Information - Flags |  | X
Alarm status: Acknowledged | 22179 | 122180 | Parameters - Mains - Emergency stop - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22180 | 122181 | Clock battery failure | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22181 | 122182 | Controller temperature too high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22182 | 122183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22183 | 122184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22184 | 122185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22185 | 122186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22186 | 122187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22187 | 122188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22188 | 122189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22189 | 122190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22190 | 122191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22191 | 122192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22192 | 122193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22193 | 122194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22194 | 122195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22195 | 122196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22196 | 122197 | EIM3.1 4 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22197 | 122198 | EIM3.1 4 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22198 | 122199 | EIM3.1 5 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22199 | 122200 | EIM3.1 5 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22200 | 122201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22201 | 122202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22202 | 122203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22203 | 122204 | EIM3.1 4 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22204 | 122205 | EIM3.1 5 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22205 | 122206 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22206 | 122207 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22207 | 122208 | AC protections not running (differential current) | X |  | X | X | X
Alarm status: Acknowledged | 22208 | 122209 | AC data is missing (differential current) | X |  | X | X | X
Alarm status: Acknowledged | 22209 | 122210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22210 | 122211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22211 | 122212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22212 | 122213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22213 | 122214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22214 | 122215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22215 | 122216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22216 | 122217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22217 | 122218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22218 | 122219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22219 | 122220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22220 | 122221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22221 | 122222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22222 | 122223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22223 | 122224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22224 | 122225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22225 | 122226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22226 | 122227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22228 | 122229 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22229 | 122230 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22231 | 122232 | Controller ID not configured | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22236 | 122237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22237 | 122238 | Blackout detection mismatch | X |  | X | X | X
Alarm status: Acknowledged | 22240 | 122241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22241 | 122242 | Parameters - Communication - NTP - NTP server 1 no response - Information - Flags - NTP server 1 is not responding | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22242 | 122243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22243 | 122244 | Parameters - Communication - NTP - NTP server 2 no response - Information - Flags - NTP server 2 is not responding | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22244 | 122245 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22245 | 122246 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22246 | 122247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22247 | 122248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22296 | 122297 | Controller not part of system | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22297 | 122298 | Different single-line configurations | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22298 | 122299 | Single-line missing/none active | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22299 | 122300 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22300 | 122301 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22301 | 122302 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22302 | 122303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22303 | 122304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22304 | 122305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22305 | 122306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22306 | 122307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22307 | 122308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22308 | 122309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22309 | 122310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22310 | 122311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22311 | 122312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22312 | 122313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22313 | 122314 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22314 | 122315 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22315 | 122316 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22316 | 122317 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22317 | 122318 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22318 | 122319 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22319 | 122320 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22320 | 122321 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22321 | 122322 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22322 | 122323 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22323 | 122324 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22324 | 122325 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22325 | 122326 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22326 | 122327 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22327 | 122328 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22328 | 122329 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22329 | 122330 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22330 | 122331 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22331 | 122332 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22332 | 122333 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22333 | 122334 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22334 | 122335 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22335 | 122336 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22336 | 122337 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22337 | 122338 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22338 | 122339 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22339 | 122340 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22340 | 122341 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22341 | 122342 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22342 | 122343 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22343 | 122344 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22344 | 122345 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22345 | 122346 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22346 | 122347 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22347 | 122348 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22348 | 122349 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22349 | 122350 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22350 | 122351 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22351 | 122352 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22352 | 122353 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22353 | 122354 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22354 | 122355 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22355 | 122356 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22356 | 122357 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22357 | 122358 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22358 | 122359 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22359 | 122360 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22360 | 122361 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22361 | 122362 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22362 | 122363 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22363 | 122364 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22364 | 122365 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22365 | 122366 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22366 | 122367 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22367 | 122368 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22368 | 122369 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22369 | 122370 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22370 | 122371 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22371 | 122372 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22372 | 122373 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22373 | 122374 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22374 | 122375 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22375 | 122376 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22376 | 122377 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22377 | 122378 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22378 | 122379 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22379 | 122380 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22380 | 122381 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22381 | 122382 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22382 | 122383 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22383 | 122384 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22384 | 122385 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22385 | 122386 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22386 | 122387 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22387 | 122388 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22388 | 122389 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22389 | 122390 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22390 | 122391 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22391 | 122392 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22392 | 122393 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22393 | 122394 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22394 | 122395 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22395 | 122396 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22396 | 122397 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22397 | 122398 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22398 | 122399 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22399 | 122400 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22400 | 122401 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22401 | 122402 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22402 | 122403 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22403 | 122404 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22404 | 122405 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22405 | 122406 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22406 | 122407 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22407 | 122408 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22408 | 122409 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22409 | 122410 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22410 | 122411 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22411 | 122412 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22412 | 122413 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22413 | 122414 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22414 | 122415 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22415 | 122416 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22416 | 122417 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22417 | 122418 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22418 | 122419 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22419 | 122420 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22420 | 122421 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22421 | 122422 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22422 | 122423 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22423 | 122424 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22424 | 122425 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22425 | 122426 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22426 | 122427 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22427 | 122428 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22428 | 122429 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22429 | 122430 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22430 | 122431 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22431 | 122432 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22432 | 122433 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22433 | 122434 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22434 | 122435 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22435 | 122436 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22436 | 122437 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22437 | 122438 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22438 | 122439 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22439 | 122440 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22440 | 122441 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22441 | 122442 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22442 | 122443 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22443 | 122444 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22444 | 122445 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22445 | 122446 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22446 | 122447 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22447 | 122448 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22448 | 122449 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22449 | 122450 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22450 | 122451 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22451 | 122452 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22452 | 122453 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22453 | 122454 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22454 | 122455 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22455 | 122456 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22456 | 122457 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22457 | 122458 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22458 | 122459 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22459 | 122460 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22460 | 122461 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22461 | 122462 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22462 | 122463 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22463 | 122464 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22464 | 122465 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22465 | 122466 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22466 | 122467 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22467 | 122468 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22468 | 122469 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22469 | 122470 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22470 | 122471 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22471 | 122472 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22472 | 122473 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22473 | 122474 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22474 | 122475 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22475 | 122476 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22476 | 122477 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22477 | 122478 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22478 | 122479 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22479 | 122480 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22480 | 122481 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22481 | 122482 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22482 | 122483 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22483 | 122484 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22484 | 122485 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22485 | 122486 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22486 | 122487 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22487 | 122488 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22488 | 122489 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22489 | 122490 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22490 | 122491 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22491 | 122492 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22492 | 122493 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22493 | 122494 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22494 | 122495 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22495 | 122496 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22496 | 122497 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22497 | 122498 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22498 | 122499 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22499 | 122500 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22500 | 122501 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22501 | 122502 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22502 | 122503 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22503 | 122504 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22504 | 122505 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22505 | 122506 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22506 | 122507 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22507 | 122508 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22508 | 122509 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22509 | 122510 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22510 | 122511 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22511 | 122512 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22512 | 122513 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22513 | 122514 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22514 | 122515 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22515 | 122516 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22516 | 122517 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22517 | 122518 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22518 | 122519 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22519 | 122520 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22520 | 122521 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22521 | 122522 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22522 | 122523 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22523 | 122524 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22524 | 122525 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22525 | 122526 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22526 | 122527 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22527 | 122528 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22528 | 122529 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22529 | 122530 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22530 | 122531 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22531 | 122532 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22532 | 122533 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22533 | 122534 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22534 | 122535 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22535 | 122536 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22536 | 122537 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22537 | 122538 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22538 | 122539 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22539 | 122540 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22540 | 122541 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22541 | 122542 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22542 | 122543 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22543 | 122544 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22544 | 122545 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22545 | 122546 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22546 | 122547 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22547 | 122548 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22548 | 122549 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22549 | 122550 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22550 | 122551 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22551 | 122552 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22552 | 122553 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22553 | 122554 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22554 | 122555 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22555 | 122556 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22556 | 122557 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22557 | 122558 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22558 | 122559 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22559 | 122560 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22560 | 122561 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22561 | 122562 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22562 | 122563 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22565 | 122566 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22566 | 122567 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | X |  | X | X | X
Alarm status: Acknowledged | 22567 | 122568 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22568 | 122569 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22569 | 122570 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22570 | 122571 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22571 | 122572 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22572 | 122573 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22573 | 122574 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22574 | 122575 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22575 | 122576 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22576 | 122577 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22577 | 122578 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22578 | 122579 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22579 | 122580 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22580 | 122581 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22581 | 122582 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22582 | 122583 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22583 | 122584 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22584 | 122585 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22585 | 122586 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22586 | 122587 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22587 | 122588 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22588 | 122589 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22589 | 122590 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22590 | 122591 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22591 | 122592 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22592 | 122593 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22593 | 122594 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22594 | 122595 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22595 | 122596 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22596 | 122597 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22597 | 122598 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22598 | 122599 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22599 | 122600 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22600 | 122601 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22601 | 122602 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22602 | 122603 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22603 | 122604 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22604 | 122605 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22605 | 122606 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22606 | 122607 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22607 | 122608 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22608 | 122609 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22609 | 122610 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22610 | 122611 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22611 | 122612 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22612 | 122613 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22613 | 122614 | DAVR unsupported AC configuration | X |  | X | X | X
Alarm status: Acknowledged | 22614 | 122615 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | X |  | X | X | X
Alarm status: Acknowledged | 22615 | 122616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | X |  | X | X | X
Alarm status: Acknowledged | 22615 | 122616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 |  | X
Alarm status: Acknowledged | 22615 | 122616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | [5 empty] | X | X
Alarm status: Acknowledged | 22616 | 122617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | X |  | X | X | X
Alarm status: Acknowledged | 22616 | 122617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 |  | X
Alarm status: Acknowledged | 22616 | 122617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | [5 empty] | X | X
Alarm status: Acknowledged | 22617 | 122618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | X |  | X | X | X
Alarm status: Acknowledged | 22617 | 122618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 |  | X
Alarm status: Acknowledged | 22617 | 122618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | [5 empty] | X | X
Alarm status: Acknowledged | 22618 | 122619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | X |  | X | X | X
Alarm status: Acknowledged | 22618 | 122619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 |  | X
Alarm status: Acknowledged | 22618 | 122619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | [5 empty] | X | X
Alarm status: Acknowledged | 22619 | 122620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | X |  | X | X | X
Alarm status: Acknowledged | 22619 | 122620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 |  | X
Alarm status: Acknowledged | 22619 | 122620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | [5 empty] | X | X
Alarm status: Acknowledged | 22620 | 122621 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | X |  | X | X | X
Alarm status: Acknowledged | 22620 | 122621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance |  | X
Alarm status: Acknowledged | 22620 | 122621 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | [5 empty] | X | X
Alarm status: Acknowledged | 22621 | 122622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | X |  | X | X | X
Alarm status: Acknowledged | 22621 | 122622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage |  | X
Alarm status: Acknowledged | 22621 | 122622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | [5 empty] | X | X
Alarm status: Acknowledged | 22622 | 122623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | X |  | X | X | X
Alarm status: Acknowledged | 22622 | 122623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage |  | X
Alarm status: Acknowledged | 22622 | 122623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | [5 empty] | X | X
Alarm status: Acknowledged | 22623 | 122624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | X |  | X | X | X
Alarm status: Acknowledged | 22623 | 122624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage |  | X
Alarm status: Acknowledged | 22623 | 122624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | [5 empty] | X | X
Alarm status: Acknowledged | 22624 | 122625 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22624 | 122625 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags |  | X
Alarm status: Acknowledged | 22624 | 122625 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22625 | 122626 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22625 | 122626 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags |  | X
Alarm status: Acknowledged | 22625 | 122626 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22626 | 122627 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22626 | 122627 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags |  | X
Alarm status: Acknowledged | 22626 | 122627 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22627 | 122628 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22627 | 122628 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags |  | X
Alarm status: Acknowledged | 22627 | 122628 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22628 | 122629 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22628 | 122629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags |  | X
Alarm status: Acknowledged | 22628 | 122629 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22629 | 122630 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22629 | 122630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags |  | X
Alarm status: Acknowledged | 22629 | 122630 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22630 | 122631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22630 | 122631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags |  | X
Alarm status: Acknowledged | 22630 | 122631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22631 | 122632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22631 | 122632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags |  | X
Alarm status: Acknowledged | 22631 | 122632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22632 | 122633 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22632 | 122633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags |  | X
Alarm status: Acknowledged | 22632 | 122633 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22633 | 122634 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22633 | 122634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags |  | X
Alarm status: Acknowledged | 22633 | 122634 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22634 | 122635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags |  | X
Alarm status: Acknowledged | 22635 | 122636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags |  | X
Alarm status: Acknowledged | 22636 | 122637 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22636 | 122637 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags |  | X
Alarm status: Acknowledged | 22636 | 122637 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22637 | 122638 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22637 | 122638 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags |  | X
Alarm status: Acknowledged | 22637 | 122638 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22638 | 122639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | X |  | X | X | X
Alarm status: Acknowledged | 22638 | 122639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 |  | X
Alarm status: Acknowledged | 22638 | 122639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | [5 empty] | X | X
Alarm status: Acknowledged | 22639 | 122640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | X |  | X | X | X
Alarm status: Acknowledged | 22639 | 122640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 |  | X
Alarm status: Acknowledged | 22639 | 122640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | [5 empty] | X | X
Alarm status: Acknowledged | 22640 | 122641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | X |  | X | X | X
Alarm status: Acknowledged | 22640 | 122641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 |  | X
Alarm status: Acknowledged | 22640 | 122641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | [5 empty] | X | X
Alarm status: Acknowledged | 22641 | 122642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | X |  | X | X | X
Alarm status: Acknowledged | 22641 | 122642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 |  | X
Alarm status: Acknowledged | 22641 | 122642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | [5 empty] | X | X
Alarm status: Acknowledged | 22642 | 122643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | X |  | X | X | X
Alarm status: Acknowledged | 22642 | 122643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 |  | X
Alarm status: Acknowledged | 22642 | 122643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | [5 empty] | X | X
Alarm status: Acknowledged | 22643 | 122644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | X |  | X | X | X
Alarm status: Acknowledged | 22643 | 122644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 |  | X
Alarm status: Acknowledged | 22643 | 122644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | [5 empty] | X | X
Alarm status: Acknowledged | 22644 | 122645 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22644 | 122645 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags |  | X
Alarm status: Acknowledged | 22644 | 122645 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22645 | 122646 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22645 | 122646 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags |  | X
Alarm status: Acknowledged | 22645 | 122646 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22646 | 122647 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22646 | 122647 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags |  | X
Alarm status: Acknowledged | 22646 | 122647 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22647 | 122648 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22647 | 122648 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags |  | X
Alarm status: Acknowledged | 22647 | 122648 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22648 | 122649 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22648 | 122649 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags |  | X
Alarm status: Acknowledged | 22648 | 122649 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22649 | 122650 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22649 | 122650 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags |  | X
Alarm status: Acknowledged | 22649 | 122650 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22650 | 122651 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22650 | 122651 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags |  | X
Alarm status: Acknowledged | 22650 | 122651 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22651 | 122652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22651 | 122652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags |  | X
Alarm status: Acknowledged | 22651 | 122652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22652 | 122653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22652 | 122653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags |  | X
Alarm status: Acknowledged | 22652 | 122653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22653 | 122654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22653 | 122654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags |  | X
Alarm status: Acknowledged | 22653 | 122654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22654 | 122655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22654 | 122655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags |  | X
Alarm status: Acknowledged | 22654 | 122655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | [5 empty] | X | X
Alarm status: Acknowledged | 22655 | 122656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 |  |  | X | X
Alarm status: Acknowledged | 22655 | 122656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22655 | 122656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 |  | X
Alarm status: Acknowledged | 22656 | 122657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 |  |  | X | X
Alarm status: Acknowledged | 22656 | 122657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22656 | 122657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 |  | X
Alarm status: Acknowledged | 22657 | 122658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 |  |  | X | X
Alarm status: Acknowledged | 22657 | 122658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22657 | 122658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 |  | X
Alarm status: Acknowledged | 22658 | 122659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 |  |  | X | X
Alarm status: Acknowledged | 22658 | 122659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22658 | 122659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 |  | X
Alarm status: Acknowledged | 22659 | 122660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 |  |  | X | X
Alarm status: Acknowledged | 22659 | 122660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22659 | 122660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 |  | X
Alarm status: Acknowledged | 22660 | 122661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 |  |  | X | X
Alarm status: Acknowledged | 22660 | 122661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22660 | 122661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 |  | X
Alarm status: Acknowledged | 22661 | 122662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 |  |  | X | X
Alarm status: Acknowledged | 22661 | 122662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22661 | 122662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 |  | X
Alarm status: Acknowledged | 22662 | 122663 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance |  |  | X | X
Alarm status: Acknowledged | 22662 | 122663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22662 | 122663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance |  | X
Alarm status: Acknowledged | 22663 | 122664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 |  |  | X | X
Alarm status: Acknowledged | 22663 | 122664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22663 | 122664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 |  | X
Alarm status: Acknowledged | 22664 | 122665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 |  |  | X | X
Alarm status: Acknowledged | 22664 | 122665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22664 | 122665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 |  | X
Alarm status: Acknowledged | 22665 | 122666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 |  |  | X | X
Alarm status: Acknowledged | 22665 | 122666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22665 | 122666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 |  | X
Alarm status: Acknowledged | 22666 | 122667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 |  |  | X | X
Alarm status: Acknowledged | 22666 | 122667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22666 | 122667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 |  | X
Alarm status: Acknowledged | 22667 | 122668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 |  |  | X | X
Alarm status: Acknowledged | 22667 | 122668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22667 | 122668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 |  | X
Alarm status: Acknowledged | 22668 | 122669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 |  |  | X | X
Alarm status: Acknowledged | 22668 | 122669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22668 | 122669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 |  | X
Alarm status: Acknowledged | 22669 | 122670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 |  |  | X | X
Alarm status: Acknowledged | 22669 | 122670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22669 | 122670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 |  | X
Alarm status: Acknowledged | 22670 | 122671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage |  |  | X | X
Alarm status: Acknowledged | 22670 | 122671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22670 | 122671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage |  | X
Alarm status: Acknowledged | 22671 | 122672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage |  |  | X | X
Alarm status: Acknowledged | 22671 | 122672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22671 | 122672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage |  | X
Alarm status: Acknowledged | 22672 | 122673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage |  |  | X | X
Alarm status: Acknowledged | 22672 | 122673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | X |  |  |  | X | X | X
Alarm status: Acknowledged | 22672 | 122673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage |  | X
Alarm status: Acknowledged | 22717 | 122718 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 1 | X |  | X | X | X
Alarm status: Acknowledged | 22718 | 122719 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 2 | X |  | X | X | X
Alarm status: Acknowledged | 22719 | 122720 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 3 | X |  | X | X | X
Alarm status: Acknowledged | 22720 | 122721 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 4 | X |  | X | X | X
Alarm status: Acknowledged | 22721 | 122722 | External MB open failure | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22722 | 122723 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22723 | 122724 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22724 | 122725 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22725 | 122726 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22726 | 122727 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - Flags | X |  | X | X | X
Alarm status: Acknowledged | 22727 | 122728 | Parameters - Breakers - Close before excitation - CBE failure - Information - Flags - Close before excitation failure | X |  | X | X | X
Alarm status: Acknowledged | 22728 | 122729 | Load too high | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22729 | 122730 | ID to run configuration failure | [5 empty] | X | X
Alarm status: Acknowledged | 22731 | 122732 | Parameters - System - Monitoring - Missing any genset controller - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22732 | 122733 | Parameters - System - Monitoring - Missing any mains controller - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22733 | 122734 | Parameters - System - Monitoring - Missing any bustie controller - Information - Flags - Missing any bus tie controller | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22734 | 122735 | Can ID not available | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22735 | 122736 | Duplicated CAN IDs | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22736 | 122737 | Parameters - Local power management - Alarms - Busbar blocked - Information - Flags - Busbar blocked due to position failure | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22737 | 122738 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Flags - Busbar A blocked due to position failure |  | X
Alarm status: Acknowledged | 22738 | 122739 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Flags - Busbar B blocked due to position failure |  | X
Alarm status: Acknowledged | 22739 | 122740 | Parameters - System - Monitoring - BTB 33 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22740 | 122741 | Parameters - System - Monitoring - BTB 34 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22741 | 122742 | Parameters - System - Monitoring - BTB 35 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22742 | 122743 | Parameters - System - Monitoring - BTB 36 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22743 | 122744 | Parameters - System - Monitoring - BTB 37 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22744 | 122745 | Parameters - System - Monitoring - BTB 38 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22745 | 122746 | Parameters - System - Monitoring - BTB 39 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22746 | 122747 | Parameters - System - Monitoring - BTB 40 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22747 | 122748 | Primary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22748 | 122749 | Primary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22749 | 122750 | Primary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22750 | 122751 | Primary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22751 | 122752 | Primary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22752 | 122753 | Primary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22753 | 122754 | Primary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22754 | 122755 | Primary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22755 | 122756 | Primary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22756 | 122757 | Primary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22757 | 122758 | Primary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22758 | 122759 | Primary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22759 | 122760 | Primary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22760 | 122761 | Primary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22761 | 122762 | Primary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22762 | 122763 | Primary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22763 | 122764 | Primary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22764 | 122765 | Primary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22765 | 122766 | Primary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22766 | 122767 | Primary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22767 | 122768 | Primary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22768 | 122769 | Primary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22769 | 122770 | Primary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22770 | 122771 | Primary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22771 | 122772 | Primary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22772 | 122773 | Primary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22773 | 122774 | Primary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22774 | 122775 | Primary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22775 | 122776 | Primary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22776 | 122777 | Primary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22777 | 122778 | Primary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22778 | 122779 | Primary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22779 | 122780 | Primary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22780 | 122781 | Primary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22781 | 122782 | Primary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22782 | 122783 | Primary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22783 | 122784 | Primary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22784 | 122785 | Primary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22785 | 122786 | Primary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22786 | 122787 | Primary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22787 | 122788 | Secondary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22788 | 122789 | Secondary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22789 | 122790 | Secondary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22790 | 122791 | Secondary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22791 | 122792 | Secondary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22792 | 122793 | Secondary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22793 | 122794 | Secondary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22794 | 122795 | Secondary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22795 | 122796 | Secondary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22796 | 122797 | Secondary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22797 | 122798 | Secondary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22798 | 122799 | Secondary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22799 | 122800 | Secondary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22800 | 122801 | Secondary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22801 | 122802 | Secondary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22802 | 122803 | Secondary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22803 | 122804 | Secondary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22804 | 122805 | Secondary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22805 | 122806 | Secondary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22806 | 122807 | Secondary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22807 | 122808 | Secondary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22808 | 122809 | Secondary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22809 | 122810 | Secondary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22810 | 122811 | Secondary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22811 | 122812 | Secondary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22812 | 122813 | Secondary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22813 | 122814 | Secondary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22814 | 122815 | Secondary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22815 | 122816 | Secondary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22816 | 122817 | Secondary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22817 | 122818 | Secondary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22818 | 122819 | Secondary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22819 | 122820 | Secondary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22820 | 122821 | Secondary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22821 | 122822 | Secondary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22822 | 122823 | Secondary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22823 | 122824 | Secondary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22824 | 122825 | Secondary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22825 | 122826 | Secondary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22826 | 122827 | Secondary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22827 | 122828 | Priority error | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22828 | 122829 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - Flags - NEL 1 over-current | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22829 | 122830 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - Flags - NEL 1 under-frequency | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22830 | 122831 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - Flags - NEL 1 overload 1 | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22831 | 122832 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - Flags - NEL 1 overload 2 | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22832 | 122833 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - Flags - NEL 1 reactive overload | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22833 | 122834 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - Flags - NEL 2 over-current | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22834 | 122835 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - Flags - NEL 2 under-frequency | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22835 | 122836 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - Flags - NEL 2 overload 1 | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22836 | 122837 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - Flags - NEL 2 overload 2 | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22837 | 122838 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - Flags - NEL 2 reactive overload | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22838 | 122839 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - Flags - NEL 3 over-current | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22839 | 122840 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - Flags - NEL 3 under-frequency | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22840 | 122841 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - Flags - NEL 3 overload 1 | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22841 | 122842 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - Flags - NEL 3 overload 2 | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22842 | 122843 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - Flags - NEL 3 reactive overload | X |  | X | X | X | X | X
Alarm status: Acknowledged | 22843 | 122844 | Parameters - System - Monitoring - Single-line hazard - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22844 | 122845 | ID not present | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22845 | 122846 | Unsupported application | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22846 | 122847 | Application internal CAN protocol conflict | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22847 | 122848 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Flags - Section P> | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22848 | 122849 | Dry mode: Voltage level unexpected | X |  | X | X | X
Alarm status: Acknowledged | 22849 | 122850 | Invalid DAVR configuration | X |  | X | X | X
Alarm status: Acknowledged | 22850 | 122851 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22852 | 122853 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22854 | 122855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | X |  | X | X | X
Alarm status: Acknowledged | 22854 | 122855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch |  | X
Alarm status: Acknowledged | 22854 | 122855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | [5 empty] | X | X
Alarm status: Acknowledged | 22855 | 122856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch |  |  |  | X
Alarm status: Acknowledged | 22855 | 122856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | [6 empty] | X
Alarm status: Acknowledged | 22857 | 122858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22858 | 122859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22859 | 122860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22860 | 122861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22861 | 122862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22862 | 122863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22863 | 122864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22864 | 122865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22865 | 122866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22866 | 122867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22867 | 122868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22868 | 122869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22869 | 122870 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22870 | 122871 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22871 | 122872 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22872 | 122873 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22873 | 122874 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22874 | 122875 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22875 | 122876 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22876 | 122877 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22877 | 122878 | Live voltage detected | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22878 | 122879 | Internal issue detected. A restart is required soon! | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22879 | 122880 | Parameters - System - Monitoring - Missing controllers - Information - Flags | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22880 | 122881 | Card issue detected | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22881 | 122882 | Card configuration failed | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22882 | 122883 | Unknown traffic on DEIF network | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22883 | 122884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Acknowledged | 22884 | 122885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Acknowledged | 22885 | 122886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Acknowledged | 22886 | 122887 | Local IO service error | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22887 | 122888 | App logging failure | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22888 | 122889 | Event logging failure | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22889 | 122890 | Licence error | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22890 | 122891 | Brightness is dimmed according to temperature | X | X | X | X | X | X | X
Alarm status: Acknowledged | 22891 | 122892 | Parameters - Grid code - Mains sync inhibit - Information - Flags |  |  | X | X
Alarm status: Acknowledged | 22892 | 122893 | Parameters - Grid code - Capability curve - Import protection - Information - Flags - Power import capability curve protection |  |  | X | X
Alarm status: Acknowledged | 22893 | 122894 | Parameters - Grid code - Capability curve - Export protection - Information - Flags - Power export capability curve protection |  |  | X | X
Alarm status: Acknowledged | 22894 | 122895 | Hardware is not compatible based on module versions | X | X | X | X | X | X | X
Alarm status: Latched | 24000 | 124001 | Application initialisation error | X | X | X | X | X | X | X
Alarm status: Latched | 24001 | 124002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm status: Latched | 24002 | 124003 | Preliminary software | X | X | X | X | X | X | X
Alarm status: Latched | 24003 | 124004 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24004 | 124005 | Parameters - Engine - Start sequence - Start failure - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24005 | 124006 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24006 | 124007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24007 | 124008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24008 | 124009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24009 | 124010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24010 | 124011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | X |  | X | X | X
Alarm status: Latched | 24011 | 124012 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24013 | 124014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24014 | 124015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24015 | 124016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24016 | 124017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24017 | 124018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24018 | 124019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24019 | 124020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24020 | 124021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24021 | 124022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24022 | 124023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24027 | 124028 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24041 | 124042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | X |  | X | X | X
Alarm status: Latched | 24041 | 124042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure |  | X
Alarm status: Latched | 24041 | 124042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | [5 empty] | X | X
Alarm status: Latched | 24042 | 124043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | X |  | X | X | X
Alarm status: Latched | 24042 | 124043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure |  | X
Alarm status: Latched | 24042 | 124043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | [5 empty] | X | X
Alarm status: Latched | 24043 | 124044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | X |  | X | X | X
Alarm status: Latched | 24043 | 124044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure |  | X
Alarm status: Latched | 24043 | 124044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | [5 empty] | X | X
Alarm status: Latched | 24044 | 124045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | X |  | X | X | X
Alarm status: Latched | 24044 | 124045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure |  | X
Alarm status: Latched | 24044 | 124045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | [5 empty] | X | X
Alarm status: Latched | 24045 | 124046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | X |  | X | X | X
Alarm status: Latched | 24045 | 124046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure |  | X
Alarm status: Latched | 24045 | 124046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | [5 empty] | X | X
Alarm status: Latched | 24046 | 124047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | X |  | X | X | X
Alarm status: Latched | 24046 | 124047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure |  | X
Alarm status: Latched | 24046 | 124047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | [5 empty] | X | X
Alarm status: Latched | 24047 | 124048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | X |  | X | X | X
Alarm status: Latched | 24047 | 124048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) |  | X
Alarm status: Latched | 24047 | 124048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | [5 empty] | X | X
Alarm status: Latched | 24048 | 124049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | X |  | X | X | X
Alarm status: Latched | 24048 | 124049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit |  | X
Alarm status: Latched | 24048 | 124049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | [5 empty] | X | X
Alarm status: Latched | 24049 | 124050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure |  |  |  | X
Alarm status: Latched | 24049 | 124050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | [6 empty] | X
Alarm status: Latched | 24050 | 124051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure |  |  |  | X
Alarm status: Latched | 24050 | 124051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | [6 empty] | X
Alarm status: Latched | 24051 | 124052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure |  |  |  | X
Alarm status: Latched | 24051 | 124052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | [6 empty] | X
Alarm status: Latched | 24052 | 124053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure |  |  |  | X
Alarm status: Latched | 24052 | 124053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | [6 empty] | X
Alarm status: Latched | 24053 | 124054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure |  |  |  | X
Alarm status: Latched | 24053 | 124054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | [6 empty] | X
Alarm status: Latched | 24054 | 124055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure |  |  |  | X
Alarm status: Latched | 24054 | 124055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | [6 empty] | X
Alarm status: Latched | 24055 | 124056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) |  |  |  | X
Alarm status: Latched | 24055 | 124056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | [6 empty] | X
Alarm status: Latched | 24056 | 124057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit |  |  |  | X
Alarm status: Latched | 24056 | 124057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | [6 empty] | X
Alarm status: Latched | 24060 | 124061 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error |  |  | X | X
Alarm status: Latched | 24060 | 124061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | X |  |  |  | X | X | X
Alarm status: Latched | 24060 | 124061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error |  | X
Alarm status: Latched | 24061 | 124062 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | X |  | X | X | X
Alarm status: Latched | 24061 | 124062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error |  | X
Alarm status: Latched | 24061 | 124062 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | [5 empty] | X | X
Alarm status: Latched | 24062 | 124063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24103 | 124104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information - Flags |  |  | X | X
Alarm status: Latched | 24103 | 124104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information - Flags | X |  |  |  | X | X | X
Alarm status: Latched | 24103 | 124104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information - Flags |  | X
Alarm status: Latched | 24104 | 124105 | Parameters - Mains - Additional protections - Vector shift - Information - Flags |  |  | X | X
Alarm status: Latched | 24104 | 124105 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | X |  |  |  | X | X | X
Alarm status: Latched | 24104 | 124105 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags |  | X
Alarm status: Latched | 24105 | 124106 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24105 | 124106 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags |  | X
Alarm status: Latched | 24105 | 124106 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24106 | 124107 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24107 | 124108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24108 | 124109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24108 | 124109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags |  | X
Alarm status: Latched | 24108 | 124109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24109 | 124110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24109 | 124110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags |  | X
Alarm status: Latched | 24109 | 124110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24110 | 124111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24110 | 124111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags |  | X
Alarm status: Latched | 24110 | 124111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24111 | 124112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24111 | 124112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags |  | X
Alarm status: Latched | 24111 | 124112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24115 | 124116 | Protection set point out of range | X | X | X | X | X | X | X
Alarm status: Latched | 24116 | 124117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | X |  | X | X | X
Alarm status: Latched | 24117 | 124118 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | X |  | X | X | X
Alarm status: Latched | 24118 | 124119 | Protection set point out of range (differential current) | X |  | X | X | X
Alarm status: Latched | 24119 | 124120 | Parameters - Local - Mode - Not under remote control - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24121 | 124122 | Parameters - Local - Monitoring - System not OK - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24122 | 124123 | Configuration update delayed | X | X | X | X | X | X | X
Alarm status: Latched | 24123 | 124124 | Critical process error | X | X | X | X | X | X | X
Alarm status: Latched | 24124 | 124125 | Restore error | X | X | X | X | X | X | X
Alarm status: Latched | 24125 | 124126 | SD-card format error | X | X | X | X | X | X | X
Alarm status: Latched | 24126 | 124127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm status: Latched | 24127 | 124128 | Fieldbus configuration exceeded maximum I/O configuration | X | X | X | X | X | X | X
Alarm status: Latched | 24128 | 124129 | Parameters - Custom alarm - Custom alarm 0 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24129 | 124130 | Parameters - Custom alarm - Custom alarm 1 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24130 | 124131 | Parameters - Custom alarm - Custom alarm 2 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24131 | 124132 | Parameters - Custom alarm - Custom alarm 3 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24132 | 124133 | Parameters - Custom alarm - Custom alarm 4 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24133 | 124134 | Parameters - Custom alarm - Custom alarm 5 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24134 | 124135 | Parameters - Custom alarm - Custom alarm 6 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24135 | 124136 | Parameters - Custom alarm - Custom alarm 7 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24136 | 124137 | Parameters - Custom alarm - Custom alarm 8 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24137 | 124138 | Parameters - Custom alarm - Custom alarm 9 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24138 | 124139 | Parameters - Custom alarm - Custom alarm 10 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24139 | 124140 | Parameters - Custom alarm - Custom alarm 11 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24140 | 124141 | Parameters - Custom alarm - Custom alarm 12 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24141 | 124142 | Parameters - Custom alarm - Custom alarm 13 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24142 | 124143 | Parameters - Custom alarm - Custom alarm 14 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24143 | 124144 | Parameters - Custom alarm - Custom alarm 15 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24144 | 124145 | Parameters - Custom alarm - Custom alarm 16 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24145 | 124146 | Parameters - Custom alarm - Custom alarm 17 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24146 | 124147 | Parameters - Custom alarm - Custom alarm 18 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24147 | 124148 | Parameters - Custom alarm - Custom alarm 19 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24148 | 124149 | Parameters - Custom alarm - Custom alarm 20 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24149 | 124150 | Parameters - Custom alarm - Custom alarm 21 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24150 | 124151 | Parameters - Custom alarm - Custom alarm 22 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24151 | 124152 | Parameters - Custom alarm - Custom alarm 23 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24152 | 124153 | Parameters - Custom alarm - Custom alarm 24 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Latched | 24153 | 124154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | X |  | X | X | X
Alarm status: Latched | 24154 | 124155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | X |  | X | X | X
Alarm status: Latched | 24163 | 124164 | Required hardware card(s) not found | X | X | X | X | X | X | X
Alarm status: Latched | 24164 | 124165 | Software mismatch on hardware module(s) | X | X | X | X | X | X | X
Alarm status: Latched | 24165 | 124166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break |  |  | X
Alarm status: Latched | 24165 | 124166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | X |  |  |  | X | X
Alarm status: Latched | 24165 | 124166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break |  | X
Alarm status: Latched | 24166 | 124167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | X |  | X |  | X
Alarm status: Latched | 24166 | 124167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break |  | X
Alarm status: Latched | 24166 | 124167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | [5 empty] | X
Alarm status: Latched | 24167 | 124168 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break |  |  | X
Alarm status: Latched | 24167 | 124168 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | X |  |  |  | X | X
Alarm status: Latched | 24167 | 124168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break |  | X
Alarm status: Latched | 24168 | 124169 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break |  |  | X
Alarm status: Latched | 24168 | 124169 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | X |  |  |  | X | X
Alarm status: Latched | 24168 | 124169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break |  | X
Alarm status: Latched | 24169 | 124170 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break |  |  | X
Alarm status: Latched | 24169 | 124170 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | X |  |  |  | X | X
Alarm status: Latched | 24169 | 124170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break |  | X
Alarm status: Latched | 24170 | 124171 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | X |  | X |  | X
Alarm status: Latched | 24170 | 124171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break |  | X
Alarm status: Latched | 24170 | 124171 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | [5 empty] | X
Alarm status: Latched | 24171 | 124172 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | X |  | X |  | X
Alarm status: Latched | 24171 | 124172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break |  | X
Alarm status: Latched | 24171 | 124172 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | [5 empty] | X
Alarm status: Latched | 24172 | 124173 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | X |  | X |  | X
Alarm status: Latched | 24172 | 124173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break |  | X
Alarm status: Latched | 24172 | 124173 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | [5 empty] | X
Alarm status: Latched | 24178 | 124179 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm |  |  | X | X |  | X | X
Alarm status: Latched | 24179 | 124180 | Parameters - Engine - Emergency stop - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24179 | 124180 | Parameters - Busbar A - Emergency stop - Information - Flags |  | X
Alarm status: Latched | 24179 | 124180 | Parameters - Mains - Emergency stop - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24180 | 124181 | Clock battery failure | X | X | X | X | X | X | X
Alarm status: Latched | 24181 | 124182 | Controller temperature too high | X | X | X | X | X | X | X
Alarm status: Latched | 24182 | 124183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24183 | 124184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | X | X | X | X | X | X | X
Alarm status: Latched | 24184 | 124185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24185 | 124186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | X | X | X | X | X | X | X
Alarm status: Latched | 24186 | 124187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24187 | 124188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | X | X | X | X | X | X | X
Alarm status: Latched | 24188 | 124189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24189 | 124190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | X | X | X | X | X | X | X
Alarm status: Latched | 24190 | 124191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24191 | 124192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Latched | 24192 | 124193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24193 | 124194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Latched | 24194 | 124195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24195 | 124196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Latched | 24196 | 124197 | EIM3.1 4 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24197 | 124198 | EIM3.1 4 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Latched | 24198 | 124199 | EIM3.1 5 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24199 | 124200 | EIM3.1 5 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Latched | 24200 | 124201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Latched | 24201 | 124202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Latched | 24202 | 124203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Latched | 24203 | 124204 | EIM3.1 4 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Latched | 24204 | 124205 | EIM3.1 5 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Latched | 24205 | 124206 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Latched | 24206 | 124207 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Latched | 24207 | 124208 | AC protections not running (differential current) | X |  | X | X | X
Alarm status: Latched | 24208 | 124209 | AC data is missing (differential current) | X |  | X | X | X
Alarm status: Latched | 24209 | 124210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24210 | 124211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Latched | 24211 | 124212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24212 | 124213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Latched | 24213 | 124214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24214 | 124215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Latched | 24215 | 124216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24216 | 124217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | X | X | X | X | X | X | X
Alarm status: Latched | 24217 | 124218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24218 | 124219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | X | X | X | X | X | X | X
Alarm status: Latched | 24219 | 124220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24220 | 124221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | X | X | X | X | X | X | X
Alarm status: Latched | 24221 | 124222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24222 | 124223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | X | X | X | X | X | X | X
Alarm status: Latched | 24223 | 124224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24224 | 124225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | X | X | X | X | X | X | X
Alarm status: Latched | 24225 | 124226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | X | X | X | X | X | X | X
Alarm status: Latched | 24226 | 124227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | X | X | X | X | X | X | X
Alarm status: Latched | 24228 | 124229 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24229 | 124230 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24231 | 124232 | Controller ID not configured | X | X | X | X | X | X | X
Alarm status: Latched | 24236 | 124237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24237 | 124238 | Blackout detection mismatch | X |  | X | X | X
Alarm status: Latched | 24240 | 124241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | X | X | X | X | X | X | X
Alarm status: Latched | 24241 | 124242 | Parameters - Communication - NTP - NTP server 1 no response - Information - Flags - NTP server 1 is not responding | X | X | X | X | X | X | X
Alarm status: Latched | 24242 | 124243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | X | X | X | X | X | X | X
Alarm status: Latched | 24243 | 124244 | Parameters - Communication - NTP - NTP server 2 no response - Information - Flags - NTP server 2 is not responding | X | X | X | X | X | X | X
Alarm status: Latched | 24244 | 124245 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24245 | 124246 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24246 | 124247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24247 | 124248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24296 | 124297 | Controller not part of system | X | X | X | X | X | X | X
Alarm status: Latched | 24297 | 124298 | Different single-line configurations | X | X | X | X | X | X | X
Alarm status: Latched | 24298 | 124299 | Single-line missing/none active | X | X | X | X | X | X | X
Alarm status: Latched | 24299 | 124300 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24300 | 124301 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | X | X | X | X | X | X | X
Alarm status: Latched | 24301 | 124302 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | X | X | X | X | X | X | X
Alarm status: Latched | 24302 | 124303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24303 | 124304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24304 | 124305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24305 | 124306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24306 | 124307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24307 | 124308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24308 | 124309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24309 | 124310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24310 | 124311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24311 | 124312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24312 | 124313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24313 | 124314 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24314 | 124315 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24315 | 124316 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24316 | 124317 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24317 | 124318 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24318 | 124319 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24319 | 124320 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24320 | 124321 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24321 | 124322 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24322 | 124323 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24323 | 124324 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24324 | 124325 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24325 | 124326 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24326 | 124327 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24327 | 124328 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24328 | 124329 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24329 | 124330 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24330 | 124331 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24331 | 124332 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24332 | 124333 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24333 | 124334 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24334 | 124335 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24335 | 124336 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24336 | 124337 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24337 | 124338 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24338 | 124339 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24339 | 124340 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24340 | 124341 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24341 | 124342 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24342 | 124343 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24343 | 124344 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24344 | 124345 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24345 | 124346 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24346 | 124347 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24347 | 124348 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24348 | 124349 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24349 | 124350 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24350 | 124351 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24351 | 124352 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24352 | 124353 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24353 | 124354 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24354 | 124355 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24355 | 124356 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24356 | 124357 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24357 | 124358 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24358 | 124359 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24359 | 124360 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24360 | 124361 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24361 | 124362 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24362 | 124363 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24363 | 124364 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24364 | 124365 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24365 | 124366 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24366 | 124367 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24367 | 124368 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24368 | 124369 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24369 | 124370 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24370 | 124371 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24371 | 124372 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24372 | 124373 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24373 | 124374 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24374 | 124375 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24375 | 124376 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24376 | 124377 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24377 | 124378 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24378 | 124379 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24379 | 124380 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24380 | 124381 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24381 | 124382 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24382 | 124383 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24383 | 124384 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24384 | 124385 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24385 | 124386 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24386 | 124387 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24387 | 124388 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24388 | 124389 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24389 | 124390 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24390 | 124391 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24391 | 124392 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24392 | 124393 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24393 | 124394 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24394 | 124395 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24395 | 124396 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24396 | 124397 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24397 | 124398 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24398 | 124399 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24399 | 124400 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24400 | 124401 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24401 | 124402 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24402 | 124403 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24403 | 124404 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24404 | 124405 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24405 | 124406 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24406 | 124407 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24407 | 124408 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24408 | 124409 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24409 | 124410 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24410 | 124411 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24411 | 124412 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24412 | 124413 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24413 | 124414 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24414 | 124415 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24415 | 124416 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24416 | 124417 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24417 | 124418 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24418 | 124419 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24419 | 124420 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24420 | 124421 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24421 | 124422 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24422 | 124423 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24423 | 124424 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24424 | 124425 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24425 | 124426 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24426 | 124427 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24427 | 124428 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24428 | 124429 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24429 | 124430 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24430 | 124431 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24431 | 124432 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24432 | 124433 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24433 | 124434 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24434 | 124435 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24435 | 124436 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24436 | 124437 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24437 | 124438 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24438 | 124439 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24439 | 124440 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24440 | 124441 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24441 | 124442 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24442 | 124443 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24443 | 124444 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24444 | 124445 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24445 | 124446 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24446 | 124447 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24447 | 124448 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24448 | 124449 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24449 | 124450 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24450 | 124451 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24451 | 124452 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24452 | 124453 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24453 | 124454 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24454 | 124455 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24455 | 124456 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24456 | 124457 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24457 | 124458 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24458 | 124459 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24459 | 124460 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24460 | 124461 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24461 | 124462 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24462 | 124463 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24463 | 124464 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24464 | 124465 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24465 | 124466 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24466 | 124467 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24467 | 124468 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24468 | 124469 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24469 | 124470 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24470 | 124471 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24471 | 124472 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24472 | 124473 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24473 | 124474 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24474 | 124475 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24475 | 124476 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24476 | 124477 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24477 | 124478 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24478 | 124479 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24479 | 124480 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24480 | 124481 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24481 | 124482 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24482 | 124483 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24483 | 124484 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24484 | 124485 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24485 | 124486 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24486 | 124487 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24487 | 124488 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24488 | 124489 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24489 | 124490 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24490 | 124491 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24491 | 124492 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24492 | 124493 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24493 | 124494 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24494 | 124495 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24495 | 124496 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24496 | 124497 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24497 | 124498 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24498 | 124499 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24499 | 124500 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24500 | 124501 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24501 | 124502 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24502 | 124503 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24503 | 124504 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24504 | 124505 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24505 | 124506 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24506 | 124507 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24507 | 124508 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24508 | 124509 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24509 | 124510 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24510 | 124511 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24511 | 124512 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24512 | 124513 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24513 | 124514 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24514 | 124515 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24515 | 124516 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24516 | 124517 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24517 | 124518 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24518 | 124519 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24519 | 124520 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24520 | 124521 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24521 | 124522 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24522 | 124523 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24523 | 124524 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24524 | 124525 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24525 | 124526 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24526 | 124527 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24527 | 124528 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24528 | 124529 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24529 | 124530 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24530 | 124531 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24531 | 124532 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24532 | 124533 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24533 | 124534 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24534 | 124535 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24535 | 124536 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24536 | 124537 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24537 | 124538 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24538 | 124539 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24539 | 124540 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24540 | 124541 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24541 | 124542 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24542 | 124543 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24543 | 124544 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24544 | 124545 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24545 | 124546 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24546 | 124547 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24547 | 124548 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24548 | 124549 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24549 | 124550 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24550 | 124551 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24551 | 124552 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24552 | 124553 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24553 | 124554 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24554 | 124555 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24555 | 124556 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24556 | 124557 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24557 | 124558 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24558 | 124559 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24559 | 124560 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24560 | 124561 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24561 | 124562 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24562 | 124563 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Latched | 24565 | 124566 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | X | X | X | X | X | X | X
Alarm status: Latched | 24566 | 124567 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | X |  | X | X | X
Alarm status: Latched | 24567 | 124568 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24568 | 124569 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24569 | 124570 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24570 | 124571 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24571 | 124572 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24572 | 124573 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24573 | 124574 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24574 | 124575 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24575 | 124576 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24576 | 124577 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24577 | 124578 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24578 | 124579 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24579 | 124580 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24580 | 124581 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24581 | 124582 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24582 | 124583 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24583 | 124584 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24584 | 124585 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24585 | 124586 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24586 | 124587 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24587 | 124588 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24588 | 124589 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24589 | 124590 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24590 | 124591 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24591 | 124592 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24592 | 124593 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24593 | 124594 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24594 | 124595 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24595 | 124596 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24596 | 124597 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24597 | 124598 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24598 | 124599 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24599 | 124600 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24600 | 124601 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24601 | 124602 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24602 | 124603 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24603 | 124604 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24604 | 124605 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24605 | 124606 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24606 | 124607 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24607 | 124608 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24608 | 124609 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24609 | 124610 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24610 | 124611 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24611 | 124612 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24612 | 124613 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24613 | 124614 | DAVR unsupported AC configuration | X |  | X | X | X
Alarm status: Latched | 24614 | 124615 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | X |  | X | X | X
Alarm status: Latched | 24615 | 124616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | X |  | X | X | X
Alarm status: Latched | 24615 | 124616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 |  | X
Alarm status: Latched | 24615 | 124616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | [5 empty] | X | X
Alarm status: Latched | 24616 | 124617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | X |  | X | X | X
Alarm status: Latched | 24616 | 124617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 |  | X
Alarm status: Latched | 24616 | 124617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | [5 empty] | X | X
Alarm status: Latched | 24617 | 124618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | X |  | X | X | X
Alarm status: Latched | 24617 | 124618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 |  | X
Alarm status: Latched | 24617 | 124618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | [5 empty] | X | X
Alarm status: Latched | 24618 | 124619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | X |  | X | X | X
Alarm status: Latched | 24618 | 124619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 |  | X
Alarm status: Latched | 24618 | 124619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | [5 empty] | X | X
Alarm status: Latched | 24619 | 124620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | X |  | X | X | X
Alarm status: Latched | 24619 | 124620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 |  | X
Alarm status: Latched | 24619 | 124620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | [5 empty] | X | X
Alarm status: Latched | 24620 | 124621 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | X |  | X | X | X
Alarm status: Latched | 24620 | 124621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance |  | X
Alarm status: Latched | 24620 | 124621 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | [5 empty] | X | X
Alarm status: Latched | 24621 | 124622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | X |  | X | X | X
Alarm status: Latched | 24621 | 124622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage |  | X
Alarm status: Latched | 24621 | 124622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | [5 empty] | X | X
Alarm status: Latched | 24622 | 124623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | X |  | X | X | X
Alarm status: Latched | 24622 | 124623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage |  | X
Alarm status: Latched | 24622 | 124623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | [5 empty] | X | X
Alarm status: Latched | 24623 | 124624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | X |  | X | X | X
Alarm status: Latched | 24623 | 124624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage |  | X
Alarm status: Latched | 24623 | 124624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | [5 empty] | X | X
Alarm status: Latched | 24624 | 124625 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24624 | 124625 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags |  | X
Alarm status: Latched | 24624 | 124625 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24625 | 124626 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24625 | 124626 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags |  | X
Alarm status: Latched | 24625 | 124626 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24626 | 124627 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24626 | 124627 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags |  | X
Alarm status: Latched | 24626 | 124627 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24627 | 124628 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24627 | 124628 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags |  | X
Alarm status: Latched | 24627 | 124628 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24628 | 124629 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24628 | 124629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags |  | X
Alarm status: Latched | 24628 | 124629 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24629 | 124630 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24629 | 124630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags |  | X
Alarm status: Latched | 24629 | 124630 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24630 | 124631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24630 | 124631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags |  | X
Alarm status: Latched | 24630 | 124631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24631 | 124632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24631 | 124632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags |  | X
Alarm status: Latched | 24631 | 124632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24632 | 124633 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24632 | 124633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags |  | X
Alarm status: Latched | 24632 | 124633 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24633 | 124634 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24633 | 124634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags |  | X
Alarm status: Latched | 24633 | 124634 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24634 | 124635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags |  | X
Alarm status: Latched | 24635 | 124636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags |  | X
Alarm status: Latched | 24636 | 124637 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24636 | 124637 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags |  | X
Alarm status: Latched | 24636 | 124637 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24637 | 124638 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24637 | 124638 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags |  | X
Alarm status: Latched | 24637 | 124638 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24638 | 124639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | X |  | X | X | X
Alarm status: Latched | 24638 | 124639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 |  | X
Alarm status: Latched | 24638 | 124639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | [5 empty] | X | X
Alarm status: Latched | 24639 | 124640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | X |  | X | X | X
Alarm status: Latched | 24639 | 124640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 |  | X
Alarm status: Latched | 24639 | 124640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | [5 empty] | X | X
Alarm status: Latched | 24640 | 124641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | X |  | X | X | X
Alarm status: Latched | 24640 | 124641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 |  | X
Alarm status: Latched | 24640 | 124641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | [5 empty] | X | X
Alarm status: Latched | 24641 | 124642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | X |  | X | X | X
Alarm status: Latched | 24641 | 124642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 |  | X
Alarm status: Latched | 24641 | 124642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | [5 empty] | X | X
Alarm status: Latched | 24642 | 124643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | X |  | X | X | X
Alarm status: Latched | 24642 | 124643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 |  | X
Alarm status: Latched | 24642 | 124643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | [5 empty] | X | X
Alarm status: Latched | 24643 | 124644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | X |  | X | X | X
Alarm status: Latched | 24643 | 124644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 |  | X
Alarm status: Latched | 24643 | 124644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | [5 empty] | X | X
Alarm status: Latched | 24644 | 124645 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24644 | 124645 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags |  | X
Alarm status: Latched | 24644 | 124645 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24645 | 124646 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24645 | 124646 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags |  | X
Alarm status: Latched | 24645 | 124646 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24646 | 124647 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24646 | 124647 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags |  | X
Alarm status: Latched | 24646 | 124647 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24647 | 124648 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24647 | 124648 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags |  | X
Alarm status: Latched | 24647 | 124648 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24648 | 124649 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24648 | 124649 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags |  | X
Alarm status: Latched | 24648 | 124649 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24649 | 124650 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24649 | 124650 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags |  | X
Alarm status: Latched | 24649 | 124650 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24650 | 124651 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24650 | 124651 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags |  | X
Alarm status: Latched | 24650 | 124651 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24651 | 124652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24651 | 124652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags |  | X
Alarm status: Latched | 24651 | 124652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24652 | 124653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24652 | 124653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags |  | X
Alarm status: Latched | 24652 | 124653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24653 | 124654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24653 | 124654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags |  | X
Alarm status: Latched | 24653 | 124654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24654 | 124655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24654 | 124655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags |  | X
Alarm status: Latched | 24654 | 124655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | [5 empty] | X | X
Alarm status: Latched | 24655 | 124656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 |  |  | X | X
Alarm status: Latched | 24655 | 124656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | X |  |  |  | X | X | X
Alarm status: Latched | 24655 | 124656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 |  | X
Alarm status: Latched | 24656 | 124657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 |  |  | X | X
Alarm status: Latched | 24656 | 124657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | X |  |  |  | X | X | X
Alarm status: Latched | 24656 | 124657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 |  | X
Alarm status: Latched | 24657 | 124658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 |  |  | X | X
Alarm status: Latched | 24657 | 124658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | X |  |  |  | X | X | X
Alarm status: Latched | 24657 | 124658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 |  | X
Alarm status: Latched | 24658 | 124659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 |  |  | X | X
Alarm status: Latched | 24658 | 124659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | X |  |  |  | X | X | X
Alarm status: Latched | 24658 | 124659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 |  | X
Alarm status: Latched | 24659 | 124660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 |  |  | X | X
Alarm status: Latched | 24659 | 124660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | X |  |  |  | X | X | X
Alarm status: Latched | 24659 | 124660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 |  | X
Alarm status: Latched | 24660 | 124661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 |  |  | X | X
Alarm status: Latched | 24660 | 124661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | X |  |  |  | X | X | X
Alarm status: Latched | 24660 | 124661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 |  | X
Alarm status: Latched | 24661 | 124662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 |  |  | X | X
Alarm status: Latched | 24661 | 124662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | X |  |  |  | X | X | X
Alarm status: Latched | 24661 | 124662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 |  | X
Alarm status: Latched | 24662 | 124663 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance |  |  | X | X
Alarm status: Latched | 24662 | 124663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | X |  |  |  | X | X | X
Alarm status: Latched | 24662 | 124663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance |  | X
Alarm status: Latched | 24663 | 124664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 |  |  | X | X
Alarm status: Latched | 24663 | 124664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | X |  |  |  | X | X | X
Alarm status: Latched | 24663 | 124664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 |  | X
Alarm status: Latched | 24664 | 124665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 |  |  | X | X
Alarm status: Latched | 24664 | 124665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | X |  |  |  | X | X | X
Alarm status: Latched | 24664 | 124665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 |  | X
Alarm status: Latched | 24665 | 124666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 |  |  | X | X
Alarm status: Latched | 24665 | 124666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | X |  |  |  | X | X | X
Alarm status: Latched | 24665 | 124666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 |  | X
Alarm status: Latched | 24666 | 124667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 |  |  | X | X
Alarm status: Latched | 24666 | 124667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | X |  |  |  | X | X | X
Alarm status: Latched | 24666 | 124667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 |  | X
Alarm status: Latched | 24667 | 124668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 |  |  | X | X
Alarm status: Latched | 24667 | 124668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | X |  |  |  | X | X | X
Alarm status: Latched | 24667 | 124668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 |  | X
Alarm status: Latched | 24668 | 124669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 |  |  | X | X
Alarm status: Latched | 24668 | 124669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | X |  |  |  | X | X | X
Alarm status: Latched | 24668 | 124669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 |  | X
Alarm status: Latched | 24669 | 124670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 |  |  | X | X
Alarm status: Latched | 24669 | 124670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | X |  |  |  | X | X | X
Alarm status: Latched | 24669 | 124670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 |  | X
Alarm status: Latched | 24670 | 124671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage |  |  | X | X
Alarm status: Latched | 24670 | 124671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | X |  |  |  | X | X | X
Alarm status: Latched | 24670 | 124671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage |  | X
Alarm status: Latched | 24671 | 124672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage |  |  | X | X
Alarm status: Latched | 24671 | 124672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | X |  |  |  | X | X | X
Alarm status: Latched | 24671 | 124672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage |  | X
Alarm status: Latched | 24672 | 124673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage |  |  | X | X
Alarm status: Latched | 24672 | 124673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | X |  |  |  | X | X | X
Alarm status: Latched | 24672 | 124673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage |  | X
Alarm status: Latched | 24717 | 124718 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 1 | X |  | X | X | X
Alarm status: Latched | 24718 | 124719 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 2 | X |  | X | X | X
Alarm status: Latched | 24719 | 124720 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 3 | X |  | X | X | X
Alarm status: Latched | 24720 | 124721 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 4 | X |  | X | X | X
Alarm status: Latched | 24721 | 124722 | External MB open failure | X | X | X | X | X | X | X
Alarm status: Latched | 24722 | 124723 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24723 | 124724 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24724 | 124725 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24725 | 124726 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24726 | 124727 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - Flags | X |  | X | X | X
Alarm status: Latched | 24727 | 124728 | Parameters - Breakers - Close before excitation - CBE failure - Information - Flags - Close before excitation failure | X |  | X | X | X
Alarm status: Latched | 24728 | 124729 | Load too high | X | X | X | X | X | X | X
Alarm status: Latched | 24729 | 124730 | ID to run configuration failure | [5 empty] | X | X
Alarm status: Latched | 24731 | 124732 | Parameters - System - Monitoring - Missing any genset controller - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24732 | 124733 | Parameters - System - Monitoring - Missing any mains controller - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24733 | 124734 | Parameters - System - Monitoring - Missing any bustie controller - Information - Flags - Missing any bus tie controller | X | X | X | X | X | X | X
Alarm status: Latched | 24734 | 124735 | Can ID not available | X | X | X | X | X | X | X
Alarm status: Latched | 24735 | 124736 | Duplicated CAN IDs | X | X | X | X | X | X | X
Alarm status: Latched | 24736 | 124737 | Parameters - Local power management - Alarms - Busbar blocked - Information - Flags - Busbar blocked due to position failure | X |  | X | X | X | X | X
Alarm status: Latched | 24737 | 124738 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Flags - Busbar A blocked due to position failure |  | X
Alarm status: Latched | 24738 | 124739 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Flags - Busbar B blocked due to position failure |  | X
Alarm status: Latched | 24739 | 124740 | Parameters - System - Monitoring - BTB 33 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24740 | 124741 | Parameters - System - Monitoring - BTB 34 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24741 | 124742 | Parameters - System - Monitoring - BTB 35 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24742 | 124743 | Parameters - System - Monitoring - BTB 36 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24743 | 124744 | Parameters - System - Monitoring - BTB 37 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24744 | 124745 | Parameters - System - Monitoring - BTB 38 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24745 | 124746 | Parameters - System - Monitoring - BTB 39 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24746 | 124747 | Parameters - System - Monitoring - BTB 40 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24747 | 124748 | Primary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm status: Latched | 24748 | 124749 | Primary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm status: Latched | 24749 | 124750 | Primary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm status: Latched | 24750 | 124751 | Primary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm status: Latched | 24751 | 124752 | Primary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm status: Latched | 24752 | 124753 | Primary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm status: Latched | 24753 | 124754 | Primary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm status: Latched | 24754 | 124755 | Primary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm status: Latched | 24755 | 124756 | Primary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm status: Latched | 24756 | 124757 | Primary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm status: Latched | 24757 | 124758 | Primary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm status: Latched | 24758 | 124759 | Primary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm status: Latched | 24759 | 124760 | Primary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm status: Latched | 24760 | 124761 | Primary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm status: Latched | 24761 | 124762 | Primary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm status: Latched | 24762 | 124763 | Primary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm status: Latched | 24763 | 124764 | Primary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm status: Latched | 24764 | 124765 | Primary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm status: Latched | 24765 | 124766 | Primary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm status: Latched | 24766 | 124767 | Primary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm status: Latched | 24767 | 124768 | Primary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm status: Latched | 24768 | 124769 | Primary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm status: Latched | 24769 | 124770 | Primary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm status: Latched | 24770 | 124771 | Primary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm status: Latched | 24771 | 124772 | Primary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm status: Latched | 24772 | 124773 | Primary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm status: Latched | 24773 | 124774 | Primary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm status: Latched | 24774 | 124775 | Primary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm status: Latched | 24775 | 124776 | Primary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm status: Latched | 24776 | 124777 | Primary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm status: Latched | 24777 | 124778 | Primary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm status: Latched | 24778 | 124779 | Primary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm status: Latched | 24779 | 124780 | Primary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm status: Latched | 24780 | 124781 | Primary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm status: Latched | 24781 | 124782 | Primary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm status: Latched | 24782 | 124783 | Primary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm status: Latched | 24783 | 124784 | Primary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm status: Latched | 24784 | 124785 | Primary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm status: Latched | 24785 | 124786 | Primary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm status: Latched | 24786 | 124787 | Primary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm status: Latched | 24787 | 124788 | Secondary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm status: Latched | 24788 | 124789 | Secondary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm status: Latched | 24789 | 124790 | Secondary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm status: Latched | 24790 | 124791 | Secondary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm status: Latched | 24791 | 124792 | Secondary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm status: Latched | 24792 | 124793 | Secondary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm status: Latched | 24793 | 124794 | Secondary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm status: Latched | 24794 | 124795 | Secondary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm status: Latched | 24795 | 124796 | Secondary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm status: Latched | 24796 | 124797 | Secondary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm status: Latched | 24797 | 124798 | Secondary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm status: Latched | 24798 | 124799 | Secondary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm status: Latched | 24799 | 124800 | Secondary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm status: Latched | 24800 | 124801 | Secondary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm status: Latched | 24801 | 124802 | Secondary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm status: Latched | 24802 | 124803 | Secondary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm status: Latched | 24803 | 124804 | Secondary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm status: Latched | 24804 | 124805 | Secondary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm status: Latched | 24805 | 124806 | Secondary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm status: Latched | 24806 | 124807 | Secondary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm status: Latched | 24807 | 124808 | Secondary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm status: Latched | 24808 | 124809 | Secondary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm status: Latched | 24809 | 124810 | Secondary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm status: Latched | 24810 | 124811 | Secondary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm status: Latched | 24811 | 124812 | Secondary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm status: Latched | 24812 | 124813 | Secondary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm status: Latched | 24813 | 124814 | Secondary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm status: Latched | 24814 | 124815 | Secondary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm status: Latched | 24815 | 124816 | Secondary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm status: Latched | 24816 | 124817 | Secondary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm status: Latched | 24817 | 124818 | Secondary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm status: Latched | 24818 | 124819 | Secondary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm status: Latched | 24819 | 124820 | Secondary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm status: Latched | 24820 | 124821 | Secondary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm status: Latched | 24821 | 124822 | Secondary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm status: Latched | 24822 | 124823 | Secondary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm status: Latched | 24823 | 124824 | Secondary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm status: Latched | 24824 | 124825 | Secondary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm status: Latched | 24825 | 124826 | Secondary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm status: Latched | 24826 | 124827 | Secondary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm status: Latched | 24827 | 124828 | Priority error | X | X | X | X | X | X | X
Alarm status: Latched | 24828 | 124829 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - Flags - NEL 1 over-current | X |  | X | X | X | X | X
Alarm status: Latched | 24829 | 124830 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - Flags - NEL 1 under-frequency | X |  | X | X | X | X | X
Alarm status: Latched | 24830 | 124831 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - Flags - NEL 1 overload 1 | X |  | X | X | X | X | X
Alarm status: Latched | 24831 | 124832 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - Flags - NEL 1 overload 2 | X |  | X | X | X | X | X
Alarm status: Latched | 24832 | 124833 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - Flags - NEL 1 reactive overload | X |  | X | X | X | X | X
Alarm status: Latched | 24833 | 124834 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - Flags - NEL 2 over-current | X |  | X | X | X | X | X
Alarm status: Latched | 24834 | 124835 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - Flags - NEL 2 under-frequency | X |  | X | X | X | X | X
Alarm status: Latched | 24835 | 124836 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - Flags - NEL 2 overload 1 | X |  | X | X | X | X | X
Alarm status: Latched | 24836 | 124837 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - Flags - NEL 2 overload 2 | X |  | X | X | X | X | X
Alarm status: Latched | 24837 | 124838 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - Flags - NEL 2 reactive overload | X |  | X | X | X | X | X
Alarm status: Latched | 24838 | 124839 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - Flags - NEL 3 over-current | X |  | X | X | X | X | X
Alarm status: Latched | 24839 | 124840 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - Flags - NEL 3 under-frequency | X |  | X | X | X | X | X
Alarm status: Latched | 24840 | 124841 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - Flags - NEL 3 overload 1 | X |  | X | X | X | X | X
Alarm status: Latched | 24841 | 124842 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - Flags - NEL 3 overload 2 | X |  | X | X | X | X | X
Alarm status: Latched | 24842 | 124843 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - Flags - NEL 3 reactive overload | X |  | X | X | X | X | X
Alarm status: Latched | 24843 | 124844 | Parameters - System - Monitoring - Single-line hazard - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24844 | 124845 | ID not present | X | X | X | X | X | X | X
Alarm status: Latched | 24845 | 124846 | Unsupported application | X | X | X | X | X | X | X
Alarm status: Latched | 24846 | 124847 | Application internal CAN protocol conflict | X | X | X | X | X | X | X
Alarm status: Latched | 24847 | 124848 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Flags - Section P> | X | X | X | X | X | X | X
Alarm status: Latched | 24848 | 124849 | Dry mode: Voltage level unexpected | X |  | X | X | X
Alarm status: Latched | 24849 | 124850 | Invalid DAVR configuration | X |  | X | X | X
Alarm status: Latched | 24850 | 124851 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24852 | 124853 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24854 | 124855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | X |  | X | X | X
Alarm status: Latched | 24854 | 124855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch |  | X
Alarm status: Latched | 24854 | 124855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | [5 empty] | X | X
Alarm status: Latched | 24855 | 124856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch |  |  |  | X
Alarm status: Latched | 24855 | 124856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | [6 empty] | X
Alarm status: Latched | 24857 | 124858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24858 | 124859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24859 | 124860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24860 | 124861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24861 | 124862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Latched | 24862 | 124863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Latched | 24863 | 124864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Latched | 24864 | 124865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Latched | 24865 | 124866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Latched | 24866 | 124867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Latched | 24867 | 124868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Latched | 24868 | 124869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Latched | 24869 | 124870 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Latched | 24870 | 124871 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Latched | 24871 | 124872 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Latched | 24872 | 124873 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Latched | 24873 | 124874 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Latched | 24874 | 124875 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Latched | 24875 | 124876 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Latched | 24876 | 124877 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Latched | 24877 | 124878 | Live voltage detected | X | X | X | X | X | X | X
Alarm status: Latched | 24878 | 124879 | Internal issue detected. A restart is required soon! | X | X | X | X | X | X | X
Alarm status: Latched | 24879 | 124880 | Parameters - System - Monitoring - Missing controllers - Information - Flags | X | X | X | X | X | X | X
Alarm status: Latched | 24880 | 124881 | Card issue detected | X | X | X | X | X | X | X
Alarm status: Latched | 24881 | 124882 | Card configuration failed | X | X | X | X | X | X | X
Alarm status: Latched | 24882 | 124883 | Unknown traffic on DEIF network | X | X | X | X | X | X | X
Alarm status: Latched | 24883 | 124884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Latched | 24884 | 124885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Latched | 24885 | 124886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Latched | 24886 | 124887 | Local IO service error | X | X | X | X | X | X | X
Alarm status: Latched | 24887 | 124888 | App logging failure | X | X | X | X | X | X | X
Alarm status: Latched | 24888 | 124889 | Event logging failure | X | X | X | X | X | X | X
Alarm status: Latched | 24889 | 124890 | Licence error | X | X | X | X | X | X | X
Alarm status: Latched | 24890 | 124891 | Brightness is dimmed according to temperature | X | X | X | X | X | X | X
Alarm status: Latched | 24891 | 124892 | Parameters - Grid code - Mains sync inhibit - Information - Flags |  |  | X | X
Alarm status: Latched | 24892 | 124893 | Parameters - Grid code - Capability curve - Import protection - Information - Flags - Power import capability curve protection |  |  | X | X
Alarm status: Latched | 24893 | 124894 | Parameters - Grid code - Capability curve - Export protection - Information - Flags - Power export capability curve protection |  |  | X | X
Alarm status: Latched | 24894 | 124895 | Hardware is not compatible based on module versions | X | X | X | X | X | X | X
Alarm status: Shelved | 26000 | 126001 | Application initialisation error | X | X | X | X | X | X | X
Alarm status: Shelved | 26001 | 126002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm status: Shelved | 26002 | 126003 | Preliminary software | X | X | X | X | X | X | X
Alarm status: Shelved | 26003 | 126004 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26004 | 126005 | Parameters - Engine - Start sequence - Start failure - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26005 | 126006 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26006 | 126007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26007 | 126008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26008 | 126009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26009 | 126010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26010 | 126011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | X |  | X | X | X
Alarm status: Shelved | 26011 | 126012 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26013 | 126014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26014 | 126015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26015 | 126016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26016 | 126017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26017 | 126018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26018 | 126019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26019 | 126020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26020 | 126021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26021 | 126022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26022 | 126023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26027 | 126028 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26041 | 126042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | X |  | X | X | X
Alarm status: Shelved | 26041 | 126042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure |  | X
Alarm status: Shelved | 26041 | 126042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | [5 empty] | X | X
Alarm status: Shelved | 26042 | 126043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | X |  | X | X | X
Alarm status: Shelved | 26042 | 126043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure |  | X
Alarm status: Shelved | 26042 | 126043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | [5 empty] | X | X
Alarm status: Shelved | 26043 | 126044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | X |  | X | X | X
Alarm status: Shelved | 26043 | 126044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure |  | X
Alarm status: Shelved | 26043 | 126044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | [5 empty] | X | X
Alarm status: Shelved | 26044 | 126045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | X |  | X | X | X
Alarm status: Shelved | 26044 | 126045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure |  | X
Alarm status: Shelved | 26044 | 126045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | [5 empty] | X | X
Alarm status: Shelved | 26045 | 126046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | X |  | X | X | X
Alarm status: Shelved | 26045 | 126046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure |  | X
Alarm status: Shelved | 26045 | 126046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | [5 empty] | X | X
Alarm status: Shelved | 26046 | 126047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | X |  | X | X | X
Alarm status: Shelved | 26046 | 126047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure |  | X
Alarm status: Shelved | 26046 | 126047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | [5 empty] | X | X
Alarm status: Shelved | 26047 | 126048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | X |  | X | X | X
Alarm status: Shelved | 26047 | 126048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) |  | X
Alarm status: Shelved | 26047 | 126048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | [5 empty] | X | X
Alarm status: Shelved | 26048 | 126049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | X |  | X | X | X
Alarm status: Shelved | 26048 | 126049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit |  | X
Alarm status: Shelved | 26048 | 126049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | [5 empty] | X | X
Alarm status: Shelved | 26049 | 126050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure |  |  |  | X
Alarm status: Shelved | 26049 | 126050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | [6 empty] | X
Alarm status: Shelved | 26050 | 126051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure |  |  |  | X
Alarm status: Shelved | 26050 | 126051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | [6 empty] | X
Alarm status: Shelved | 26051 | 126052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure |  |  |  | X
Alarm status: Shelved | 26051 | 126052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | [6 empty] | X
Alarm status: Shelved | 26052 | 126053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure |  |  |  | X
Alarm status: Shelved | 26052 | 126053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | [6 empty] | X
Alarm status: Shelved | 26053 | 126054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure |  |  |  | X
Alarm status: Shelved | 26053 | 126054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | [6 empty] | X
Alarm status: Shelved | 26054 | 126055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure |  |  |  | X
Alarm status: Shelved | 26054 | 126055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | [6 empty] | X
Alarm status: Shelved | 26055 | 126056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) |  |  |  | X
Alarm status: Shelved | 26055 | 126056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | [6 empty] | X
Alarm status: Shelved | 26056 | 126057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit |  |  |  | X
Alarm status: Shelved | 26056 | 126057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | [6 empty] | X
Alarm status: Shelved | 26060 | 126061 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error |  |  | X | X
Alarm status: Shelved | 26060 | 126061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | X |  |  |  | X | X | X
Alarm status: Shelved | 26060 | 126061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error |  | X
Alarm status: Shelved | 26061 | 126062 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | X |  | X | X | X
Alarm status: Shelved | 26061 | 126062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error |  | X
Alarm status: Shelved | 26061 | 126062 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | [5 empty] | X | X
Alarm status: Shelved | 26062 | 126063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26103 | 126104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information - Flags |  |  | X | X
Alarm status: Shelved | 26103 | 126104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information - Flags | X |  |  |  | X | X | X
Alarm status: Shelved | 26103 | 126104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information - Flags |  | X
Alarm status: Shelved | 26104 | 126105 | Parameters - Mains - Additional protections - Vector shift - Information - Flags |  |  | X | X
Alarm status: Shelved | 26104 | 126105 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | X |  |  |  | X | X | X
Alarm status: Shelved | 26104 | 126105 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags |  | X
Alarm status: Shelved | 26105 | 126106 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26105 | 126106 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags |  | X
Alarm status: Shelved | 26105 | 126106 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26106 | 126107 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26107 | 126108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26108 | 126109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26108 | 126109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags |  | X
Alarm status: Shelved | 26108 | 126109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26109 | 126110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26109 | 126110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags |  | X
Alarm status: Shelved | 26109 | 126110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26110 | 126111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26110 | 126111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags |  | X
Alarm status: Shelved | 26110 | 126111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26111 | 126112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26111 | 126112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags |  | X
Alarm status: Shelved | 26111 | 126112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26115 | 126116 | Protection set point out of range | X | X | X | X | X | X | X
Alarm status: Shelved | 26116 | 126117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | X |  | X | X | X
Alarm status: Shelved | 26117 | 126118 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | X |  | X | X | X
Alarm status: Shelved | 26118 | 126119 | Protection set point out of range (differential current) | X |  | X | X | X
Alarm status: Shelved | 26119 | 126120 | Parameters - Local - Mode - Not under remote control - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26121 | 126122 | Parameters - Local - Monitoring - System not OK - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26122 | 126123 | Configuration update delayed | X | X | X | X | X | X | X
Alarm status: Shelved | 26123 | 126124 | Critical process error | X | X | X | X | X | X | X
Alarm status: Shelved | 26124 | 126125 | Restore error | X | X | X | X | X | X | X
Alarm status: Shelved | 26125 | 126126 | SD-card format error | X | X | X | X | X | X | X
Alarm status: Shelved | 26126 | 126127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm status: Shelved | 26127 | 126128 | Fieldbus configuration exceeded maximum I/O configuration | X | X | X | X | X | X | X
Alarm status: Shelved | 26128 | 126129 | Parameters - Custom alarm - Custom alarm 0 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26129 | 126130 | Parameters - Custom alarm - Custom alarm 1 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26130 | 126131 | Parameters - Custom alarm - Custom alarm 2 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26131 | 126132 | Parameters - Custom alarm - Custom alarm 3 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26132 | 126133 | Parameters - Custom alarm - Custom alarm 4 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26133 | 126134 | Parameters - Custom alarm - Custom alarm 5 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26134 | 126135 | Parameters - Custom alarm - Custom alarm 6 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26135 | 126136 | Parameters - Custom alarm - Custom alarm 7 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26136 | 126137 | Parameters - Custom alarm - Custom alarm 8 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26137 | 126138 | Parameters - Custom alarm - Custom alarm 9 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26138 | 126139 | Parameters - Custom alarm - Custom alarm 10 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26139 | 126140 | Parameters - Custom alarm - Custom alarm 11 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26140 | 126141 | Parameters - Custom alarm - Custom alarm 12 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26141 | 126142 | Parameters - Custom alarm - Custom alarm 13 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26142 | 126143 | Parameters - Custom alarm - Custom alarm 14 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26143 | 126144 | Parameters - Custom alarm - Custom alarm 15 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26144 | 126145 | Parameters - Custom alarm - Custom alarm 16 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26145 | 126146 | Parameters - Custom alarm - Custom alarm 17 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26146 | 126147 | Parameters - Custom alarm - Custom alarm 18 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26147 | 126148 | Parameters - Custom alarm - Custom alarm 19 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26148 | 126149 | Parameters - Custom alarm - Custom alarm 20 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26149 | 126150 | Parameters - Custom alarm - Custom alarm 21 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26150 | 126151 | Parameters - Custom alarm - Custom alarm 22 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26151 | 126152 | Parameters - Custom alarm - Custom alarm 23 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26152 | 126153 | Parameters - Custom alarm - Custom alarm 24 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Shelved | 26153 | 126154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | X |  | X | X | X
Alarm status: Shelved | 26154 | 126155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | X |  | X | X | X
Alarm status: Shelved | 26163 | 126164 | Required hardware card(s) not found | X | X | X | X | X | X | X
Alarm status: Shelved | 26164 | 126165 | Software mismatch on hardware module(s) | X | X | X | X | X | X | X
Alarm status: Shelved | 26165 | 126166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break |  |  | X
Alarm status: Shelved | 26165 | 126166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | X |  |  |  | X | X
Alarm status: Shelved | 26165 | 126166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break |  | X
Alarm status: Shelved | 26166 | 126167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | X |  | X |  | X
Alarm status: Shelved | 26166 | 126167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break |  | X
Alarm status: Shelved | 26166 | 126167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | [5 empty] | X
Alarm status: Shelved | 26167 | 126168 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break |  |  | X
Alarm status: Shelved | 26167 | 126168 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | X |  |  |  | X | X
Alarm status: Shelved | 26167 | 126168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break |  | X
Alarm status: Shelved | 26168 | 126169 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break |  |  | X
Alarm status: Shelved | 26168 | 126169 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | X |  |  |  | X | X
Alarm status: Shelved | 26168 | 126169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break |  | X
Alarm status: Shelved | 26169 | 126170 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break |  |  | X
Alarm status: Shelved | 26169 | 126170 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | X |  |  |  | X | X
Alarm status: Shelved | 26169 | 126170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break |  | X
Alarm status: Shelved | 26170 | 126171 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | X |  | X |  | X
Alarm status: Shelved | 26170 | 126171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break |  | X
Alarm status: Shelved | 26170 | 126171 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | [5 empty] | X
Alarm status: Shelved | 26171 | 126172 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | X |  | X |  | X
Alarm status: Shelved | 26171 | 126172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break |  | X
Alarm status: Shelved | 26171 | 126172 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | [5 empty] | X
Alarm status: Shelved | 26172 | 126173 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | X |  | X |  | X
Alarm status: Shelved | 26172 | 126173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break |  | X
Alarm status: Shelved | 26172 | 126173 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | [5 empty] | X
Alarm status: Shelved | 26178 | 126179 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm |  |  | X | X |  | X | X
Alarm status: Shelved | 26179 | 126180 | Parameters - Engine - Emergency stop - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26179 | 126180 | Parameters - Busbar A - Emergency stop - Information - Flags |  | X
Alarm status: Shelved | 26179 | 126180 | Parameters - Mains - Emergency stop - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26180 | 126181 | Clock battery failure | X | X | X | X | X | X | X
Alarm status: Shelved | 26181 | 126182 | Controller temperature too high | X | X | X | X | X | X | X
Alarm status: Shelved | 26182 | 126183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26183 | 126184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | X | X | X | X | X | X | X
Alarm status: Shelved | 26184 | 126185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26185 | 126186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | X | X | X | X | X | X | X
Alarm status: Shelved | 26186 | 126187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26187 | 126188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | X | X | X | X | X | X | X
Alarm status: Shelved | 26188 | 126189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26189 | 126190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | X | X | X | X | X | X | X
Alarm status: Shelved | 26190 | 126191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26191 | 126192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Shelved | 26192 | 126193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26193 | 126194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Shelved | 26194 | 126195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26195 | 126196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Shelved | 26196 | 126197 | EIM3.1 4 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26197 | 126198 | EIM3.1 4 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Shelved | 26198 | 126199 | EIM3.1 5 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26199 | 126200 | EIM3.1 5 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Shelved | 26200 | 126201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Shelved | 26201 | 126202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Shelved | 26202 | 126203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Shelved | 26203 | 126204 | EIM3.1 4 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Shelved | 26204 | 126205 | EIM3.1 5 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Shelved | 26205 | 126206 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Shelved | 26206 | 126207 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Shelved | 26207 | 126208 | AC protections not running (differential current) | X |  | X | X | X
Alarm status: Shelved | 26208 | 126209 | AC data is missing (differential current) | X |  | X | X | X
Alarm status: Shelved | 26209 | 126210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26210 | 126211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Shelved | 26211 | 126212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26212 | 126213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Shelved | 26213 | 126214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26214 | 126215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Shelved | 26215 | 126216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26216 | 126217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | X | X | X | X | X | X | X
Alarm status: Shelved | 26217 | 126218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26218 | 126219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | X | X | X | X | X | X | X
Alarm status: Shelved | 26219 | 126220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26220 | 126221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | X | X | X | X | X | X | X
Alarm status: Shelved | 26221 | 126222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26222 | 126223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | X | X | X | X | X | X | X
Alarm status: Shelved | 26223 | 126224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26224 | 126225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | X | X | X | X | X | X | X
Alarm status: Shelved | 26225 | 126226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | X | X | X | X | X | X | X
Alarm status: Shelved | 26226 | 126227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | X | X | X | X | X | X | X
Alarm status: Shelved | 26228 | 126229 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26229 | 126230 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26231 | 126232 | Controller ID not configured | X | X | X | X | X | X | X
Alarm status: Shelved | 26236 | 126237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26237 | 126238 | Blackout detection mismatch | X |  | X | X | X
Alarm status: Shelved | 26240 | 126241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | X | X | X | X | X | X | X
Alarm status: Shelved | 26241 | 126242 | Parameters - Communication - NTP - NTP server 1 no response - Information - Flags - NTP server 1 is not responding | X | X | X | X | X | X | X
Alarm status: Shelved | 26242 | 126243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | X | X | X | X | X | X | X
Alarm status: Shelved | 26243 | 126244 | Parameters - Communication - NTP - NTP server 2 no response - Information - Flags - NTP server 2 is not responding | X | X | X | X | X | X | X
Alarm status: Shelved | 26244 | 126245 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26245 | 126246 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26246 | 126247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26247 | 126248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26296 | 126297 | Controller not part of system | X | X | X | X | X | X | X
Alarm status: Shelved | 26297 | 126298 | Different single-line configurations | X | X | X | X | X | X | X
Alarm status: Shelved | 26298 | 126299 | Single-line missing/none active | X | X | X | X | X | X | X
Alarm status: Shelved | 26299 | 126300 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26300 | 126301 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | X | X | X | X | X | X | X
Alarm status: Shelved | 26301 | 126302 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | X | X | X | X | X | X | X
Alarm status: Shelved | 26302 | 126303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26303 | 126304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26304 | 126305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26305 | 126306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26306 | 126307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26307 | 126308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26308 | 126309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26309 | 126310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26310 | 126311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26311 | 126312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26312 | 126313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26313 | 126314 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26314 | 126315 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26315 | 126316 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26316 | 126317 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26317 | 126318 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26318 | 126319 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26319 | 126320 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26320 | 126321 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26321 | 126322 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26322 | 126323 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26323 | 126324 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26324 | 126325 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26325 | 126326 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26326 | 126327 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26327 | 126328 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26328 | 126329 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26329 | 126330 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26330 | 126331 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26331 | 126332 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26332 | 126333 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26333 | 126334 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26334 | 126335 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26335 | 126336 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26336 | 126337 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26337 | 126338 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26338 | 126339 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26339 | 126340 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26340 | 126341 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26341 | 126342 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26342 | 126343 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26343 | 126344 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26344 | 126345 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26345 | 126346 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26346 | 126347 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26347 | 126348 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26348 | 126349 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26349 | 126350 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26350 | 126351 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26351 | 126352 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26352 | 126353 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26353 | 126354 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26354 | 126355 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26355 | 126356 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26356 | 126357 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26357 | 126358 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26358 | 126359 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26359 | 126360 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26360 | 126361 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26361 | 126362 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26362 | 126363 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26363 | 126364 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26364 | 126365 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26365 | 126366 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26366 | 126367 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26367 | 126368 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26368 | 126369 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26369 | 126370 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26370 | 126371 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26371 | 126372 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26372 | 126373 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26373 | 126374 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26374 | 126375 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26375 | 126376 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26376 | 126377 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26377 | 126378 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26378 | 126379 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26379 | 126380 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26380 | 126381 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26381 | 126382 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26382 | 126383 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26383 | 126384 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26384 | 126385 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26385 | 126386 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26386 | 126387 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26387 | 126388 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26388 | 126389 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26389 | 126390 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26390 | 126391 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26391 | 126392 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26392 | 126393 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26393 | 126394 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26394 | 126395 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26395 | 126396 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26396 | 126397 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26397 | 126398 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26398 | 126399 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26399 | 126400 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26400 | 126401 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26401 | 126402 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26402 | 126403 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26403 | 126404 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26404 | 126405 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26405 | 126406 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26406 | 126407 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26407 | 126408 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26408 | 126409 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26409 | 126410 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26410 | 126411 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26411 | 126412 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26412 | 126413 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26413 | 126414 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26414 | 126415 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26415 | 126416 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26416 | 126417 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26417 | 126418 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26418 | 126419 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26419 | 126420 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26420 | 126421 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26421 | 126422 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26422 | 126423 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26423 | 126424 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26424 | 126425 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26425 | 126426 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26426 | 126427 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26427 | 126428 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26428 | 126429 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26429 | 126430 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26430 | 126431 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26431 | 126432 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26432 | 126433 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26433 | 126434 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26434 | 126435 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26435 | 126436 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26436 | 126437 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26437 | 126438 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26438 | 126439 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26439 | 126440 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26440 | 126441 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26441 | 126442 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26442 | 126443 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26443 | 126444 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26444 | 126445 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26445 | 126446 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26446 | 126447 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26447 | 126448 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26448 | 126449 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26449 | 126450 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26450 | 126451 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26451 | 126452 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26452 | 126453 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26453 | 126454 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26454 | 126455 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26455 | 126456 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26456 | 126457 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26457 | 126458 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26458 | 126459 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26459 | 126460 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26460 | 126461 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26461 | 126462 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26462 | 126463 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26463 | 126464 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26464 | 126465 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26465 | 126466 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26466 | 126467 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26467 | 126468 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26468 | 126469 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26469 | 126470 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26470 | 126471 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26471 | 126472 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26472 | 126473 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26473 | 126474 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26474 | 126475 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26475 | 126476 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26476 | 126477 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26477 | 126478 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26478 | 126479 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26479 | 126480 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26480 | 126481 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26481 | 126482 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26482 | 126483 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26483 | 126484 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26484 | 126485 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26485 | 126486 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26486 | 126487 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26487 | 126488 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26488 | 126489 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26489 | 126490 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26490 | 126491 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26491 | 126492 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26492 | 126493 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26493 | 126494 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26494 | 126495 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26495 | 126496 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26496 | 126497 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26497 | 126498 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26498 | 126499 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26499 | 126500 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26500 | 126501 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26501 | 126502 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26502 | 126503 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26503 | 126504 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26504 | 126505 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26505 | 126506 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26506 | 126507 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26507 | 126508 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26508 | 126509 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26509 | 126510 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26510 | 126511 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26511 | 126512 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26512 | 126513 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26513 | 126514 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26514 | 126515 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26515 | 126516 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26516 | 126517 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26517 | 126518 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26518 | 126519 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26519 | 126520 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26520 | 126521 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26521 | 126522 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26522 | 126523 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26523 | 126524 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26524 | 126525 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26525 | 126526 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26526 | 126527 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26527 | 126528 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26528 | 126529 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26529 | 126530 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26530 | 126531 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26531 | 126532 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26532 | 126533 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26533 | 126534 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26534 | 126535 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26535 | 126536 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26536 | 126537 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26537 | 126538 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26538 | 126539 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26539 | 126540 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26540 | 126541 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26541 | 126542 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26542 | 126543 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26543 | 126544 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26544 | 126545 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26545 | 126546 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26546 | 126547 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26547 | 126548 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26548 | 126549 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26549 | 126550 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26550 | 126551 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26551 | 126552 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26552 | 126553 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26553 | 126554 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26554 | 126555 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26555 | 126556 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26556 | 126557 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26557 | 126558 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26558 | 126559 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26559 | 126560 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26560 | 126561 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26561 | 126562 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26562 | 126563 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Shelved | 26565 | 126566 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | X | X | X | X | X | X | X
Alarm status: Shelved | 26566 | 126567 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | X |  | X | X | X
Alarm status: Shelved | 26567 | 126568 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26568 | 126569 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26569 | 126570 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26570 | 126571 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26571 | 126572 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26572 | 126573 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26573 | 126574 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26574 | 126575 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26575 | 126576 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26576 | 126577 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26577 | 126578 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26578 | 126579 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26579 | 126580 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26580 | 126581 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26581 | 126582 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26582 | 126583 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26583 | 126584 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26584 | 126585 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26585 | 126586 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26586 | 126587 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26587 | 126588 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26588 | 126589 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26589 | 126590 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26590 | 126591 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26591 | 126592 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26592 | 126593 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26593 | 126594 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26594 | 126595 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26595 | 126596 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26596 | 126597 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26597 | 126598 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26598 | 126599 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26599 | 126600 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26600 | 126601 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26601 | 126602 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26602 | 126603 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26603 | 126604 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26604 | 126605 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26605 | 126606 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26606 | 126607 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26607 | 126608 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26608 | 126609 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26609 | 126610 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26610 | 126611 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26611 | 126612 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26612 | 126613 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26613 | 126614 | DAVR unsupported AC configuration | X |  | X | X | X
Alarm status: Shelved | 26614 | 126615 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | X |  | X | X | X
Alarm status: Shelved | 26615 | 126616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | X |  | X | X | X
Alarm status: Shelved | 26615 | 126616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 |  | X
Alarm status: Shelved | 26615 | 126616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | [5 empty] | X | X
Alarm status: Shelved | 26616 | 126617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | X |  | X | X | X
Alarm status: Shelved | 26616 | 126617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 |  | X
Alarm status: Shelved | 26616 | 126617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | [5 empty] | X | X
Alarm status: Shelved | 26617 | 126618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | X |  | X | X | X
Alarm status: Shelved | 26617 | 126618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 |  | X
Alarm status: Shelved | 26617 | 126618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | [5 empty] | X | X
Alarm status: Shelved | 26618 | 126619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | X |  | X | X | X
Alarm status: Shelved | 26618 | 126619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 |  | X
Alarm status: Shelved | 26618 | 126619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | [5 empty] | X | X
Alarm status: Shelved | 26619 | 126620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | X |  | X | X | X
Alarm status: Shelved | 26619 | 126620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 |  | X
Alarm status: Shelved | 26619 | 126620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | [5 empty] | X | X
Alarm status: Shelved | 26620 | 126621 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | X |  | X | X | X
Alarm status: Shelved | 26620 | 126621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance |  | X
Alarm status: Shelved | 26620 | 126621 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | [5 empty] | X | X
Alarm status: Shelved | 26621 | 126622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | X |  | X | X | X
Alarm status: Shelved | 26621 | 126622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage |  | X
Alarm status: Shelved | 26621 | 126622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | [5 empty] | X | X
Alarm status: Shelved | 26622 | 126623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | X |  | X | X | X
Alarm status: Shelved | 26622 | 126623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage |  | X
Alarm status: Shelved | 26622 | 126623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | [5 empty] | X | X
Alarm status: Shelved | 26623 | 126624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | X |  | X | X | X
Alarm status: Shelved | 26623 | 126624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage |  | X
Alarm status: Shelved | 26623 | 126624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | [5 empty] | X | X
Alarm status: Shelved | 26624 | 126625 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26624 | 126625 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags |  | X
Alarm status: Shelved | 26624 | 126625 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26625 | 126626 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26625 | 126626 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags |  | X
Alarm status: Shelved | 26625 | 126626 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26626 | 126627 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26626 | 126627 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags |  | X
Alarm status: Shelved | 26626 | 126627 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26627 | 126628 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26627 | 126628 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags |  | X
Alarm status: Shelved | 26627 | 126628 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26628 | 126629 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26628 | 126629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags |  | X
Alarm status: Shelved | 26628 | 126629 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26629 | 126630 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26629 | 126630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags |  | X
Alarm status: Shelved | 26629 | 126630 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26630 | 126631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26630 | 126631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags |  | X
Alarm status: Shelved | 26630 | 126631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26631 | 126632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26631 | 126632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags |  | X
Alarm status: Shelved | 26631 | 126632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26632 | 126633 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26632 | 126633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags |  | X
Alarm status: Shelved | 26632 | 126633 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26633 | 126634 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26633 | 126634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags |  | X
Alarm status: Shelved | 26633 | 126634 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26634 | 126635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags |  | X
Alarm status: Shelved | 26635 | 126636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags |  | X
Alarm status: Shelved | 26636 | 126637 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26636 | 126637 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags |  | X
Alarm status: Shelved | 26636 | 126637 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26637 | 126638 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26637 | 126638 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags |  | X
Alarm status: Shelved | 26637 | 126638 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26638 | 126639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | X |  | X | X | X
Alarm status: Shelved | 26638 | 126639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 |  | X
Alarm status: Shelved | 26638 | 126639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | [5 empty] | X | X
Alarm status: Shelved | 26639 | 126640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | X |  | X | X | X
Alarm status: Shelved | 26639 | 126640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 |  | X
Alarm status: Shelved | 26639 | 126640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | [5 empty] | X | X
Alarm status: Shelved | 26640 | 126641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | X |  | X | X | X
Alarm status: Shelved | 26640 | 126641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 |  | X
Alarm status: Shelved | 26640 | 126641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | [5 empty] | X | X
Alarm status: Shelved | 26641 | 126642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | X |  | X | X | X
Alarm status: Shelved | 26641 | 126642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 |  | X
Alarm status: Shelved | 26641 | 126642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | [5 empty] | X | X
Alarm status: Shelved | 26642 | 126643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | X |  | X | X | X
Alarm status: Shelved | 26642 | 126643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 |  | X
Alarm status: Shelved | 26642 | 126643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | [5 empty] | X | X
Alarm status: Shelved | 26643 | 126644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | X |  | X | X | X
Alarm status: Shelved | 26643 | 126644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 |  | X
Alarm status: Shelved | 26643 | 126644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | [5 empty] | X | X
Alarm status: Shelved | 26644 | 126645 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26644 | 126645 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags |  | X
Alarm status: Shelved | 26644 | 126645 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26645 | 126646 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26645 | 126646 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags |  | X
Alarm status: Shelved | 26645 | 126646 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26646 | 126647 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26646 | 126647 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags |  | X
Alarm status: Shelved | 26646 | 126647 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26647 | 126648 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26647 | 126648 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags |  | X
Alarm status: Shelved | 26647 | 126648 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26648 | 126649 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26648 | 126649 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags |  | X
Alarm status: Shelved | 26648 | 126649 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26649 | 126650 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26649 | 126650 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags |  | X
Alarm status: Shelved | 26649 | 126650 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26650 | 126651 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26650 | 126651 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags |  | X
Alarm status: Shelved | 26650 | 126651 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26651 | 126652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26651 | 126652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags |  | X
Alarm status: Shelved | 26651 | 126652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26652 | 126653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26652 | 126653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags |  | X
Alarm status: Shelved | 26652 | 126653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26653 | 126654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26653 | 126654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags |  | X
Alarm status: Shelved | 26653 | 126654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26654 | 126655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26654 | 126655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags |  | X
Alarm status: Shelved | 26654 | 126655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | [5 empty] | X | X
Alarm status: Shelved | 26655 | 126656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 |  |  | X | X
Alarm status: Shelved | 26655 | 126656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | X |  |  |  | X | X | X
Alarm status: Shelved | 26655 | 126656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 |  | X
Alarm status: Shelved | 26656 | 126657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 |  |  | X | X
Alarm status: Shelved | 26656 | 126657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | X |  |  |  | X | X | X
Alarm status: Shelved | 26656 | 126657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 |  | X
Alarm status: Shelved | 26657 | 126658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 |  |  | X | X
Alarm status: Shelved | 26657 | 126658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | X |  |  |  | X | X | X
Alarm status: Shelved | 26657 | 126658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 |  | X
Alarm status: Shelved | 26658 | 126659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 |  |  | X | X
Alarm status: Shelved | 26658 | 126659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | X |  |  |  | X | X | X
Alarm status: Shelved | 26658 | 126659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 |  | X
Alarm status: Shelved | 26659 | 126660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 |  |  | X | X
Alarm status: Shelved | 26659 | 126660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | X |  |  |  | X | X | X
Alarm status: Shelved | 26659 | 126660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 |  | X
Alarm status: Shelved | 26660 | 126661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 |  |  | X | X
Alarm status: Shelved | 26660 | 126661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | X |  |  |  | X | X | X
Alarm status: Shelved | 26660 | 126661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 |  | X
Alarm status: Shelved | 26661 | 126662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 |  |  | X | X
Alarm status: Shelved | 26661 | 126662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | X |  |  |  | X | X | X
Alarm status: Shelved | 26661 | 126662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 |  | X
Alarm status: Shelved | 26662 | 126663 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance |  |  | X | X
Alarm status: Shelved | 26662 | 126663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | X |  |  |  | X | X | X
Alarm status: Shelved | 26662 | 126663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance |  | X
Alarm status: Shelved | 26663 | 126664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 |  |  | X | X
Alarm status: Shelved | 26663 | 126664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | X |  |  |  | X | X | X
Alarm status: Shelved | 26663 | 126664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 |  | X
Alarm status: Shelved | 26664 | 126665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 |  |  | X | X
Alarm status: Shelved | 26664 | 126665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | X |  |  |  | X | X | X
Alarm status: Shelved | 26664 | 126665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 |  | X
Alarm status: Shelved | 26665 | 126666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 |  |  | X | X
Alarm status: Shelved | 26665 | 126666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | X |  |  |  | X | X | X
Alarm status: Shelved | 26665 | 126666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 |  | X
Alarm status: Shelved | 26666 | 126667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 |  |  | X | X
Alarm status: Shelved | 26666 | 126667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | X |  |  |  | X | X | X
Alarm status: Shelved | 26666 | 126667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 |  | X
Alarm status: Shelved | 26667 | 126668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 |  |  | X | X
Alarm status: Shelved | 26667 | 126668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | X |  |  |  | X | X | X
Alarm status: Shelved | 26667 | 126668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 |  | X
Alarm status: Shelved | 26668 | 126669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 |  |  | X | X
Alarm status: Shelved | 26668 | 126669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | X |  |  |  | X | X | X
Alarm status: Shelved | 26668 | 126669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 |  | X
Alarm status: Shelved | 26669 | 126670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 |  |  | X | X
Alarm status: Shelved | 26669 | 126670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | X |  |  |  | X | X | X
Alarm status: Shelved | 26669 | 126670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 |  | X
Alarm status: Shelved | 26670 | 126671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage |  |  | X | X
Alarm status: Shelved | 26670 | 126671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | X |  |  |  | X | X | X
Alarm status: Shelved | 26670 | 126671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage |  | X
Alarm status: Shelved | 26671 | 126672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage |  |  | X | X
Alarm status: Shelved | 26671 | 126672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | X |  |  |  | X | X | X
Alarm status: Shelved | 26671 | 126672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage |  | X
Alarm status: Shelved | 26672 | 126673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage |  |  | X | X
Alarm status: Shelved | 26672 | 126673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | X |  |  |  | X | X | X
Alarm status: Shelved | 26672 | 126673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage |  | X
Alarm status: Shelved | 26717 | 126718 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 1 | X |  | X | X | X
Alarm status: Shelved | 26718 | 126719 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 2 | X |  | X | X | X
Alarm status: Shelved | 26719 | 126720 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 3 | X |  | X | X | X
Alarm status: Shelved | 26720 | 126721 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 4 | X |  | X | X | X
Alarm status: Shelved | 26721 | 126722 | External MB open failure | X | X | X | X | X | X | X
Alarm status: Shelved | 26722 | 126723 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26723 | 126724 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26724 | 126725 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26725 | 126726 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26726 | 126727 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - Flags | X |  | X | X | X
Alarm status: Shelved | 26727 | 126728 | Parameters - Breakers - Close before excitation - CBE failure - Information - Flags - Close before excitation failure | X |  | X | X | X
Alarm status: Shelved | 26728 | 126729 | Load too high | X | X | X | X | X | X | X
Alarm status: Shelved | 26729 | 126730 | ID to run configuration failure | [5 empty] | X | X
Alarm status: Shelved | 26731 | 126732 | Parameters - System - Monitoring - Missing any genset controller - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26732 | 126733 | Parameters - System - Monitoring - Missing any mains controller - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26733 | 126734 | Parameters - System - Monitoring - Missing any bustie controller - Information - Flags - Missing any bus tie controller | X | X | X | X | X | X | X
Alarm status: Shelved | 26734 | 126735 | Can ID not available | X | X | X | X | X | X | X
Alarm status: Shelved | 26735 | 126736 | Duplicated CAN IDs | X | X | X | X | X | X | X
Alarm status: Shelved | 26736 | 126737 | Parameters - Local power management - Alarms - Busbar blocked - Information - Flags - Busbar blocked due to position failure | X |  | X | X | X | X | X
Alarm status: Shelved | 26737 | 126738 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Flags - Busbar A blocked due to position failure |  | X
Alarm status: Shelved | 26738 | 126739 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Flags - Busbar B blocked due to position failure |  | X
Alarm status: Shelved | 26739 | 126740 | Parameters - System - Monitoring - BTB 33 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26740 | 126741 | Parameters - System - Monitoring - BTB 34 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26741 | 126742 | Parameters - System - Monitoring - BTB 35 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26742 | 126743 | Parameters - System - Monitoring - BTB 36 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26743 | 126744 | Parameters - System - Monitoring - BTB 37 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26744 | 126745 | Parameters - System - Monitoring - BTB 38 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26745 | 126746 | Parameters - System - Monitoring - BTB 39 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26746 | 126747 | Parameters - System - Monitoring - BTB 40 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26747 | 126748 | Primary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm status: Shelved | 26748 | 126749 | Primary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm status: Shelved | 26749 | 126750 | Primary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm status: Shelved | 26750 | 126751 | Primary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm status: Shelved | 26751 | 126752 | Primary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm status: Shelved | 26752 | 126753 | Primary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm status: Shelved | 26753 | 126754 | Primary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm status: Shelved | 26754 | 126755 | Primary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm status: Shelved | 26755 | 126756 | Primary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm status: Shelved | 26756 | 126757 | Primary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm status: Shelved | 26757 | 126758 | Primary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm status: Shelved | 26758 | 126759 | Primary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm status: Shelved | 26759 | 126760 | Primary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm status: Shelved | 26760 | 126761 | Primary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm status: Shelved | 26761 | 126762 | Primary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm status: Shelved | 26762 | 126763 | Primary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm status: Shelved | 26763 | 126764 | Primary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm status: Shelved | 26764 | 126765 | Primary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm status: Shelved | 26765 | 126766 | Primary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm status: Shelved | 26766 | 126767 | Primary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm status: Shelved | 26767 | 126768 | Primary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm status: Shelved | 26768 | 126769 | Primary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm status: Shelved | 26769 | 126770 | Primary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm status: Shelved | 26770 | 126771 | Primary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm status: Shelved | 26771 | 126772 | Primary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm status: Shelved | 26772 | 126773 | Primary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm status: Shelved | 26773 | 126774 | Primary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm status: Shelved | 26774 | 126775 | Primary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm status: Shelved | 26775 | 126776 | Primary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm status: Shelved | 26776 | 126777 | Primary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm status: Shelved | 26777 | 126778 | Primary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm status: Shelved | 26778 | 126779 | Primary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm status: Shelved | 26779 | 126780 | Primary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm status: Shelved | 26780 | 126781 | Primary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm status: Shelved | 26781 | 126782 | Primary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm status: Shelved | 26782 | 126783 | Primary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm status: Shelved | 26783 | 126784 | Primary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm status: Shelved | 26784 | 126785 | Primary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm status: Shelved | 26785 | 126786 | Primary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm status: Shelved | 26786 | 126787 | Primary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm status: Shelved | 26787 | 126788 | Secondary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm status: Shelved | 26788 | 126789 | Secondary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm status: Shelved | 26789 | 126790 | Secondary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm status: Shelved | 26790 | 126791 | Secondary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm status: Shelved | 26791 | 126792 | Secondary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm status: Shelved | 26792 | 126793 | Secondary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm status: Shelved | 26793 | 126794 | Secondary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm status: Shelved | 26794 | 126795 | Secondary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm status: Shelved | 26795 | 126796 | Secondary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm status: Shelved | 26796 | 126797 | Secondary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm status: Shelved | 26797 | 126798 | Secondary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm status: Shelved | 26798 | 126799 | Secondary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm status: Shelved | 26799 | 126800 | Secondary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm status: Shelved | 26800 | 126801 | Secondary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm status: Shelved | 26801 | 126802 | Secondary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm status: Shelved | 26802 | 126803 | Secondary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm status: Shelved | 26803 | 126804 | Secondary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm status: Shelved | 26804 | 126805 | Secondary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm status: Shelved | 26805 | 126806 | Secondary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm status: Shelved | 26806 | 126807 | Secondary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm status: Shelved | 26807 | 126808 | Secondary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm status: Shelved | 26808 | 126809 | Secondary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm status: Shelved | 26809 | 126810 | Secondary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm status: Shelved | 26810 | 126811 | Secondary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm status: Shelved | 26811 | 126812 | Secondary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm status: Shelved | 26812 | 126813 | Secondary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm status: Shelved | 26813 | 126814 | Secondary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm status: Shelved | 26814 | 126815 | Secondary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm status: Shelved | 26815 | 126816 | Secondary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm status: Shelved | 26816 | 126817 | Secondary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm status: Shelved | 26817 | 126818 | Secondary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm status: Shelved | 26818 | 126819 | Secondary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm status: Shelved | 26819 | 126820 | Secondary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm status: Shelved | 26820 | 126821 | Secondary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm status: Shelved | 26821 | 126822 | Secondary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm status: Shelved | 26822 | 126823 | Secondary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm status: Shelved | 26823 | 126824 | Secondary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm status: Shelved | 26824 | 126825 | Secondary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm status: Shelved | 26825 | 126826 | Secondary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm status: Shelved | 26826 | 126827 | Secondary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm status: Shelved | 26827 | 126828 | Priority error | X | X | X | X | X | X | X
Alarm status: Shelved | 26828 | 126829 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - Flags - NEL 1 over-current | X |  | X | X | X | X | X
Alarm status: Shelved | 26829 | 126830 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - Flags - NEL 1 under-frequency | X |  | X | X | X | X | X
Alarm status: Shelved | 26830 | 126831 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - Flags - NEL 1 overload 1 | X |  | X | X | X | X | X
Alarm status: Shelved | 26831 | 126832 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - Flags - NEL 1 overload 2 | X |  | X | X | X | X | X
Alarm status: Shelved | 26832 | 126833 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - Flags - NEL 1 reactive overload | X |  | X | X | X | X | X
Alarm status: Shelved | 26833 | 126834 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - Flags - NEL 2 over-current | X |  | X | X | X | X | X
Alarm status: Shelved | 26834 | 126835 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - Flags - NEL 2 under-frequency | X |  | X | X | X | X | X
Alarm status: Shelved | 26835 | 126836 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - Flags - NEL 2 overload 1 | X |  | X | X | X | X | X
Alarm status: Shelved | 26836 | 126837 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - Flags - NEL 2 overload 2 | X |  | X | X | X | X | X
Alarm status: Shelved | 26837 | 126838 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - Flags - NEL 2 reactive overload | X |  | X | X | X | X | X
Alarm status: Shelved | 26838 | 126839 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - Flags - NEL 3 over-current | X |  | X | X | X | X | X
Alarm status: Shelved | 26839 | 126840 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - Flags - NEL 3 under-frequency | X |  | X | X | X | X | X
Alarm status: Shelved | 26840 | 126841 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - Flags - NEL 3 overload 1 | X |  | X | X | X | X | X
Alarm status: Shelved | 26841 | 126842 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - Flags - NEL 3 overload 2 | X |  | X | X | X | X | X
Alarm status: Shelved | 26842 | 126843 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - Flags - NEL 3 reactive overload | X |  | X | X | X | X | X
Alarm status: Shelved | 26843 | 126844 | Parameters - System - Monitoring - Single-line hazard - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26844 | 126845 | ID not present | X | X | X | X | X | X | X
Alarm status: Shelved | 26845 | 126846 | Unsupported application | X | X | X | X | X | X | X
Alarm status: Shelved | 26846 | 126847 | Application internal CAN protocol conflict | X | X | X | X | X | X | X
Alarm status: Shelved | 26847 | 126848 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Flags - Section P> | X | X | X | X | X | X | X
Alarm status: Shelved | 26848 | 126849 | Dry mode: Voltage level unexpected | X |  | X | X | X
Alarm status: Shelved | 26849 | 126850 | Invalid DAVR configuration | X |  | X | X | X
Alarm status: Shelved | 26850 | 126851 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26852 | 126853 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26854 | 126855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | X |  | X | X | X
Alarm status: Shelved | 26854 | 126855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch |  | X
Alarm status: Shelved | 26854 | 126855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | [5 empty] | X | X
Alarm status: Shelved | 26855 | 126856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch |  |  |  | X
Alarm status: Shelved | 26855 | 126856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | [6 empty] | X
Alarm status: Shelved | 26857 | 126858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26858 | 126859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26859 | 126860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26860 | 126861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26861 | 126862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Shelved | 26862 | 126863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Shelved | 26863 | 126864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Shelved | 26864 | 126865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Shelved | 26865 | 126866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Shelved | 26866 | 126867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Shelved | 26867 | 126868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Shelved | 26868 | 126869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Shelved | 26869 | 126870 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Shelved | 26870 | 126871 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Shelved | 26871 | 126872 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Shelved | 26872 | 126873 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Shelved | 26873 | 126874 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Shelved | 26874 | 126875 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Shelved | 26875 | 126876 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Shelved | 26876 | 126877 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Shelved | 26877 | 126878 | Live voltage detected | X | X | X | X | X | X | X
Alarm status: Shelved | 26878 | 126879 | Internal issue detected. A restart is required soon! | X | X | X | X | X | X | X
Alarm status: Shelved | 26879 | 126880 | Parameters - System - Monitoring - Missing controllers - Information - Flags | X | X | X | X | X | X | X
Alarm status: Shelved | 26880 | 126881 | Card issue detected | X | X | X | X | X | X | X
Alarm status: Shelved | 26881 | 126882 | Card configuration failed | X | X | X | X | X | X | X
Alarm status: Shelved | 26882 | 126883 | Unknown traffic on DEIF network | X | X | X | X | X | X | X
Alarm status: Shelved | 26883 | 126884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Shelved | 26884 | 126885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Shelved | 26885 | 126886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Shelved | 26886 | 126887 | Local IO service error | X | X | X | X | X | X | X
Alarm status: Shelved | 26887 | 126888 | App logging failure | X | X | X | X | X | X | X
Alarm status: Shelved | 26888 | 126889 | Event logging failure | X | X | X | X | X | X | X
Alarm status: Shelved | 26889 | 126890 | Licence error | X | X | X | X | X | X | X
Alarm status: Shelved | 26890 | 126891 | Brightness is dimmed according to temperature | X | X | X | X | X | X | X
Alarm status: Shelved | 26891 | 126892 | Parameters - Grid code - Mains sync inhibit - Information - Flags |  |  | X | X
Alarm status: Shelved | 26892 | 126893 | Parameters - Grid code - Capability curve - Import protection - Information - Flags - Power import capability curve protection |  |  | X | X
Alarm status: Shelved | 26893 | 126894 | Parameters - Grid code - Capability curve - Export protection - Information - Flags - Power export capability curve protection |  |  | X | X
Alarm status: Shelved | 26894 | 126895 | Hardware is not compatible based on module versions | X | X | X | X | X | X | X
Alarm status: Inhibited | 28000 | 128001 | Application initialisation error | X | X | X | X | X | X | X
Alarm status: Inhibited | 28001 | 128002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm status: Inhibited | 28002 | 128003 | Preliminary software | X | X | X | X | X | X | X
Alarm status: Inhibited | 28003 | 128004 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28004 | 128005 | Parameters - Engine - Start sequence - Start failure - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28005 | 128006 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28006 | 128007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28007 | 128008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28008 | 128009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28009 | 128010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28010 | 128011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | X |  | X | X | X
Alarm status: Inhibited | 28011 | 128012 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28013 | 128014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28014 | 128015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28015 | 128016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28016 | 128017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28017 | 128018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28018 | 128019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28019 | 128020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28020 | 128021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28021 | 128022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28022 | 128023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28027 | 128028 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28041 | 128042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | X |  | X | X | X
Alarm status: Inhibited | 28041 | 128042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure |  | X
Alarm status: Inhibited | 28041 | 128042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | [5 empty] | X | X
Alarm status: Inhibited | 28042 | 128043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | X |  | X | X | X
Alarm status: Inhibited | 28042 | 128043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure |  | X
Alarm status: Inhibited | 28042 | 128043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | [5 empty] | X | X
Alarm status: Inhibited | 28043 | 128044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | X |  | X | X | X
Alarm status: Inhibited | 28043 | 128044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure |  | X
Alarm status: Inhibited | 28043 | 128044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | [5 empty] | X | X
Alarm status: Inhibited | 28044 | 128045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | X |  | X | X | X
Alarm status: Inhibited | 28044 | 128045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure |  | X
Alarm status: Inhibited | 28044 | 128045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | [5 empty] | X | X
Alarm status: Inhibited | 28045 | 128046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | X |  | X | X | X
Alarm status: Inhibited | 28045 | 128046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure |  | X
Alarm status: Inhibited | 28045 | 128046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | [5 empty] | X | X
Alarm status: Inhibited | 28046 | 128047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | X |  | X | X | X
Alarm status: Inhibited | 28046 | 128047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure |  | X
Alarm status: Inhibited | 28046 | 128047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | [5 empty] | X | X
Alarm status: Inhibited | 28047 | 128048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | X |  | X | X | X
Alarm status: Inhibited | 28047 | 128048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) |  | X
Alarm status: Inhibited | 28047 | 128048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | [5 empty] | X | X
Alarm status: Inhibited | 28048 | 128049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | X |  | X | X | X
Alarm status: Inhibited | 28048 | 128049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit |  | X
Alarm status: Inhibited | 28048 | 128049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | [5 empty] | X | X
Alarm status: Inhibited | 28049 | 128050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure |  |  |  | X
Alarm status: Inhibited | 28049 | 128050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | [6 empty] | X
Alarm status: Inhibited | 28050 | 128051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure |  |  |  | X
Alarm status: Inhibited | 28050 | 128051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | [6 empty] | X
Alarm status: Inhibited | 28051 | 128052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure |  |  |  | X
Alarm status: Inhibited | 28051 | 128052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | [6 empty] | X
Alarm status: Inhibited | 28052 | 128053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure |  |  |  | X
Alarm status: Inhibited | 28052 | 128053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | [6 empty] | X
Alarm status: Inhibited | 28053 | 128054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure |  |  |  | X
Alarm status: Inhibited | 28053 | 128054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | [6 empty] | X
Alarm status: Inhibited | 28054 | 128055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure |  |  |  | X
Alarm status: Inhibited | 28054 | 128055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | [6 empty] | X
Alarm status: Inhibited | 28055 | 128056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) |  |  |  | X
Alarm status: Inhibited | 28055 | 128056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | [6 empty] | X
Alarm status: Inhibited | 28056 | 128057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit |  |  |  | X
Alarm status: Inhibited | 28056 | 128057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | [6 empty] | X
Alarm status: Inhibited | 28060 | 128061 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error |  |  | X | X
Alarm status: Inhibited | 28060 | 128061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | X |  |  |  | X | X | X
Alarm status: Inhibited | 28060 | 128061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error |  | X
Alarm status: Inhibited | 28061 | 128062 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | X |  | X | X | X
Alarm status: Inhibited | 28061 | 128062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error |  | X
Alarm status: Inhibited | 28061 | 128062 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | [5 empty] | X | X
Alarm status: Inhibited | 28062 | 128063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28103 | 128104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information - Flags |  |  | X | X
Alarm status: Inhibited | 28103 | 128104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information - Flags | X |  |  |  | X | X | X
Alarm status: Inhibited | 28103 | 128104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information - Flags |  | X
Alarm status: Inhibited | 28104 | 128105 | Parameters - Mains - Additional protections - Vector shift - Information - Flags |  |  | X | X
Alarm status: Inhibited | 28104 | 128105 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | X |  |  |  | X | X | X
Alarm status: Inhibited | 28104 | 128105 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags |  | X
Alarm status: Inhibited | 28105 | 128106 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28105 | 128106 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags |  | X
Alarm status: Inhibited | 28105 | 128106 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28106 | 128107 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28107 | 128108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28108 | 128109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28108 | 128109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags |  | X
Alarm status: Inhibited | 28108 | 128109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28109 | 128110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28109 | 128110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags |  | X
Alarm status: Inhibited | 28109 | 128110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28110 | 128111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28110 | 128111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags |  | X
Alarm status: Inhibited | 28110 | 128111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28111 | 128112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28111 | 128112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags |  | X
Alarm status: Inhibited | 28111 | 128112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28115 | 128116 | Protection set point out of range | X | X | X | X | X | X | X
Alarm status: Inhibited | 28116 | 128117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | X |  | X | X | X
Alarm status: Inhibited | 28117 | 128118 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | X |  | X | X | X
Alarm status: Inhibited | 28118 | 128119 | Protection set point out of range (differential current) | X |  | X | X | X
Alarm status: Inhibited | 28119 | 128120 | Parameters - Local - Mode - Not under remote control - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28121 | 128122 | Parameters - Local - Monitoring - System not OK - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28122 | 128123 | Configuration update delayed | X | X | X | X | X | X | X
Alarm status: Inhibited | 28123 | 128124 | Critical process error | X | X | X | X | X | X | X
Alarm status: Inhibited | 28124 | 128125 | Restore error | X | X | X | X | X | X | X
Alarm status: Inhibited | 28125 | 128126 | SD-card format error | X | X | X | X | X | X | X
Alarm status: Inhibited | 28126 | 128127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm status: Inhibited | 28127 | 128128 | Fieldbus configuration exceeded maximum I/O configuration | X | X | X | X | X | X | X
Alarm status: Inhibited | 28128 | 128129 | Parameters - Custom alarm - Custom alarm 0 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28129 | 128130 | Parameters - Custom alarm - Custom alarm 1 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28130 | 128131 | Parameters - Custom alarm - Custom alarm 2 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28131 | 128132 | Parameters - Custom alarm - Custom alarm 3 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28132 | 128133 | Parameters - Custom alarm - Custom alarm 4 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28133 | 128134 | Parameters - Custom alarm - Custom alarm 5 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28134 | 128135 | Parameters - Custom alarm - Custom alarm 6 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28135 | 128136 | Parameters - Custom alarm - Custom alarm 7 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28136 | 128137 | Parameters - Custom alarm - Custom alarm 8 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28137 | 128138 | Parameters - Custom alarm - Custom alarm 9 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28138 | 128139 | Parameters - Custom alarm - Custom alarm 10 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28139 | 128140 | Parameters - Custom alarm - Custom alarm 11 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28140 | 128141 | Parameters - Custom alarm - Custom alarm 12 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28141 | 128142 | Parameters - Custom alarm - Custom alarm 13 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28142 | 128143 | Parameters - Custom alarm - Custom alarm 14 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28143 | 128144 | Parameters - Custom alarm - Custom alarm 15 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28144 | 128145 | Parameters - Custom alarm - Custom alarm 16 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28145 | 128146 | Parameters - Custom alarm - Custom alarm 17 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28146 | 128147 | Parameters - Custom alarm - Custom alarm 18 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28147 | 128148 | Parameters - Custom alarm - Custom alarm 19 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28148 | 128149 | Parameters - Custom alarm - Custom alarm 20 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28149 | 128150 | Parameters - Custom alarm - Custom alarm 21 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28150 | 128151 | Parameters - Custom alarm - Custom alarm 22 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28151 | 128152 | Parameters - Custom alarm - Custom alarm 23 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28152 | 128153 | Parameters - Custom alarm - Custom alarm 24 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Inhibited | 28153 | 128154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | X |  | X | X | X
Alarm status: Inhibited | 28154 | 128155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | X |  | X | X | X
Alarm status: Inhibited | 28163 | 128164 | Required hardware card(s) not found | X | X | X | X | X | X | X
Alarm status: Inhibited | 28164 | 128165 | Software mismatch on hardware module(s) | X | X | X | X | X | X | X
Alarm status: Inhibited | 28165 | 128166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break |  |  | X
Alarm status: Inhibited | 28165 | 128166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | X |  |  |  | X | X
Alarm status: Inhibited | 28165 | 128166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break |  | X
Alarm status: Inhibited | 28166 | 128167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | X |  | X |  | X
Alarm status: Inhibited | 28166 | 128167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break |  | X
Alarm status: Inhibited | 28166 | 128167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | [5 empty] | X
Alarm status: Inhibited | 28167 | 128168 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break |  |  | X
Alarm status: Inhibited | 28167 | 128168 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | X |  |  |  | X | X
Alarm status: Inhibited | 28167 | 128168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break |  | X
Alarm status: Inhibited | 28168 | 128169 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break |  |  | X
Alarm status: Inhibited | 28168 | 128169 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | X |  |  |  | X | X
Alarm status: Inhibited | 28168 | 128169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break |  | X
Alarm status: Inhibited | 28169 | 128170 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break |  |  | X
Alarm status: Inhibited | 28169 | 128170 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | X |  |  |  | X | X
Alarm status: Inhibited | 28169 | 128170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break |  | X
Alarm status: Inhibited | 28170 | 128171 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | X |  | X |  | X
Alarm status: Inhibited | 28170 | 128171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break |  | X
Alarm status: Inhibited | 28170 | 128171 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | [5 empty] | X
Alarm status: Inhibited | 28171 | 128172 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | X |  | X |  | X
Alarm status: Inhibited | 28171 | 128172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break |  | X
Alarm status: Inhibited | 28171 | 128172 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | [5 empty] | X
Alarm status: Inhibited | 28172 | 128173 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | X |  | X |  | X
Alarm status: Inhibited | 28172 | 128173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break |  | X
Alarm status: Inhibited | 28172 | 128173 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | [5 empty] | X
Alarm status: Inhibited | 28178 | 128179 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm |  |  | X | X |  | X | X
Alarm status: Inhibited | 28179 | 128180 | Parameters - Engine - Emergency stop - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28179 | 128180 | Parameters - Busbar A - Emergency stop - Information - Flags |  | X
Alarm status: Inhibited | 28179 | 128180 | Parameters - Mains - Emergency stop - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28180 | 128181 | Clock battery failure | X | X | X | X | X | X | X
Alarm status: Inhibited | 28181 | 128182 | Controller temperature too high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28182 | 128183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28183 | 128184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | X | X | X | X | X | X | X
Alarm status: Inhibited | 28184 | 128185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28185 | 128186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | X | X | X | X | X | X | X
Alarm status: Inhibited | 28186 | 128187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28187 | 128188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | X | X | X | X | X | X | X
Alarm status: Inhibited | 28188 | 128189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28189 | 128190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | X | X | X | X | X | X | X
Alarm status: Inhibited | 28190 | 128191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28191 | 128192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Inhibited | 28192 | 128193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28193 | 128194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Inhibited | 28194 | 128195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28195 | 128196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Inhibited | 28196 | 128197 | EIM3.1 4 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28197 | 128198 | EIM3.1 4 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Inhibited | 28198 | 128199 | EIM3.1 5 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28199 | 128200 | EIM3.1 5 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Inhibited | 28200 | 128201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Inhibited | 28201 | 128202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Inhibited | 28202 | 128203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Inhibited | 28203 | 128204 | EIM3.1 4 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Inhibited | 28204 | 128205 | EIM3.1 5 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Inhibited | 28205 | 128206 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Inhibited | 28206 | 128207 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Inhibited | 28207 | 128208 | AC protections not running (differential current) | X |  | X | X | X
Alarm status: Inhibited | 28208 | 128209 | AC data is missing (differential current) | X |  | X | X | X
Alarm status: Inhibited | 28209 | 128210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28210 | 128211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Inhibited | 28211 | 128212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28212 | 128213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Inhibited | 28213 | 128214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28214 | 128215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Inhibited | 28215 | 128216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28216 | 128217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | X | X | X | X | X | X | X
Alarm status: Inhibited | 28217 | 128218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28218 | 128219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | X | X | X | X | X | X | X
Alarm status: Inhibited | 28219 | 128220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28220 | 128221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | X | X | X | X | X | X | X
Alarm status: Inhibited | 28221 | 128222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28222 | 128223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | X | X | X | X | X | X | X
Alarm status: Inhibited | 28223 | 128224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28224 | 128225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | X | X | X | X | X | X | X
Alarm status: Inhibited | 28225 | 128226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28226 | 128227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | X | X | X | X | X | X | X
Alarm status: Inhibited | 28228 | 128229 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28229 | 128230 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28231 | 128232 | Controller ID not configured | X | X | X | X | X | X | X
Alarm status: Inhibited | 28236 | 128237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28237 | 128238 | Blackout detection mismatch | X |  | X | X | X
Alarm status: Inhibited | 28240 | 128241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | X | X | X | X | X | X | X
Alarm status: Inhibited | 28241 | 128242 | Parameters - Communication - NTP - NTP server 1 no response - Information - Flags - NTP server 1 is not responding | X | X | X | X | X | X | X
Alarm status: Inhibited | 28242 | 128243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | X | X | X | X | X | X | X
Alarm status: Inhibited | 28243 | 128244 | Parameters - Communication - NTP - NTP server 2 no response - Information - Flags - NTP server 2 is not responding | X | X | X | X | X | X | X
Alarm status: Inhibited | 28244 | 128245 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28245 | 128246 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28246 | 128247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28247 | 128248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28296 | 128297 | Controller not part of system | X | X | X | X | X | X | X
Alarm status: Inhibited | 28297 | 128298 | Different single-line configurations | X | X | X | X | X | X | X
Alarm status: Inhibited | 28298 | 128299 | Single-line missing/none active | X | X | X | X | X | X | X
Alarm status: Inhibited | 28299 | 128300 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28300 | 128301 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | X | X | X | X | X | X | X
Alarm status: Inhibited | 28301 | 128302 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | X | X | X | X | X | X | X
Alarm status: Inhibited | 28302 | 128303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28303 | 128304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28304 | 128305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28305 | 128306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28306 | 128307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28307 | 128308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28308 | 128309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28309 | 128310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28310 | 128311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28311 | 128312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28312 | 128313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28313 | 128314 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28314 | 128315 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28315 | 128316 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28316 | 128317 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28317 | 128318 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28318 | 128319 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28319 | 128320 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28320 | 128321 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28321 | 128322 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28322 | 128323 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28323 | 128324 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28324 | 128325 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28325 | 128326 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28326 | 128327 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28327 | 128328 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28328 | 128329 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28329 | 128330 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28330 | 128331 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28331 | 128332 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28332 | 128333 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28333 | 128334 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28334 | 128335 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28335 | 128336 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28336 | 128337 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28337 | 128338 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28338 | 128339 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28339 | 128340 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28340 | 128341 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28341 | 128342 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28342 | 128343 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28343 | 128344 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28344 | 128345 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28345 | 128346 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28346 | 128347 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28347 | 128348 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28348 | 128349 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28349 | 128350 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28350 | 128351 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28351 | 128352 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28352 | 128353 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28353 | 128354 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28354 | 128355 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28355 | 128356 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28356 | 128357 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28357 | 128358 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28358 | 128359 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28359 | 128360 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28360 | 128361 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28361 | 128362 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28362 | 128363 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28363 | 128364 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28364 | 128365 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28365 | 128366 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28366 | 128367 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28367 | 128368 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28368 | 128369 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28369 | 128370 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28370 | 128371 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28371 | 128372 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28372 | 128373 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28373 | 128374 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28374 | 128375 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28375 | 128376 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28376 | 128377 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28377 | 128378 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28378 | 128379 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28379 | 128380 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28380 | 128381 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28381 | 128382 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28382 | 128383 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28383 | 128384 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28384 | 128385 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28385 | 128386 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28386 | 128387 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28387 | 128388 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28388 | 128389 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28389 | 128390 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28390 | 128391 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28391 | 128392 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28392 | 128393 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28393 | 128394 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28394 | 128395 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28395 | 128396 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28396 | 128397 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28397 | 128398 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28398 | 128399 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28399 | 128400 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28400 | 128401 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28401 | 128402 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28402 | 128403 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28403 | 128404 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28404 | 128405 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28405 | 128406 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28406 | 128407 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28407 | 128408 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28408 | 128409 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28409 | 128410 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28410 | 128411 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28411 | 128412 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28412 | 128413 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28413 | 128414 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28414 | 128415 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28415 | 128416 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28416 | 128417 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28417 | 128418 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28418 | 128419 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28419 | 128420 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28420 | 128421 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28421 | 128422 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28422 | 128423 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28423 | 128424 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28424 | 128425 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28425 | 128426 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28426 | 128427 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28427 | 128428 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28428 | 128429 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28429 | 128430 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28430 | 128431 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28431 | 128432 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28432 | 128433 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28433 | 128434 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28434 | 128435 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28435 | 128436 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28436 | 128437 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28437 | 128438 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28438 | 128439 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28439 | 128440 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28440 | 128441 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28441 | 128442 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28442 | 128443 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28443 | 128444 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28444 | 128445 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28445 | 128446 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28446 | 128447 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28447 | 128448 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28448 | 128449 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28449 | 128450 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28450 | 128451 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28451 | 128452 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28452 | 128453 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28453 | 128454 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28454 | 128455 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28455 | 128456 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28456 | 128457 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28457 | 128458 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28458 | 128459 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28459 | 128460 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28460 | 128461 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28461 | 128462 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28462 | 128463 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28463 | 128464 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28464 | 128465 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28465 | 128466 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28466 | 128467 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28467 | 128468 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28468 | 128469 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28469 | 128470 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28470 | 128471 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28471 | 128472 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28472 | 128473 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28473 | 128474 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28474 | 128475 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28475 | 128476 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28476 | 128477 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28477 | 128478 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28478 | 128479 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28479 | 128480 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28480 | 128481 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28481 | 128482 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28482 | 128483 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28483 | 128484 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28484 | 128485 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28485 | 128486 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28486 | 128487 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28487 | 128488 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28488 | 128489 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28489 | 128490 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28490 | 128491 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28491 | 128492 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28492 | 128493 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28493 | 128494 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28494 | 128495 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28495 | 128496 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28496 | 128497 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28497 | 128498 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28498 | 128499 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28499 | 128500 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28500 | 128501 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28501 | 128502 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28502 | 128503 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28503 | 128504 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28504 | 128505 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28505 | 128506 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28506 | 128507 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28507 | 128508 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28508 | 128509 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28509 | 128510 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28510 | 128511 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28511 | 128512 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28512 | 128513 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28513 | 128514 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28514 | 128515 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28515 | 128516 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28516 | 128517 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28517 | 128518 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28518 | 128519 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28519 | 128520 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28520 | 128521 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28521 | 128522 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28522 | 128523 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28523 | 128524 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28524 | 128525 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28525 | 128526 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28526 | 128527 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28527 | 128528 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28528 | 128529 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28529 | 128530 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28530 | 128531 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28531 | 128532 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28532 | 128533 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28533 | 128534 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28534 | 128535 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28535 | 128536 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28536 | 128537 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28537 | 128538 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28538 | 128539 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28539 | 128540 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28540 | 128541 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28541 | 128542 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28542 | 128543 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28543 | 128544 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28544 | 128545 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28545 | 128546 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28546 | 128547 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28547 | 128548 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28548 | 128549 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28549 | 128550 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28550 | 128551 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28551 | 128552 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28552 | 128553 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28553 | 128554 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28554 | 128555 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28555 | 128556 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28556 | 128557 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28557 | 128558 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28558 | 128559 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28559 | 128560 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28560 | 128561 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28561 | 128562 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28562 | 128563 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Inhibited | 28565 | 128566 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | X | X | X | X | X | X | X
Alarm status: Inhibited | 28566 | 128567 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | X |  | X | X | X
Alarm status: Inhibited | 28567 | 128568 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28568 | 128569 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28569 | 128570 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28570 | 128571 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28571 | 128572 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28572 | 128573 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28573 | 128574 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28574 | 128575 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28575 | 128576 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28576 | 128577 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28577 | 128578 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28578 | 128579 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28579 | 128580 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28580 | 128581 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28581 | 128582 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28582 | 128583 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28583 | 128584 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28584 | 128585 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28585 | 128586 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28586 | 128587 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28587 | 128588 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28588 | 128589 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28589 | 128590 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28590 | 128591 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28591 | 128592 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28592 | 128593 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28593 | 128594 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28594 | 128595 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28595 | 128596 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28596 | 128597 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28597 | 128598 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28598 | 128599 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28599 | 128600 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28600 | 128601 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28601 | 128602 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28602 | 128603 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28603 | 128604 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28604 | 128605 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28605 | 128606 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28606 | 128607 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28607 | 128608 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28608 | 128609 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28609 | 128610 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28610 | 128611 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28611 | 128612 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28612 | 128613 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28613 | 128614 | DAVR unsupported AC configuration | X |  | X | X | X
Alarm status: Inhibited | 28614 | 128615 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | X |  | X | X | X
Alarm status: Inhibited | 28615 | 128616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | X |  | X | X | X
Alarm status: Inhibited | 28615 | 128616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 |  | X
Alarm status: Inhibited | 28615 | 128616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | [5 empty] | X | X
Alarm status: Inhibited | 28616 | 128617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | X |  | X | X | X
Alarm status: Inhibited | 28616 | 128617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 |  | X
Alarm status: Inhibited | 28616 | 128617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | [5 empty] | X | X
Alarm status: Inhibited | 28617 | 128618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | X |  | X | X | X
Alarm status: Inhibited | 28617 | 128618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 |  | X
Alarm status: Inhibited | 28617 | 128618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | [5 empty] | X | X
Alarm status: Inhibited | 28618 | 128619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | X |  | X | X | X
Alarm status: Inhibited | 28618 | 128619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 |  | X
Alarm status: Inhibited | 28618 | 128619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | [5 empty] | X | X
Alarm status: Inhibited | 28619 | 128620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | X |  | X | X | X
Alarm status: Inhibited | 28619 | 128620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 |  | X
Alarm status: Inhibited | 28619 | 128620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | [5 empty] | X | X
Alarm status: Inhibited | 28620 | 128621 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | X |  | X | X | X
Alarm status: Inhibited | 28620 | 128621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance |  | X
Alarm status: Inhibited | 28620 | 128621 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | [5 empty] | X | X
Alarm status: Inhibited | 28621 | 128622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | X |  | X | X | X
Alarm status: Inhibited | 28621 | 128622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage |  | X
Alarm status: Inhibited | 28621 | 128622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | [5 empty] | X | X
Alarm status: Inhibited | 28622 | 128623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | X |  | X | X | X
Alarm status: Inhibited | 28622 | 128623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage |  | X
Alarm status: Inhibited | 28622 | 128623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | [5 empty] | X | X
Alarm status: Inhibited | 28623 | 128624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | X |  | X | X | X
Alarm status: Inhibited | 28623 | 128624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage |  | X
Alarm status: Inhibited | 28623 | 128624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | [5 empty] | X | X
Alarm status: Inhibited | 28624 | 128625 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28624 | 128625 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags |  | X
Alarm status: Inhibited | 28624 | 128625 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28625 | 128626 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28625 | 128626 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags |  | X
Alarm status: Inhibited | 28625 | 128626 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28626 | 128627 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28626 | 128627 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags |  | X
Alarm status: Inhibited | 28626 | 128627 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28627 | 128628 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28627 | 128628 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags |  | X
Alarm status: Inhibited | 28627 | 128628 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28628 | 128629 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28628 | 128629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags |  | X
Alarm status: Inhibited | 28628 | 128629 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28629 | 128630 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28629 | 128630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags |  | X
Alarm status: Inhibited | 28629 | 128630 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28630 | 128631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28630 | 128631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags |  | X
Alarm status: Inhibited | 28630 | 128631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28631 | 128632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28631 | 128632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags |  | X
Alarm status: Inhibited | 28631 | 128632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28632 | 128633 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28632 | 128633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags |  | X
Alarm status: Inhibited | 28632 | 128633 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28633 | 128634 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28633 | 128634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags |  | X
Alarm status: Inhibited | 28633 | 128634 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28634 | 128635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags |  | X
Alarm status: Inhibited | 28635 | 128636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags |  | X
Alarm status: Inhibited | 28636 | 128637 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28636 | 128637 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags |  | X
Alarm status: Inhibited | 28636 | 128637 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28637 | 128638 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28637 | 128638 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags |  | X
Alarm status: Inhibited | 28637 | 128638 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28638 | 128639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | X |  | X | X | X
Alarm status: Inhibited | 28638 | 128639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 |  | X
Alarm status: Inhibited | 28638 | 128639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | [5 empty] | X | X
Alarm status: Inhibited | 28639 | 128640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | X |  | X | X | X
Alarm status: Inhibited | 28639 | 128640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 |  | X
Alarm status: Inhibited | 28639 | 128640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | [5 empty] | X | X
Alarm status: Inhibited | 28640 | 128641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | X |  | X | X | X
Alarm status: Inhibited | 28640 | 128641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 |  | X
Alarm status: Inhibited | 28640 | 128641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | [5 empty] | X | X
Alarm status: Inhibited | 28641 | 128642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | X |  | X | X | X
Alarm status: Inhibited | 28641 | 128642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 |  | X
Alarm status: Inhibited | 28641 | 128642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | [5 empty] | X | X
Alarm status: Inhibited | 28642 | 128643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | X |  | X | X | X
Alarm status: Inhibited | 28642 | 128643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 |  | X
Alarm status: Inhibited | 28642 | 128643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | [5 empty] | X | X
Alarm status: Inhibited | 28643 | 128644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | X |  | X | X | X
Alarm status: Inhibited | 28643 | 128644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 |  | X
Alarm status: Inhibited | 28643 | 128644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | [5 empty] | X | X
Alarm status: Inhibited | 28644 | 128645 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28644 | 128645 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags |  | X
Alarm status: Inhibited | 28644 | 128645 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28645 | 128646 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28645 | 128646 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags |  | X
Alarm status: Inhibited | 28645 | 128646 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28646 | 128647 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28646 | 128647 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags |  | X
Alarm status: Inhibited | 28646 | 128647 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28647 | 128648 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28647 | 128648 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags |  | X
Alarm status: Inhibited | 28647 | 128648 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28648 | 128649 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28648 | 128649 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags |  | X
Alarm status: Inhibited | 28648 | 128649 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28649 | 128650 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28649 | 128650 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags |  | X
Alarm status: Inhibited | 28649 | 128650 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28650 | 128651 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28650 | 128651 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags |  | X
Alarm status: Inhibited | 28650 | 128651 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28651 | 128652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28651 | 128652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags |  | X
Alarm status: Inhibited | 28651 | 128652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28652 | 128653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28652 | 128653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags |  | X
Alarm status: Inhibited | 28652 | 128653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28653 | 128654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28653 | 128654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags |  | X
Alarm status: Inhibited | 28653 | 128654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28654 | 128655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28654 | 128655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags |  | X
Alarm status: Inhibited | 28654 | 128655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | [5 empty] | X | X
Alarm status: Inhibited | 28655 | 128656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 |  |  | X | X
Alarm status: Inhibited | 28655 | 128656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | X |  |  |  | X | X | X
Alarm status: Inhibited | 28655 | 128656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 |  | X
Alarm status: Inhibited | 28656 | 128657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 |  |  | X | X
Alarm status: Inhibited | 28656 | 128657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | X |  |  |  | X | X | X
Alarm status: Inhibited | 28656 | 128657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 |  | X
Alarm status: Inhibited | 28657 | 128658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 |  |  | X | X
Alarm status: Inhibited | 28657 | 128658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | X |  |  |  | X | X | X
Alarm status: Inhibited | 28657 | 128658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 |  | X
Alarm status: Inhibited | 28658 | 128659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 |  |  | X | X
Alarm status: Inhibited | 28658 | 128659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | X |  |  |  | X | X | X
Alarm status: Inhibited | 28658 | 128659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 |  | X
Alarm status: Inhibited | 28659 | 128660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 |  |  | X | X
Alarm status: Inhibited | 28659 | 128660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | X |  |  |  | X | X | X
Alarm status: Inhibited | 28659 | 128660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 |  | X
Alarm status: Inhibited | 28660 | 128661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 |  |  | X | X
Alarm status: Inhibited | 28660 | 128661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | X |  |  |  | X | X | X
Alarm status: Inhibited | 28660 | 128661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 |  | X
Alarm status: Inhibited | 28661 | 128662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 |  |  | X | X
Alarm status: Inhibited | 28661 | 128662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | X |  |  |  | X | X | X
Alarm status: Inhibited | 28661 | 128662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 |  | X
Alarm status: Inhibited | 28662 | 128663 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance |  |  | X | X
Alarm status: Inhibited | 28662 | 128663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | X |  |  |  | X | X | X
Alarm status: Inhibited | 28662 | 128663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance |  | X
Alarm status: Inhibited | 28663 | 128664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 |  |  | X | X
Alarm status: Inhibited | 28663 | 128664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | X |  |  |  | X | X | X
Alarm status: Inhibited | 28663 | 128664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 |  | X
Alarm status: Inhibited | 28664 | 128665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 |  |  | X | X
Alarm status: Inhibited | 28664 | 128665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | X |  |  |  | X | X | X
Alarm status: Inhibited | 28664 | 128665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 |  | X
Alarm status: Inhibited | 28665 | 128666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 |  |  | X | X
Alarm status: Inhibited | 28665 | 128666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | X |  |  |  | X | X | X
Alarm status: Inhibited | 28665 | 128666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 |  | X
Alarm status: Inhibited | 28666 | 128667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 |  |  | X | X
Alarm status: Inhibited | 28666 | 128667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | X |  |  |  | X | X | X
Alarm status: Inhibited | 28666 | 128667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 |  | X
Alarm status: Inhibited | 28667 | 128668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 |  |  | X | X
Alarm status: Inhibited | 28667 | 128668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | X |  |  |  | X | X | X
Alarm status: Inhibited | 28667 | 128668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 |  | X
Alarm status: Inhibited | 28668 | 128669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 |  |  | X | X
Alarm status: Inhibited | 28668 | 128669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | X |  |  |  | X | X | X
Alarm status: Inhibited | 28668 | 128669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 |  | X
Alarm status: Inhibited | 28669 | 128670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 |  |  | X | X
Alarm status: Inhibited | 28669 | 128670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | X |  |  |  | X | X | X
Alarm status: Inhibited | 28669 | 128670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 |  | X
Alarm status: Inhibited | 28670 | 128671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage |  |  | X | X
Alarm status: Inhibited | 28670 | 128671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | X |  |  |  | X | X | X
Alarm status: Inhibited | 28670 | 128671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage |  | X
Alarm status: Inhibited | 28671 | 128672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage |  |  | X | X
Alarm status: Inhibited | 28671 | 128672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | X |  |  |  | X | X | X
Alarm status: Inhibited | 28671 | 128672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage |  | X
Alarm status: Inhibited | 28672 | 128673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage |  |  | X | X
Alarm status: Inhibited | 28672 | 128673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | X |  |  |  | X | X | X
Alarm status: Inhibited | 28672 | 128673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage |  | X
Alarm status: Inhibited | 28717 | 128718 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 1 | X |  | X | X | X
Alarm status: Inhibited | 28718 | 128719 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 2 | X |  | X | X | X
Alarm status: Inhibited | 28719 | 128720 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 3 | X |  | X | X | X
Alarm status: Inhibited | 28720 | 128721 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 4 | X |  | X | X | X
Alarm status: Inhibited | 28721 | 128722 | External MB open failure | X | X | X | X | X | X | X
Alarm status: Inhibited | 28722 | 128723 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28723 | 128724 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28724 | 128725 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28725 | 128726 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28726 | 128727 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - Flags | X |  | X | X | X
Alarm status: Inhibited | 28727 | 128728 | Parameters - Breakers - Close before excitation - CBE failure - Information - Flags - Close before excitation failure | X |  | X | X | X
Alarm status: Inhibited | 28728 | 128729 | Load too high | X | X | X | X | X | X | X
Alarm status: Inhibited | 28729 | 128730 | ID to run configuration failure | [5 empty] | X | X
Alarm status: Inhibited | 28731 | 128732 | Parameters - System - Monitoring - Missing any genset controller - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28732 | 128733 | Parameters - System - Monitoring - Missing any mains controller - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28733 | 128734 | Parameters - System - Monitoring - Missing any bustie controller - Information - Flags - Missing any bus tie controller | X | X | X | X | X | X | X
Alarm status: Inhibited | 28734 | 128735 | Can ID not available | X | X | X | X | X | X | X
Alarm status: Inhibited | 28735 | 128736 | Duplicated CAN IDs | X | X | X | X | X | X | X
Alarm status: Inhibited | 28736 | 128737 | Parameters - Local power management - Alarms - Busbar blocked - Information - Flags - Busbar blocked due to position failure | X |  | X | X | X | X | X
Alarm status: Inhibited | 28737 | 128738 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Flags - Busbar A blocked due to position failure |  | X
Alarm status: Inhibited | 28738 | 128739 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Flags - Busbar B blocked due to position failure |  | X
Alarm status: Inhibited | 28739 | 128740 | Parameters - System - Monitoring - BTB 33 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28740 | 128741 | Parameters - System - Monitoring - BTB 34 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28741 | 128742 | Parameters - System - Monitoring - BTB 35 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28742 | 128743 | Parameters - System - Monitoring - BTB 36 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28743 | 128744 | Parameters - System - Monitoring - BTB 37 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28744 | 128745 | Parameters - System - Monitoring - BTB 38 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28745 | 128746 | Parameters - System - Monitoring - BTB 39 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28746 | 128747 | Parameters - System - Monitoring - BTB 40 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28747 | 128748 | Primary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28748 | 128749 | Primary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28749 | 128750 | Primary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28750 | 128751 | Primary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28751 | 128752 | Primary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28752 | 128753 | Primary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28753 | 128754 | Primary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28754 | 128755 | Primary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28755 | 128756 | Primary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28756 | 128757 | Primary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28757 | 128758 | Primary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28758 | 128759 | Primary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28759 | 128760 | Primary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28760 | 128761 | Primary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28761 | 128762 | Primary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28762 | 128763 | Primary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28763 | 128764 | Primary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28764 | 128765 | Primary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28765 | 128766 | Primary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28766 | 128767 | Primary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28767 | 128768 | Primary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28768 | 128769 | Primary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28769 | 128770 | Primary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28770 | 128771 | Primary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28771 | 128772 | Primary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28772 | 128773 | Primary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28773 | 128774 | Primary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28774 | 128775 | Primary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28775 | 128776 | Primary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28776 | 128777 | Primary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28777 | 128778 | Primary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28778 | 128779 | Primary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28779 | 128780 | Primary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28780 | 128781 | Primary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28781 | 128782 | Primary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28782 | 128783 | Primary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28783 | 128784 | Primary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28784 | 128785 | Primary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28785 | 128786 | Primary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28786 | 128787 | Primary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28787 | 128788 | Secondary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28788 | 128789 | Secondary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28789 | 128790 | Secondary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28790 | 128791 | Secondary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28791 | 128792 | Secondary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28792 | 128793 | Secondary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28793 | 128794 | Secondary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28794 | 128795 | Secondary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28795 | 128796 | Secondary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28796 | 128797 | Secondary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28797 | 128798 | Secondary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28798 | 128799 | Secondary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28799 | 128800 | Secondary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28800 | 128801 | Secondary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28801 | 128802 | Secondary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28802 | 128803 | Secondary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28803 | 128804 | Secondary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28804 | 128805 | Secondary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28805 | 128806 | Secondary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28806 | 128807 | Secondary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28807 | 128808 | Secondary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28808 | 128809 | Secondary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28809 | 128810 | Secondary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28810 | 128811 | Secondary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28811 | 128812 | Secondary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28812 | 128813 | Secondary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28813 | 128814 | Secondary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28814 | 128815 | Secondary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28815 | 128816 | Secondary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28816 | 128817 | Secondary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28817 | 128818 | Secondary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28818 | 128819 | Secondary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28819 | 128820 | Secondary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28820 | 128821 | Secondary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28821 | 128822 | Secondary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28822 | 128823 | Secondary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28823 | 128824 | Secondary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28824 | 128825 | Secondary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28825 | 128826 | Secondary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28826 | 128827 | Secondary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm status: Inhibited | 28827 | 128828 | Priority error | X | X | X | X | X | X | X
Alarm status: Inhibited | 28828 | 128829 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - Flags - NEL 1 over-current | X |  | X | X | X | X | X
Alarm status: Inhibited | 28829 | 128830 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - Flags - NEL 1 under-frequency | X |  | X | X | X | X | X
Alarm status: Inhibited | 28830 | 128831 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - Flags - NEL 1 overload 1 | X |  | X | X | X | X | X
Alarm status: Inhibited | 28831 | 128832 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - Flags - NEL 1 overload 2 | X |  | X | X | X | X | X
Alarm status: Inhibited | 28832 | 128833 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - Flags - NEL 1 reactive overload | X |  | X | X | X | X | X
Alarm status: Inhibited | 28833 | 128834 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - Flags - NEL 2 over-current | X |  | X | X | X | X | X
Alarm status: Inhibited | 28834 | 128835 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - Flags - NEL 2 under-frequency | X |  | X | X | X | X | X
Alarm status: Inhibited | 28835 | 128836 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - Flags - NEL 2 overload 1 | X |  | X | X | X | X | X
Alarm status: Inhibited | 28836 | 128837 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - Flags - NEL 2 overload 2 | X |  | X | X | X | X | X
Alarm status: Inhibited | 28837 | 128838 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - Flags - NEL 2 reactive overload | X |  | X | X | X | X | X
Alarm status: Inhibited | 28838 | 128839 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - Flags - NEL 3 over-current | X |  | X | X | X | X | X
Alarm status: Inhibited | 28839 | 128840 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - Flags - NEL 3 under-frequency | X |  | X | X | X | X | X
Alarm status: Inhibited | 28840 | 128841 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - Flags - NEL 3 overload 1 | X |  | X | X | X | X | X
Alarm status: Inhibited | 28841 | 128842 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - Flags - NEL 3 overload 2 | X |  | X | X | X | X | X
Alarm status: Inhibited | 28842 | 128843 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - Flags - NEL 3 reactive overload | X |  | X | X | X | X | X
Alarm status: Inhibited | 28843 | 128844 | Parameters - System - Monitoring - Single-line hazard - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28844 | 128845 | ID not present | X | X | X | X | X | X | X
Alarm status: Inhibited | 28845 | 128846 | Unsupported application | X | X | X | X | X | X | X
Alarm status: Inhibited | 28846 | 128847 | Application internal CAN protocol conflict | X | X | X | X | X | X | X
Alarm status: Inhibited | 28847 | 128848 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Flags - Section P> | X | X | X | X | X | X | X
Alarm status: Inhibited | 28848 | 128849 | Dry mode: Voltage level unexpected | X |  | X | X | X
Alarm status: Inhibited | 28849 | 128850 | Invalid DAVR configuration | X |  | X | X | X
Alarm status: Inhibited | 28850 | 128851 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28852 | 128853 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28854 | 128855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | X |  | X | X | X
Alarm status: Inhibited | 28854 | 128855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch |  | X
Alarm status: Inhibited | 28854 | 128855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | [5 empty] | X | X
Alarm status: Inhibited | 28855 | 128856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch |  |  |  | X
Alarm status: Inhibited | 28855 | 128856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | [6 empty] | X
Alarm status: Inhibited | 28857 | 128858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28858 | 128859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28859 | 128860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28860 | 128861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28861 | 128862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Inhibited | 28862 | 128863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Inhibited | 28863 | 128864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Inhibited | 28864 | 128865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Inhibited | 28865 | 128866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Inhibited | 28866 | 128867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Inhibited | 28867 | 128868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Inhibited | 28868 | 128869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Inhibited | 28869 | 128870 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Inhibited | 28870 | 128871 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Inhibited | 28871 | 128872 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Inhibited | 28872 | 128873 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Inhibited | 28873 | 128874 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Inhibited | 28874 | 128875 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Inhibited | 28875 | 128876 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Inhibited | 28876 | 128877 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Inhibited | 28877 | 128878 | Live voltage detected | X | X | X | X | X | X | X
Alarm status: Inhibited | 28878 | 128879 | Internal issue detected. A restart is required soon! | X | X | X | X | X | X | X
Alarm status: Inhibited | 28879 | 128880 | Parameters - System - Monitoring - Missing controllers - Information - Flags | X | X | X | X | X | X | X
Alarm status: Inhibited | 28880 | 128881 | Card issue detected | X | X | X | X | X | X | X
Alarm status: Inhibited | 28881 | 128882 | Card configuration failed | X | X | X | X | X | X | X
Alarm status: Inhibited | 28882 | 128883 | Unknown traffic on DEIF network | X | X | X | X | X | X | X
Alarm status: Inhibited | 28883 | 128884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Inhibited | 28884 | 128885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Inhibited | 28885 | 128886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Inhibited | 28886 | 128887 | Local IO service error | X | X | X | X | X | X | X
Alarm status: Inhibited | 28887 | 128888 | App logging failure | X | X | X | X | X | X | X
Alarm status: Inhibited | 28888 | 128889 | Event logging failure | X | X | X | X | X | X | X
Alarm status: Inhibited | 28889 | 128890 | Licence error | X | X | X | X | X | X | X
Alarm status: Inhibited | 28890 | 128891 | Brightness is dimmed according to temperature | X | X | X | X | X | X | X
Alarm status: Inhibited | 28891 | 128892 | Parameters - Grid code - Mains sync inhibit - Information - Flags |  |  | X | X
Alarm status: Inhibited | 28892 | 128893 | Parameters - Grid code - Capability curve - Import protection - Information - Flags - Power import capability curve protection |  |  | X | X
Alarm status: Inhibited | 28893 | 128894 | Parameters - Grid code - Capability curve - Export protection - Information - Flags - Power export capability curve protection |  |  | X | X
Alarm status: Inhibited | 28894 | 128895 | Hardware is not compatible based on module versions | X | X | X | X | X | X | X
Alarm status: Out of service | 30000 | 130001 | Application initialisation error | X | X | X | X | X | X | X
Alarm status: Out of service | 30001 | 130002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm status: Out of service | 30002 | 130003 | Preliminary software | X | X | X | X | X | X | X
Alarm status: Out of service | 30003 | 130004 | Parameters - Engine - Stop sequence - Stop failure - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30004 | 130005 | Parameters - Engine - Start sequence - Start failure - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30005 | 130006 | Parameters - Engine - Start sequence - Crank failure - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30006 | 130007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30007 | 130008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30008 | 130009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30009 | 130010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30010 | 130011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Flags - Magnetic pickup wire break alarm | X |  | X | X | X
Alarm status: Out of service | 30011 | 130012 | Parameters - Engine - Stop sequence - Externally stopped - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30013 | 130014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30014 | 130015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30015 | 130016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30016 | 130017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30017 | 130018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30018 | 130019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30019 | 130020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30020 | 130021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30021 | 130022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30022 | 130023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30027 | 130028 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30041 | 130042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Flags - GB closing failure | X |  | X | X | X
Alarm status: Out of service | 30041 | 130042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Flags - BTB closing failure |  | X
Alarm status: Out of service | 30041 | 130042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure | [5 empty] | X | X
Alarm status: Out of service | 30042 | 130043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Flags - GB opening failure | X |  | X | X | X
Alarm status: Out of service | 30042 | 130043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Flags - BTB opening failure |  | X
Alarm status: Out of service | 30042 | 130043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure | [5 empty] | X | X
Alarm status: Out of service | 30043 | 130044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Flags - GB position failure | X |  | X | X | X
Alarm status: Out of service | 30043 | 130044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Flags - BTB position failure |  | X
Alarm status: Out of service | 30043 | 130044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure | [5 empty] | X | X
Alarm status: Out of service | 30044 | 130045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Flags - GB configuration failure | X |  | X | X | X
Alarm status: Out of service | 30044 | 130045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Flags - BTB configuration failure |  | X
Alarm status: Out of service | 30044 | 130045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure | [5 empty] | X | X
Alarm status: Out of service | 30045 | 130046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Flags - GB synchronisation failure | X |  | X | X | X
Alarm status: Out of service | 30045 | 130046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Flags - BTB synchronisation failure |  | X
Alarm status: Out of service | 30045 | 130046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure | [5 empty] | X | X
Alarm status: Out of service | 30046 | 130047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Flags - GB de-load failure | X |  | X | X | X
Alarm status: Out of service | 30046 | 130047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Flags - BTB de-load failure |  | X
Alarm status: Out of service | 30046 | 130047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure | [5 empty] | X | X
Alarm status: Out of service | 30047 | 130048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - Flags - GB tripped (external) | X |  | X | X | X
Alarm status: Out of service | 30047 | 130048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - Flags - BTB tripped (external) |  | X
Alarm status: Out of service | 30047 | 130048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) | [5 empty] | X | X
Alarm status: Out of service | 30048 | 130049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - Flags - GB short circuit | X |  | X | X | X
Alarm status: Out of service | 30048 | 130049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - Flags - BTB short circuit |  | X
Alarm status: Out of service | 30048 | 130049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit | [5 empty] | X | X
Alarm status: Out of service | 30049 | 130050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Flags - MB closing failure |  |  |  | X
Alarm status: Out of service | 30049 | 130050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Flags - TB closing failure | [6 empty] | X
Alarm status: Out of service | 30050 | 130051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Flags - MB opening failure |  |  |  | X
Alarm status: Out of service | 30050 | 130051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Flags - TB opening failure | [6 empty] | X
Alarm status: Out of service | 30051 | 130052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Flags - MB position failure |  |  |  | X
Alarm status: Out of service | 30051 | 130052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Flags - TB position failure | [6 empty] | X
Alarm status: Out of service | 30052 | 130053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Flags - MB configuration failure |  |  |  | X
Alarm status: Out of service | 30052 | 130053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Flags - TB configuration failure | [6 empty] | X
Alarm status: Out of service | 30053 | 130054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Flags - MB synchronisation failure |  |  |  | X
Alarm status: Out of service | 30053 | 130054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Flags - TB synchronisation failure | [6 empty] | X
Alarm status: Out of service | 30054 | 130055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Flags - MB de-load failure |  |  |  | X
Alarm status: Out of service | 30054 | 130055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Flags - TB de-load failure | [6 empty] | X
Alarm status: Out of service | 30055 | 130056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - Flags - MB tripped (external) |  |  |  | X
Alarm status: Out of service | 30055 | 130056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - Flags - TB tripped (external) | [6 empty] | X
Alarm status: Out of service | 30056 | 130057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - Flags - MB short circuit |  |  |  | X
Alarm status: Out of service | 30056 | 130057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - Flags - TB short circuit | [6 empty] | X
Alarm status: Out of service | 30060 | 130061 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error |  |  | X | X
Alarm status: Out of service | 30060 | 130061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Flags - Busbar phase sequence error | X |  |  |  | X | X | X
Alarm status: Out of service | 30060 | 130061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Flags - Busbar B phase sequence error |  | X
Alarm status: Out of service | 30061 | 130062 | Parameters - Generator - AC setup - Phase sequence error - Information - Flags - Generator phase sequence error | X |  | X | X | X
Alarm status: Out of service | 30061 | 130062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Flags - Busbar A phase sequence error |  | X
Alarm status: Out of service | 30061 | 130062 | Parameters - Mains - AC setup - Phase sequence error - Information - Flags - Mains phase sequence error | [5 empty] | X | X
Alarm status: Out of service | 30062 | 130063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30103 | 130104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information - Flags |  |  | X | X
Alarm status: Out of service | 30103 | 130104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information - Flags | X |  |  |  | X | X | X
Alarm status: Out of service | 30103 | 130104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information - Flags |  | X
Alarm status: Out of service | 30104 | 130105 | Parameters - Mains - Additional protections - Vector shift - Information - Flags |  |  | X | X
Alarm status: Out of service | 30104 | 130105 | Parameters - Busbar - Additional protections - Vector shift - Information - Flags | X |  |  |  | X | X | X
Alarm status: Out of service | 30104 | 130105 | Parameters - Busbar B - Additional protections - Vector shift - Information - Flags |  | X
Alarm status: Out of service | 30105 | 130106 | Parameters - Generator - Current protections - Inverse time over-current - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30105 | 130106 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - Flags |  | X
Alarm status: Out of service | 30105 | 130106 | Parameters - Mains - Current protections - Inverse time over-current - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30106 | 130107 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30107 | 130108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30108 | 130109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30108 | 130109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Flags |  | X
Alarm status: Out of service | 30108 | 130109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30109 | 130110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30109 | 130110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Flags |  | X
Alarm status: Out of service | 30109 | 130110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30110 | 130111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30110 | 130111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Flags |  | X
Alarm status: Out of service | 30110 | 130111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30111 | 130112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30111 | 130112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Flags |  | X
Alarm status: Out of service | 30111 | 130112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30115 | 130116 | Protection set point out of range | X | X | X | X | X | X | X
Alarm status: Out of service | 30116 | 130117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Flags - Stabilised differential | X |  | X | X | X
Alarm status: Out of service | 30117 | 130118 | Parameters - Generator - Current protections - High set differential current - Information - Flags - High set differential | X |  | X | X | X
Alarm status: Out of service | 30118 | 130119 | Protection set point out of range (differential current) | X |  | X | X | X
Alarm status: Out of service | 30119 | 130120 | Parameters - Local - Mode - Not under remote control - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30121 | 130122 | Parameters - Local - Monitoring - System not OK - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30122 | 130123 | Configuration update delayed | X | X | X | X | X | X | X
Alarm status: Out of service | 30123 | 130124 | Critical process error | X | X | X | X | X | X | X
Alarm status: Out of service | 30124 | 130125 | Restore error | X | X | X | X | X | X | X
Alarm status: Out of service | 30125 | 130126 | SD-card format error | X | X | X | X | X | X | X
Alarm status: Out of service | 30126 | 130127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | X | X | X | X | X | X | X
Alarm status: Out of service | 30127 | 130128 | Fieldbus configuration exceeded maximum I/O configuration | X | X | X | X | X | X | X
Alarm status: Out of service | 30128 | 130129 | Parameters - Custom alarm - Custom alarm 0 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30129 | 130130 | Parameters - Custom alarm - Custom alarm 1 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30130 | 130131 | Parameters - Custom alarm - Custom alarm 2 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30131 | 130132 | Parameters - Custom alarm - Custom alarm 3 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30132 | 130133 | Parameters - Custom alarm - Custom alarm 4 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30133 | 130134 | Parameters - Custom alarm - Custom alarm 5 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30134 | 130135 | Parameters - Custom alarm - Custom alarm 6 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30135 | 130136 | Parameters - Custom alarm - Custom alarm 7 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30136 | 130137 | Parameters - Custom alarm - Custom alarm 8 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30137 | 130138 | Parameters - Custom alarm - Custom alarm 9 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30138 | 130139 | Parameters - Custom alarm - Custom alarm 10 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30139 | 130140 | Parameters - Custom alarm - Custom alarm 11 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30140 | 130141 | Parameters - Custom alarm - Custom alarm 12 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30141 | 130142 | Parameters - Custom alarm - Custom alarm 13 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30142 | 130143 | Parameters - Custom alarm - Custom alarm 14 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30143 | 130144 | Parameters - Custom alarm - Custom alarm 15 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30144 | 130145 | Parameters - Custom alarm - Custom alarm 16 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30145 | 130146 | Parameters - Custom alarm - Custom alarm 17 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30146 | 130147 | Parameters - Custom alarm - Custom alarm 18 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30147 | 130148 | Parameters - Custom alarm - Custom alarm 19 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30148 | 130149 | Parameters - Custom alarm - Custom alarm 20 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30149 | 130150 | Parameters - Custom alarm - Custom alarm 21 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30150 | 130151 | Parameters - Custom alarm - Custom alarm 22 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30151 | 130152 | Parameters - Custom alarm - Custom alarm 23 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30152 | 130153 | Parameters - Custom alarm - Custom alarm 24 - Information - Flags - | X | X | X | X | X | X | X
Alarm status: Out of service | 30153 | 130154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Flags - GOV regulation error | X |  | X | X | X
Alarm status: Out of service | 30154 | 130155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Flags - AVR regulation error | X |  | X | X | X
Alarm status: Out of service | 30163 | 130164 | Required hardware card(s) not found | X | X | X | X | X | X | X
Alarm status: Out of service | 30164 | 130165 | Software mismatch on hardware module(s) | X | X | X | X | X | X | X
Alarm status: Out of service | 30165 | 130166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break |  |  | X
Alarm status: Out of service | 30165 | 130166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Flags - Busbar L1-L2-L3 wire break | X |  |  |  | X | X
Alarm status: Out of service | 30165 | 130166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Flags - Busbar B L1-L2-L3 wire break |  | X
Alarm status: Out of service | 30166 | 130167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Flags - Generator L1-L2-L3 wire break | X |  | X |  | X
Alarm status: Out of service | 30166 | 130167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Flags - Busbar A L1-L2-L3 wire break |  | X
Alarm status: Out of service | 30166 | 130167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Flags - Mains L1-L2-L3 wire break | [5 empty] | X
Alarm status: Out of service | 30167 | 130168 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break |  |  | X
Alarm status: Out of service | 30167 | 130168 | Parameters - Busbar - AC setup - L1 wire break - Information - Flags - Busbar L1 wire break | X |  |  |  | X | X
Alarm status: Out of service | 30167 | 130168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Flags - Busbar B L1 wire break |  | X
Alarm status: Out of service | 30168 | 130169 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break |  |  | X
Alarm status: Out of service | 30168 | 130169 | Parameters - Busbar - AC setup - L2 wire break - Information - Flags - Busbar L2 wire break | X |  |  |  | X | X
Alarm status: Out of service | 30168 | 130169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Flags - Busbar B L2 wire break |  | X
Alarm status: Out of service | 30169 | 130170 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break |  |  | X
Alarm status: Out of service | 30169 | 130170 | Parameters - Busbar - AC setup - L3 wire break - Information - Flags - Busbar L3 wire break | X |  |  |  | X | X
Alarm status: Out of service | 30169 | 130170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Flags - Busbar B L3 wire break |  | X
Alarm status: Out of service | 30170 | 130171 | Parameters - Generator - AC setup - L1 wire break - Information - Flags - Generator L1 wire break | X |  | X |  | X
Alarm status: Out of service | 30170 | 130171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Flags - Busbar A L1 wire break |  | X
Alarm status: Out of service | 30170 | 130171 | Parameters - Mains - AC setup - L1 wire break - Information - Flags - Mains L1 wire break | [5 empty] | X
Alarm status: Out of service | 30171 | 130172 | Parameters - Generator - AC setup - L2 wire break - Information - Flags - Generator L2 wire break | X |  | X |  | X
Alarm status: Out of service | 30171 | 130172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Flags - Busbar A L2 wire break |  | X
Alarm status: Out of service | 30171 | 130172 | Parameters - Mains - AC setup - L2 wire break - Information - Flags - Mains L2 wire break | [5 empty] | X
Alarm status: Out of service | 30172 | 130173 | Parameters - Generator - AC setup - L3 wire break - Information - Flags - Generator L3 wire break | X |  | X |  | X
Alarm status: Out of service | 30172 | 130173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Flags - Busbar A L3 wire break |  | X
Alarm status: Out of service | 30172 | 130173 | Parameters - Mains - AC setup - L3 wire break - Information - Flags - Mains L3 wire break | [5 empty] | X
Alarm status: Out of service | 30178 | 130179 | Parameters - Mains - AC setup - Supervision alarm - Information - Flags - Mains supervision alarm |  |  | X | X |  | X | X
Alarm status: Out of service | 30179 | 130180 | Parameters - Engine - Emergency stop - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30179 | 130180 | Parameters - Busbar A - Emergency stop - Information - Flags |  | X
Alarm status: Out of service | 30179 | 130180 | Parameters - Mains - Emergency stop - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30180 | 130181 | Clock battery failure | X | X | X | X | X | X | X
Alarm status: Out of service | 30181 | 130182 | Controller temperature too high | X | X | X | X | X | X | X
Alarm status: Out of service | 30182 | 130183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Flags - PSM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30183 | 130184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Flags - PSM3.1 1 supply voltage low | X | X | X | X | X | X | X
Alarm status: Out of service | 30184 | 130185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Flags - PSM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30185 | 130186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Flags - PSM3.2 1 supply voltage low | X | X | X | X | X | X | X
Alarm status: Out of service | 30186 | 130187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Flags - PSM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30187 | 130188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Flags - PSM3.2 2 supply voltage low | X | X | X | X | X | X | X
Alarm status: Out of service | 30188 | 130189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Flags - PSM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30189 | 130190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Flags - PSM3.2 3 supply voltage low | X | X | X | X | X | X | X
Alarm status: Out of service | 30190 | 130191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Flags - EIM3.1 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30191 | 130192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Flags - EIM3.1 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Out of service | 30192 | 130193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Flags - EIM3.1 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30193 | 130194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Flags - EIM3.1 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Out of service | 30194 | 130195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Flags - EIM3.1 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30195 | 130196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Flags - EIM3.1 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Out of service | 30196 | 130197 | EIM3.1 4 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30197 | 130198 | EIM3.1 4 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Out of service | 30198 | 130199 | EIM3.1 5 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30199 | 130200 | EIM3.1 5 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Out of service | 30200 | 130201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Flags - EIM3.1 1 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Out of service | 30201 | 130202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Flags - EIM3.1 2 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Out of service | 30202 | 130203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Flags - EIM3.1 3 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Out of service | 30203 | 130204 | EIM3.1 4 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Out of service | 30204 | 130205 | EIM3.1 5 relay 4 wire break | X | X | X | X | X | X | X
Alarm status: Out of service | 30205 | 130206 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Out of service | 30206 | 130207 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Out of service | 30207 | 130208 | AC protections not running (differential current) | X |  | X | X | X
Alarm status: Out of service | 30208 | 130209 | AC data is missing (differential current) | X |  | X | X | X
Alarm status: Out of service | 30209 | 130210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Flags - GAM3.2 1 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30210 | 130211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Flags - GAM3.2 1 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Out of service | 30211 | 130212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Flags - GAM3.2 2 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30212 | 130213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Flags - GAM3.2 2 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Out of service | 30213 | 130214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Flags - GAM3.2 3 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30214 | 130215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Flags - GAM3.2 3 supply voltage low or missing | X | X | X | X | X | X | X
Alarm status: Out of service | 30215 | 130216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Flags - PSM3.2 4 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30216 | 130217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Flags - PSM3.2 4 supply voltage low | X | X | X | X | X | X | X
Alarm status: Out of service | 30217 | 130218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Flags - PSM3.2 5 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30218 | 130219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Flags - PSM3.2 5 supply voltage low | X | X | X | X | X | X | X
Alarm status: Out of service | 30219 | 130220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Flags - PSM3.2 6 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30220 | 130221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Flags - PSM3.2 6 supply voltage low | X | X | X | X | X | X | X
Alarm status: Out of service | 30221 | 130222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Flags - PSM3.2 7 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30222 | 130223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Flags - PSM3.2 7 supply voltage low | X | X | X | X | X | X | X
Alarm status: Out of service | 30223 | 130224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Flags - PSM3.2 8 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30224 | 130225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Flags - PSM3.2 8 supply voltage low | X | X | X | X | X | X | X
Alarm status: Out of service | 30225 | 130226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Flags - PSM3.2 9 supply voltage high | X | X | X | X | X | X | X
Alarm status: Out of service | 30226 | 130227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Flags - PSM3.2 9 supply voltage low | X | X | X | X | X | X | X
Alarm status: Out of service | 30228 | 130229 | Parameters - System - Monitoring - Duplicate controller ID - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30229 | 130230 | Parameters - System - Monitoring - Missing all controllers - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30231 | 130232 | Controller ID not configured | X | X | X | X | X | X | X
Alarm status: Out of service | 30236 | 130237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30237 | 130238 | Blackout detection mismatch | X |  | X | X | X
Alarm status: Out of service | 30240 | 130241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Flags - NTP server 1 could not connect | X | X | X | X | X | X | X
Alarm status: Out of service | 30241 | 130242 | Parameters - Communication - NTP - NTP server 1 no response - Information - Flags - NTP server 1 is not responding | X | X | X | X | X | X | X
Alarm status: Out of service | 30242 | 130243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Flags - NTP server 2 could not connect | X | X | X | X | X | X | X
Alarm status: Out of service | 30243 | 130244 | Parameters - Communication - NTP - NTP server 2 no response - Information - Flags - NTP server 2 is not responding | X | X | X | X | X | X | X
Alarm status: Out of service | 30244 | 130245 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30245 | 130246 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30246 | 130247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30247 | 130248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30296 | 130297 | Controller not part of system | X | X | X | X | X | X | X
Alarm status: Out of service | 30297 | 130298 | Different single-line configurations | X | X | X | X | X | X | X
Alarm status: Out of service | 30298 | 130299 | Single-line missing/none active | X | X | X | X | X | X | X
Alarm status: Out of service | 30299 | 130300 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30300 | 130301 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - Flags - CODESYS configuration conflict | X | X | X | X | X | X | X
Alarm status: Out of service | 30301 | 130302 | Parameters - CODESYS - Monitoring - Application not OK - Information - Flags - CODESYS application not OK | X | X | X | X | X | X | X
Alarm status: Out of service | 30302 | 130303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30303 | 130304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30304 | 130305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30305 | 130306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30306 | 130307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30307 | 130308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30308 | 130309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30309 | 130310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30310 | 130311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30311 | 130312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30312 | 130313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30313 | 130314 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30314 | 130315 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30315 | 130316 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30316 | 130317 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30317 | 130318 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30318 | 130319 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30319 | 130320 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30320 | 130321 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30321 | 130322 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30322 | 130323 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30323 | 130324 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30324 | 130325 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30325 | 130326 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30326 | 130327 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30327 | 130328 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30328 | 130329 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30329 | 130330 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30330 | 130331 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30331 | 130332 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30332 | 130333 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30333 | 130334 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30334 | 130335 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30335 | 130336 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30336 | 130337 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30337 | 130338 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30338 | 130339 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30339 | 130340 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30340 | 130341 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30341 | 130342 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30342 | 130343 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30343 | 130344 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30344 | 130345 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30345 | 130346 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30346 | 130347 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30347 | 130348 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30348 | 130349 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30349 | 130350 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30350 | 130351 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30351 | 130352 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30352 | 130353 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30353 | 130354 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30354 | 130355 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30355 | 130356 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30356 | 130357 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30357 | 130358 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30358 | 130359 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30359 | 130360 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30360 | 130361 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30361 | 130362 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30362 | 130363 | Digital custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30363 | 130364 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30364 | 130365 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30365 | 130366 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30366 | 130367 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30367 | 130368 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30368 | 130369 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30369 | 130370 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30370 | 130371 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30371 | 130372 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30372 | 130373 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30373 | 130374 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30374 | 130375 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30375 | 130376 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30376 | 130377 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30377 | 130378 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30378 | 130379 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30379 | 130380 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30380 | 130381 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30381 | 130382 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30382 | 130383 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30383 | 130384 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30384 | 130385 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30385 | 130386 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30386 | 130387 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30387 | 130388 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30388 | 130389 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30389 | 130390 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30390 | 130391 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30391 | 130392 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30392 | 130393 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30393 | 130394 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30394 | 130395 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30395 | 130396 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30396 | 130397 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30397 | 130398 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30398 | 130399 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30399 | 130400 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30400 | 130401 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30401 | 130402 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30402 | 130403 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30403 | 130404 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30404 | 130405 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30405 | 130406 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30406 | 130407 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30407 | 130408 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30408 | 130409 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30409 | 130410 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30410 | 130411 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30411 | 130412 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30412 | 130413 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30413 | 130414 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30414 | 130415 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30415 | 130416 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30416 | 130417 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30417 | 130418 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30418 | 130419 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30419 | 130420 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30420 | 130421 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30421 | 130422 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30422 | 130423 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30423 | 130424 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30424 | 130425 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30425 | 130426 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30426 | 130427 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30427 | 130428 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30428 | 130429 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30429 | 130430 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30430 | 130431 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30431 | 130432 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30432 | 130433 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30433 | 130434 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30434 | 130435 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30435 | 130436 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30436 | 130437 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30437 | 130438 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30438 | 130439 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30439 | 130440 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30440 | 130441 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30441 | 130442 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30442 | 130443 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30443 | 130444 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30444 | 130445 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30445 | 130446 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30446 | 130447 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30447 | 130448 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30448 | 130449 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30449 | 130450 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30450 | 130451 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30451 | 130452 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30452 | 130453 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30453 | 130454 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30454 | 130455 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30455 | 130456 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30456 | 130457 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30457 | 130458 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30458 | 130459 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30459 | 130460 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30460 | 130461 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30461 | 130462 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30462 | 130463 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30463 | 130464 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30464 | 130465 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30465 | 130466 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30466 | 130467 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30467 | 130468 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30468 | 130469 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30469 | 130470 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30470 | 130471 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30471 | 130472 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30472 | 130473 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30473 | 130474 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30474 | 130475 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30475 | 130476 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30476 | 130477 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30477 | 130478 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30478 | 130479 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30479 | 130480 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30480 | 130481 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30481 | 130482 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30482 | 130483 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30483 | 130484 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30484 | 130485 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30485 | 130486 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30486 | 130487 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30487 | 130488 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30488 | 130489 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30489 | 130490 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30490 | 130491 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30491 | 130492 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30492 | 130493 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30493 | 130494 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30494 | 130495 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30495 | 130496 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30496 | 130497 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30497 | 130498 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30498 | 130499 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30499 | 130500 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30500 | 130501 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30501 | 130502 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30502 | 130503 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30503 | 130504 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30504 | 130505 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30505 | 130506 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30506 | 130507 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30507 | 130508 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30508 | 130509 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30509 | 130510 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30510 | 130511 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30511 | 130512 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30512 | 130513 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30513 | 130514 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30514 | 130515 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30515 | 130516 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30516 | 130517 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30517 | 130518 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30518 | 130519 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30519 | 130520 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30520 | 130521 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30521 | 130522 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30522 | 130523 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30523 | 130524 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30524 | 130525 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30525 | 130526 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30526 | 130527 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30527 | 130528 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30528 | 130529 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30529 | 130530 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30530 | 130531 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30531 | 130532 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30532 | 130533 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30533 | 130534 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30534 | 130535 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30535 | 130536 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30536 | 130537 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30537 | 130538 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30538 | 130539 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30539 | 130540 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30540 | 130541 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30541 | 130542 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30542 | 130543 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30543 | 130544 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30544 | 130545 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30545 | 130546 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30546 | 130547 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30547 | 130548 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30548 | 130549 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30549 | 130550 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30550 | 130551 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30551 | 130552 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30552 | 130553 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30553 | 130554 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30554 | 130555 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30555 | 130556 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30556 | 130557 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30557 | 130558 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30558 | 130559 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30559 | 130560 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30560 | 130561 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30561 | 130562 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30562 | 130563 | Analogue custom alarm | X | X | X | X | X | X | X
Alarm status: Out of service | 30565 | 130566 | Parameters - Local - CustomLogic - Configuration invalid - Information - Flags - CustomLogic configuration invalid | X | X | X | X | X | X | X
Alarm status: Out of service | 30566 | 130567 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Flags - Digital AVR communication error | X |  | X | X | X
Alarm status: Out of service | 30567 | 130568 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30568 | 130569 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30569 | 130570 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30570 | 130571 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30571 | 130572 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30572 | 130573 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30573 | 130574 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30574 | 130575 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30575 | 130576 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30576 | 130577 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30577 | 130578 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30578 | 130579 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30579 | 130580 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30580 | 130581 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30581 | 130582 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30582 | 130583 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30583 | 130584 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30584 | 130585 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30585 | 130586 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30586 | 130587 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30587 | 130588 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30588 | 130589 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30589 | 130590 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30590 | 130591 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30591 | 130592 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30592 | 130593 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30593 | 130594 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30594 | 130595 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30595 | 130596 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30596 | 130597 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30597 | 130598 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30598 | 130599 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30599 | 130600 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30600 | 130601 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30601 | 130602 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30602 | 130603 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30603 | 130604 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30604 | 130605 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30605 | 130606 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30606 | 130607 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30607 | 130608 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30608 | 130609 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30609 | 130610 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30610 | 130611 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30611 | 130612 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30612 | 130613 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30613 | 130614 | DAVR unsupported AC configuration | X |  | X | X | X
Alarm status: Out of service | 30614 | 130615 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Flags - Illegal DAVR configuration | X |  | X | X | X
Alarm status: Out of service | 30615 | 130616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Flags - Generator under-voltage 1 | X |  | X | X | X
Alarm status: Out of service | 30615 | 130616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Flags - Busbar A under-voltage 1 |  | X
Alarm status: Out of service | 30615 | 130616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 | [5 empty] | X | X
Alarm status: Out of service | 30616 | 130617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Flags - Generator under-voltage 2 | X |  | X | X | X
Alarm status: Out of service | 30616 | 130617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Flags - Busbar A under-voltage 2 |  | X
Alarm status: Out of service | 30616 | 130617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 | [5 empty] | X | X
Alarm status: Out of service | 30617 | 130618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Flags - Generator under-voltage 3 | X |  | X | X | X
Alarm status: Out of service | 30617 | 130618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Flags - Busbar A under-voltage 3 |  | X
Alarm status: Out of service | 30617 | 130618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 | [5 empty] | X | X
Alarm status: Out of service | 30618 | 130619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Flags - Generator over-voltage 1 | X |  | X | X | X
Alarm status: Out of service | 30618 | 130619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Flags - Busbar A over-voltage 1 |  | X
Alarm status: Out of service | 30618 | 130619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 | [5 empty] | X | X
Alarm status: Out of service | 30619 | 130620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Flags - Generator over-voltage 2 | X |  | X | X | X
Alarm status: Out of service | 30619 | 130620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Flags - Busbar A over-voltage 2 |  | X
Alarm status: Out of service | 30619 | 130620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 | [5 empty] | X | X
Alarm status: Out of service | 30620 | 130621 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Flags - Generator voltage unbalance | X |  | X | X | X
Alarm status: Out of service | 30620 | 130621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Flags - Busbar A voltage unbalance |  | X
Alarm status: Out of service | 30620 | 130621 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance | [5 empty] | X | X
Alarm status: Out of service | 30621 | 130622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Flags - Generator negative sequence voltage | X |  | X | X | X
Alarm status: Out of service | 30621 | 130622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Flags - Busbar A negative sequence voltage |  | X
Alarm status: Out of service | 30621 | 130622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Mains negative sequence voltage | [5 empty] | X | X
Alarm status: Out of service | 30622 | 130623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Flags - Generator zero sequence voltage | X |  | X | X | X
Alarm status: Out of service | 30622 | 130623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Flags - Busbar A zero sequence voltage |  | X
Alarm status: Out of service | 30622 | 130623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Mains zero sequence voltage | [5 empty] | X | X
Alarm status: Out of service | 30623 | 130624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Flags - Generator positive sequence under-voltage | X |  | X | X | X
Alarm status: Out of service | 30623 | 130624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar A positive sequence under-voltage |  | X
Alarm status: Out of service | 30623 | 130624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Mains positive sequence under-voltage | [5 empty] | X | X
Alarm status: Out of service | 30624 | 130625 | Parameters - Generator - Current protections - Over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30624 | 130625 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Flags |  | X
Alarm status: Out of service | 30624 | 130625 | Parameters - Mains - Current protections - Over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30625 | 130626 | Parameters - Generator - Current protections - Over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30625 | 130626 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Flags |  | X
Alarm status: Out of service | 30625 | 130626 | Parameters - Mains - Current protections - Over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30626 | 130627 | Parameters - Generator - Current protections - Over-current 3 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30626 | 130627 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Flags |  | X
Alarm status: Out of service | 30626 | 130627 | Parameters - Mains - Current protections - Over-current 3 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30627 | 130628 | Parameters - Generator - Current protections - Over-current 4 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30627 | 130628 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Flags |  | X
Alarm status: Out of service | 30627 | 130628 | Parameters - Mains - Current protections - Over-current 4 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30628 | 130629 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30628 | 130629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Flags |  | X
Alarm status: Out of service | 30628 | 130629 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30629 | 130630 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30629 | 130630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Flags |  | X
Alarm status: Out of service | 30629 | 130630 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30630 | 130631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30630 | 130631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Flags |  | X
Alarm status: Out of service | 30630 | 130631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30631 | 130632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30631 | 130632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Flags |  | X
Alarm status: Out of service | 30631 | 130632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30632 | 130633 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30632 | 130633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Flags |  | X
Alarm status: Out of service | 30632 | 130633 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30633 | 130634 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30633 | 130634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Flags |  | X
Alarm status: Out of service | 30633 | 130634 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30634 | 130635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Flags |  | X
Alarm status: Out of service | 30635 | 130636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Flags |  | X
Alarm status: Out of service | 30636 | 130637 | Parameters - Generator - Current protections - Negative sequence current - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30636 | 130637 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Flags |  | X
Alarm status: Out of service | 30636 | 130637 | Parameters - Mains - Current protections - Negative sequence current - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30637 | 130638 | Parameters - Generator - Current protections - Zero sequence current - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30637 | 130638 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Flags |  | X
Alarm status: Out of service | 30637 | 130638 | Parameters - Mains - Current protections - Zero sequence current - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30638 | 130639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Flags - Generator over-frequency 1 | X |  | X | X | X
Alarm status: Out of service | 30638 | 130639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Flags - Busbar A over-frequency 1 |  | X
Alarm status: Out of service | 30638 | 130639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 | [5 empty] | X | X
Alarm status: Out of service | 30639 | 130640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Flags - Generator over-frequency 2 | X |  | X | X | X
Alarm status: Out of service | 30639 | 130640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Flags - Busbar A over-frequency 2 |  | X
Alarm status: Out of service | 30639 | 130640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 | [5 empty] | X | X
Alarm status: Out of service | 30640 | 130641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Flags - Generator over-frequency 3 | X |  | X | X | X
Alarm status: Out of service | 30640 | 130641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Flags - Busbar A over-frequency 3 |  | X
Alarm status: Out of service | 30640 | 130641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 | [5 empty] | X | X
Alarm status: Out of service | 30641 | 130642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Flags - Generator under-frequency 1 | X |  | X | X | X
Alarm status: Out of service | 30641 | 130642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Flags - Busbar A under-frequency 1 |  | X
Alarm status: Out of service | 30641 | 130642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 | [5 empty] | X | X
Alarm status: Out of service | 30642 | 130643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Flags - Generator under-frequency 2 | X |  | X | X | X
Alarm status: Out of service | 30642 | 130643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Flags - Busbar A under-frequency 2 |  | X
Alarm status: Out of service | 30642 | 130643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 | [5 empty] | X | X
Alarm status: Out of service | 30643 | 130644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Flags - Generator under-frequency 3 | X |  | X | X | X
Alarm status: Out of service | 30643 | 130644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Flags - Busbar A under-frequency 3 |  | X
Alarm status: Out of service | 30643 | 130644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 | [5 empty] | X | X
Alarm status: Out of service | 30644 | 130645 | Parameters - Generator - Power protections - Overload 1 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30644 | 130645 | Parameters - Busbar A - Power protections - Power export 1 - Information - Flags |  | X
Alarm status: Out of service | 30644 | 130645 | Parameters - Mains - Power protections - Overload 1 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30645 | 130646 | Parameters - Generator - Power protections - Overload 2 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30645 | 130646 | Parameters - Busbar A - Power protections - Power export 2 - Information - Flags |  | X
Alarm status: Out of service | 30645 | 130646 | Parameters - Mains - Power protections - Overload 2 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30646 | 130647 | Parameters - Generator - Power protections - Overload 3 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30646 | 130647 | Parameters - Busbar A - Power protections - Power export 3 - Information - Flags |  | X
Alarm status: Out of service | 30646 | 130647 | Parameters - Mains - Power protections - Overload 3 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30647 | 130648 | Parameters - Generator - Power protections - Overload 4 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30647 | 130648 | Parameters - Busbar A - Power protections - Power export 4 - Information - Flags |  | X
Alarm status: Out of service | 30647 | 130648 | Parameters - Mains - Power protections - Overload 4 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30648 | 130649 | Parameters - Generator - Power protections - Overload 5 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30648 | 130649 | Parameters - Busbar A - Power protections - Power export 5 - Information - Flags |  | X
Alarm status: Out of service | 30648 | 130649 | Parameters - Mains - Power protections - Overload 5 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30649 | 130650 | Parameters - Generator - Power protections - Reverse power 1 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30649 | 130650 | Parameters - Busbar A - Power protections - Power import 1 - Information - Flags |  | X
Alarm status: Out of service | 30649 | 130650 | Parameters - Mains - Power protections - Reverse power 1 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30650 | 130651 | Parameters - Generator - Power protections - Reverse power 2 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30650 | 130651 | Parameters - Busbar A - Power protections - Power import 2 - Information - Flags |  | X
Alarm status: Out of service | 30650 | 130651 | Parameters - Mains - Power protections - Reverse power 2 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30651 | 130652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30651 | 130652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Flags |  | X
Alarm status: Out of service | 30651 | 130652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30652 | 130653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30652 | 130653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Flags |  | X
Alarm status: Out of service | 30652 | 130653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30653 | 130654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30653 | 130654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Flags |  | X
Alarm status: Out of service | 30653 | 130654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30654 | 130655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30654 | 130655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Flags |  | X
Alarm status: Out of service | 30654 | 130655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Flags | [5 empty] | X | X
Alarm status: Out of service | 30655 | 130656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Flags - Mains over-voltage 1 |  |  | X | X
Alarm status: Out of service | 30655 | 130656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Flags - Busbar over-voltage 1 | X |  |  |  | X | X | X
Alarm status: Out of service | 30655 | 130656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Flags - Busbar B over-voltage 1 |  | X
Alarm status: Out of service | 30656 | 130657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Flags - Mains over-voltage 2 |  |  | X | X
Alarm status: Out of service | 30656 | 130657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Flags - Busbar over-voltage 2 | X |  |  |  | X | X | X
Alarm status: Out of service | 30656 | 130657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Flags - Busbar B over-voltage 2 |  | X
Alarm status: Out of service | 30657 | 130658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Flags - Mains over-voltage 3 |  |  | X | X
Alarm status: Out of service | 30657 | 130658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Flags - Busbar over-voltage 3 | X |  |  |  | X | X | X
Alarm status: Out of service | 30657 | 130658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Flags - Busbar B over-voltage 3 |  | X
Alarm status: Out of service | 30658 | 130659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Flags - Mains under-voltage 1 |  |  | X | X
Alarm status: Out of service | 30658 | 130659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Flags - Busbar under-voltage 1 | X |  |  |  | X | X | X
Alarm status: Out of service | 30658 | 130659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Flags - Busbar B under-voltage 1 |  | X
Alarm status: Out of service | 30659 | 130660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Flags - Mains under-voltage 2 |  |  | X | X
Alarm status: Out of service | 30659 | 130660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Flags - Busbar under-voltage 2 | X |  |  |  | X | X | X
Alarm status: Out of service | 30659 | 130660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Flags - Busbar B under-voltage 2 |  | X
Alarm status: Out of service | 30660 | 130661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Flags - Mains under-voltage 3 |  |  | X | X
Alarm status: Out of service | 30660 | 130661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Flags - Busbar under-voltage 3 | X |  |  |  | X | X | X
Alarm status: Out of service | 30660 | 130661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Flags - Busbar B under-voltage 3 |  | X
Alarm status: Out of service | 30661 | 130662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Flags - Mains under-voltage 4 |  |  | X | X
Alarm status: Out of service | 30661 | 130662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Flags - Busbar under-voltage 4 | X |  |  |  | X | X | X
Alarm status: Out of service | 30661 | 130662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Flags - Busbar B under-voltage 4 |  | X
Alarm status: Out of service | 30662 | 130663 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Flags - Mains voltage unbalance |  |  | X | X
Alarm status: Out of service | 30662 | 130663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Flags - Busbar voltage unbalance | X |  |  |  | X | X | X
Alarm status: Out of service | 30662 | 130663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Flags - Busbar B voltage unbalance |  | X
Alarm status: Out of service | 30663 | 130664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Flags - Mains over-frequency 1 |  |  | X | X
Alarm status: Out of service | 30663 | 130664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Flags - Busbar over-frequency 1 | X |  |  |  | X | X | X
Alarm status: Out of service | 30663 | 130664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Flags - Busbar B over-frequency 1 |  | X
Alarm status: Out of service | 30664 | 130665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Flags - Mains over-frequency 2 |  |  | X | X
Alarm status: Out of service | 30664 | 130665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Flags - Busbar over-frequency 2 | X |  |  |  | X | X | X
Alarm status: Out of service | 30664 | 130665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Flags - Busbar B over-frequency 2 |  | X
Alarm status: Out of service | 30665 | 130666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Flags - Mains over-frequency 3 |  |  | X | X
Alarm status: Out of service | 30665 | 130666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Flags - Busbar over-frequency 3 | X |  |  |  | X | X | X
Alarm status: Out of service | 30665 | 130666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Flags - Busbar B over-frequency 3 |  | X
Alarm status: Out of service | 30666 | 130667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Flags - Mains under-frequency 1 |  |  | X | X
Alarm status: Out of service | 30666 | 130667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Flags - Busbar under-frequency 1 | X |  |  |  | X | X | X
Alarm status: Out of service | 30666 | 130667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Flags - Busbar B under-frequency 1 |  | X
Alarm status: Out of service | 30667 | 130668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Flags - Mains under-frequency 2 |  |  | X | X
Alarm status: Out of service | 30667 | 130668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Flags - Busbar under-frequency 2 | X |  |  |  | X | X | X
Alarm status: Out of service | 30667 | 130668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Flags - Busbar B under-frequency 2 |  | X
Alarm status: Out of service | 30668 | 130669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Flags - Mains under-frequency 3 |  |  | X | X
Alarm status: Out of service | 30668 | 130669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Flags - Busbar under-frequency 3 | X |  |  |  | X | X | X
Alarm status: Out of service | 30668 | 130669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Flags - Busbar B under-frequency 3 |  | X
Alarm status: Out of service | 30669 | 130670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Flags - Mains under-frequency 4 |  |  | X | X
Alarm status: Out of service | 30669 | 130670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Flags - Busbar under-frequency 4 | X |  |  |  | X | X | X
Alarm status: Out of service | 30669 | 130670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Flags - Busbar B under-frequency 4 |  | X
Alarm status: Out of service | 30670 | 130671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage |  |  | X | X
Alarm status: Out of service | 30670 | 130671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Flags - Busbar negative sequence voltage | X |  |  |  | X | X | X
Alarm status: Out of service | 30670 | 130671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Flags - Busbar B negative sequence voltage |  | X
Alarm status: Out of service | 30671 | 130672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage |  |  | X | X
Alarm status: Out of service | 30671 | 130672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Flags - Busbar zero sequence voltage | X |  |  |  | X | X | X
Alarm status: Out of service | 30671 | 130672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Flags - Busbar B zero sequence voltage |  | X
Alarm status: Out of service | 30672 | 130673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage |  |  | X | X
Alarm status: Out of service | 30672 | 130673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar positive sequence under-voltage | X |  |  |  | X | X | X
Alarm status: Out of service | 30672 | 130673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Flags - Busbar B positive sequence under-voltage |  | X
Alarm status: Out of service | 30717 | 130718 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 1 | X |  | X | X | X
Alarm status: Out of service | 30718 | 130719 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 2 | X |  | X | X | X
Alarm status: Out of service | 30719 | 130720 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 3 | X |  | X | X | X
Alarm status: Out of service | 30720 | 130721 | Parameters - Engine - Maintenance - Service timer - Information - Flags - Service timer 4 | X |  | X | X | X
Alarm status: Out of service | 30721 | 130722 | External MB open failure | X | X | X | X | X | X | X
Alarm status: Out of service | 30722 | 130723 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30723 | 130724 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30724 | 130725 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30725 | 130726 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30726 | 130727 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - Flags | X |  | X | X | X
Alarm status: Out of service | 30727 | 130728 | Parameters - Breakers - Close before excitation - CBE failure - Information - Flags - Close before excitation failure | X |  | X | X | X
Alarm status: Out of service | 30728 | 130729 | Load too high | X | X | X | X | X | X | X
Alarm status: Out of service | 30729 | 130730 | ID to run configuration failure | [5 empty] | X | X
Alarm status: Out of service | 30731 | 130732 | Parameters - System - Monitoring - Missing any genset controller - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30732 | 130733 | Parameters - System - Monitoring - Missing any mains controller - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30733 | 130734 | Parameters - System - Monitoring - Missing any bustie controller - Information - Flags - Missing any bus tie controller | X | X | X | X | X | X | X
Alarm status: Out of service | 30734 | 130735 | Can ID not available | X | X | X | X | X | X | X
Alarm status: Out of service | 30735 | 130736 | Duplicated CAN IDs | X | X | X | X | X | X | X
Alarm status: Out of service | 30736 | 130737 | Parameters - Local power management - Alarms - Busbar blocked - Information - Flags - Busbar blocked due to position failure | X |  | X | X | X | X | X
Alarm status: Out of service | 30737 | 130738 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Flags - Busbar A blocked due to position failure |  | X
Alarm status: Out of service | 30738 | 130739 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Flags - Busbar B blocked due to position failure |  | X
Alarm status: Out of service | 30739 | 130740 | Parameters - System - Monitoring - BTB 33 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30740 | 130741 | Parameters - System - Monitoring - BTB 34 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30741 | 130742 | Parameters - System - Monitoring - BTB 35 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30742 | 130743 | Parameters - System - Monitoring - BTB 36 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30743 | 130744 | Parameters - System - Monitoring - BTB 37 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30744 | 130745 | Parameters - System - Monitoring - BTB 38 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30745 | 130746 | Parameters - System - Monitoring - BTB 39 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30746 | 130747 | Parameters - System - Monitoring - BTB 40 position failure - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30747 | 130748 | Primary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm status: Out of service | 30748 | 130749 | Primary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm status: Out of service | 30749 | 130750 | Primary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm status: Out of service | 30750 | 130751 | Primary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm status: Out of service | 30751 | 130752 | Primary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm status: Out of service | 30752 | 130753 | Primary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm status: Out of service | 30753 | 130754 | Primary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm status: Out of service | 30754 | 130755 | Primary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm status: Out of service | 30755 | 130756 | Primary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm status: Out of service | 30756 | 130757 | Primary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm status: Out of service | 30757 | 130758 | Primary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm status: Out of service | 30758 | 130759 | Primary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm status: Out of service | 30759 | 130760 | Primary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm status: Out of service | 30760 | 130761 | Primary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm status: Out of service | 30761 | 130762 | Primary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm status: Out of service | 30762 | 130763 | Primary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm status: Out of service | 30763 | 130764 | Primary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm status: Out of service | 30764 | 130765 | Primary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm status: Out of service | 30765 | 130766 | Primary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm status: Out of service | 30766 | 130767 | Primary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm status: Out of service | 30767 | 130768 | Primary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm status: Out of service | 30768 | 130769 | Primary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm status: Out of service | 30769 | 130770 | Primary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm status: Out of service | 30770 | 130771 | Primary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm status: Out of service | 30771 | 130772 | Primary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm status: Out of service | 30772 | 130773 | Primary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm status: Out of service | 30773 | 130774 | Primary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm status: Out of service | 30774 | 130775 | Primary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm status: Out of service | 30775 | 130776 | Primary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm status: Out of service | 30776 | 130777 | Primary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm status: Out of service | 30777 | 130778 | Primary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm status: Out of service | 30778 | 130779 | Primary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm status: Out of service | 30779 | 130780 | Primary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm status: Out of service | 30780 | 130781 | Primary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm status: Out of service | 30781 | 130782 | Primary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm status: Out of service | 30782 | 130783 | Primary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm status: Out of service | 30783 | 130784 | Primary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm status: Out of service | 30784 | 130785 | Primary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm status: Out of service | 30785 | 130786 | Primary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm status: Out of service | 30786 | 130787 | Primary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm status: Out of service | 30787 | 130788 | Secondary CAN missing ID 1 | X | X | X | X | X | X | X
Alarm status: Out of service | 30788 | 130789 | Secondary CAN missing ID 2 | X | X | X | X | X | X | X
Alarm status: Out of service | 30789 | 130790 | Secondary CAN missing ID 3 | X | X | X | X | X | X | X
Alarm status: Out of service | 30790 | 130791 | Secondary CAN missing ID 4 | X | X | X | X | X | X | X
Alarm status: Out of service | 30791 | 130792 | Secondary CAN missing ID 5 | X | X | X | X | X | X | X
Alarm status: Out of service | 30792 | 130793 | Secondary CAN missing ID 6 | X | X | X | X | X | X | X
Alarm status: Out of service | 30793 | 130794 | Secondary CAN missing ID 7 | X | X | X | X | X | X | X
Alarm status: Out of service | 30794 | 130795 | Secondary CAN missing ID 8 | X | X | X | X | X | X | X
Alarm status: Out of service | 30795 | 130796 | Secondary CAN missing ID 9 | X | X | X | X | X | X | X
Alarm status: Out of service | 30796 | 130797 | Secondary CAN missing ID 10 | X | X | X | X | X | X | X
Alarm status: Out of service | 30797 | 130798 | Secondary CAN missing ID 11 | X | X | X | X | X | X | X
Alarm status: Out of service | 30798 | 130799 | Secondary CAN missing ID 12 | X | X | X | X | X | X | X
Alarm status: Out of service | 30799 | 130800 | Secondary CAN missing ID 13 | X | X | X | X | X | X | X
Alarm status: Out of service | 30800 | 130801 | Secondary CAN missing ID 14 | X | X | X | X | X | X | X
Alarm status: Out of service | 30801 | 130802 | Secondary CAN missing ID 15 | X | X | X | X | X | X | X
Alarm status: Out of service | 30802 | 130803 | Secondary CAN missing ID 16 | X | X | X | X | X | X | X
Alarm status: Out of service | 30803 | 130804 | Secondary CAN missing ID 17 | X | X | X | X | X | X | X
Alarm status: Out of service | 30804 | 130805 | Secondary CAN missing ID 18 | X | X | X | X | X | X | X
Alarm status: Out of service | 30805 | 130806 | Secondary CAN missing ID 19 | X | X | X | X | X | X | X
Alarm status: Out of service | 30806 | 130807 | Secondary CAN missing ID 20 | X | X | X | X | X | X | X
Alarm status: Out of service | 30807 | 130808 | Secondary CAN missing ID 21 | X | X | X | X | X | X | X
Alarm status: Out of service | 30808 | 130809 | Secondary CAN missing ID 22 | X | X | X | X | X | X | X
Alarm status: Out of service | 30809 | 130810 | Secondary CAN missing ID 23 | X | X | X | X | X | X | X
Alarm status: Out of service | 30810 | 130811 | Secondary CAN missing ID 24 | X | X | X | X | X | X | X
Alarm status: Out of service | 30811 | 130812 | Secondary CAN missing ID 25 | X | X | X | X | X | X | X
Alarm status: Out of service | 30812 | 130813 | Secondary CAN missing ID 26 | X | X | X | X | X | X | X
Alarm status: Out of service | 30813 | 130814 | Secondary CAN missing ID 27 | X | X | X | X | X | X | X
Alarm status: Out of service | 30814 | 130815 | Secondary CAN missing ID 28 | X | X | X | X | X | X | X
Alarm status: Out of service | 30815 | 130816 | Secondary CAN missing ID 29 | X | X | X | X | X | X | X
Alarm status: Out of service | 30816 | 130817 | Secondary CAN missing ID 30 | X | X | X | X | X | X | X
Alarm status: Out of service | 30817 | 130818 | Secondary CAN missing ID 31 | X | X | X | X | X | X | X
Alarm status: Out of service | 30818 | 130819 | Secondary CAN missing ID 32 | X | X | X | X | X | X | X
Alarm status: Out of service | 30819 | 130820 | Secondary CAN missing ID 33 | X | X | X | X | X | X | X
Alarm status: Out of service | 30820 | 130821 | Secondary CAN missing ID 34 | X | X | X | X | X | X | X
Alarm status: Out of service | 30821 | 130822 | Secondary CAN missing ID 35 | X | X | X | X | X | X | X
Alarm status: Out of service | 30822 | 130823 | Secondary CAN missing ID 36 | X | X | X | X | X | X | X
Alarm status: Out of service | 30823 | 130824 | Secondary CAN missing ID 37 | X | X | X | X | X | X | X
Alarm status: Out of service | 30824 | 130825 | Secondary CAN missing ID 38 | X | X | X | X | X | X | X
Alarm status: Out of service | 30825 | 130826 | Secondary CAN missing ID 39 | X | X | X | X | X | X | X
Alarm status: Out of service | 30826 | 130827 | Secondary CAN missing ID 40 | X | X | X | X | X | X | X
Alarm status: Out of service | 30827 | 130828 | Priority error | X | X | X | X | X | X | X
Alarm status: Out of service | 30828 | 130829 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - Flags - NEL 1 over-current | X |  | X | X | X | X | X
Alarm status: Out of service | 30829 | 130830 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - Flags - NEL 1 under-frequency | X |  | X | X | X | X | X
Alarm status: Out of service | 30830 | 130831 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - Flags - NEL 1 overload 1 | X |  | X | X | X | X | X
Alarm status: Out of service | 30831 | 130832 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - Flags - NEL 1 overload 2 | X |  | X | X | X | X | X
Alarm status: Out of service | 30832 | 130833 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - Flags - NEL 1 reactive overload | X |  | X | X | X | X | X
Alarm status: Out of service | 30833 | 130834 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - Flags - NEL 2 over-current | X |  | X | X | X | X | X
Alarm status: Out of service | 30834 | 130835 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - Flags - NEL 2 under-frequency | X |  | X | X | X | X | X
Alarm status: Out of service | 30835 | 130836 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - Flags - NEL 2 overload 1 | X |  | X | X | X | X | X
Alarm status: Out of service | 30836 | 130837 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - Flags - NEL 2 overload 2 | X |  | X | X | X | X | X
Alarm status: Out of service | 30837 | 130838 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - Flags - NEL 2 reactive overload | X |  | X | X | X | X | X
Alarm status: Out of service | 30838 | 130839 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - Flags - NEL 3 over-current | X |  | X | X | X | X | X
Alarm status: Out of service | 30839 | 130840 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - Flags - NEL 3 under-frequency | X |  | X | X | X | X | X
Alarm status: Out of service | 30840 | 130841 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - Flags - NEL 3 overload 1 | X |  | X | X | X | X | X
Alarm status: Out of service | 30841 | 130842 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - Flags - NEL 3 overload 2 | X |  | X | X | X | X | X
Alarm status: Out of service | 30842 | 130843 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - Flags - NEL 3 reactive overload | X |  | X | X | X | X | X
Alarm status: Out of service | 30843 | 130844 | Parameters - System - Monitoring - Single-line hazard - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30844 | 130845 | ID not present | X | X | X | X | X | X | X
Alarm status: Out of service | 30845 | 130846 | Unsupported application | X | X | X | X | X | X | X
Alarm status: Out of service | 30846 | 130847 | Application internal CAN protocol conflict | X | X | X | X | X | X | X
Alarm status: Out of service | 30847 | 130848 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Flags - Section P> | X | X | X | X | X | X | X
Alarm status: Out of service | 30848 | 130849 | Dry mode: Voltage level unexpected | X |  | X | X | X
Alarm status: Out of service | 30849 | 130850 | Invalid DAVR configuration | X |  | X | X | X
Alarm status: Out of service | 30850 | 130851 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30852 | 130853 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30854 | 130855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | X |  | X | X | X
Alarm status: Out of service | 30854 | 130855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch |  | X
Alarm status: Out of service | 30854 | 130855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | [5 empty] | X | X
Alarm status: Out of service | 30855 | 130856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch |  |  |  | X
Alarm status: Out of service | 30855 | 130856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Flags - Breaker vector mismatch | [6 empty] | X
Alarm status: Out of service | 30857 | 130858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30858 | 130859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30859 | 130860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30860 | 130861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30861 | 130862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Out of service | 30862 | 130863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Out of service | 30863 | 130864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Out of service | 30864 | 130865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Flags - Reference B phase sequence error | X | X | X | X | X | X | X
Alarm status: Out of service | 30865 | 130866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Out of service | 30866 | 130867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Out of service | 30867 | 130868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Out of service | 30868 | 130869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Flags - Reference A phase sequence error | X | X | X | X | X | X | X
Alarm status: Out of service | 30869 | 130870 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Out of service | 30870 | 130871 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Out of service | 30871 | 130872 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Out of service | 30872 | 130873 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Out of service | 30873 | 130874 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Out of service | 30874 | 130875 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Out of service | 30875 | 130876 | AC protections not running | X | X | X | X | X | X | X
Alarm status: Out of service | 30876 | 130877 | AC data is missing | X | X | X | X | X | X | X
Alarm status: Out of service | 30877 | 130878 | Live voltage detected | X | X | X | X | X | X | X
Alarm status: Out of service | 30878 | 130879 | Internal issue detected. A restart is required soon! | X | X | X | X | X | X | X
Alarm status: Out of service | 30879 | 130880 | Parameters - System - Monitoring - Missing controllers - Information - Flags | X | X | X | X | X | X | X
Alarm status: Out of service | 30880 | 130881 | Card issue detected | X | X | X | X | X | X | X
Alarm status: Out of service | 30881 | 130882 | Card configuration failed | X | X | X | X | X | X | X
Alarm status: Out of service | 30882 | 130883 | Unknown traffic on DEIF network | X | X | X | X | X | X | X
Alarm status: Out of service | 30883 | 130884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Out of service | 30884 | 130885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Out of service | 30885 | 130886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Flags - Fill failure | X |  | X | X | X
Alarm status: Out of service | 30886 | 130887 | Local IO service error | X | X | X | X | X | X | X
Alarm status: Out of service | 30887 | 130888 | App logging failure | X | X | X | X | X | X | X
Alarm status: Out of service | 30888 | 130889 | Event logging failure | X | X | X | X | X | X | X
Alarm status: Out of service | 30889 | 130890 | Licence error | X | X | X | X | X | X | X
Alarm status: Out of service | 30890 | 130891 | Brightness is dimmed according to temperature | X | X | X | X | X | X | X
Alarm status: Out of service | 30891 | 130892 | Parameters - Grid code - Mains sync inhibit - Information - Flags |  |  | X | X
Alarm status: Out of service | 30892 | 130893 | Parameters - Grid code - Capability curve - Import protection - Information - Flags - Power import capability curve protection |  |  | X | X
Alarm status: Out of service | 30893 | 130894 | Parameters - Grid code - Capability curve - Export protection - Information - Flags - Power export capability curve protection |  |  | X | X
Alarm status: Out of service | 30894 | 130895 | Hardware is not compatible based on module versions | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32003 | 132004 | Parameters - Engine - Stop sequence - Stop failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32005 | 132006 | Parameters - Engine - Start sequence - Crank failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32006 | 132007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32007 | 132008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32008 | 132009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32009 | 132010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32010 | 132011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32013 | 132014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32014 | 132015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32015 | 132016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32016 | 132017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32017 | 132018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32018 | 132019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32019 | 132020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32020 | 132021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32021 | 132022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32022 | 132023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32027 | 132028 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32041 | 132042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32041 | 132042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Delay |  | X
Alarm status: Delay timer running | 32041 | 132042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32042 | 132043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32042 | 132043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Delay |  | X
Alarm status: Delay timer running | 32042 | 132043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32043 | 132044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32043 | 132044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Delay |  | X
Alarm status: Delay timer running | 32043 | 132044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32044 | 132045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32044 | 132045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Delay |  | X
Alarm status: Delay timer running | 32044 | 132045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32045 | 132046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32045 | 132046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Delay |  | X
Alarm status: Delay timer running | 32045 | 132046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32046 | 132047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32046 | 132047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Delay |  | X
Alarm status: Delay timer running | 32046 | 132047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32049 | 132050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Delay |  |  |  | X
Alarm status: Delay timer running | 32049 | 132050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Delay | [6 empty] | X
Alarm status: Delay timer running | 32050 | 132051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Delay |  |  |  | X
Alarm status: Delay timer running | 32050 | 132051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Delay | [6 empty] | X
Alarm status: Delay timer running | 32051 | 132052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Delay |  |  |  | X
Alarm status: Delay timer running | 32051 | 132052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Delay | [6 empty] | X
Alarm status: Delay timer running | 32052 | 132053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Delay |  |  |  | X
Alarm status: Delay timer running | 32052 | 132053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Delay | [6 empty] | X
Alarm status: Delay timer running | 32053 | 132054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Delay |  |  |  | X
Alarm status: Delay timer running | 32053 | 132054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Delay | [6 empty] | X
Alarm status: Delay timer running | 32054 | 132055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Delay |  |  |  | X
Alarm status: Delay timer running | 32054 | 132055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Delay | [6 empty] | X
Alarm status: Delay timer running | 32060 | 132061 | Parameters - Mains - AC setup - Phase sequence error - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32060 | 132061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32060 | 132061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Delay |  | X
Alarm status: Delay timer running | 32061 | 132062 | Parameters - Generator - AC setup - Phase sequence error - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32061 | 132062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Delay |  | X
Alarm status: Delay timer running | 32061 | 132062 | Parameters - Mains - AC setup - Phase sequence error - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32062 | 132063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32103 | 132104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32103 | 132104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32103 | 132104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information - Delay |  | X
Alarm status: Delay timer running | 32108 | 132109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32108 | 132109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32108 | 132109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32109 | 132110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32109 | 132110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32109 | 132110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32110 | 132111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32110 | 132111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32110 | 132111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32111 | 132112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32111 | 132112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32111 | 132112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32116 | 132117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32117 | 132118 | Parameters - Generator - Current protections - High set differential current - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32119 | 132120 | Parameters - Local - Mode - Not under remote control - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32128 | 132129 | Parameters - Custom alarm - Custom alarm 0 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32129 | 132130 | Parameters - Custom alarm - Custom alarm 1 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32130 | 132131 | Parameters - Custom alarm - Custom alarm 2 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32131 | 132132 | Parameters - Custom alarm - Custom alarm 3 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32132 | 132133 | Parameters - Custom alarm - Custom alarm 4 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32133 | 132134 | Parameters - Custom alarm - Custom alarm 5 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32134 | 132135 | Parameters - Custom alarm - Custom alarm 6 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32135 | 132136 | Parameters - Custom alarm - Custom alarm 7 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32136 | 132137 | Parameters - Custom alarm - Custom alarm 8 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32137 | 132138 | Parameters - Custom alarm - Custom alarm 9 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32138 | 132139 | Parameters - Custom alarm - Custom alarm 10 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32139 | 132140 | Parameters - Custom alarm - Custom alarm 11 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32140 | 132141 | Parameters - Custom alarm - Custom alarm 12 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32141 | 132142 | Parameters - Custom alarm - Custom alarm 13 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32142 | 132143 | Parameters - Custom alarm - Custom alarm 14 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32143 | 132144 | Parameters - Custom alarm - Custom alarm 15 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32144 | 132145 | Parameters - Custom alarm - Custom alarm 16 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32145 | 132146 | Parameters - Custom alarm - Custom alarm 17 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32146 | 132147 | Parameters - Custom alarm - Custom alarm 18 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32147 | 132148 | Parameters - Custom alarm - Custom alarm 19 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32148 | 132149 | Parameters - Custom alarm - Custom alarm 20 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32149 | 132150 | Parameters - Custom alarm - Custom alarm 21 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32150 | 132151 | Parameters - Custom alarm - Custom alarm 22 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32151 | 132152 | Parameters - Custom alarm - Custom alarm 23 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32152 | 132153 | Parameters - Custom alarm - Custom alarm 24 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32153 | 132154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32154 | 132155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32163 | 132164 | Required hardware card(s) not found - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32164 | 132165 | Software mismatch on hardware module(s) - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32165 | 132166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Delay |  |  | X
Alarm status: Delay timer running | 32165 | 132166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Delay | X |  |  |  | X | X
Alarm status: Delay timer running | 32165 | 132166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Delay |  | X
Alarm status: Delay timer running | 32166 | 132167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Delay | X |  | X |  | X
Alarm status: Delay timer running | 32166 | 132167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Delay |  | X
Alarm status: Delay timer running | 32166 | 132167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Delay | [5 empty] | X
Alarm status: Delay timer running | 32167 | 132168 | Parameters - Mains - AC setup - L1 wire break - Information - Delay |  |  | X
Alarm status: Delay timer running | 32167 | 132168 | Parameters - Busbar - AC setup - L1 wire break - Information - Delay | X |  |  |  | X | X
Alarm status: Delay timer running | 32167 | 132168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Delay |  | X
Alarm status: Delay timer running | 32168 | 132169 | Parameters - Mains - AC setup - L2 wire break - Information - Delay |  |  | X
Alarm status: Delay timer running | 32168 | 132169 | Parameters - Busbar - AC setup - L2 wire break - Information - Delay | X |  |  |  | X | X
Alarm status: Delay timer running | 32168 | 132169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Delay |  | X
Alarm status: Delay timer running | 32169 | 132170 | Parameters - Mains - AC setup - L3 wire break - Information - Delay |  |  | X
Alarm status: Delay timer running | 32169 | 132170 | Parameters - Busbar - AC setup - L3 wire break - Information - Delay | X |  |  |  | X | X
Alarm status: Delay timer running | 32169 | 132170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Delay |  | X
Alarm status: Delay timer running | 32170 | 132171 | Parameters - Generator - AC setup - L1 wire break - Information - Delay | X |  | X |  | X
Alarm status: Delay timer running | 32170 | 132171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Delay |  | X
Alarm status: Delay timer running | 32170 | 132171 | Parameters - Mains - AC setup - L1 wire break - Information - Delay | [5 empty] | X
Alarm status: Delay timer running | 32171 | 132172 | Parameters - Generator - AC setup - L2 wire break - Information - Delay | X |  | X |  | X
Alarm status: Delay timer running | 32171 | 132172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Delay |  | X
Alarm status: Delay timer running | 32171 | 132172 | Parameters - Mains - AC setup - L2 wire break - Information - Delay | [5 empty] | X
Alarm status: Delay timer running | 32172 | 132173 | Parameters - Generator - AC setup - L3 wire break - Information - Delay | X |  | X |  | X
Alarm status: Delay timer running | 32172 | 132173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Delay |  | X
Alarm status: Delay timer running | 32172 | 132173 | Parameters - Mains - AC setup - L3 wire break - Information - Delay | [5 empty] | X
Alarm status: Delay timer running | 32179 | 132180 | Parameters - Engine - Emergency stop - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32179 | 132180 | Parameters - Busbar A - Emergency stop - Information - Delay |  | X
Alarm status: Delay timer running | 32179 | 132180 | Parameters - Mains - Emergency stop - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32180 | 132181 | Clock battery failure - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32181 | 132182 | Controller temperature too high - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32182 | 132183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32183 | 132184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32184 | 132185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32185 | 132186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32186 | 132187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32187 | 132188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32188 | 132189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32189 | 132190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32190 | 132191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32191 | 132192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32192 | 132193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32193 | 132194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32194 | 132195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32195 | 132196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32196 | 132197 | EIM3.1 4 supply voltage high - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32197 | 132198 | EIM3.1 4 supply voltage low or missing - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32198 | 132199 | EIM3.1 5 supply voltage high - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32199 | 132200 | EIM3.1 5 supply voltage low or missing - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32200 | 132201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32201 | 132202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32202 | 132203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32203 | 132204 | EIM3.1 4 relay 4 wire break - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32204 | 132205 | EIM3.1 5 relay 4 wire break - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32205 | 132206 | AC protections not running - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32206 | 132207 | AC data is missing - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32207 | 132208 | AC protections not running (differential current) - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32208 | 132209 | AC data is missing (differential current) - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32209 | 132210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32210 | 132211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32211 | 132212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32212 | 132213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32213 | 132214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32214 | 132215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32215 | 132216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32216 | 132217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32217 | 132218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32218 | 132219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32219 | 132220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32220 | 132221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32221 | 132222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32222 | 132223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32223 | 132224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32224 | 132225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32225 | 132226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32226 | 132227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32237 | 132238 | Blackout detection mismatch - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32240 | 132241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32242 | 132243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32245 | 132246 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32297 | 132298 | Different single-line configurations - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32299 | 132300 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32301 | 132302 | Parameters - CODESYS - Monitoring - Application not OK - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32306 | 132307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32313 | 132314 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32314 | 132315 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32315 | 132316 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32316 | 132317 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32317 | 132318 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32318 | 132319 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32319 | 132320 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32320 | 132321 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32321 | 132322 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32322 | 132323 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32323 | 132324 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32324 | 132325 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32325 | 132326 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32326 | 132327 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32327 | 132328 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32328 | 132329 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32329 | 132330 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32330 | 132331 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32331 | 132332 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32332 | 132333 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32333 | 132334 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32334 | 132335 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32335 | 132336 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32336 | 132337 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32337 | 132338 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32338 | 132339 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32339 | 132340 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32340 | 132341 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32341 | 132342 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32342 | 132343 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32343 | 132344 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32344 | 132345 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32345 | 132346 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32346 | 132347 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32347 | 132348 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32348 | 132349 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32349 | 132350 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32350 | 132351 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32351 | 132352 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32352 | 132353 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32353 | 132354 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32354 | 132355 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32355 | 132356 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32356 | 132357 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32357 | 132358 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32358 | 132359 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32359 | 132360 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32360 | 132361 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32361 | 132362 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32362 | 132363 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32363 | 132364 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32364 | 132365 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32365 | 132366 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32366 | 132367 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32367 | 132368 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32368 | 132369 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32369 | 132370 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32370 | 132371 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32371 | 132372 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32372 | 132373 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32373 | 132374 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32374 | 132375 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32375 | 132376 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32376 | 132377 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32377 | 132378 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32378 | 132379 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32379 | 132380 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32380 | 132381 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32381 | 132382 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32382 | 132383 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32383 | 132384 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32384 | 132385 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32385 | 132386 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32386 | 132387 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32387 | 132388 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32388 | 132389 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32389 | 132390 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32390 | 132391 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32391 | 132392 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32392 | 132393 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32393 | 132394 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32394 | 132395 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32395 | 132396 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32396 | 132397 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32397 | 132398 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32398 | 132399 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32399 | 132400 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32400 | 132401 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32401 | 132402 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32402 | 132403 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32403 | 132404 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32404 | 132405 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32405 | 132406 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32406 | 132407 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32407 | 132408 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32408 | 132409 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32409 | 132410 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32410 | 132411 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32411 | 132412 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32412 | 132413 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32413 | 132414 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32414 | 132415 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32415 | 132416 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32416 | 132417 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32417 | 132418 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32418 | 132419 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32419 | 132420 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32420 | 132421 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32421 | 132422 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32422 | 132423 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32423 | 132424 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32424 | 132425 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32425 | 132426 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32426 | 132427 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32427 | 132428 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32428 | 132429 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32429 | 132430 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32430 | 132431 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32431 | 132432 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32432 | 132433 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32433 | 132434 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32434 | 132435 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32435 | 132436 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32436 | 132437 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32437 | 132438 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32438 | 132439 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32439 | 132440 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32440 | 132441 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32441 | 132442 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32442 | 132443 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32443 | 132444 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32444 | 132445 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32445 | 132446 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32446 | 132447 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32447 | 132448 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32448 | 132449 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32449 | 132450 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32450 | 132451 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32451 | 132452 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32452 | 132453 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32453 | 132454 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32454 | 132455 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32455 | 132456 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32456 | 132457 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32457 | 132458 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32458 | 132459 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32459 | 132460 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32460 | 132461 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32461 | 132462 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32462 | 132463 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32463 | 132464 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32464 | 132465 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32465 | 132466 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32466 | 132467 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32467 | 132468 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32468 | 132469 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32469 | 132470 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32470 | 132471 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32471 | 132472 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32472 | 132473 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32473 | 132474 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32474 | 132475 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32475 | 132476 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32476 | 132477 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32477 | 132478 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32478 | 132479 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32479 | 132480 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32480 | 132481 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32481 | 132482 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32482 | 132483 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32483 | 132484 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32484 | 132485 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32485 | 132486 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32486 | 132487 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32487 | 132488 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32488 | 132489 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32489 | 132490 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32490 | 132491 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32491 | 132492 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32492 | 132493 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32493 | 132494 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32494 | 132495 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32495 | 132496 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32496 | 132497 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32497 | 132498 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32498 | 132499 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32499 | 132500 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32500 | 132501 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32501 | 132502 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32502 | 132503 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32503 | 132504 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32504 | 132505 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32505 | 132506 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32506 | 132507 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32507 | 132508 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32508 | 132509 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32509 | 132510 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32510 | 132511 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32511 | 132512 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32512 | 132513 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32513 | 132514 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32514 | 132515 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32515 | 132516 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32516 | 132517 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32517 | 132518 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32518 | 132519 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32519 | 132520 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32520 | 132521 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32521 | 132522 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32522 | 132523 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32523 | 132524 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32524 | 132525 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32525 | 132526 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32526 | 132527 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32527 | 132528 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32528 | 132529 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32529 | 132530 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32530 | 132531 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32531 | 132532 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32532 | 132533 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32533 | 132534 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32534 | 132535 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32535 | 132536 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32536 | 132537 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32537 | 132538 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32538 | 132539 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32539 | 132540 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32540 | 132541 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32541 | 132542 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32542 | 132543 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32543 | 132544 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32544 | 132545 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32545 | 132546 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32546 | 132547 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32547 | 132548 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32548 | 132549 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32549 | 132550 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32550 | 132551 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32551 | 132552 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32552 | 132553 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32553 | 132554 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32554 | 132555 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32555 | 132556 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32556 | 132557 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32557 | 132558 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32558 | 132559 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32559 | 132560 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32560 | 132561 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32561 | 132562 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32562 | 132563 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32566 | 132567 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32614 | 132615 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32615 | 132616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32615 | 132616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32615 | 132616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32616 | 132617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32616 | 132617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32616 | 132617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32617 | 132618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32617 | 132618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Delay |  | X
Alarm status: Delay timer running | 32617 | 132618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32618 | 132619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32618 | 132619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32618 | 132619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32619 | 132620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32619 | 132620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32619 | 132620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32620 | 132621 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32620 | 132621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Delay |  | X
Alarm status: Delay timer running | 32620 | 132621 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32621 | 132622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32621 | 132622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Delay |  | X
Alarm status: Delay timer running | 32621 | 132622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32622 | 132623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32622 | 132623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Delay |  | X
Alarm status: Delay timer running | 32622 | 132623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32623 | 132624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32623 | 132624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Delay |  | X
Alarm status: Delay timer running | 32623 | 132624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32624 | 132625 | Parameters - Generator - Current protections - Over-current 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32624 | 132625 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32624 | 132625 | Parameters - Mains - Current protections - Over-current 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32625 | 132626 | Parameters - Generator - Current protections - Over-current 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32625 | 132626 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32625 | 132626 | Parameters - Mains - Current protections - Over-current 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32626 | 132627 | Parameters - Generator - Current protections - Over-current 3 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32626 | 132627 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Delay |  | X
Alarm status: Delay timer running | 32626 | 132627 | Parameters - Mains - Current protections - Over-current 3 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32627 | 132628 | Parameters - Generator - Current protections - Over-current 4 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32627 | 132628 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Delay |  | X
Alarm status: Delay timer running | 32627 | 132628 | Parameters - Mains - Current protections - Over-current 4 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32628 | 132629 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32628 | 132629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32628 | 132629 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32629 | 132630 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32629 | 132630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32629 | 132630 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32630 | 132631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32630 | 132631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Delay |  | X
Alarm status: Delay timer running | 32630 | 132631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32631 | 132632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32631 | 132632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Delay |  | X
Alarm status: Delay timer running | 32631 | 132632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32632 | 132633 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32632 | 132633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32632 | 132633 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32633 | 132634 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32633 | 132634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32633 | 132634 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32634 | 132635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Delay |  | X
Alarm status: Delay timer running | 32635 | 132636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Delay |  | X
Alarm status: Delay timer running | 32636 | 132637 | Parameters - Generator - Current protections - Negative sequence current - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32636 | 132637 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Delay |  | X
Alarm status: Delay timer running | 32636 | 132637 | Parameters - Mains - Current protections - Negative sequence current - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32637 | 132638 | Parameters - Generator - Current protections - Zero sequence current - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32637 | 132638 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Delay |  | X
Alarm status: Delay timer running | 32637 | 132638 | Parameters - Mains - Current protections - Zero sequence current - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32638 | 132639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32638 | 132639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32638 | 132639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32639 | 132640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32639 | 132640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32639 | 132640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32640 | 132641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32640 | 132641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Delay |  | X
Alarm status: Delay timer running | 32640 | 132641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32641 | 132642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32641 | 132642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32641 | 132642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32642 | 132643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32642 | 132643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32642 | 132643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32643 | 132644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32643 | 132644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Delay |  | X
Alarm status: Delay timer running | 32643 | 132644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32644 | 132645 | Parameters - Generator - Power protections - Overload 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32644 | 132645 | Parameters - Busbar A - Power protections - Power export 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32644 | 132645 | Parameters - Mains - Power protections - Overload 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32645 | 132646 | Parameters - Generator - Power protections - Overload 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32645 | 132646 | Parameters - Busbar A - Power protections - Power export 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32645 | 132646 | Parameters - Mains - Power protections - Overload 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32646 | 132647 | Parameters - Generator - Power protections - Overload 3 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32646 | 132647 | Parameters - Busbar A - Power protections - Power export 3 - Information - Delay |  | X
Alarm status: Delay timer running | 32646 | 132647 | Parameters - Mains - Power protections - Overload 3 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32647 | 132648 | Parameters - Generator - Power protections - Overload 4 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32647 | 132648 | Parameters - Busbar A - Power protections - Power export 4 - Information - Delay |  | X
Alarm status: Delay timer running | 32647 | 132648 | Parameters - Mains - Power protections - Overload 4 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32648 | 132649 | Parameters - Generator - Power protections - Overload 5 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32648 | 132649 | Parameters - Busbar A - Power protections - Power export 5 - Information - Delay |  | X
Alarm status: Delay timer running | 32648 | 132649 | Parameters - Mains - Power protections - Overload 5 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32649 | 132650 | Parameters - Generator - Power protections - Reverse power 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32649 | 132650 | Parameters - Busbar A - Power protections - Power import 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32649 | 132650 | Parameters - Mains - Power protections - Reverse power 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32650 | 132651 | Parameters - Generator - Power protections - Reverse power 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32650 | 132651 | Parameters - Busbar A - Power protections - Power import 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32650 | 132651 | Parameters - Mains - Power protections - Reverse power 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32651 | 132652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32651 | 132652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32651 | 132652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32652 | 132653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32652 | 132653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32652 | 132653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32653 | 132654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32653 | 132654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32653 | 132654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32654 | 132655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32654 | 132655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32654 | 132655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32655 | 132656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32655 | 132656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32655 | 132656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32656 | 132657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32656 | 132657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32656 | 132657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32657 | 132658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32657 | 132658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32657 | 132658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Delay |  | X
Alarm status: Delay timer running | 32658 | 132659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32658 | 132659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32658 | 132659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32659 | 132660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32659 | 132660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32659 | 132660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32660 | 132661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32660 | 132661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32660 | 132661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Delay |  | X
Alarm status: Delay timer running | 32661 | 132662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32661 | 132662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32661 | 132662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Delay |  | X
Alarm status: Delay timer running | 32662 | 132663 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32662 | 132663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32662 | 132663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Delay |  | X
Alarm status: Delay timer running | 32663 | 132664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32663 | 132664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32663 | 132664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32664 | 132665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32664 | 132665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32664 | 132665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32665 | 132666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32665 | 132666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32665 | 132666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Delay |  | X
Alarm status: Delay timer running | 32666 | 132667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32666 | 132667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32666 | 132667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Delay |  | X
Alarm status: Delay timer running | 32667 | 132668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32667 | 132668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32667 | 132668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Delay |  | X
Alarm status: Delay timer running | 32668 | 132669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32668 | 132669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32668 | 132669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Delay |  | X
Alarm status: Delay timer running | 32669 | 132670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32669 | 132670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32669 | 132670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Delay |  | X
Alarm status: Delay timer running | 32670 | 132671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32670 | 132671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32670 | 132671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Delay |  | X
Alarm status: Delay timer running | 32671 | 132672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32671 | 132672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32671 | 132672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Delay |  | X
Alarm status: Delay timer running | 32672 | 132673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32672 | 132673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer running | 32672 | 132673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Delay |  | X
Alarm status: Delay timer running | 32721 | 132722 | External MB open failure - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32722 | 132723 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32723 | 132724 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32724 | 132725 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32725 | 132726 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32726 | 132727 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32727 | 132728 | Parameters - Breakers - Close before excitation - CBE failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32728 | 132729 | Load too high - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32729 | 132730 | ID to run configuration failure - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32734 | 132735 | Can ID not available - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32735 | 132736 | Duplicated CAN IDs - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32736 | 132737 | Parameters - Local power management - Alarms - Busbar blocked - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32737 | 132738 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Delay |  | X
Alarm status: Delay timer running | 32738 | 132739 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Delay |  | X
Alarm status: Delay timer running | 32739 | 132740 | Parameters - System - Monitoring - BTB 33 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32740 | 132741 | Parameters - System - Monitoring - BTB 34 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32741 | 132742 | Parameters - System - Monitoring - BTB 35 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32742 | 132743 | Parameters - System - Monitoring - BTB 36 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32743 | 132744 | Parameters - System - Monitoring - BTB 37 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32744 | 132745 | Parameters - System - Monitoring - BTB 38 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32745 | 132746 | Parameters - System - Monitoring - BTB 39 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32746 | 132747 | Parameters - System - Monitoring - BTB 40 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32828 | 132829 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32829 | 132830 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32830 | 132831 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32831 | 132832 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32832 | 132833 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32833 | 132834 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32834 | 132835 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32835 | 132836 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32836 | 132837 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32837 | 132838 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32838 | 132839 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32839 | 132840 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32840 | 132841 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32841 | 132842 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32842 | 132843 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer running | 32843 | 132844 | Parameters - System - Monitoring - Single-line hazard - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32844 | 132845 | ID not present - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32845 | 132846 | Unsupported application - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32846 | 132847 | Application internal CAN protocol conflict - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32847 | 132848 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32848 | 132849 | Dry mode: Voltage level unexpected - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32854 | 132855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32854 | 132855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Delay |  | X
Alarm status: Delay timer running | 32854 | 132855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer running | 32855 | 132856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Delay |  |  |  | X
Alarm status: Delay timer running | 32855 | 132856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Delay | [6 empty] | X
Alarm status: Delay timer running | 32857 | 132858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32858 | 132859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32859 | 132860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32860 | 132861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32861 | 132862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32862 | 132863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32863 | 132864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32864 | 132865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32865 | 132866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32866 | 132867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32867 | 132868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32868 | 132869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32869 | 132870 | AC protections not running - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32870 | 132871 | AC data is missing - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32871 | 132872 | AC protections not running - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32872 | 132873 | AC data is missing - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32873 | 132874 | AC protections not running - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32874 | 132875 | AC data is missing - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32875 | 132876 | AC protections not running - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32876 | 132877 | AC data is missing - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32877 | 132878 | Live voltage detected - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32881 | 132882 | Card configuration failed - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32883 | 132884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32884 | 132885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32885 | 132886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Delay | X |  | X | X | X
Alarm status: Delay timer running | 32889 | 132890 | Licence error - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer running | 32892 | 132893 | Parameters - Grid code - Capability curve - Import protection - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32893 | 132894 | Parameters - Grid code - Capability curve - Export protection - Information - Delay |  |  | X | X
Alarm status: Delay timer running | 32894 | 132895 | Hardware is not compatible based on module versions - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34003 | 134004 | Parameters - Engine - Stop sequence - Stop failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34005 | 134006 | Parameters - Engine - Start sequence - Crank failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34006 | 134007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34007 | 134008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34008 | 134009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34009 | 134010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34010 | 134011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34013 | 134014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34014 | 134015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34015 | 134016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34016 | 134017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34017 | 134018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34018 | 134019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34019 | 134020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34020 | 134021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34021 | 134022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34022 | 134023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34027 | 134028 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34041 | 134042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34041 | 134042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Delay |  | X
Alarm status: Delay timer expired | 34041 | 134042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34042 | 134043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34042 | 134043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Delay |  | X
Alarm status: Delay timer expired | 34042 | 134043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34043 | 134044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34043 | 134044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Delay |  | X
Alarm status: Delay timer expired | 34043 | 134044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34044 | 134045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34044 | 134045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Delay |  | X
Alarm status: Delay timer expired | 34044 | 134045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34045 | 134046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34045 | 134046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Delay |  | X
Alarm status: Delay timer expired | 34045 | 134046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34046 | 134047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34046 | 134047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Delay |  | X
Alarm status: Delay timer expired | 34046 | 134047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34049 | 134050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Delay |  |  |  | X
Alarm status: Delay timer expired | 34049 | 134050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Delay | [6 empty] | X
Alarm status: Delay timer expired | 34050 | 134051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Delay |  |  |  | X
Alarm status: Delay timer expired | 34050 | 134051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Delay | [6 empty] | X
Alarm status: Delay timer expired | 34051 | 134052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Delay |  |  |  | X
Alarm status: Delay timer expired | 34051 | 134052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Delay | [6 empty] | X
Alarm status: Delay timer expired | 34052 | 134053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Delay |  |  |  | X
Alarm status: Delay timer expired | 34052 | 134053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Delay | [6 empty] | X
Alarm status: Delay timer expired | 34053 | 134054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Delay |  |  |  | X
Alarm status: Delay timer expired | 34053 | 134054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Delay | [6 empty] | X
Alarm status: Delay timer expired | 34054 | 134055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Delay |  |  |  | X
Alarm status: Delay timer expired | 34054 | 134055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Delay | [6 empty] | X
Alarm status: Delay timer expired | 34060 | 134061 | Parameters - Mains - AC setup - Phase sequence error - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34060 | 134061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34060 | 134061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Delay |  | X
Alarm status: Delay timer expired | 34061 | 134062 | Parameters - Generator - AC setup - Phase sequence error - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34061 | 134062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Delay |  | X
Alarm status: Delay timer expired | 34061 | 134062 | Parameters - Mains - AC setup - Phase sequence error - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34062 | 134063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34103 | 134104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34103 | 134104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34103 | 134104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information - Delay |  | X
Alarm status: Delay timer expired | 34108 | 134109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34108 | 134109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34108 | 134109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34109 | 134110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34109 | 134110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34109 | 134110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34110 | 134111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34110 | 134111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34110 | 134111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34111 | 134112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34111 | 134112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34111 | 134112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34116 | 134117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34117 | 134118 | Parameters - Generator - Current protections - High set differential current - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34119 | 134120 | Parameters - Local - Mode - Not under remote control - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34128 | 134129 | Parameters - Custom alarm - Custom alarm 0 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34129 | 134130 | Parameters - Custom alarm - Custom alarm 1 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34130 | 134131 | Parameters - Custom alarm - Custom alarm 2 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34131 | 134132 | Parameters - Custom alarm - Custom alarm 3 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34132 | 134133 | Parameters - Custom alarm - Custom alarm 4 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34133 | 134134 | Parameters - Custom alarm - Custom alarm 5 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34134 | 134135 | Parameters - Custom alarm - Custom alarm 6 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34135 | 134136 | Parameters - Custom alarm - Custom alarm 7 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34136 | 134137 | Parameters - Custom alarm - Custom alarm 8 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34137 | 134138 | Parameters - Custom alarm - Custom alarm 9 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34138 | 134139 | Parameters - Custom alarm - Custom alarm 10 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34139 | 134140 | Parameters - Custom alarm - Custom alarm 11 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34140 | 134141 | Parameters - Custom alarm - Custom alarm 12 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34141 | 134142 | Parameters - Custom alarm - Custom alarm 13 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34142 | 134143 | Parameters - Custom alarm - Custom alarm 14 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34143 | 134144 | Parameters - Custom alarm - Custom alarm 15 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34144 | 134145 | Parameters - Custom alarm - Custom alarm 16 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34145 | 134146 | Parameters - Custom alarm - Custom alarm 17 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34146 | 134147 | Parameters - Custom alarm - Custom alarm 18 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34147 | 134148 | Parameters - Custom alarm - Custom alarm 19 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34148 | 134149 | Parameters - Custom alarm - Custom alarm 20 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34149 | 134150 | Parameters - Custom alarm - Custom alarm 21 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34150 | 134151 | Parameters - Custom alarm - Custom alarm 22 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34151 | 134152 | Parameters - Custom alarm - Custom alarm 23 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34152 | 134153 | Parameters - Custom alarm - Custom alarm 24 - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34153 | 134154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34154 | 134155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34163 | 134164 | Required hardware card(s) not found - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34164 | 134165 | Software mismatch on hardware module(s) - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34165 | 134166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Delay |  |  | X
Alarm status: Delay timer expired | 34165 | 134166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Delay | X |  |  |  | X | X
Alarm status: Delay timer expired | 34165 | 134166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Delay |  | X
Alarm status: Delay timer expired | 34166 | 134167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Delay | X |  | X |  | X
Alarm status: Delay timer expired | 34166 | 134167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Delay |  | X
Alarm status: Delay timer expired | 34166 | 134167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Delay | [5 empty] | X
Alarm status: Delay timer expired | 34167 | 134168 | Parameters - Mains - AC setup - L1 wire break - Information - Delay |  |  | X
Alarm status: Delay timer expired | 34167 | 134168 | Parameters - Busbar - AC setup - L1 wire break - Information - Delay | X |  |  |  | X | X
Alarm status: Delay timer expired | 34167 | 134168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Delay |  | X
Alarm status: Delay timer expired | 34168 | 134169 | Parameters - Mains - AC setup - L2 wire break - Information - Delay |  |  | X
Alarm status: Delay timer expired | 34168 | 134169 | Parameters - Busbar - AC setup - L2 wire break - Information - Delay | X |  |  |  | X | X
Alarm status: Delay timer expired | 34168 | 134169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Delay |  | X
Alarm status: Delay timer expired | 34169 | 134170 | Parameters - Mains - AC setup - L3 wire break - Information - Delay |  |  | X
Alarm status: Delay timer expired | 34169 | 134170 | Parameters - Busbar - AC setup - L3 wire break - Information - Delay | X |  |  |  | X | X
Alarm status: Delay timer expired | 34169 | 134170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Delay |  | X
Alarm status: Delay timer expired | 34170 | 134171 | Parameters - Generator - AC setup - L1 wire break - Information - Delay | X |  | X |  | X
Alarm status: Delay timer expired | 34170 | 134171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Delay |  | X
Alarm status: Delay timer expired | 34170 | 134171 | Parameters - Mains - AC setup - L1 wire break - Information - Delay | [5 empty] | X
Alarm status: Delay timer expired | 34171 | 134172 | Parameters - Generator - AC setup - L2 wire break - Information - Delay | X |  | X |  | X
Alarm status: Delay timer expired | 34171 | 134172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Delay |  | X
Alarm status: Delay timer expired | 34171 | 134172 | Parameters - Mains - AC setup - L2 wire break - Information - Delay | [5 empty] | X
Alarm status: Delay timer expired | 34172 | 134173 | Parameters - Generator - AC setup - L3 wire break - Information - Delay | X |  | X |  | X
Alarm status: Delay timer expired | 34172 | 134173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Delay |  | X
Alarm status: Delay timer expired | 34172 | 134173 | Parameters - Mains - AC setup - L3 wire break - Information - Delay | [5 empty] | X
Alarm status: Delay timer expired | 34179 | 134180 | Parameters - Engine - Emergency stop - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34179 | 134180 | Parameters - Busbar A - Emergency stop - Information - Delay |  | X
Alarm status: Delay timer expired | 34179 | 134180 | Parameters - Mains - Emergency stop - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34180 | 134181 | Clock battery failure - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34181 | 134182 | Controller temperature too high - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34182 | 134183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34183 | 134184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34184 | 134185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34185 | 134186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34186 | 134187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34187 | 134188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34188 | 134189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34189 | 134190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34190 | 134191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34191 | 134192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34192 | 134193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34193 | 134194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34194 | 134195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34195 | 134196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34196 | 134197 | EIM3.1 4 supply voltage high - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34197 | 134198 | EIM3.1 4 supply voltage low or missing - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34198 | 134199 | EIM3.1 5 supply voltage high - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34199 | 134200 | EIM3.1 5 supply voltage low or missing - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34200 | 134201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34201 | 134202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34202 | 134203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34203 | 134204 | EIM3.1 4 relay 4 wire break - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34204 | 134205 | EIM3.1 5 relay 4 wire break - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34205 | 134206 | AC protections not running - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34206 | 134207 | AC data is missing - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34207 | 134208 | AC protections not running (differential current) - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34208 | 134209 | AC data is missing (differential current) - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34209 | 134210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34210 | 134211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34211 | 134212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34212 | 134213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34213 | 134214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34214 | 134215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34215 | 134216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34216 | 134217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34217 | 134218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34218 | 134219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34219 | 134220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34220 | 134221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34221 | 134222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34222 | 134223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34223 | 134224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34224 | 134225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34225 | 134226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34226 | 134227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34237 | 134238 | Blackout detection mismatch - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34240 | 134241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34242 | 134243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34245 | 134246 | Parameters - Communication - NTP - No NTP server(s) connected - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34297 | 134298 | Different single-line configurations - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34299 | 134300 | Parameters - Communication - Modbus - Modbus communication timeout - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34301 | 134302 | Parameters - CODESYS - Monitoring - Application not OK - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34306 | 134307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34313 | 134314 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34314 | 134315 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34315 | 134316 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34316 | 134317 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34317 | 134318 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34318 | 134319 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34319 | 134320 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34320 | 134321 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34321 | 134322 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34322 | 134323 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34323 | 134324 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34324 | 134325 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34325 | 134326 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34326 | 134327 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34327 | 134328 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34328 | 134329 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34329 | 134330 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34330 | 134331 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34331 | 134332 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34332 | 134333 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34333 | 134334 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34334 | 134335 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34335 | 134336 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34336 | 134337 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34337 | 134338 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34338 | 134339 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34339 | 134340 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34340 | 134341 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34341 | 134342 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34342 | 134343 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34343 | 134344 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34344 | 134345 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34345 | 134346 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34346 | 134347 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34347 | 134348 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34348 | 134349 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34349 | 134350 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34350 | 134351 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34351 | 134352 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34352 | 134353 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34353 | 134354 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34354 | 134355 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34355 | 134356 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34356 | 134357 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34357 | 134358 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34358 | 134359 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34359 | 134360 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34360 | 134361 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34361 | 134362 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34362 | 134363 | Digital custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34363 | 134364 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34364 | 134365 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34365 | 134366 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34366 | 134367 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34367 | 134368 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34368 | 134369 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34369 | 134370 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34370 | 134371 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34371 | 134372 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34372 | 134373 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34373 | 134374 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34374 | 134375 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34375 | 134376 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34376 | 134377 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34377 | 134378 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34378 | 134379 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34379 | 134380 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34380 | 134381 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34381 | 134382 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34382 | 134383 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34383 | 134384 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34384 | 134385 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34385 | 134386 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34386 | 134387 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34387 | 134388 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34388 | 134389 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34389 | 134390 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34390 | 134391 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34391 | 134392 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34392 | 134393 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34393 | 134394 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34394 | 134395 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34395 | 134396 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34396 | 134397 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34397 | 134398 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34398 | 134399 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34399 | 134400 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34400 | 134401 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34401 | 134402 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34402 | 134403 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34403 | 134404 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34404 | 134405 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34405 | 134406 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34406 | 134407 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34407 | 134408 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34408 | 134409 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34409 | 134410 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34410 | 134411 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34411 | 134412 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34412 | 134413 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34413 | 134414 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34414 | 134415 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34415 | 134416 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34416 | 134417 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34417 | 134418 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34418 | 134419 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34419 | 134420 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34420 | 134421 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34421 | 134422 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34422 | 134423 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34423 | 134424 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34424 | 134425 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34425 | 134426 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34426 | 134427 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34427 | 134428 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34428 | 134429 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34429 | 134430 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34430 | 134431 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34431 | 134432 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34432 | 134433 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34433 | 134434 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34434 | 134435 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34435 | 134436 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34436 | 134437 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34437 | 134438 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34438 | 134439 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34439 | 134440 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34440 | 134441 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34441 | 134442 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34442 | 134443 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34443 | 134444 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34444 | 134445 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34445 | 134446 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34446 | 134447 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34447 | 134448 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34448 | 134449 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34449 | 134450 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34450 | 134451 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34451 | 134452 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34452 | 134453 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34453 | 134454 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34454 | 134455 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34455 | 134456 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34456 | 134457 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34457 | 134458 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34458 | 134459 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34459 | 134460 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34460 | 134461 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34461 | 134462 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34462 | 134463 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34463 | 134464 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34464 | 134465 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34465 | 134466 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34466 | 134467 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34467 | 134468 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34468 | 134469 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34469 | 134470 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34470 | 134471 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34471 | 134472 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34472 | 134473 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34473 | 134474 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34474 | 134475 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34475 | 134476 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34476 | 134477 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34477 | 134478 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34478 | 134479 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34479 | 134480 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34480 | 134481 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34481 | 134482 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34482 | 134483 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34483 | 134484 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34484 | 134485 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34485 | 134486 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34486 | 134487 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34487 | 134488 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34488 | 134489 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34489 | 134490 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34490 | 134491 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34491 | 134492 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34492 | 134493 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34493 | 134494 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34494 | 134495 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34495 | 134496 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34496 | 134497 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34497 | 134498 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34498 | 134499 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34499 | 134500 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34500 | 134501 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34501 | 134502 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34502 | 134503 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34503 | 134504 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34504 | 134505 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34505 | 134506 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34506 | 134507 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34507 | 134508 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34508 | 134509 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34509 | 134510 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34510 | 134511 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34511 | 134512 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34512 | 134513 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34513 | 134514 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34514 | 134515 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34515 | 134516 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34516 | 134517 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34517 | 134518 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34518 | 134519 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34519 | 134520 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34520 | 134521 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34521 | 134522 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34522 | 134523 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34523 | 134524 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34524 | 134525 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34525 | 134526 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34526 | 134527 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34527 | 134528 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34528 | 134529 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34529 | 134530 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34530 | 134531 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34531 | 134532 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34532 | 134533 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34533 | 134534 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34534 | 134535 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34535 | 134536 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34536 | 134537 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34537 | 134538 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34538 | 134539 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34539 | 134540 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34540 | 134541 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34541 | 134542 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34542 | 134543 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34543 | 134544 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34544 | 134545 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34545 | 134546 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34546 | 134547 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34547 | 134548 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34548 | 134549 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34549 | 134550 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34550 | 134551 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34551 | 134552 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34552 | 134553 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34553 | 134554 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34554 | 134555 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34555 | 134556 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34556 | 134557 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34557 | 134558 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34558 | 134559 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34559 | 134560 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34560 | 134561 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34561 | 134562 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34562 | 134563 | Analogue custom alarm - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34566 | 134567 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34614 | 134615 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34615 | 134616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34615 | 134616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34615 | 134616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34616 | 134617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34616 | 134617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34616 | 134617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34617 | 134618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34617 | 134618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Delay |  | X
Alarm status: Delay timer expired | 34617 | 134618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34618 | 134619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34618 | 134619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34618 | 134619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34619 | 134620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34619 | 134620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34619 | 134620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34620 | 134621 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34620 | 134621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Delay |  | X
Alarm status: Delay timer expired | 34620 | 134621 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34621 | 134622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34621 | 134622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Delay |  | X
Alarm status: Delay timer expired | 34621 | 134622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34622 | 134623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34622 | 134623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Delay |  | X
Alarm status: Delay timer expired | 34622 | 134623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34623 | 134624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34623 | 134624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Delay |  | X
Alarm status: Delay timer expired | 34623 | 134624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34624 | 134625 | Parameters - Generator - Current protections - Over-current 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34624 | 134625 | Parameters - Busbar A - Current protections - Over-current 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34624 | 134625 | Parameters - Mains - Current protections - Over-current 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34625 | 134626 | Parameters - Generator - Current protections - Over-current 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34625 | 134626 | Parameters - Busbar A - Current protections - Over-current 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34625 | 134626 | Parameters - Mains - Current protections - Over-current 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34626 | 134627 | Parameters - Generator - Current protections - Over-current 3 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34626 | 134627 | Parameters - Busbar A - Current protections - Over-current 3 - Information - Delay |  | X
Alarm status: Delay timer expired | 34626 | 134627 | Parameters - Mains - Current protections - Over-current 3 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34627 | 134628 | Parameters - Generator - Current protections - Over-current 4 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34627 | 134628 | Parameters - Busbar A - Current protections - Over-current 4 - Information - Delay |  | X
Alarm status: Delay timer expired | 34627 | 134628 | Parameters - Mains - Current protections - Over-current 4 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34628 | 134629 | Parameters - Generator - Current protections - Fast over-current 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34628 | 134629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34628 | 134629 | Parameters - Mains - Current protections - Fast over-current 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34629 | 134630 | Parameters - Generator - Current protections - Fast over-current 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34629 | 134630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34629 | 134630 | Parameters - Mains - Current protections - Fast over-current 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34630 | 134631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34630 | 134631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - Delay |  | X
Alarm status: Delay timer expired | 34630 | 134631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34631 | 134632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34631 | 134632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - Delay |  | X
Alarm status: Delay timer expired | 34631 | 134632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34632 | 134633 | Parameters - Generator - Current protections - Directional over-current 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34632 | 134633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34632 | 134633 | Parameters - Mains - Current protections - Directional over-current 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34633 | 134634 | Parameters - Generator - Current protections - Directional over-current 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34633 | 134634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34633 | 134634 | Parameters - Mains - Current protections - Directional over-current 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34634 | 134635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - Delay |  | X
Alarm status: Delay timer expired | 34635 | 134636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - Delay |  | X
Alarm status: Delay timer expired | 34636 | 134637 | Parameters - Generator - Current protections - Negative sequence current - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34636 | 134637 | Parameters - Busbar A - Current protections - Negative sequence current - Information - Delay |  | X
Alarm status: Delay timer expired | 34636 | 134637 | Parameters - Mains - Current protections - Negative sequence current - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34637 | 134638 | Parameters - Generator - Current protections - Zero sequence current - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34637 | 134638 | Parameters - Busbar A - Current protections - Zero sequence current - Information - Delay |  | X
Alarm status: Delay timer expired | 34637 | 134638 | Parameters - Mains - Current protections - Zero sequence current - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34638 | 134639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34638 | 134639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34638 | 134639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34639 | 134640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34639 | 134640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34639 | 134640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34640 | 134641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34640 | 134641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Delay |  | X
Alarm status: Delay timer expired | 34640 | 134641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34641 | 134642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34641 | 134642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34641 | 134642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34642 | 134643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34642 | 134643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34642 | 134643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34643 | 134644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34643 | 134644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Delay |  | X
Alarm status: Delay timer expired | 34643 | 134644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34644 | 134645 | Parameters - Generator - Power protections - Overload 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34644 | 134645 | Parameters - Busbar A - Power protections - Power export 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34644 | 134645 | Parameters - Mains - Power protections - Overload 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34645 | 134646 | Parameters - Generator - Power protections - Overload 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34645 | 134646 | Parameters - Busbar A - Power protections - Power export 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34645 | 134646 | Parameters - Mains - Power protections - Overload 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34646 | 134647 | Parameters - Generator - Power protections - Overload 3 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34646 | 134647 | Parameters - Busbar A - Power protections - Power export 3 - Information - Delay |  | X
Alarm status: Delay timer expired | 34646 | 134647 | Parameters - Mains - Power protections - Overload 3 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34647 | 134648 | Parameters - Generator - Power protections - Overload 4 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34647 | 134648 | Parameters - Busbar A - Power protections - Power export 4 - Information - Delay |  | X
Alarm status: Delay timer expired | 34647 | 134648 | Parameters - Mains - Power protections - Overload 4 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34648 | 134649 | Parameters - Generator - Power protections - Overload 5 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34648 | 134649 | Parameters - Busbar A - Power protections - Power export 5 - Information - Delay |  | X
Alarm status: Delay timer expired | 34648 | 134649 | Parameters - Mains - Power protections - Overload 5 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34649 | 134650 | Parameters - Generator - Power protections - Reverse power 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34649 | 134650 | Parameters - Busbar A - Power protections - Power import 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34649 | 134650 | Parameters - Mains - Power protections - Reverse power 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34650 | 134651 | Parameters - Generator - Power protections - Reverse power 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34650 | 134651 | Parameters - Busbar A - Power protections - Power import 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34650 | 134651 | Parameters - Mains - Power protections - Reverse power 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34651 | 134652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34651 | 134652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34651 | 134652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34652 | 134653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34652 | 134653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34652 | 134653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34653 | 134654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34653 | 134654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34653 | 134654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34654 | 134655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34654 | 134655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34654 | 134655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34655 | 134656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34655 | 134656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34655 | 134656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34656 | 134657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34656 | 134657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34656 | 134657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34657 | 134658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34657 | 134658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34657 | 134658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Delay |  | X
Alarm status: Delay timer expired | 34658 | 134659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34658 | 134659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34658 | 134659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34659 | 134660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34659 | 134660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34659 | 134660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34660 | 134661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34660 | 134661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34660 | 134661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Delay |  | X
Alarm status: Delay timer expired | 34661 | 134662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34661 | 134662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34661 | 134662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Delay |  | X
Alarm status: Delay timer expired | 34662 | 134663 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34662 | 134663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34662 | 134663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Delay |  | X
Alarm status: Delay timer expired | 34663 | 134664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34663 | 134664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34663 | 134664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34664 | 134665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34664 | 134665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34664 | 134665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34665 | 134666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34665 | 134666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34665 | 134666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Delay |  | X
Alarm status: Delay timer expired | 34666 | 134667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34666 | 134667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34666 | 134667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Delay |  | X
Alarm status: Delay timer expired | 34667 | 134668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34667 | 134668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34667 | 134668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Delay |  | X
Alarm status: Delay timer expired | 34668 | 134669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34668 | 134669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34668 | 134669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Delay |  | X
Alarm status: Delay timer expired | 34669 | 134670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34669 | 134670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34669 | 134670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Delay |  | X
Alarm status: Delay timer expired | 34670 | 134671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34670 | 134671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34670 | 134671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Delay |  | X
Alarm status: Delay timer expired | 34671 | 134672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34671 | 134672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34671 | 134672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Delay |  | X
Alarm status: Delay timer expired | 34672 | 134673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34672 | 134673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Delay | X |  |  |  | X | X | X
Alarm status: Delay timer expired | 34672 | 134673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Delay |  | X
Alarm status: Delay timer expired | 34721 | 134722 | External MB open failure - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34722 | 134723 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34723 | 134724 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34724 | 134725 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34725 | 134726 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34726 | 134727 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34727 | 134728 | Parameters - Breakers - Close before excitation - CBE failure - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34728 | 134729 | Load too high - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34729 | 134730 | ID to run configuration failure - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34734 | 134735 | Can ID not available - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34735 | 134736 | Duplicated CAN IDs - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34736 | 134737 | Parameters - Local power management - Alarms - Busbar blocked - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34737 | 134738 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Delay |  | X
Alarm status: Delay timer expired | 34738 | 134739 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Delay |  | X
Alarm status: Delay timer expired | 34739 | 134740 | Parameters - System - Monitoring - BTB 33 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34740 | 134741 | Parameters - System - Monitoring - BTB 34 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34741 | 134742 | Parameters - System - Monitoring - BTB 35 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34742 | 134743 | Parameters - System - Monitoring - BTB 36 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34743 | 134744 | Parameters - System - Monitoring - BTB 37 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34744 | 134745 | Parameters - System - Monitoring - BTB 38 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34745 | 134746 | Parameters - System - Monitoring - BTB 39 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34746 | 134747 | Parameters - System - Monitoring - BTB 40 position failure - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34828 | 134829 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34829 | 134830 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34830 | 134831 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34831 | 134832 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34832 | 134833 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34833 | 134834 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34834 | 134835 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34835 | 134836 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34836 | 134837 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34837 | 134838 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34838 | 134839 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34839 | 134840 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34840 | 134841 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34841 | 134842 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34842 | 134843 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - Delay | X |  | X | X | X | X | X
Alarm status: Delay timer expired | 34843 | 134844 | Parameters - System - Monitoring - Single-line hazard - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34844 | 134845 | ID not present - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34845 | 134846 | Unsupported application - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34846 | 134847 | Application internal CAN protocol conflict - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34847 | 134848 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34848 | 134849 | Dry mode: Voltage level unexpected - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34854 | 134855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34854 | 134855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Delay |  | X
Alarm status: Delay timer expired | 34854 | 134855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Delay | [5 empty] | X | X
Alarm status: Delay timer expired | 34855 | 134856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Delay |  |  |  | X
Alarm status: Delay timer expired | 34855 | 134856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Delay | [6 empty] | X
Alarm status: Delay timer expired | 34857 | 134858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34858 | 134859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34859 | 134860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34860 | 134861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34861 | 134862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34862 | 134863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34863 | 134864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34864 | 134865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34865 | 134866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34866 | 134867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34867 | 134868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34868 | 134869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34869 | 134870 | AC protections not running - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34870 | 134871 | AC data is missing - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34871 | 134872 | AC protections not running - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34872 | 134873 | AC data is missing - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34873 | 134874 | AC protections not running - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34874 | 134875 | AC data is missing - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34875 | 134876 | AC protections not running - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34876 | 134877 | AC data is missing - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34877 | 134878 | Live voltage detected - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34881 | 134882 | Card configuration failed - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34883 | 134884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34884 | 134885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34885 | 134886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Delay | X |  | X | X | X
Alarm status: Delay timer expired | 34889 | 134890 | Licence error - Delay | X | X | X | X | X | X | X
Alarm status: Delay timer expired | 34892 | 134893 | Parameters - Grid code - Capability curve - Import protection - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34893 | 134894 | Parameters - Grid code - Capability curve - Export protection - Information - Delay |  |  | X | X
Alarm status: Delay timer expired | 34894 | 134895 | Hardware is not compatible based on module versions - Delay | X | X | X | X | X | X | X
General parameter: Delay timer running | 46000 | 146001 | Parameters - Engine - Start sequence - Start prepare - Information | X |  | X | X | X
General parameter: Delay timer running | 46001 | 146002 | Parameters - Engine - Start sequence - Crank - Crank on - Information | X |  | X | X | X
General parameter: Delay timer running | 46002 | 146003 | Parameters - Engine - Start sequence - Crank - Crank off - Information | X |  | X | X | X
General parameter: Delay timer running | 46003 | 146004 | Parameters - Engine - Start sequence - Run coil - Run coil before crank - Information | X |  | X | X | X
General parameter: Delay timer running | 46005 | 146006 | Parameters - Engine - Start sequence - Start prepare - Extended start prepare - Information | X |  | X | X | X
General parameter: Delay timer running | 46006 | 146007 | Parameters - Engine - Stop sequence - Cooldown - Cooldown time - Information | X |  | X | X | X
General parameter: Delay timer running | 46008 | 146009 | Parameters - Engine - Stop sequence - Extended stop - Information | X |  | X | X | X
General parameter: Delay timer running | 46018 | 146019 | Parameters - Engine - Idle run start - Minimum - Delay - Information | X |  | X | X | X
General parameter: Delay timer running | 46027 | 146028 | Parameters - Engine - Idle run stop - Minimum - Delay - Information | X |  | X | X | X
General parameter: Delay timer running | 46033 | 146034 | Parameters - Engine - Idle run start - Idle run - Extended inhibit - Information | X |  | X | X | X
General parameter: Delay timer running | 46038 | 146039 | Parameters - Engine - Running detection - Engine ready - Delay - Information | X |  | X | X | X
General parameter: Delay timer running | 46049 | 146050 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump OFF delay - Information | X |  | X | X | X
General parameter: Delay timer running | 46050 | 146051 | Pump source select | X |  | X | X | X
General parameter: Delay timer running | 46052 | 146053 | Parameters - Breakers - Generator breaker configuration - Configuration - Pulse time ON - Information | X |  | X | X | X
General parameter: Delay timer running | 46052 | 146053 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Pulse time ON - Information |  | X
General parameter: Delay timer running | 46052 | 146053 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time ON - Information | [5 empty] | X | X
General parameter: Delay timer running | 46053 | 146054 | Parameters - Breakers - Generator breaker configuration - Configuration - Pulse time OFF - Information | X |  | X | X | X
General parameter: Delay timer running | 46053 | 146054 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Pulse time OFF - Information |  | X
General parameter: Delay timer running | 46053 | 146054 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time OFF - Information | [5 empty] | X | X
General parameter: Delay timer running | 46054 | 146055 | Parameters - Breakers - Generator breaker configuration - Configuration - Spring load time - Information | X |  | X | X | X
General parameter: Delay timer running | 46054 | 146055 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Spring load time - Information |  | X
General parameter: Delay timer running | 46054 | 146055 | Parameters - Breakers - Mains breaker configuration - Configuration - Spring-load time - Information | [5 empty] | X | X
General parameter: Delay timer running | 46057 | 146058 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time ON - Information |  |  |  | X
General parameter: Delay timer running | 46057 | 146058 | Parameters - Breakers - Tie breaker configuration - Configuration - Pulse time ON - Information | [6 empty] | X
General parameter: Delay timer running | 46058 | 146059 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time OFF - Information |  |  |  | X
General parameter: Delay timer running | 46058 | 146059 | Parameters - Breakers - Tie breaker configuration - Configuration - Pulse time OFF - Information | [6 empty] | X
General parameter: Delay timer running | 46059 | 146060 | Parameters - Breakers - Mains breaker configuration - Configuration - Spring-load time - Information |  |  |  | X
General parameter: Delay timer running | 46059 | 146060 | Parameters - Breakers - Tie breaker configuration - Configuration - Spring-load time - Information | [6 empty] | X
General parameter: Delay timer running | 46200 | 146201 | Parameters - Generator - Production counters - Active energy export - Pulse length - Information | X |  | X | X | X
General parameter: Delay timer running | 46200 | 146201 | Parameters - Busbar A - Production counters - Active energy export - Pulse length - Information |  | X
General parameter: Delay timer running | 46200 | 146201 | Parameters - Mains - Production counters - Active energy export - Pulse length - Information | [5 empty] | X | X
General parameter: Delay timer running | 46202 | 146203 | Parameters - Generator - Production counters - Reactive energy export - Pulse length - Information | X |  | X | X | X
General parameter: Delay timer running | 46202 | 146203 | Parameters - Busbar A - Production counters - Reactive energy export - Pulse length - Information |  | X
General parameter: Delay timer running | 46202 | 146203 | Parameters - Mains - Production counters - Reactive energy export - Pulse length - Information | [5 empty] | X | X
General parameter: Delay timer running | 46204 | 146205 | Parameters - Busbar A - Production counters - Active energy import - Pulse length - Information |  | X
General parameter: Delay timer running | 46204 | 146205 | Parameters - Mains - Production counters - Active energy import - Pulse length - Information | [5 empty] | X | X
General parameter: Delay timer running | 46206 | 146207 | Parameters - Busbar A - Production counters - Reactive energy import - Pulse length - Information |  | X
General parameter: Delay timer running | 46206 | 146207 | Parameters - Mains - Production counters - Reactive energy import - Pulse length - Information | [5 empty] | X | X
General parameter: Delay timer running | 46208 | 146209 | Parameters - Busbar A - Production counters - Active energy difference - Pulse length - Information |  | X
General parameter: Delay timer running | 46208 | 146209 | Parameters - Mains - Production counters - Active energy difference - Pulse length - Information | [5 empty] | X | X
General parameter: Delay timer running | 46210 | 146211 | Parameters - Busbar A - Production counters - Reactive energy difference - Pulse length - Information |  | X
General parameter: Delay timer running | 46210 | 146211 | Parameters - Mains - Production counters - Reactive energy difference - Pulse length - Information | [5 empty] | X | X
General parameter: Delay timer running | 46225 | 146226 | Parameters - Mains - AC setup - Voltage and frequency OK - Information |  |  | X | X
General parameter: Delay timer running | 46225 | 146226 | Parameters - Busbar - AC setup - Voltage and frequency OK - Information | X |  |  |  | X | X | X
General parameter: Delay timer running | 46225 | 146226 | Parameters - Busbar B - AC setup - Voltage and frequency OK - Information |  | X
General parameter: Delay timer running | 46233 | 146234 | Blackout delay |  |  | X | X
General parameter: Delay timer running | 46233 | 146234 | Parameters - Busbar - AC setup - Blackout detection - Blackout delay - Information | X |  |  |  | X | X | X
General parameter: Delay timer running | 46233 | 146234 | Parameters - Busbar B - AC setup - Blackout detection - Blackout delay - Information |  | X
General parameter: Delay timer running | 46234 | 146235 | Parameters - Generator - AC setup - Voltage and frequency OK - Information | X |  | X | X | X
General parameter: Delay timer running | 46234 | 146235 | Parameters - Busbar A - AC setup - Voltage and frequency OK - Information |  | X
General parameter: Delay timer running | 46234 | 146235 | Parameters - Mains - AC setup - Voltage and frequency OK - Information | [5 empty] | X | X
General parameter: Delay timer running | 46242 | 146243 | Blackout delay | X |  | X | X | X | X | X
General parameter: Delay timer running | 46242 | 146243 | Parameters - Busbar A - AC setup - Blackout detection - Blackout delay - Information |  | X
General parameter: Delay timer running | 46243 | 146244 | Parameters - Generator - AC setup - Voltage and frequency OK (blackout) - Voltage and frequency OK - Information | X |  | X | X | X
General parameter: Delay timer running | 46641 | 146642 | Parameters - Local - Alarm horn - Horn 1 - Minimum down time - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 46642 | 146643 | Parameters - Local - Alarm horn - Horn 1 - Minimum up time - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 46645 | 146646 | Parameters - Local - Alarm horn - Horn 2 - Minimum down time - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 46646 | 146647 | Parameters - Local - Alarm horn - Horn 2 - Minimum up time - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 46649 | 146650 | Parameters - Local - Alarm horn - Horn 3 - Minimum down time - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 46650 | 146651 | Parameters - Local - Alarm horn - Horn 3 - Minimum up time - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 46652 | 146653 | Parameters - Local - Alive - Alive configuration - Period - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 46705 | 146706 | Parameters - Regulators - GOV - General configuration - Regulation delay - Regulator delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47041 | 147042 | Parameters - Mains - AC setup - Supervision selector - Recovery selector time - Information |  |  | X | X |  | X | X
General parameter: Delay timer running | 47042 | 147043 | Parameters - Mains - AC setup - Supervision selector - Recovery time fast - Information |  |  | X | X |  | X | X
General parameter: Delay timer running | 47043 | 147044 | Parameters - Mains - AC setup - Supervision selector - Recovery time slow - Information |  |  | X | X |  | X | X
General parameter: Delay timer running | 47070 | 147071 | Parameters - Test functions - Lamp test - Duration - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47071 | 147072 | Parameters - Test functions - Lamp test - Colour cycle time - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47073 | 147074 | Parameters - CODESYS - Monitoring - Application not OK - Startup time - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47076 | 147077 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU powerup time - Information | X |  | X | X | X
General parameter: Delay timer running | 47106 | 147107 | Parameters - Engine - ECU - Controls - Reset - Power off timer - Information | X |  | X | X | X
General parameter: Delay timer running | 47147 | 147148 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Power-up time - Information | X |  | X | X | X
General parameter: Delay timer running | 47206 | 147207 | Parameters - Engine - Stop sequence - Externally stopped - Information - Delay | X |  | X | X | X
General parameter: Delay timer running | 47209 | 147210 | Parameters - Engine - Start sequence - Run detection not reached - Information | X |  | X | X | X
General parameter: Delay timer running | 47210 | 147211 | Parameters - Breakers - Generator breaker configuration - Configuration - Delay after Hz/V OK before close - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47211 | 147212 | Parameters - Local power management - Mains configuration - Mains breaker configuration - MB close delay - Information | X |  | X | X | X | X | X
General parameter: Delay timer running | 47223 | 147224 | Parameters - Breakers - Close before excitation - Configuration - Timer crank release to AVR on - Information | X |  | X | X | X
General parameter: Delay timer running | 47225 | 147226 | Parameters - Breakers - Close before excitation - Configuration - Soft-start timer - Information | X |  | X | X | X
General parameter: Delay timer running | 47227 | 147228 | Parameters - Breakers - Close before excitation - Configuration - Voltage discharge timer for GB close - Information | X |  | X | X | X
General parameter: Delay timer running | 47234 | 147235 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Voltage failure delay - Information | X |  | X | X | X | X | X
General parameter: Delay timer running | 47235 | 147236 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Voltage OK delay - Information | X |  | X | X | X | X | X
General parameter: Delay timer running | 47240 | 147241 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Frequency failure delay - Information | X |  | X | X | X | X | X
General parameter: Delay timer running | 47241 | 147242 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Frequency OK delay - Information | X |  | X | X | X | X | X
General parameter: Delay timer running | 47305 | 147306 | Parameters - Local power management - Mains configuration - Tie breaker configuration - Power capacity overrule delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47358 | 147359 | Parameters - Power management rules - Load-dependent start/stop - Start 1 - Delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47362 | 147363 | Parameters - Power management rules - Load-dependent start/stop - Stop 1 - Delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47811 | 147812 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47813 | 147814 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47815 | 147816 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47817 | 147818 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47819 | 147820 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47821 | 147822 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47823 | 147824 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47825 | 147826 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47827 | 147828 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47829 | 147830 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47831 | 147832 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47833 | 147834 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47835 | 147836 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47837 | 147838 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47839 | 147840 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47841 | 147842 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47843 | 147844 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47845 | 147846 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47847 | 147848 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47849 | 147850 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47851 | 147852 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47853 | 147854 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47855 | 147856 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47857 | 147858 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47890 | 147891 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47898 | 147899 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47899 | 147900 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47907 | 147908 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47908 | 147909 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47916 | 147917 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47917 | 147918 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47925 | 147926 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47926 | 147927 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47934 | 147935 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47935 | 147936 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47943 | 147944 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47944 | 147945 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47952 | 147953 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47953 | 147954 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47961 | 147962 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer running | 47980 | 147981 | Parameters - Breakers - Short-time parallel - Configuration - Maximum overlap time - Information | X |  | X | X | X | X | X
General parameter: Delay timer running | 47989 | 147990 | Parameters - Local power management - Genset test - Settings - Test time - Information | X |  | X | X | X
General parameter: Delay timer running | 47989 | 147990 | Parameters - Power management rules - Mains power - Mains test - Test time - Information | [5 empty] | X | X
General parameter: Delay timer running | 47990 | 147991 | Parameters - Power management rules - Mains power - Peak shaving - Stop delay - Information | X |  | X | X | X
General parameter: Delay timer running | 47998 | 147999 | Parameters - Engine - ECU diagnostic - Time to enable function - Information | X |  | X | X | X
General parameter: Delay timer running | 48000 | 148001 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump ON delay - Information | X |  | X | X | X
General parameter: Delay timer running | 48004 | 148005 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump ON delay - Information | X |  | X | X | X
General parameter: Delay timer running | 48005 | 148006 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump OFF delay - Information | X |  | X | X | X
General parameter: Delay timer running | 48010 | 148011 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump ON delay - Information | X |  | X | X | X
General parameter: Delay timer running | 48011 | 148012 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump OFF delay - Information | X |  | X | X | X
General parameter: Delay timer running | 48211 | 148212 | Parameters - Grid code - Mains sync inhibit - Recovery delay select time - Information |  |  | X | X
General parameter: Delay timer running | 48213 | 148214 | Parameters - Grid code - Mains sync inhibit - Recovery delay 1 time - Information |  |  | X | X
General parameter: Delay timer running | 48215 | 148216 | Parameters - Grid code - Mains sync inhibit - Recovery delay 2 time - Information |  |  | X | X
General parameter: Delay timer expired | 52000 | 152001 | Parameters - Engine - Start sequence - Start prepare - Information | X |  | X | X | X
General parameter: Delay timer expired | 52001 | 152002 | Parameters - Engine - Start sequence - Crank - Crank on - Information | X |  | X | X | X
General parameter: Delay timer expired | 52002 | 152003 | Parameters - Engine - Start sequence - Crank - Crank off - Information | X |  | X | X | X
General parameter: Delay timer expired | 52003 | 152004 | Parameters - Engine - Start sequence - Run coil - Run coil before crank - Information | X |  | X | X | X
General parameter: Delay timer expired | 52004 | 152005 | During start attempts | X |  | X | X | X
General parameter: Delay timer expired | 52005 | 152006 | Parameters - Engine - Start sequence - Start prepare - Extended start prepare - Information | X |  | X | X | X
General parameter: Delay timer expired | 52006 | 152007 | Parameters - Engine - Stop sequence - Cooldown - Cooldown time - Information | X |  | X | X | X
General parameter: Delay timer expired | 52008 | 152009 | Parameters - Engine - Stop sequence - Extended stop - Information | X |  | X | X | X
General parameter: Delay timer expired | 52010 | 152011 | Normal | X |  | X | X | X
General parameter: Delay timer expired | 52011 | 152012 | Suppress alarm action | X |  | X | X | X
General parameter: Delay timer expired | 52015 | 152016 | Enable | X |  | X | X | X
General parameter: Delay timer expired | 52017 | 152018 | Use | X |  | X | X | X
General parameter: Delay timer expired | 52018 | 152019 | Parameters - Engine - Idle run start - Minimum - Delay - Information | X |  | X | X | X
General parameter: Delay timer expired | 52026 | 152027 | Use | X |  | X | X | X
General parameter: Delay timer expired | 52027 | 152028 | Parameters - Engine - Idle run stop - Minimum - Delay - Information | X |  | X | X | X
General parameter: Delay timer expired | 52033 | 152034 | Parameters - Engine - Idle run start - Idle run - Extended inhibit - Information | X |  | X | X | X
General parameter: Delay timer expired | 52034 | 152035 | RPM | X |  | X | X | X
General parameter: Delay timer expired | 52035 | 152036 | Frequency | X |  | X | X | X
General parameter: Delay timer expired | 52036 | 152037 | Oil pressure | X |  | X | X | X
General parameter: Delay timer expired | 52037 | 152038 | Primary running feedback | X |  | X | X | X
General parameter: Delay timer expired | 52038 | 152039 | Parameters - Engine - Running detection - Engine ready - Delay - Information | X |  | X | X | X
General parameter: Delay timer expired | 52039 | 152040 | Disengage crank | X |  | X | X | X
General parameter: Delay timer expired | 52040 | 152041 | Number of MPU teeth | X |  | X | X | X
General parameter: Delay timer expired | 52042 | 152043 | Use oil pressure | X |  | X | X | X
General parameter: Delay timer expired | 52043 | 152044 | Use engine speed | X |  | X | X | X
General parameter: Delay timer expired | 52047 | 152048 | Pump ON set point | X |  | X | X | X
General parameter: Delay timer expired | 52048 | 152049 | Pump OFF set point | X |  | X | X | X
General parameter: Delay timer expired | 52049 | 152050 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump OFF delay - Information | X |  | X | X | X
General parameter: Delay timer expired | 52050 | 152051 | Pump source select | X |  | X | X | X
General parameter: Delay timer expired | 52051 | 152052 | Breaker type | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52052 | 152053 | Parameters - Breakers - Generator breaker configuration - Configuration - Pulse time ON - Information | X |  | X | X | X
General parameter: Delay timer expired | 52052 | 152053 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Pulse time ON - Information |  | X
General parameter: Delay timer expired | 52052 | 152053 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time ON - Information | [5 empty] | X | X
General parameter: Delay timer expired | 52053 | 152054 | Parameters - Breakers - Generator breaker configuration - Configuration - Pulse time OFF - Information | X |  | X | X | X
General parameter: Delay timer expired | 52053 | 152054 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Pulse time OFF - Information |  | X
General parameter: Delay timer expired | 52053 | 152054 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time OFF - Information | [5 empty] | X | X
General parameter: Delay timer expired | 52054 | 152055 | Parameters - Breakers - Generator breaker configuration - Configuration - Spring load time - Information | X |  | X | X | X
General parameter: Delay timer expired | 52054 | 152055 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Spring load time - Information |  | X
General parameter: Delay timer expired | 52054 | 152055 | Parameters - Breakers - Mains breaker configuration - Configuration - Spring-load time - Information | [5 empty] | X | X
General parameter: Delay timer expired | 52055 | 152056 | Open point (de-loading) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52056 | 152057 | Breaker type |  |  |  | X |  |  | X
General parameter: Delay timer expired | 52057 | 152058 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time ON - Information |  |  |  | X
General parameter: Delay timer expired | 52057 | 152058 | Parameters - Breakers - Tie breaker configuration - Configuration - Pulse time ON - Information | [6 empty] | X
General parameter: Delay timer expired | 52058 | 152059 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time OFF - Information |  |  |  | X
General parameter: Delay timer expired | 52058 | 152059 | Parameters - Breakers - Tie breaker configuration - Configuration - Pulse time OFF - Information | [6 empty] | X
General parameter: Delay timer expired | 52059 | 152060 | Parameters - Breakers - Mains breaker configuration - Configuration - Spring-load time - Information |  |  |  | X
General parameter: Delay timer expired | 52059 | 152060 | Parameters - Breakers - Tie breaker configuration - Configuration - Spring-load time - Information | [6 empty] | X
General parameter: Delay timer expired | 52060 | 152061 | Open point (de-loading) |  |  |  | X |  |  | X
General parameter: Delay timer expired | 52093 | 152094 | Selection | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52094 | 152095 | Source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52118 | 152119 | GOV output offset 1 | X |  | X | X | X
General parameter: Delay timer expired | 52119 | 152120 | AVR output offset 1 | X |  | X | X | X
General parameter: Delay timer expired | 52166 | 152167 | GOV output offset 2 | X |  | X | X | X
General parameter: Delay timer expired | 52167 | 152168 | AVR output offset 2 | X |  | X | X | X
General parameter: Delay timer expired | 52180 | 152181 | GOV output offset 3 | X |  | X | X | X
General parameter: Delay timer expired | 52181 | 152182 | AVR output offset 3 | X |  | X | X | X
General parameter: Delay timer expired | 52194 | 152195 | GOV output offset 4 | X |  | X | X | X
General parameter: Delay timer expired | 52195 | 152196 | AVR output offset 4 | X |  | X | X | X
General parameter: Delay timer expired | 52200 | 152201 | Parameters - Generator - Production counters - Active energy export - Pulse length - Information | X |  | X | X | X
General parameter: Delay timer expired | 52200 | 152201 | Parameters - Busbar A - Production counters - Active energy export - Pulse length - Information |  | X
General parameter: Delay timer expired | 52200 | 152201 | Parameters - Mains - Production counters - Active energy export - Pulse length - Information | [5 empty] | X | X
General parameter: Delay timer expired | 52202 | 152203 | Parameters - Generator - Production counters - Reactive energy export - Pulse length - Information | X |  | X | X | X
General parameter: Delay timer expired | 52202 | 152203 | Parameters - Busbar A - Production counters - Reactive energy export - Pulse length - Information |  | X
General parameter: Delay timer expired | 52202 | 152203 | Parameters - Mains - Production counters - Reactive energy export - Pulse length - Information | [5 empty] | X | X
General parameter: Delay timer expired | 52204 | 152205 | Parameters - Busbar A - Production counters - Active energy import - Pulse length - Information |  | X
General parameter: Delay timer expired | 52204 | 152205 | Parameters - Mains - Production counters - Active energy import - Pulse length - Information | [5 empty] | X | X
General parameter: Delay timer expired | 52206 | 152207 | Parameters - Busbar A - Production counters - Reactive energy import - Pulse length - Information |  | X
General parameter: Delay timer expired | 52206 | 152207 | Parameters - Mains - Production counters - Reactive energy import - Pulse length - Information | [5 empty] | X | X
General parameter: Delay timer expired | 52208 | 152209 | Parameters - Busbar A - Production counters - Active energy difference - Pulse length - Information |  | X
General parameter: Delay timer expired | 52208 | 152209 | Parameters - Mains - Production counters - Active energy difference - Pulse length - Information | [5 empty] | X | X
General parameter: Delay timer expired | 52210 | 152211 | Parameters - Busbar A - Production counters - Reactive energy difference - Pulse length - Information |  | X
General parameter: Delay timer expired | 52210 | 152211 | Parameters - Mains - Production counters - Reactive energy difference - Pulse length - Information | [5 empty] | X | X
General parameter: Delay timer expired | 52211 | 152212 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52212 | 152213 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52213 | 152214 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52214 | 152215 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52215 | 152216 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52216 | 152217 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52217 | 152218 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52218 | 152219 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52219 | 152220 | Primary | X |  | X | X | X
General parameter: Delay timer expired | 52220 | 152221 | Secondary | X |  | X | X | X
General parameter: Delay timer expired | 52221 | 152222 | Primary | X |  | X | X | X
General parameter: Delay timer expired | 52222 | 152223 | Secondary | X |  | X | X | X
General parameter: Delay timer expired | 52223 | 152224 | Current reference dir. | X |  | X | X | X
General parameter: Delay timer expired | 52224 | 152225 | Current reference dir. | X |  | X | X | X
General parameter: Delay timer expired | 52225 | 152226 | Parameters - Mains - AC setup - Voltage and frequency OK - Information |  |  | X | X
General parameter: Delay timer expired | 52225 | 152226 | Parameters - Busbar - AC setup - Voltage and frequency OK - Information | X |  |  |  | X | X | X
General parameter: Delay timer expired | 52225 | 152226 | Parameters - Busbar B - AC setup - Voltage and frequency OK - Information |  | X
General parameter: Delay timer expired | 52226 | 152227 | Minimum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52227 | 152228 | Maximum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52228 | 152229 | Minimum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52229 | 152230 | Maximum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52230 | 152231 | Maximum voltage balance deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52231 | 152232 | Maximum phase deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52232 | 152233 | Detection voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52233 | 152234 | Blackout delay |  |  | X | X
General parameter: Delay timer expired | 52233 | 152234 | Parameters - Busbar - AC setup - Blackout detection - Blackout delay - Information | X |  |  |  | X | X | X
General parameter: Delay timer expired | 52233 | 152234 | Parameters - Busbar B - AC setup - Blackout detection - Blackout delay - Information |  | X
General parameter: Delay timer expired | 52234 | 152235 | Parameters - Generator - AC setup - Voltage and frequency OK - Information | X |  | X | X | X
General parameter: Delay timer expired | 52234 | 152235 | Parameters - Busbar A - AC setup - Voltage and frequency OK - Information |  | X
General parameter: Delay timer expired | 52234 | 152235 | Parameters - Mains - AC setup - Voltage and frequency OK - Information | [5 empty] | X | X
General parameter: Delay timer expired | 52235 | 152236 | Minimum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52236 | 152237 | Maximum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52237 | 152238 | Minimum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52238 | 152239 | Maximum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52239 | 152240 | Maximum voltage balance deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52240 | 152241 | Maximum phase deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52241 | 152242 | Detection voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52242 | 152243 | Blackout delay | X |  | X | X | X | X | X
General parameter: Delay timer expired | 52242 | 152243 | Parameters - Busbar A - AC setup - Blackout detection - Blackout delay - Information |  | X
General parameter: Delay timer expired | 52243 | 152244 | Parameters - Generator - AC setup - Voltage and frequency OK (blackout) - Voltage and frequency OK - Information | X |  | X | X | X
General parameter: Delay timer expired | 52244 | 152245 | Minimum OK voltage | X |  | X | X | X
General parameter: Delay timer expired | 52245 | 152246 | Maximum OK voltage | X |  | X | X | X
General parameter: Delay timer expired | 52246 | 152247 | Minimum OK frequency | X |  | X | X | X
General parameter: Delay timer expired | 52247 | 152248 | Maximum OK frequency | X |  | X | X | X
General parameter: Delay timer expired | 52248 | 152249 | AC configuration | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52249 | 152250 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52250 | 152251 | AC phase rotation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52251 | 152252 | Source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52252 | 152253 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52253 | 152254 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52254 | 152255 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52255 | 152256 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52256 | 152257 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52257 | 152258 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52258 | 152259 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52259 | 152260 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52260 | 152261 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52261 | 152262 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52262 | 152263 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52263 | 152264 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52264 | 152265 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52265 | 152266 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52266 | 152267 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52267 | 152268 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52268 | 152269 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52269 | 152270 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52270 | 152271 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52271 | 152272 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52272 | 152273 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52273 | 152274 | Enable derate | X |  | X | X | X
General parameter: Delay timer expired | 52274 | 152275 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52275 | 152276 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52276 | 152277 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52277 | 152278 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52278 | 152279 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52279 | 152280 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52280 | 152281 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52281 | 152282 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52282 | 152283 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52283 | 152284 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52284 | 152285 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52285 | 152286 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52286 | 152287 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52287 | 152288 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52288 | 152289 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52289 | 152290 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52290 | 152291 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52291 | 152292 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52292 | 152293 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52293 | 152294 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52294 | 152295 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52295 | 152296 | Enable derate | X |  | X | X | X
General parameter: Delay timer expired | 52296 | 152297 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52297 | 152298 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52298 | 152299 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52299 | 152300 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52300 | 152301 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52301 | 152302 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52302 | 152303 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52303 | 152304 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52304 | 152305 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52305 | 152306 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52306 | 152307 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52307 | 152308 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52308 | 152309 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52309 | 152310 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52310 | 152311 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52311 | 152312 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52312 | 152313 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52313 | 152314 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52314 | 152315 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52315 | 152316 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52316 | 152317 | Derate curve | X |  | X | X | X
General parameter: Delay timer expired | 52317 | 152318 | Enable derate | X |  | X | X | X
General parameter: Delay timer expired | 52318 | 152319 | Enable derate | X |  | X | X | X
General parameter: Delay timer expired | 52319 | 152320 | Voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52320 | 152321 | Current | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52321 | 152322 | Active power | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52322 | 152323 | Reactive power | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52323 | 152324 | Apparent power | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52324 | 152325 | Power factor and cos phi | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52325 | 152326 | Frequency from voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52326 | 152327 | Frequency from current | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52370 | 152371 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52371 | 152372 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52372 | 152373 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52373 | 152374 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52374 | 152375 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52375 | 152376 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52376 | 152377 | Vector shift select | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52377 | 152378 | Curve | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52378 | 152379 | Limit | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52379 | 152380 | Time multiplier setting | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52380 | 152381 | k | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52381 | 152382 | c | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52382 | 152383 | alpha | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52383 | 152384 | Curve | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52384 | 152385 | Limit | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52385 | 152386 | Time multiplier setting | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52386 | 152387 | k | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52387 | 152388 | c | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52388 | 152389 | alpha | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52389 | 152390 | Curve | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52390 | 152391 | Limit | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52391 | 152392 | Time multiplier setting | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52392 | 152393 | k | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52393 | 152394 | c | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52394 | 152395 | alpha | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52395 | 152396 | Threshold | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52396 | 152397 | Threshold | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52397 | 152398 | Threshold | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52398 | 152399 | I min. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52399 | 152400 | Angle min. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52400 | 152401 | I min. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52401 | 152402 | Angle min. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52402 | 152403 | V> aggregate time | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52403 | 152404 | V> aggregate time | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52404 | 152405 | ROCOF (df/dt) measurement half period | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52405 | 152406 | ROCOF (df/dt) positive set point | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52406 | 152407 | ROCOF (df/dt) negative set point | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52621 | 152622 | Stabilised differential | X |  | X | X | X
General parameter: Delay timer expired | 52622 | 152623 | I diff. min. | X |  | X | X | X
General parameter: Delay timer expired | 52623 | 152624 | Region 1: End | X |  | X | X | X
General parameter: Delay timer expired | 52624 | 152625 | Region 2: Slope | X |  | X | X | X
General parameter: Delay timer expired | 52625 | 152626 | Region 2: End | X |  | X | X | X
General parameter: Delay timer expired | 52626 | 152627 | Region 3: Slope | X |  | X | X | X
General parameter: Delay timer expired | 52627 | 152628 | PICUS commands | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52628 | 152629 | Modbus commands | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52629 | 152630 | I/O commands | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52630 | 152631 | CustomLogic commands | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52631 | 152632 | CODESYS commands | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52632 | 152633 | Display commands | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52633 | 152634 | PICUS commands | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52634 | 152635 | Modbus commands | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52635 | 152636 | I/O commands | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52636 | 152637 | CustomLogic commands | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52637 | 152638 | CODESYS commands | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52638 | 152639 | Display commands | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52639 | 152640 | De-energise when all alarms are acknowledged | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52640 | 152641 | Reset when new alarm | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52641 | 152642 | Parameters - Local - Alarm horn - Horn 1 - Minimum down time - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52642 | 152643 | Parameters - Local - Alarm horn - Horn 1 - Minimum up time - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52643 | 152644 | De-energise when all alarms are acknowledged | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52644 | 152645 | Reset when new alarm | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52645 | 152646 | Parameters - Local - Alarm horn - Horn 2 - Minimum down time - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52646 | 152647 | Parameters - Local - Alarm horn - Horn 2 - Minimum up time - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52647 | 152648 | De-energise when all alarms are acknowledged | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52648 | 152649 | Reset when new alarm | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52649 | 152650 | Parameters - Local - Alarm horn - Horn 3 - Minimum down time - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52650 | 152651 | Parameters - Local - Alarm horn - Horn 3 - Minimum up time - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52651 | 152652 | Duty cycle | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52652 | 152653 | Parameters - Local - Alive - Alive configuration - Period - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52653 | 152654 | Enable | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52654 | 152655 | Period time | X |  | X | X | X
General parameter: Delay timer expired | 52655 | 152656 | Minimum ON time | X |  | X | X | X
General parameter: Delay timer expired | 52656 | 152657 | Period time | X |  | X | X | X
General parameter: Delay timer expired | 52657 | 152658 | Minimum ON time | X |  | X | X | X
General parameter: Delay timer expired | 52658 | 152659 | Kp | X |  | X | X | X
General parameter: Delay timer expired | 52659 | 152660 | Ti | X |  | X | X | X
General parameter: Delay timer expired | 52660 | 152661 | Td | X |  | X | X | X
General parameter: Delay timer expired | 52661 | 152662 | Kp | X |  | X | X | X
General parameter: Delay timer expired | 52662 | 152663 | Ti | X |  | X | X | X
General parameter: Delay timer expired | 52663 | 152664 | Td | X |  | X | X | X
General parameter: Delay timer expired | 52664 | 152665 | Kp | X |  | X | X | X
General parameter: Delay timer expired | 52665 | 152666 | Ti | X |  | X | X | X
General parameter: Delay timer expired | 52666 | 152667 | Td | X |  | X | X | X
General parameter: Delay timer expired | 52667 | 152668 | Kp | X |  | X | X | X
General parameter: Delay timer expired | 52668 | 152669 | Ti | X |  | X | X | X
General parameter: Delay timer expired | 52669 | 152670 | Td | X |  | X | X | X
General parameter: Delay timer expired | 52670 | 152671 | P weight | X |  | X | X | X
General parameter: Delay timer expired | 52671 | 152672 | Q weight | X |  | X | X | X
General parameter: Delay timer expired | 52672 | 152673 | Kp | X |  | X | X | X
General parameter: Delay timer expired | 52673 | 152674 | Ti | X |  | X | X | X
General parameter: Delay timer expired | 52674 | 152675 | Td | X |  | X | X | X
General parameter: Delay timer expired | 52675 | 152676 | Kp | X |  | X | X | X
General parameter: Delay timer expired | 52676 | 152677 | Kp | X |  | X | X | X
General parameter: Delay timer expired | 52677 | 152678 | Kp | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52678 | 152679 | Deadband | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52679 | 152680 | Kp | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52680 | 152681 | Deadband | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52681 | 152682 | Kp | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52682 | 152683 | f deadband | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52683 | 152684 | P deadband | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52684 | 152685 | P weight | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52685 | 152686 | Q weight | X |  | X | X | X
General parameter: Delay timer expired | 52686 | 152687 | Kp | X |  | X | X | X
General parameter: Delay timer expired | 52687 | 152688 | Ti | X |  | X | X | X
General parameter: Delay timer expired | 52688 | 152689 | Td | X |  | X | X | X
General parameter: Delay timer expired | 52689 | 152690 | Kp | X |  | X | X | X
General parameter: Delay timer expired | 52690 | 152691 | Ti | X |  | X | X | X
General parameter: Delay timer expired | 52691 | 152692 | Td | X |  | X | X | X
General parameter: Delay timer expired | 52692 | 152693 | Kp | X |  | X | X | X
General parameter: Delay timer expired | 52693 | 152694 | Ti | X |  | X | X | X
General parameter: Delay timer expired | 52694 | 152695 | Td | X |  | X | X | X
General parameter: Delay timer expired | 52695 | 152696 | Kp | X |  | X | X | X
General parameter: Delay timer expired | 52696 | 152697 | Deadband | X |  | X | X | X
General parameter: Delay timer expired | 52697 | 152698 | Kp | X |  | X | X | X
General parameter: Delay timer expired | 52698 | 152699 | V deadband | X |  | X | X | X
General parameter: Delay timer expired | 52699 | 152700 | Kp | X |  | X | X | X
General parameter: Delay timer expired | 52700 | 152701 | Deadband | X |  | X | X | X
General parameter: Delay timer expired | 52701 | 152702 | Q deadband | X |  | X | X | X
General parameter: Delay timer expired | 52705 | 152706 | Parameters - Regulators - GOV - General configuration - Regulation delay - Regulator delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52706 | 152707 | Output type | X |  | X | X | X
General parameter: Delay timer expired | 52707 | 152708 | Output type | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52745 | 152746 | Period time | X | X | X | X | X | X | X
General parameter: Delay timer expired | 52748 | 152749 | Period time | X |  | X | X | X
General parameter: Delay timer expired | 53039 | 153040 | Delta speed min. | X |  | X | X | X
General parameter: Delay timer expired | 53040 | 153041 | Delta speed max. | X |  | X | X | X
General parameter: Delay timer expired | 53041 | 153042 | Parameters - Mains - AC setup - Supervision selector - Recovery selector time - Information |  |  | X | X |  | X | X
General parameter: Delay timer expired | 53042 | 153043 | Parameters - Mains - AC setup - Supervision selector - Recovery time fast - Information |  |  | X | X |  | X | X
General parameter: Delay timer expired | 53043 | 153044 | Parameters - Mains - AC setup - Supervision selector - Recovery time slow - Information |  |  | X | X |  | X | X
General parameter: Delay timer expired | 53044 | 153045 | Voltage low |  |  | X | X |  | X | X
General parameter: Delay timer expired | 53045 | 153046 | Voltage high |  |  | X | X |  | X | X
General parameter: Delay timer expired | 53046 | 153047 | Frequency low |  |  | X | X |  | X | X
General parameter: Delay timer expired | 53047 | 153048 | Frequency high |  |  | X | X |  | X | X
General parameter: Delay timer expired | 53048 | 153049 | Enable supervision |  |  | X | X |  | X | X
General parameter: Delay timer expired | 53049 | 153050 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53050 | 153051 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53051 | 153052 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53052 | 153053 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53053 | 153054 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53054 | 153055 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53055 | 153056 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53056 | 153057 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53057 | 153058 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53058 | 153059 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53059 | 153060 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53060 | 153061 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53061 | 153062 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53062 | 153063 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53063 | 153064 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53064 | 153065 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53065 | 153066 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53066 | 153067 | Diode offset | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53069 | 153070 | Activate | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53070 | 153071 | Parameters - Test functions - Lamp test - Duration - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53071 | 153072 | Parameters - Test functions - Lamp test - Colour cycle time - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53072 | 153073 | Active application | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53073 | 153074 | Parameters - CODESYS - Monitoring - Application not OK - Startup time - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53074 | 153075 | Enable | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53075 | 153076 | ECU Power configuration | X |  | X | X | X
General parameter: Delay timer expired | 53076 | 153077 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU powerup time - Information | X |  | X | X | X
General parameter: Delay timer expired | 53077 | 153078 | Enable | X |  | X | X | X
General parameter: Delay timer expired | 53078 | 153079 | Source address | X |  | X | X | X
General parameter: Delay timer expired | 53079 | 153080 | Enable | X |  | X | X | X
General parameter: Delay timer expired | 53080 | 153081 | Source address | X |  | X | X | X
General parameter: Delay timer expired | 53081 | 153082 | Source address | X |  | X | X | X
General parameter: Delay timer expired | 53082 | 153083 | EIC derate | X |  | X | X | X
General parameter: Delay timer expired | 53083 | 153084 | Use nominal RPM as reference | X |  | X | X | X
General parameter: Delay timer expired | 53084 | 153085 | Enable | X |  | X | X | X
General parameter: Delay timer expired | 53085 | 153086 | Aftertreatment Regeneration Inhibit Switch | X |  | X | X | X
General parameter: Delay timer expired | 53086 | 153087 | Aftertreatment Regeneration Force Switch | X |  | X | X | X
General parameter: Delay timer expired | 53087 | 153088 | Droop settings | X |  | X | X | X
General parameter: Delay timer expired | 53088 | 153089 | Droop value | X |  | X | X | X
General parameter: Delay timer expired | 53089 | 153090 | Busbar side winding nominal voltage | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53089 | 153090 | Busbar A side winding nominal voltage |  | X
General parameter: Delay timer expired | 53090 | 153091 | Generator side winding nominal voltage | X |  | X | X | X
General parameter: Delay timer expired | 53090 | 153091 | Busbar B side winding nominal voltage |  | X
General parameter: Delay timer expired | 53090 | 153091 | Mains side winding nominal voltage | [5 empty] | X | X
General parameter: Delay timer expired | 53091 | 153092 | Phase shift | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53092 | 153093 | Winding nominal voltage source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53093 | 153094 | Busbar side winding nominal voltage | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53093 | 153094 | Busbar A side winding nominal voltage |  | X
General parameter: Delay timer expired | 53094 | 153095 | Generator side winding nominal voltage | X |  | X | X | X
General parameter: Delay timer expired | 53094 | 153095 | Busbar B side winding nominal voltage |  | X
General parameter: Delay timer expired | 53094 | 153095 | Mains side winding nominal voltage | [5 empty] | X | X
General parameter: Delay timer expired | 53095 | 153096 | Phase shift | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53096 | 153097 | Winding nominal voltage source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53097 | 153098 | Busbar side winding nominal voltage | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53097 | 153098 | Busbar A side winding nominal voltage |  | X
General parameter: Delay timer expired | 53098 | 153099 | Generator side winding nominal voltage | X |  | X | X | X
General parameter: Delay timer expired | 53098 | 153099 | Busbar B side winding nominal voltage |  | X
General parameter: Delay timer expired | 53098 | 153099 | Mains side winding nominal voltage | [5 empty] | X | X
General parameter: Delay timer expired | 53099 | 153100 | Phase shift | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53100 | 153101 | Winding nominal voltage source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53101 | 153102 | Busbar side winding nominal voltage | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53101 | 153102 | Busbar A side winding nominal voltage |  | X
General parameter: Delay timer expired | 53102 | 153103 | Generator side winding nominal voltage | X |  | X | X | X
General parameter: Delay timer expired | 53102 | 153103 | Busbar B side winding nominal voltage |  | X
General parameter: Delay timer expired | 53102 | 153103 | Mains side winding nominal voltage | [5 empty] | X | X
General parameter: Delay timer expired | 53103 | 153104 | Phase shift | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53104 | 153105 | Winding nominal voltage source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53105 | 153106 | Emulation active | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53106 | 153107 | Parameters - Engine - ECU - Controls - Reset - Power off timer - Information | X |  | X | X | X
General parameter: Delay timer expired | 53117 | 153118 | Primary | X |  | X | X | X
General parameter: Delay timer expired | 53118 | 153119 | Secondary | X |  | X | X | X
General parameter: Delay timer expired | 53119 | 153120 | Primary | X |  | X | X | X
General parameter: Delay timer expired | 53120 | 153121 | Secondary | X |  | X | X | X
General parameter: Delay timer expired | 53121 | 153122 | Enable VT | X |  | X | X | X
General parameter: Delay timer expired | 53122 | 153123 | Start on threshold PWM | X |  | X | X | X
General parameter: Delay timer expired | 53123 | 153124 | Start on threshold activation | X |  | X | X | X
General parameter: Delay timer expired | 53124 | 153125 | Soft-start ramp | X |  | X | X | X
General parameter: Delay timer expired | 53125 | 153126 | Knee set point | X |  | X | X | X
General parameter: Delay timer expired | 53126 | 153127 | U/f variable slope | X |  | X | X | X
General parameter: Delay timer expired | 53127 | 153128 | Soft voltage recovery | X |  | X | X | X
General parameter: Delay timer expired | 53128 | 153129 | Adjust LAM | X |  | X | X | X
General parameter: Delay timer expired | 53129 | 153130 | Reactive droop compensation | X |  | X | X | X
General parameter: Delay timer expired | 53130 | 153131 | Voltage droop compensation | X |  | X | X | X
General parameter: Delay timer expired | 53131 | 153132 | Droop type | X |  | X | X | X
General parameter: Delay timer expired | 53132 | 153133 | Current limitation transformer | X |  | X | X | X
General parameter: Delay timer expired | 53133 | 153134 | Current limitation induction motor | X |  | X | X | X
General parameter: Delay timer expired | 53134 | 153135 | Current limitation type | X |  | X | X | X
General parameter: Delay timer expired | 53135 | 153136 | PID gain factor | X |  | X | X | X
General parameter: Delay timer expired | 53136 | 153137 | Write all settings | X |  | X | X | X
General parameter: Delay timer expired | 53137 | 153138 | Bias scale | X |  | X | X | X
General parameter: Delay timer expired | 53138 | 153139 | Controls | X |  | X | X | X
General parameter: Delay timer expired | 53139 | 153140 | Analogue bias input type | X |  | X | X | X
General parameter: Delay timer expired | 53140 | 153141 | AC configuration | X |  | X | X | X
General parameter: Delay timer expired | 53141 | 153142 | Minimum frequency threshold | X |  | X | X | X
General parameter: Delay timer expired | 53142 | 153143 | Minimum VBus threshold | X |  | X | X | X
General parameter: Delay timer expired | 53143 | 153144 | SVR and LAM configuration | X |  | X | X | X
General parameter: Delay timer expired | 53144 | 153145 | LAM duration | X |  | X | X | X
General parameter: Delay timer expired | 53145 | 153146 | Reset all DVC alarms | X |  | X | X | X
General parameter: Delay timer expired | 53146 | 153147 | Regulation selection | X |  | X | X | X
General parameter: Delay timer expired | 53147 | 153148 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Power-up time - Information | X |  | X | X | X
General parameter: Delay timer expired | 53148 | 153149 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53149 | 153150 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53150 | 153151 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53151 | 153152 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53152 | 153153 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53153 | 153154 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53154 | 153155 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53155 | 153156 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53156 | 153157 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53157 | 153158 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53158 | 153159 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53159 | 153160 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53160 | 153161 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53161 | 153162 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53162 | 153163 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53163 | 153164 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53164 | 153165 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53165 | 153166 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53166 | 153167 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53167 | 153168 | AC setup |  | X
General parameter: Delay timer expired | 53168 | 153169 | AC setup |  | X
General parameter: Delay timer expired | 53169 | 153170 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53170 | 153171 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53171 | 153172 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53172 | 153173 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53173 | 153174 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53174 | 153175 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53175 | 153176 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53176 | 153177 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53177 | 153178 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53178 | 153179 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53179 | 153180 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53180 | 153181 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53181 | 153182 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53182 | 153183 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53183 | 153184 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53184 | 153185 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53185 | 153186 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53186 | 153187 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53187 | 153188 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53188 | 153189 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53189 | 153190 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53190 | 153191 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53191 | 153192 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53192 | 153193 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53193 | 153194 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53194 | 153195 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53195 | 153196 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53196 | 153197 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53197 | 153198 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53198 | 153199 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53199 | 153200 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53200 | 153201 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53201 | 153202 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53202 | 153203 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53203 | 153204 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53204 | 153205 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53205 | 153206 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53206 | 153207 | Parameters - Engine - Stop sequence - Externally stopped - Information - Delay | X |  | X | X | X
General parameter: Delay timer expired | 53209 | 153210 | Parameters - Engine - Start sequence - Run detection not reached - Information | X |  | X | X | X
General parameter: Delay timer expired | 53210 | 153211 | Parameters - Breakers - Generator breaker configuration - Configuration - Delay after Hz/V OK before close - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53211 | 153212 | Parameters - Local power management - Mains configuration - Mains breaker configuration - MB close delay - Information | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53212 | 153213 | BTB supply |  | X
General parameter: Delay timer expired | 53213 | 153214 | Overlap | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53215 | 153216 | Tie breaker normally open/closed |  | X |  |  |  |  | X
General parameter: Delay timer expired | 53216 | 153217 | Relay type | X |  | X | X | X
General parameter: Delay timer expired | 53217 | 153218 | Close configuration | X |  | X | X | X
General parameter: Delay timer expired | 53218 | 153219 | Open configuration | X |  | X | X | X
General parameter: Delay timer expired | 53219 | 153220 | Ground relay | X |  | X | X | X
General parameter: Delay timer expired | 53220 | 153221 | RPM level | X |  | X | X | X
General parameter: Delay timer expired | 53221 | 153222 | Breaker close set point | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53223 | 153224 | Parameters - Breakers - Close before excitation - Configuration - Timer crank release to AVR on - Information | X |  | X | X | X
General parameter: Delay timer expired | 53224 | 153225 | Breakers to close | X |  | X | X | X
General parameter: Delay timer expired | 53225 | 153226 | Parameters - Breakers - Close before excitation - Configuration - Soft-start timer - Information | X |  | X | X | X
General parameter: Delay timer expired | 53226 | 153227 | Minimum RPM for excitation | X |  | X | X | X
General parameter: Delay timer expired | 53227 | 153228 | Parameters - Breakers - Close before excitation - Configuration - Voltage discharge timer for GB close - Information | X |  | X | X | X
General parameter: Delay timer expired | 53228 | 153229 | Maximum rerun voltage for GB close | X |  | X | X | X
General parameter: Delay timer expired | 53229 | 153230 | Excitation control during cooldown | X |  | X | X | X
General parameter: Delay timer expired | 53230 | 153231 | Low voltage hysteresis | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53231 | 153232 | High voltage hysteresis | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53232 | 153233 | Low frequency hysteresis | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53233 | 153234 | High frequency hysteresis | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53234 | 153235 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Voltage failure delay - Information | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53235 | 153236 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Voltage OK delay - Information | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53236 | 153237 | Low voltage | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53237 | 153238 | High voltage | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53238 | 153239 | Voltage failure sequence | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53239 | 153240 | Unbalance voltage | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53240 | 153241 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Frequency failure delay - Information | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53241 | 153242 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Frequency OK delay - Information | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53242 | 153243 | Low frequency | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53243 | 153244 | High frequency | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53244 | 153245 | Current PMS mode | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53245 | 153246 | Previous PMS mode | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53248 | 153249 | Warm up set point | X |  | X | X | X
General parameter: Delay timer expired | 53249 | 153250 | Island ramping | X |  | X | X | X
General parameter: Delay timer expired | 53250 | 153251 | Return mode | X |  | X | X | X
General parameter: Delay timer expired | 53255 | 153256 | TB de-load before GB | [5 empty] | X | X
General parameter: Delay timer expired | 53256 | 153257 | Parameters - Local power management - Non-connected genset - Stop timer - Delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53258 | 153259 | Breaker type | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53259 | 153260 | MB breaker type | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53260 | 153261 | Measurement configuration |  |  | X | X |  | X | X
General parameter: Delay timer expired | 53261 | 153262 | Mode | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53262 | 153263 | Missing controllers | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53263 | 153264 | Internal CAN protocol | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53264 | 153265 | Start generator | X |  | X | X | X
General parameter: Delay timer expired | 53266 | 153267 | Minimum load | X |  | X | X | X
General parameter: Delay timer expired | 53267 | 153268 | Stop generator | X |  | X | X | X
General parameter: Delay timer expired | 53269 | 153270 | Selection | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53270 | 153271 | Set point | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53271 | 153272 | Type | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53272 | 153273 | Usage | [5 empty] | X | X
General parameter: Delay timer expired | 53273 | 153274 | Controller settings Q | X |  | X | X | X
General parameter: Delay timer expired | 53274 | 153275 | Controller settings cos phi or Q | X |  | X | X | X
General parameter: Delay timer expired | 53275 | 153276 | Minimum load | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53276 | 153277 | Parameters - Power management rules - Mains power - Peak shaving - Start delay - Information | X |  | X | X | X
General parameter: Delay timer expired | 53277 | 153278 | Offset 1 | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53278 | 153279 | Offset 2 | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53279 | 153280 | Offset 3 | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53280 | 153281 | Offset 1 | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53281 | 153282 | Offset 1 | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53282 | 153283 | Offset 2 | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53283 | 153284 | Offset 2 | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53284 | 153285 | Offset 3 | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53285 | 153286 | Offset 3 | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53286 | 153287 | Fixed power | X |  | X | X |  | X | X
General parameter: Delay timer expired | 53287 | 153288 | Percent of nominal | X |  | X | X |  | X | X
General parameter: Delay timer expired | 53288 | 153289 | Selection | X |  | X | X |  | X | X
General parameter: Delay timer expired | 53289 | 153290 | Ring close allowed |  | X
General parameter: Delay timer expired | 53290 | 153291 | Genset mode | X |  | X | X | X
General parameter: Delay timer expired | 53291 | 153292 | Plant mode |  | X |  |  |  | X | X
General parameter: Delay timer expired | 53292 | 153293 | Store common settings | X |  |  |  | X | X | X
General parameter: Delay timer expired | 53293 | 153294 | Back synchronising | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53294 | 153295 | Synchronisation to mains | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53295 | 153296 | Parallel |  | X |  |  |  | X | X
General parameter: Delay timer expired | 53296 | 153297 | No break transfer |  | X |  |  |  | X | X
General parameter: Delay timer expired | 53297 | 153298 | Auto switch | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53298 | 153299 | Run type | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53299 | 153300 | ID to run | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53300 | 153301 | MB failure start | [5 empty] | X | X
General parameter: Delay timer expired | 53301 | 153302 | TB open point | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53303 | 153304 | Power capacity set point | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53305 | 153306 | Parameters - Local power management - Mains configuration - Tie breaker configuration - Power capacity overrule delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53306 | 153307 | Power capacity overrule enable | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53307 | 153308 | Exclude run all | [5 empty] | X | X
General parameter: Delay timer expired | 53308 | 153309 | Method | X |  | X | X | X
General parameter: Delay timer expired | 53309 | 153310 | Activate priority update | X |  | X | X | X
General parameter: Delay timer expired | 53310 | 153311 | Method | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53312 | 153313 | Transmit | X |  | X | X | X
General parameter: Delay timer expired | 53313 | 153314 | Priority 1 | X |  | X | X | X
General parameter: Delay timer expired | 53314 | 153315 | Priority 2 | X |  | X | X | X
General parameter: Delay timer expired | 53315 | 153316 | Priority 3 | X |  | X | X | X
General parameter: Delay timer expired | 53316 | 153317 | Priority 4 | X |  | X | X | X
General parameter: Delay timer expired | 53317 | 153318 | Priority 5 | X |  | X | X | X
General parameter: Delay timer expired | 53318 | 153319 | Priority 6 | X |  | X | X | X
General parameter: Delay timer expired | 53319 | 153320 | Priority 7 | X |  | X | X | X
General parameter: Delay timer expired | 53320 | 153321 | Priority 8 | X |  | X | X | X
General parameter: Delay timer expired | 53321 | 153322 | Priority 9 | X |  | X | X | X
General parameter: Delay timer expired | 53322 | 153323 | Priority 10 | X |  | X | X | X
General parameter: Delay timer expired | 53323 | 153324 | Priority 11 | X |  | X | X | X
General parameter: Delay timer expired | 53324 | 153325 | Priority 12 | X |  | X | X | X
General parameter: Delay timer expired | 53325 | 153326 | Priority 13 | X |  | X | X | X
General parameter: Delay timer expired | 53326 | 153327 | Priority 14 | X |  | X | X | X
General parameter: Delay timer expired | 53327 | 153328 | Priority 15 | X |  | X | X | X
General parameter: Delay timer expired | 53328 | 153329 | Priority 16 | X |  | X | X | X
General parameter: Delay timer expired | 53329 | 153330 | Priority 17 | X |  | X | X | X
General parameter: Delay timer expired | 53330 | 153331 | Priority 18 | X |  | X | X | X
General parameter: Delay timer expired | 53331 | 153332 | Priority 19 | X |  | X | X | X
General parameter: Delay timer expired | 53332 | 153333 | Priority 20 | X |  | X | X | X
General parameter: Delay timer expired | 53333 | 153334 | Priority 21 | X |  | X | X | X
General parameter: Delay timer expired | 53334 | 153335 | Priority 22 | X |  | X | X | X
General parameter: Delay timer expired | 53335 | 153336 | Priority 23 | X |  | X | X | X
General parameter: Delay timer expired | 53336 | 153337 | Priority 24 | X |  | X | X | X
General parameter: Delay timer expired | 53337 | 153338 | Priority 25 | X |  | X | X | X
General parameter: Delay timer expired | 53338 | 153339 | Priority 26 | X |  | X | X | X
General parameter: Delay timer expired | 53339 | 153340 | Priority 27 | X |  | X | X | X
General parameter: Delay timer expired | 53340 | 153341 | Priority 28 | X |  | X | X | X
General parameter: Delay timer expired | 53341 | 153342 | Priority 29 | X |  | X | X | X
General parameter: Delay timer expired | 53342 | 153343 | Priority 30 | X |  | X | X | X
General parameter: Delay timer expired | 53343 | 153344 | Priority 31 | X |  | X | X | X
General parameter: Delay timer expired | 53344 | 153345 | Priority 32 | X |  | X | X | X
General parameter: Delay timer expired | 53345 | 153346 | Trip when breaker trips | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53346 | 153347 | Trip when breaker trips | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53347 | 153348 | Trip when breaker trips | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53349 | 153350 | Broadcast application | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53350 | 153351 | Application to broadcast | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53351 | 153352 | Section P> | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53352 | 153353 | Section P> factor | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53353 | 153354 | Mode shift | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53354 | 153355 | N + X setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53355 | 153356 | P available limit | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53356 | 153357 | S available limit | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53357 | 153358 | Load limit | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53358 | 153359 | Parameters - Power management rules - Load-dependent start/stop - Start 1 - Delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53359 | 153360 | P available limit | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53360 | 153361 | S available limit | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53361 | 153362 | Load limit | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53362 | 153363 | Parameters - Power management rules - Load-dependent start/stop - Stop 1 - Delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53363 | 153364 | Power selection | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53364 | 153365 | Method | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53365 | 153366 | P available limit | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53366 | 153367 | S available limit | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53367 | 153368 | Load limit | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53368 | 153369 | Parameters - Power management rules - Load-dependent start/stop - Start 2 - Delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53370 | 153371 | P available limit | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53371 | 153372 | S available limit | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53372 | 153373 | Load limit | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53373 | 153374 | Parameters - Power management rules - Load-dependent start/stop - Stop 2 - Delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53377 | 153378 | Set point | X | X | X | X | X
General parameter: Delay timer expired | 53379 | 153380 | Set point | X |  | X | X | X
General parameter: Delay timer expired | 53380 | 153381 | Set point | X |  | X | X | X
General parameter: Delay timer expired | 53381 | 153382 | Multi-start set 1 | X |  | X | X | X
General parameter: Delay timer expired | 53382 | 153383 | Multi-start set 2 | X |  | X | X | X
General parameter: Delay timer expired | 53383 | 153384 | Multi-start selection | X |  | X | X | X
General parameter: Delay timer expired | 53384 | 153385 | Multi-start set during AMF | X
General parameter: Delay timer expired | 53385 | 153386 | Excitation reference for dry alternator | X |  | X | X | X
General parameter: Delay timer expired | 53386 | 153387 | Digital AVR modes | X |  | X | X | X
General parameter: Delay timer expired | 53387 | 153388 | Enter operation ramp enable | X |  | X | X | X
General parameter: Delay timer expired | 53388 | 153389 | Deload ramp enable | X |  | X | X | X
General parameter: Delay timer expired | 53389 | 153390 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53390 | 153391 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53391 | 153392 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53392 | 153393 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53393 | 153394 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53394 | 153395 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53395 | 153396 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53396 | 153397 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53397 | 153398 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53398 | 153399 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53399 | 153400 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53400 | 153401 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53401 | 153402 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53402 | 153403 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53403 | 153404 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53404 | 153405 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53405 | 153406 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53406 | 153407 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53407 | 153408 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53408 | 153409 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53409 | 153410 | Operation ramp up 1 | X |  | X | X | X
General parameter: Delay timer expired | 53410 | 153411 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53411 | 153412 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53412 | 153413 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53413 | 153414 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53414 | 153415 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53415 | 153416 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53416 | 153417 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53417 | 153418 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53418 | 153419 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53419 | 153420 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53420 | 153421 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53421 | 153422 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53422 | 153423 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53423 | 153424 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53424 | 153425 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53425 | 153426 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53426 | 153427 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53427 | 153428 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53428 | 153429 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53429 | 153430 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53430 | 153431 | Operation ramp down 1 | X |  | X | X | X
General parameter: Delay timer expired | 53431 | 153432 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53432 | 153433 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53433 | 153434 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53434 | 153435 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53435 | 153436 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53436 | 153437 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53437 | 153438 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53438 | 153439 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53439 | 153440 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53440 | 153441 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53441 | 153442 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53442 | 153443 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53443 | 153444 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53444 | 153445 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53445 | 153446 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53446 | 153447 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53447 | 153448 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53448 | 153449 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53449 | 153450 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53450 | 153451 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53451 | 153452 | Enter operation ramp | X |  | X | X | X
General parameter: Delay timer expired | 53452 | 153453 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53453 | 153454 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53454 | 153455 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53455 | 153456 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53456 | 153457 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53457 | 153458 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53458 | 153459 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53459 | 153460 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53460 | 153461 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53461 | 153462 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53462 | 153463 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53463 | 153464 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53464 | 153465 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53465 | 153466 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53466 | 153467 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53467 | 153468 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53468 | 153469 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53469 | 153470 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53470 | 153471 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53471 | 153472 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53472 | 153473 | Deload ramp | X |  | X | X | X
General parameter: Delay timer expired | 53473 | 153474 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53474 | 153475 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53475 | 153476 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53476 | 153477 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53477 | 153478 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53478 | 153479 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53479 | 153480 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53480 | 153481 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53481 | 153482 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53482 | 153483 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53483 | 153484 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53484 | 153485 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53485 | 153486 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53486 | 153487 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53487 | 153488 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53488 | 153489 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53489 | 153490 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53490 | 153491 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53491 | 153492 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53492 | 153493 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53493 | 153494 | Operation ramp up | X |  | X | X | X
General parameter: Delay timer expired | 53494 | 153495 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53495 | 153496 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53496 | 153497 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53497 | 153498 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53498 | 153499 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53499 | 153500 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53500 | 153501 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53501 | 153502 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53502 | 153503 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53503 | 153504 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53504 | 153505 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53505 | 153506 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53506 | 153507 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53507 | 153508 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53508 | 153509 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53509 | 153510 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53510 | 153511 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53511 | 153512 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53512 | 153513 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53513 | 153514 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53514 | 153515 | Operation ramp down | X |  | X | X | X
General parameter: Delay timer expired | 53515 | 153516 | Delta frequency min. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53516 | 153517 | Delta frequency max. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53517 | 153518 | Delta voltage min. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53518 | 153519 | Delta voltage max. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53519 | 153520 | Breaker close time | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53520 | 153521 | Phase window | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53521 | 153522 | Minimum time in phase window | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53522 | 153523 | Sync type | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53523 | 153524 | Sync behavior | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53524 | 153525 | Delta frequency min. |  |  |  | X |  |  | X
General parameter: Delay timer expired | 53525 | 153526 | Delta frequency max. |  |  |  | X |  |  | X
General parameter: Delay timer expired | 53526 | 153527 | Delta voltage min. |  |  |  | X |  |  | X
General parameter: Delay timer expired | 53527 | 153528 | Delta voltage max. |  |  |  | X |  |  | X
General parameter: Delay timer expired | 53528 | 153529 | Breaker close time |  |  |  | X |  |  | X
General parameter: Delay timer expired | 53529 | 153530 | Phase window |  |  |  | X |  |  | X
General parameter: Delay timer expired | 53530 | 153531 | Minimum time in phase window |  |  |  | X |  |  | X
General parameter: Delay timer expired | 53531 | 153532 | Sync type |  |  |  | X |  |  | X
General parameter: Delay timer expired | 53532 | 153533 | Sync behavior |  |  |  | X |  |  | X
General parameter: Delay timer expired | 53542 | 153543 | Delta frequency min. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53543 | 153544 | Delta frequency max. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53544 | 153545 | Delta voltage min. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53545 | 153546 | Delta voltage max. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53546 | 153547 | Breaker close time | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53547 | 153548 | Phase window | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53548 | 153549 | Minimum time in phase window | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53549 | 153550 | Sync type | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53550 | 153551 | Sync behavior | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53551 | 153552 | Delta frequency min. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53552 | 153553 | Delta frequency max. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53553 | 153554 | Delta voltage min. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53554 | 153555 | Delta voltage max. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53555 | 153556 | Breaker close time | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53556 | 153557 | Phase window | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53557 | 153558 | Minimum time in phase window | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53558 | 153559 | Sync type | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53559 | 153560 | Sync behavior | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53560 | 153561 | Delta frequency min. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53561 | 153562 | Delta frequency max. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53562 | 153563 | Delta voltage min. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53563 | 153564 | Delta voltage max. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53564 | 153565 | Breaker close time | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53565 | 153566 | Phase window | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53566 | 153567 | Minimum time in phase window | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53567 | 153568 | Sync type | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53568 | 153569 | Sync behavior | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53569 | 153570 | Delta frequency min. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53570 | 153571 | Delta frequency max. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53571 | 153572 | Delta voltage min. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53572 | 153573 | Delta voltage max. | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53573 | 153574 | Breaker close time | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53574 | 153575 | Phase window | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53575 | 153576 | Minimum time in phase window | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53576 | 153577 | Sync type | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53577 | 153578 | Sync behavior | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53578 | 153579 | Selection | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53579 | 153580 | Selection | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53580 | 153581 | Selection | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53581 | 153582 | Selection | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53582 | 153583 | Source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53583 | 153584 | Source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53584 | 153585 | Source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53585 | 153586 | Source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53586 | 153587 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53587 | 153588 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53588 | 153589 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53589 | 153590 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53590 | 153591 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53591 | 153592 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53592 | 153593 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53593 | 153594 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53594 | 153595 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53595 | 153596 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53596 | 153597 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53597 | 153598 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53598 | 153599 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53599 | 153600 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53600 | 153601 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53601 | 153602 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53602 | 153603 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53603 | 153604 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53604 | 153605 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53605 | 153606 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53606 | 153607 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53607 | 153608 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53608 | 153609 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53609 | 153610 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53610 | 153611 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53611 | 153612 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53612 | 153613 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53613 | 153614 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53614 | 153615 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53615 | 153616 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53616 | 153617 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53617 | 153618 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53618 | 153619 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53619 | 153620 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53620 | 153621 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53621 | 153622 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53622 | 153623 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53623 | 153624 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53624 | 153625 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53625 | 153626 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53626 | 153627 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53627 | 153628 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53628 | 153629 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53629 | 153630 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53630 | 153631 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53631 | 153632 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53632 | 153633 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53633 | 153634 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53634 | 153635 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53635 | 153636 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53636 | 153637 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53637 | 153638 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53638 | 153639 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53639 | 153640 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53640 | 153641 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53641 | 153642 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53642 | 153643 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53643 | 153644 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53644 | 153645 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53645 | 153646 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53646 | 153647 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53647 | 153648 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53648 | 153649 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53649 | 153650 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53650 | 153651 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53651 | 153652 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53652 | 153653 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53653 | 153654 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53654 | 153655 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53655 | 153656 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53656 | 153657 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53657 | 153658 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53658 | 153659 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53659 | 153660 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53660 | 153661 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53661 | 153662 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53662 | 153663 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53663 | 153664 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53664 | 153665 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53665 | 153666 | Nominal value source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53666 | 153667 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53667 | 153668 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53668 | 153669 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53669 | 153670 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53670 | 153671 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53671 | 153672 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53672 | 153673 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53673 | 153674 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53674 | 153675 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53675 | 153676 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53676 | 153677 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53677 | 153678 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53678 | 153679 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53679 | 153680 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53680 | 153681 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53681 | 153682 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53682 | 153683 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53683 | 153684 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53684 | 153685 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53685 | 153686 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53686 | 153687 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53687 | 153688 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53688 | 153689 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53689 | 153690 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53690 | 153691 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53691 | 153692 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53692 | 153693 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53693 | 153694 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53694 | 153695 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53695 | 153696 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53696 | 153697 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53697 | 153698 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53698 | 153699 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53699 | 153700 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53700 | 153701 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53701 | 153702 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53702 | 153703 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53703 | 153704 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53704 | 153705 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53705 | 153706 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53706 | 153707 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53707 | 153708 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53708 | 153709 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53709 | 153710 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53710 | 153711 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53711 | 153712 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53712 | 153713 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53713 | 153714 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53714 | 153715 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53715 | 153716 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53716 | 153717 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53717 | 153718 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53718 | 153719 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53719 | 153720 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53720 | 153721 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53721 | 153722 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53722 | 153723 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53723 | 153724 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53724 | 153725 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53725 | 153726 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53726 | 153727 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53727 | 153728 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53728 | 153729 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53729 | 153730 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53730 | 153731 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53731 | 153732 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53732 | 153733 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53733 | 153734 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53734 | 153735 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53735 | 153736 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53736 | 153737 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53737 | 153738 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53738 | 153739 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53739 | 153740 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53740 | 153741 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53741 | 153742 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53742 | 153743 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53743 | 153744 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53744 | 153745 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53745 | 153746 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53746 | 153747 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53747 | 153748 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53748 | 153749 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53749 | 153750 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53750 | 153751 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53751 | 153752 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53752 | 153753 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53753 | 153754 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53754 | 153755 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53755 | 153756 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53756 | 153757 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53757 | 153758 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53758 | 153759 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53759 | 153760 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53760 | 153761 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53761 | 153762 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53762 | 153763 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53763 | 153764 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53764 | 153765 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53765 | 153766 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53766 | 153767 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53767 | 153768 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53768 | 153769 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53769 | 153770 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53770 | 153771 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53771 | 153772 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53772 | 153773 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53773 | 153774 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53774 | 153775 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53775 | 153776 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53776 | 153777 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53777 | 153778 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53778 | 153779 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53779 | 153780 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53780 | 153781 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53781 | 153782 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53782 | 153783 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53783 | 153784 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53784 | 153785 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53785 | 153786 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53786 | 153787 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53787 | 153788 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53788 | 153789 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53789 | 153790 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53790 | 153791 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53791 | 153792 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53792 | 153793 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53793 | 153794 | Nominal (calculated) | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53794 | 153795 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53795 | 153796 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53796 | 153797 | Reactive power (Q) nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53797 | 153798 | P or S nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53798 | 153799 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53799 | 153800 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53800 | 153801 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53801 | 153802 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53802 | 153803 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53803 | 153804 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53804 | 153805 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53805 | 153806 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53806 | 153807 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53807 | 153808 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53808 | 153809 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53809 | 153810 | Nominal | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53810 | 153811 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53811 | 153812 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53812 | 153813 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53813 | 153814 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53814 | 153815 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53815 | 153816 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53816 | 153817 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53817 | 153818 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53818 | 153819 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53819 | 153820 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53820 | 153821 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53821 | 153822 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53822 | 153823 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53823 | 153824 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53824 | 153825 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53825 | 153826 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53826 | 153827 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53827 | 153828 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53828 | 153829 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53829 | 153830 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53830 | 153831 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53831 | 153832 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53832 | 153833 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53833 | 153834 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53834 | 153835 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53835 | 153836 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53836 | 153837 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53837 | 153838 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53838 | 153839 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53839 | 153840 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53840 | 153841 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53841 | 153842 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53842 | 153843 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53843 | 153844 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53844 | 153845 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53845 | 153846 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53846 | 153847 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53847 | 153848 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53848 | 153849 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53849 | 153850 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy export - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53850 | 153851 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53851 | 153852 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53852 | 153853 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53853 | 153854 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy import - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53854 | 153855 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53855 | 153856 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53856 | 153857 | Pulse every | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53857 | 153858 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy difference - Pulse length - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53858 | 153859 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53859 | 153860 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53860 | 153861 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53861 | 153862 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53862 | 153863 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53863 | 153864 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53864 | 153865 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53865 | 153866 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53866 | 153867 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53867 | 153868 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53868 | 153869 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53869 | 153870 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53870 | 153871 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53871 | 153872 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53872 | 153873 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53873 | 153874 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53874 | 153875 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53875 | 153876 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53876 | 153877 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53877 | 153878 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53878 | 153879 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53879 | 153880 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53880 | 153881 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53881 | 153882 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53882 | 153883 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53883 | 153884 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53884 | 153885 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53885 | 153886 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53886 | 153887 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53887 | 153888 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53888 | 153889 | Primary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53889 | 153890 | Secondary | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53890 | 153891 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53891 | 153892 | Minimum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53892 | 153893 | Maximum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53893 | 153894 | Minimum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53894 | 153895 | Maximum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53895 | 153896 | Maximum voltage balance deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53896 | 153897 | Maximum phase deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53897 | 153898 | Detection voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53898 | 153899 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53899 | 153900 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53900 | 153901 | Minimum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53901 | 153902 | Maximum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53902 | 153903 | Minimum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53903 | 153904 | Maximum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53904 | 153905 | Maximum voltage balance deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53905 | 153906 | Maximum phase deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53906 | 153907 | Detection voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53907 | 153908 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53908 | 153909 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53909 | 153910 | Minimum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53910 | 153911 | Maximum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53911 | 153912 | Minimum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53912 | 153913 | Maximum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53913 | 153914 | Maximum voltage balance deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53914 | 153915 | Maximum phase deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53915 | 153916 | Detection voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53916 | 153917 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53917 | 153918 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53918 | 153919 | Minimum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53919 | 153920 | Maximum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53920 | 153921 | Minimum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53921 | 153922 | Maximum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53922 | 153923 | Maximum voltage balance deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53923 | 153924 | Maximum phase deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53924 | 153925 | Detection voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53925 | 153926 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53926 | 153927 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53927 | 153928 | Minimum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53928 | 153929 | Maximum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53929 | 153930 | Minimum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53930 | 153931 | Maximum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53931 | 153932 | Maximum voltage balance deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53932 | 153933 | Maximum phase deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53933 | 153934 | Detection voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53934 | 153935 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53935 | 153936 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53936 | 153937 | Minimum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53937 | 153938 | Maximum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53938 | 153939 | Minimum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53939 | 153940 | Maximum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53940 | 153941 | Maximum voltage balance deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53941 | 153942 | Maximum phase deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53942 | 153943 | Detection voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53943 | 153944 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53944 | 153945 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53945 | 153946 | Minimum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53946 | 153947 | Maximum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53947 | 153948 | Minimum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53948 | 153949 | Maximum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53949 | 153950 | Maximum voltage balance deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53950 | 153951 | Maximum phase deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53951 | 153952 | Detection voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53952 | 153953 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53953 | 153954 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Voltage and frequency OK - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53954 | 153955 | Minimum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53955 | 153956 | Maximum OK voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53956 | 153957 | Minimum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53957 | 153958 | Maximum OK frequency | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53958 | 153959 | Maximum voltage balance deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53959 | 153960 | Maximum phase deviation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53960 | 153961 | Detection voltage | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53961 | 153962 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Blackout detection - Blackout delay - Information | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53962 | 153963 | AC configuration | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53963 | 153964 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53964 | 153965 | AC phase rotation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53965 | 153966 | AC configuration | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53966 | 153967 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53967 | 153968 | AC phase rotation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53968 | 153969 | AC configuration | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53969 | 153970 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53970 | 153971 | AC phase rotation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53971 | 153972 | AC configuration | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53972 | 153973 | AC setup | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53973 | 153974 | AC phase rotation | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53974 | 153975 | Source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53975 | 153976 | Source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53976 | 153977 | Source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53977 | 153978 | Source | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53978 | 153979 | Selected mode | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53979 | 153980 | Boot mode | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53980 | 153981 | Parameters - Breakers - Short-time parallel - Configuration - Maximum overlap time - Information | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53981 | 153982 | Enable | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53982 | 153983 | Base load | X |  | X | X | X
General parameter: Delay timer expired | 53983 | 153984 | Set point | X |  | X | X | X
General parameter: Delay timer expired | 53984 | 153985 | Enable | X | X | X | X | X
General parameter: Delay timer expired | 53985 | 153986 | Set point | X | X | X | X | X
General parameter: Delay timer expired | 53986 | 153987 | Type | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53987 | 153988 | Base load | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53988 | 153989 | Mode | X |  | X | X | X | X | X
General parameter: Delay timer expired | 53989 | 153990 | Parameters - Local power management - Genset test - Settings - Test time - Information | X |  | X | X | X
General parameter: Delay timer expired | 53989 | 153990 | Parameters - Power management rules - Mains power - Mains test - Test time - Information | [5 empty] | X | X
General parameter: Delay timer expired | 53990 | 153991 | Parameters - Power management rules - Mains power - Peak shaving - Stop delay - Information | X |  | X | X | X
General parameter: Delay timer expired | 53991 | 153992 | Enable | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53992 | 153993 | Enable | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53993 | 153994 | Enable | X | X | X | X | X
General parameter: Delay timer expired | 53994 | 153995 | Destination address | X |  | X | X | X
General parameter: Delay timer expired | 53995 | 153996 | Application selector | X | X | X | X | X | X | X
General parameter: Delay timer expired | 53996 | 153997 | Enable | X |  | X | X | X
General parameter: Delay timer expired | 53997 | 153998 | Use timer | X |  | X | X | X
General parameter: Delay timer expired | 53998 | 153999 | Parameters - Engine - ECU diagnostic - Time to enable function - Information | X |  | X | X | X
General parameter: Delay timer expired | 53999 | 154000 | Mode | X |  | X | X | X
General parameter: Delay timer expired | 54000 | 154001 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump ON delay - Information | X |  | X | X | X
General parameter: Delay timer expired | 54001 | 154002 | Fill check slope | X |  | X | X | X
General parameter: Delay timer expired | 54002 | 154003 | Pump ON set point | X |  | X | X | X
General parameter: Delay timer expired | 54003 | 154004 | Pump OFF set point | X |  | X | X | X
General parameter: Delay timer expired | 54004 | 154005 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump ON delay - Information | X |  | X | X | X
General parameter: Delay timer expired | 54005 | 154006 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump OFF delay - Information | X |  | X | X | X
General parameter: Delay timer expired | 54006 | 154007 | Pump source select | X |  | X | X | X
General parameter: Delay timer expired | 54007 | 154008 | Fill check slope | X |  | X | X | X
General parameter: Delay timer expired | 54008 | 154009 | Pump ON set point | X |  | X | X | X
General parameter: Delay timer expired | 54009 | 154010 | Pump OFF set point | X |  | X | X | X
General parameter: Delay timer expired | 54010 | 154011 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump ON delay - Information | X |  | X | X | X
General parameter: Delay timer expired | 54011 | 154012 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump OFF delay - Information | X |  | X | X | X
General parameter: Delay timer expired | 54012 | 154013 | Pump source select | X |  | X | X | X
General parameter: Delay timer expired | 54013 | 154014 | Fill check slope | X |  | X | X | X
General parameter: Delay timer expired | 54014 | 154015 | Frequency offset source |  |  | X | X
General parameter: Delay timer expired | 54015 | 154016 | Frequency offset enable |  |  | X | X
General parameter: Delay timer expired | 54016 | 154017 | RRCR inputs enable |  |  | X | X
General parameter: Delay timer expired | 54017 | 154018 | RRCR outputs enable |  |  | X | X
General parameter: Delay timer expired | 54020 | 154021 | Droop curve 1 enable |  |  | X | X
General parameter: Delay timer expired | 54030 | 154031 | Dependency |  |  | X | X
General parameter: Delay timer expired | 54046 | 154047 | FeedForwardVolt_KFF |  |  | X | X
General parameter: Delay timer expired | 54047 | 154048 | FeedForwardVolt_Ena |  |  | X | X
General parameter: Delay timer expired | 54048 | 154049 | FeedForwardFreq_KFF |  |  | X | X
General parameter: Delay timer expired | 54049 | 154050 | FeedForwardFreq_Ena |  |  | X | X
General parameter: Delay timer expired | 54050 | 154051 | Enable ramping |  |  | X | X
General parameter: Delay timer expired | 54051 | 154052 | Enable operation ramp 2 |  |  | X | X
General parameter: Delay timer expired | 54052 | 154053 | Enable operation ramp 3 |  |  | X | X
General parameter: Delay timer expired | 54053 | 154054 | Enable operation ramp 4 |  |  | X | X
General parameter: Delay timer expired | 54054 | 154055 | Time constant |  |  | X | X
General parameter: Delay timer expired | 54055 | 154056 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54056 | 154057 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54057 | 154058 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54058 | 154059 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54059 | 154060 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54060 | 154061 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54061 | 154062 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54062 | 154063 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54063 | 154064 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54064 | 154065 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54065 | 154066 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54066 | 154067 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54067 | 154068 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54068 | 154069 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54069 | 154070 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54070 | 154071 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54071 | 154072 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54072 | 154073 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54073 | 154074 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54074 | 154075 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54075 | 154076 | Operation ramp up 2 |  |  | X | X
General parameter: Delay timer expired | 54076 | 154077 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54077 | 154078 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54078 | 154079 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54079 | 154080 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54080 | 154081 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54081 | 154082 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54082 | 154083 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54083 | 154084 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54084 | 154085 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54085 | 154086 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54086 | 154087 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54087 | 154088 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54088 | 154089 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54089 | 154090 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54090 | 154091 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54091 | 154092 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54092 | 154093 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54093 | 154094 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54094 | 154095 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54095 | 154096 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54096 | 154097 | Operation ramp down 2 |  |  | X | X
General parameter: Delay timer expired | 54097 | 154098 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54098 | 154099 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54099 | 154100 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54100 | 154101 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54101 | 154102 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54102 | 154103 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54103 | 154104 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54104 | 154105 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54105 | 154106 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54106 | 154107 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54107 | 154108 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54108 | 154109 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54109 | 154110 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54110 | 154111 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54111 | 154112 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54112 | 154113 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54113 | 154114 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54114 | 154115 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54115 | 154116 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54116 | 154117 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54117 | 154118 | Operation ramp up 3 |  |  | X | X
General parameter: Delay timer expired | 54118 | 154119 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54119 | 154120 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54120 | 154121 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54121 | 154122 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54122 | 154123 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54123 | 154124 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54124 | 154125 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54125 | 154126 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54126 | 154127 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54127 | 154128 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54128 | 154129 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54129 | 154130 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54130 | 154131 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54131 | 154132 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54132 | 154133 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54133 | 154134 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54134 | 154135 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54135 | 154136 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54136 | 154137 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54137 | 154138 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54138 | 154139 | Operation ramp down 3 |  |  | X | X
General parameter: Delay timer expired | 54139 | 154140 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54140 | 154141 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54141 | 154142 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54142 | 154143 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54143 | 154144 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54144 | 154145 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54145 | 154146 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54146 | 154147 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54147 | 154148 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54148 | 154149 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54149 | 154150 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54150 | 154151 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54151 | 154152 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54152 | 154153 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54153 | 154154 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54154 | 154155 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54155 | 154156 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54156 | 154157 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54157 | 154158 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54158 | 154159 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54159 | 154160 | Operation ramp up 4 |  |  | X | X
General parameter: Delay timer expired | 54160 | 154161 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54161 | 154162 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54162 | 154163 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54163 | 154164 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54164 | 154165 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54165 | 154166 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54166 | 154167 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54167 | 154168 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54168 | 154169 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54169 | 154170 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54170 | 154171 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54171 | 154172 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54172 | 154173 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54173 | 154174 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54174 | 154175 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54175 | 154176 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54176 | 154177 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54177 | 154178 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54178 | 154179 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54179 | 154180 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54180 | 154181 | Operation ramp down 4 |  |  | X | X
General parameter: Delay timer expired | 54188 | 154189 | Type selection |  |  | X | X
General parameter: Delay timer expired | 54189 | 154190 | Ramp switch timer |  |  | X | X
General parameter: Delay timer expired | 54190 | 154191 | Limit Q under-excited |  |  | X | X
General parameter: Delay timer expired | 54191 | 154192 | Limit Q over-excited |  |  | X | X
General parameter: Delay timer expired | 54192 | 154193 | Voltage deadband |  |  | X | X
General parameter: Delay timer expired | 54193 | 154194 | Reference voltage at Q=0 |  |  | X | X
General parameter: Delay timer expired | 54194 | 154195 | Maximum voltage at Q max |  |  | X | X
General parameter: Delay timer expired | 54195 | 154196 | Maximum Q during over-voltage |  |  | X | X
General parameter: Delay timer expired | 54196 | 154197 | Minimum Q during under-voltage |  |  | X | X
General parameter: Delay timer expired | 54197 | 154198 | Reference voltage offset value |  |  | X | X
General parameter: Delay timer expired | 54198 | 154199 | External control |  |  | X | X
General parameter: Delay timer expired | 54199 | 154200 | Q/Pnom offset |  |  | X | X
General parameter: Delay timer expired | 54200 | 154201 | External control |  |  | X | X
General parameter: Delay timer expired | 54201 | 154202 | Cos phi set point |  |  | X | X
General parameter: Delay timer expired | 54202 | 154203 | Cos phi direction |  |  | X | X
General parameter: Delay timer expired | 54203 | 154204 | Cos phi offset |  |  | X | X
General parameter: Delay timer expired | 54204 | 154205 | External control |  |  | X | X
General parameter: Delay timer expired | 54205 | 154206 | Q set point |  |  | X | X
General parameter: Delay timer expired | 54206 | 154207 | Voltage low limit |  |  | X | X
General parameter: Delay timer expired | 54207 | 154208 | Voltage high limit |  |  | X | X
General parameter: Delay timer expired | 54208 | 154209 | Frequency low limit |  |  | X | X
General parameter: Delay timer expired | 54209 | 154210 | Frequency high limit |  |  | X | X
General parameter: Delay timer expired | 54210 | 154211 | Recovery delay select |  |  | X | X
General parameter: Delay timer expired | 54211 | 154212 | Parameters - Grid code - Mains sync inhibit - Recovery delay select time - Information |  |  | X | X
General parameter: Delay timer expired | 54212 | 154213 | Recovery delay 1 |  |  | X | X
General parameter: Delay timer expired | 54213 | 154214 | Parameters - Grid code - Mains sync inhibit - Recovery delay 1 time - Information |  |  | X | X
General parameter: Delay timer expired | 54214 | 154215 | Recovery delay 2 |  |  | X | X
General parameter: Delay timer expired | 54215 | 154216 | Parameters - Grid code - Mains sync inhibit - Recovery delay 2 time - Information |  |  | X | X
General parameter: Delay timer expired | 54216 | 154217 | Calculation method |  |  | X | X
General parameter: Delay timer expired | 54217 | 154218 | Slope calculation method |  |  | X | X
General parameter: Delay timer expired | 54218 | 154219 | Slope low percentage |  |  | X | X
General parameter: Delay timer expired | 54219 | 154220 | Slope high percentage |  |  | X | X
General parameter: Delay timer expired | 54220 | 154221 | Slope low absolute |  |  | X | X
General parameter: Delay timer expired | 54221 | 154222 | Slope high absolute |  |  | X | X
General parameter: Delay timer expired | 54222 | 154223 | Minimum active power |  |  | X | X
General parameter: Delay timer expired | 54223 | 154224 | Maximum active power |  |  | X | X
General parameter: Delay timer expired | 54224 | 154225 | Deadband low |  |  | X | X
General parameter: Delay timer expired | 54225 | 154226 | Deadband high |  |  | X | X
General parameter: Delay timer expired | 54226 | 154227 | Hysteresis low |  |  | X | X
General parameter: Delay timer expired | 54227 | 154228 | Hysteresis high |  |  | X | X
General parameter: Delay timer expired | 54228 | 154229 | Recovery delay |  |  | X | X
General parameter: Delay timer expired | 54229 | 154230 | Ramp 3 activation delay |  |  | X | X
General parameter: Delay timer expired | 54230 | 154231 | Droop curve 2 enable |  |  | X | X
General parameter: Delay timer expired | 54231 | 154232 | Curve output |  |  | X | X
General parameter: Delay timer expired | 54232 | 154233 | Dependency |  |  | X | X
General parameter: Delay timer expired | 54233 | 154234 | Cos phi slope low |  |  | X | X
General parameter: Delay timer expired | 54234 | 154235 | Cos phi slope high |  |  | X | X
General parameter: Delay timer expired | 54235 | 154236 | Cos phi minimum |  |  | X | X
General parameter: Delay timer expired | 54236 | 154237 | Cos phi minimum direction |  |  | X | X
General parameter: Delay timer expired | 54237 | 154238 | Cos phi maximum |  |  | X | X
General parameter: Delay timer expired | 54238 | 154239 | Cos phi maximum direction |  |  | X | X
General parameter: Delay timer expired | 54239 | 154240 | Reactive power slope low |  |  | X | X
General parameter: Delay timer expired | 54240 | 154241 | Reactive power slope high |  |  | X | X
General parameter: Delay timer expired | 54241 | 154242 | Reactive power minimum |  |  | X | X
General parameter: Delay timer expired | 54242 | 154243 | Reactive power maximum |  |  | X | X
General parameter: Delay timer expired | 54243 | 154244 | Deadband low |  |  | X | X
General parameter: Delay timer expired | 54244 | 154245 | Deadband high |  |  | X | X
General parameter: Delay timer expired | 54245 | 154246 | Hysteresis low |  |  | X | X
General parameter: Delay timer expired | 54246 | 154247 | Hysteresis high |  |  | X | X
General parameter: Delay timer expired | 54247 | 154248 | AVR limiting set point |  |  | X | X
General parameter: Delay timer expired | 54248 | 154249 | AVR limiting type |  |  | X | X
General parameter: Delay timer expired | 54249 | 154250 | y-axis select |  |  | X | X
General parameter: Delay timer expired | 54250 | 154251 | Capability curve import |  |  | X | X
General parameter: Delay timer expired | 54251 | 154252 | Capability curve import |  |  | X | X
General parameter: Delay timer expired | 54252 | 154253 | Capability curve import |  |  | X | X
General parameter: Delay timer expired | 54253 | 154254 | Capability curve import |  |  | X | X
General parameter: Delay timer expired | 54254 | 154255 | Capability curve import |  |  | X | X
General parameter: Delay timer expired | 54255 | 154256 | Capability curve import |  |  | X | X
General parameter: Delay timer expired | 54256 | 154257 | Capability curve import |  |  | X | X
General parameter: Delay timer expired | 54257 | 154258 | Capability curve import |  |  | X | X
General parameter: Delay timer expired | 54258 | 154259 | Capability curve import |  |  | X | X
General parameter: Delay timer expired | 54259 | 154260 | Capability curve import |  |  | X | X
General parameter: Delay timer expired | 54260 | 154261 | Capability curve import |  |  | X | X
General parameter: Delay timer expired | 54261 | 154262 | Capability curve import |  |  | X | X
General parameter: Delay timer expired | 54262 | 154263 | Capability curve import |  |  | X | X
General parameter: Delay timer expired | 54263 | 154264 | Capability curve export |  |  | X | X
General parameter: Delay timer expired | 54264 | 154265 | Capability curve export |  |  | X | X
General parameter: Delay timer expired | 54265 | 154266 | Capability curve export |  |  | X | X
General parameter: Delay timer expired | 54266 | 154267 | Capability curve export |  |  | X | X
General parameter: Delay timer expired | 54267 | 154268 | Capability curve export |  |  | X | X
General parameter: Delay timer expired | 54268 | 154269 | Capability curve export |  |  | X | X
General parameter: Delay timer expired | 54269 | 154270 | Capability curve export |  |  | X | X
General parameter: Delay timer expired | 54270 | 154271 | Capability curve export |  |  | X | X
General parameter: Delay timer expired | 54271 | 154272 | Capability curve export |  |  | X | X
General parameter: Delay timer expired | 54272 | 154273 | Capability curve export |  |  | X | X
General parameter: Delay timer expired | 54273 | 154274 | Capability curve export |  |  | X | X
General parameter: Delay timer expired | 54274 | 154275 | Capability curve export |  |  | X | X
General parameter: Delay timer expired | 54275 | 154276 | Capability curve export |  |  | X | X
General parameter: Delay timer expired | 54276 | 154277 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54277 | 154278 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54278 | 154279 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54279 | 154280 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54280 | 154281 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54281 | 154282 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54282 | 154283 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54283 | 154284 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54284 | 154285 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54285 | 154286 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54286 | 154287 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54287 | 154288 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54288 | 154289 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54289 | 154290 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54290 | 154291 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54291 | 154292 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54292 | 154293 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54293 | 154294 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54294 | 154295 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54295 | 154296 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54296 | 154297 | Q(P) curve |  |  | X | X
General parameter: Delay timer expired | 54297 | 154298 | Q(U) Q-shift curve |  |  | X | X
General parameter: Delay timer expired | 54298 | 154299 | Q(U) Q-shift curve |  |  | X | X
General parameter: Delay timer expired | 54299 | 154300 | Q(U) Q-shift curve |  |  | X | X
General parameter: Delay timer expired | 54300 | 154301 | Q(U) Q-shift curve |  |  | X | X
General parameter: Delay timer expired | 54301 | 154302 | Q(U) Q-shift curve |  |  | X | X
General parameter: Delay timer expired | 54302 | 154303 | Q(U) Q-shift curve |  |  | X | X
General parameter: Delay timer expired | 54303 | 154304 | Q(U) Q-shift curve |  |  | X | X
General parameter: Delay timer expired | 54304 | 154305 | Q(U) Q-shift curve |  |  | X | X
General parameter: Delay timer expired | 54305 | 154306 | Q(U) Q-shift curve |  |  | X | X
General parameter: Delay timer expired | 54306 | 154307 | Source |  |  | X | X
General parameter: Delay timer expired | 54307 | 154308 | Nominal |  |  | X | X

## Holding register (03;06;16)
Holding register (03;06;16)
Function group | Modbus address | Bit | PLC address | Controller function name | Data type | Output conversion | Input conversion | Unit | LC_GENSET_GB | LC_BUSTIE_BTB | LC_SINGLE_GENSET_GB | LC_SINGLE_GENSET_GB_MB | LC_SINGLE_GENSET_GB_NO_MAINS | LC_MAINS_MB | LC_MAINS_MB_TB
Function | 8000 |  | 408001 | Functions - Analogue input functions - Engine - Measurements - Coolant - Engine coolant water | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
Function | 8001 |  | 408002 | Functions - Analogue input functions - Engine - Measurements - Lube oil - Engine oil temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
Function | 8002 |  | 408003 | Functions - Analogue input functions - Engine - Measurements - Coolant - Engine coolant level | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Function | 8003 |  | 408004 | Functions - Analogue input functions - Engine - Measurements - Lube oil - Engine oil pressure | INT16 | X * 10 | X * 0.1 | bar | X |  | X | X | X
Function | 8004 |  | 408005 | Functions - Digital output functions - Auxiliary - Pump logic - Activate pump 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Function | 8005 |  | 408006 | Functions - Analogue input functions - Engine - Power derate - Temperature - Derate 1 temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
Function | 8006 |  | 408007 | Functions - Analogue input functions - Engine - Power derate - Temperature - Derate 2 temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
Function | 8007 |  | 408008 | Functions - Analogue input functions - Engine - Power derate - Temperature - Derate 3 temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
Function | 8008 |  | 408009 | Functions - Analogue input functions - Engine - Power derate - Percentage - Derate percentage | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
Function | 8009 |  | 408010 | Functions - Analogue input functions - Grid code - Frequency offset | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Function | 8010 |  | 408011 | Functions - Analogue input functions - Mains - External set points - Power set point | INT16 | X * 1 | X * 1 | % | X |  | X | X |  | X | X
Function | 8014 |  | 408015 | Functions - Analogue output functions - Hardware - Power supply - PSM3.2 4 - PSM3.2 4 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Function | 8015 |  | 408016 | Functions - Analogue output functions - Hardware - Power supply - PSM3.2 5 - PSM3.2 5 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Function | 8016 |  | 408017 | Functions - Analogue output functions - Hardware - Power supply - PSM3.2 6 - PSM3.2 6 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Function | 8017 |  | 408018 | Functions - Analogue output functions - Hardware - Power supply - PSM3.2 7 - PSM3.2 7 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Function | 8018 |  | 408019 | Functions - Analogue output functions - Hardware - Power supply - PSM3.2 8 - PSM3.2 8 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Function | 8019 |  | 408020 | Functions - Analogue output functions - Hardware - Power supply - PSM3.2 9 - PSM3.2 9 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Function | 8020 |  | 408021 | Functions - Analogue input functions - Engine - Measurements - Fuel - Engine fuel level | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Function | 8021 |  | 408022 | Functions - Analogue input functions - Engine - Measurements - Lube oil - Engine oil level | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
Function | 8022 |  | 408023 | Functions - Analogue input functions - Auxiliary - Pump logic - Custom analogue input 1 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Function | 8023 |  | 408024 | Functions - Analogue input functions - Auxiliary - Pump logic - Custom analogue input 2 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Function | 8024 |  | 408025 | Functions - Analogue input functions - Auxiliary - Pump logic - Custom analogue input 3 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Function | 8029 |  | 408030 | Functions - Analogue input functions - Grid code - var(Q) regulation - External control U-shift | INT16 | X * 1 | X * 1 |  |  |  | X | X
Function | 8030 |  | 408031 | Functions - Analogue input functions - Grid code - var(Q) regulation - External control Q-shift | INT16 | X * 1 | X * 1 |  |  |  | X | X
Function | 8031 |  | 408032 | Functions - Analogue input functions - Grid code - var(Q) regulation - External control fixed cos phi | INT16 | X * 1 | X * 1 |  |  |  | X | X
Function | 8032 |  | 408033 | Functions - Analogue input functions - Mains - Analogue - Connection point voltage measurement | INT16 | X * 1 | X * 1 | V |  |  | X | X
CustomLogic: Modbus analogue signal | 12000 |  | 412001 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 1 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12001 |  | 412002 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 2 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12002 |  | 412003 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 3 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12003 |  | 412004 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 4 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12004 |  | 412005 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 5 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12005 |  | 412006 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 6 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12006 |  | 412007 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 7 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12007 |  | 412008 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 8 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12008 |  | 412009 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 9 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12009 |  | 412010 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 10 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12010 |  | 412011 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 11 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12011 |  | 412012 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 12 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12012 |  | 412013 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 13 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12013 |  | 412014 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 14 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12014 |  | 412015 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 15 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12015 |  | 412016 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 16 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12016 |  | 412017 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 17 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12017 |  | 412018 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 18 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12018 |  | 412019 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 19 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
CustomLogic: Modbus analogue signal | 12019 |  | 412020 | Functions - Analogue output functions - Local - CustomLogic - Signals - Signal 20 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12100 |  | 412101 | Parameters - Custom parameters - Custom parameter 0 - Integer 0 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12102 |  | 412103 | Parameters - Custom parameters - Custom parameter 1 - Integer 1 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12104 |  | 412105 | Parameters - Custom parameters - Custom parameter 2 - Integer 2 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12106 |  | 412107 | Parameters - Custom parameters - Custom parameter 3 - Integer 3 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12108 |  | 412109 | Parameters - Custom parameters - Custom parameter 4 - Integer 4 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12110 |  | 412111 | Parameters - Custom parameters - Custom parameter 5 - Integer 5 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12112 |  | 412113 | Parameters - Custom parameters - Custom parameter 6 - Integer 6 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12114 |  | 412115 | Parameters - Custom parameters - Custom parameter 7 - Integer 7 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12116 |  | 412117 | Parameters - Custom parameters - Custom parameter 8 - Integer 8 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12118 |  | 412119 | Parameters - Custom parameters - Custom parameter 9 - Integer 9 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12120 |  | 412121 | Parameters - Custom parameters - Custom parameter 10 - Integer 10 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12122 |  | 412123 | Parameters - Custom parameters - Custom parameter 11 - Integer 11 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12124 |  | 412125 | Parameters - Custom parameters - Custom parameter 12 - Integer 12 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12126 |  | 412127 | Parameters - Custom parameters - Custom parameter 13 - Integer 13 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12128 |  | 412129 | Parameters - Custom parameters - Custom parameter 14 - Integer 14 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12130 |  | 412131 | Parameters - Custom parameters - Custom parameter 15 - Integer 15 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12132 |  | 412133 | Parameters - Custom parameters - Custom parameter 16 - Integer 16 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12134 |  | 412135 | Parameters - Custom parameters - Custom parameter 17 - Integer 17 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12136 |  | 412137 | Parameters - Custom parameters - Custom parameter 18 - Integer 18 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12138 |  | 412139 | Parameters - Custom parameters - Custom parameter 19 - Integer 19 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12140 |  | 412141 | Parameters - Custom parameters - Custom parameter 20 - Integer 20 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12142 |  | 412143 | Parameters - Custom parameters - Custom parameter 21 - Integer 21 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12144 |  | 412145 | Parameters - Custom parameters - Custom parameter 22 - Integer 22 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12146 |  | 412147 | Parameters - Custom parameters - Custom parameter 23 - Integer 23 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12148 |  | 412149 | Parameters - Custom parameters - Custom parameter 24 - Integer 24 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12150 |  | 412151 | Parameters - Custom parameters - Custom parameter 25 - Integer 25 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12152 |  | 412153 | Parameters - Custom parameters - Custom parameter 26 - Integer 26 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12154 |  | 412155 | Parameters - Custom parameters - Custom parameter 27 - Integer 27 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12156 |  | 412157 | Parameters - Custom parameters - Custom parameter 28 - Integer 28 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12158 |  | 412159 | Parameters - Custom parameters - Custom parameter 29 - Integer 29 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12160 |  | 412161 | Parameters - Custom parameters - Custom parameter 30 - Integer 30 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12162 |  | 412163 | Parameters - Custom parameters - Custom parameter 31 - Integer 31 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12164 |  | 412165 | Parameters - Custom parameters - Custom parameter 32 - Integer 32 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12166 |  | 412167 | Parameters - Custom parameters - Custom parameter 33 - Integer 33 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12168 |  | 412169 | Parameters - Custom parameters - Custom parameter 34 - Integer 34 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12170 |  | 412171 | Parameters - Custom parameters - Custom parameter 35 - Integer 35 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12172 |  | 412173 | Parameters - Custom parameters - Custom parameter 36 - Integer 36 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12174 |  | 412175 | Parameters - Custom parameters - Custom parameter 37 - Integer 37 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12176 |  | 412177 | Parameters - Custom parameters - Custom parameter 38 - Integer 38 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12178 |  | 412179 | Parameters - Custom parameters - Custom parameter 39 - Integer 39 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12180 |  | 412181 | Parameters - Custom parameters - Custom parameter 40 - Integer 40 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12182 |  | 412183 | Parameters - Custom parameters - Custom parameter 41 - Integer 41 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12184 |  | 412185 | Parameters - Custom parameters - Custom parameter 42 - Integer 42 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12186 |  | 412187 | Parameters - Custom parameters - Custom parameter 43 - Integer 43 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12188 |  | 412189 | Parameters - Custom parameters - Custom parameter 44 - Integer 44 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12190 |  | 412191 | Parameters - Custom parameters - Custom parameter 45 - Integer 45 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12192 |  | 412193 | Parameters - Custom parameters - Custom parameter 46 - Integer 46 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12194 |  | 412195 | Parameters - Custom parameters - Custom parameter 47 - Integer 47 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12196 |  | 412197 | Parameters - Custom parameters - Custom parameter 48 - Integer 48 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Integer | 12198 |  | 412199 | Parameters - Custom parameters - Custom parameter 49 - Integer 49 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12300 |  | 412301 | Parameters - Custom parameters - Custom parameter 0 - Float 0 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12302 |  | 412303 | Parameters - Custom parameters - Custom parameter 1 - Float 1 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12304 |  | 412305 | Parameters - Custom parameters - Custom parameter 2 - Float 2 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12306 |  | 412307 | Parameters - Custom parameters - Custom parameter 3 - Float 3 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12308 |  | 412309 | Parameters - Custom parameters - Custom parameter 4 - Float 4 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12310 |  | 412311 | Parameters - Custom parameters - Custom parameter 5 - Float 5 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12312 |  | 412313 | Parameters - Custom parameters - Custom parameter 6 - Float 6 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12314 |  | 412315 | Parameters - Custom parameters - Custom parameter 7 - Float 7 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12316 |  | 412317 | Parameters - Custom parameters - Custom parameter 8 - Float 8 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12318 |  | 412319 | Parameters - Custom parameters - Custom parameter 9 - Float 9 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12320 |  | 412321 | Parameters - Custom parameters - Custom parameter 10 - Float 10 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12322 |  | 412323 | Parameters - Custom parameters - Custom parameter 11 - Float 11 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12324 |  | 412325 | Parameters - Custom parameters - Custom parameter 12 - Float 12 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12326 |  | 412327 | Parameters - Custom parameters - Custom parameter 13 - Float 13 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12328 |  | 412329 | Parameters - Custom parameters - Custom parameter 14 - Float 14 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12330 |  | 412331 | Parameters - Custom parameters - Custom parameter 15 - Float 15 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12332 |  | 412333 | Parameters - Custom parameters - Custom parameter 16 - Float 16 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12334 |  | 412335 | Parameters - Custom parameters - Custom parameter 17 - Float 17 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12336 |  | 412337 | Parameters - Custom parameters - Custom parameter 18 - Float 18 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12338 |  | 412339 | Parameters - Custom parameters - Custom parameter 19 - Float 19 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12340 |  | 412341 | Parameters - Custom parameters - Custom parameter 20 - Float 20 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12342 |  | 412343 | Parameters - Custom parameters - Custom parameter 21 - Float 21 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12344 |  | 412345 | Parameters - Custom parameters - Custom parameter 22 - Float 22 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12346 |  | 412347 | Parameters - Custom parameters - Custom parameter 23 - Float 23 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12348 |  | 412349 | Parameters - Custom parameters - Custom parameter 24 - Float 24 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12350 |  | 412351 | Parameters - Custom parameters - Custom parameter 25 - Float 25 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12352 |  | 412353 | Parameters - Custom parameters - Custom parameter 26 - Float 26 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12354 |  | 412355 | Parameters - Custom parameters - Custom parameter 27 - Float 27 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12356 |  | 412357 | Parameters - Custom parameters - Custom parameter 28 - Float 28 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12358 |  | 412359 | Parameters - Custom parameters - Custom parameter 29 - Float 29 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12360 |  | 412361 | Parameters - Custom parameters - Custom parameter 30 - Float 30 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12362 |  | 412363 | Parameters - Custom parameters - Custom parameter 31 - Float 31 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12364 |  | 412365 | Parameters - Custom parameters - Custom parameter 32 - Float 32 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12366 |  | 412367 | Parameters - Custom parameters - Custom parameter 33 - Float 33 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12368 |  | 412369 | Parameters - Custom parameters - Custom parameter 34 - Float 34 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12370 |  | 412371 | Parameters - Custom parameters - Custom parameter 35 - Float 35 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12372 |  | 412373 | Parameters - Custom parameters - Custom parameter 36 - Float 36 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12374 |  | 412375 | Parameters - Custom parameters - Custom parameter 37 - Float 37 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12376 |  | 412377 | Parameters - Custom parameters - Custom parameter 38 - Float 38 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12378 |  | 412379 | Parameters - Custom parameters - Custom parameter 39 - Float 39 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12380 |  | 412381 | Parameters - Custom parameters - Custom parameter 40 - Float 40 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12382 |  | 412383 | Parameters - Custom parameters - Custom parameter 41 - Float 41 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12384 |  | 412385 | Parameters - Custom parameters - Custom parameter 42 - Float 42 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12386 |  | 412387 | Parameters - Custom parameters - Custom parameter 43 - Float 43 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12388 |  | 412389 | Parameters - Custom parameters - Custom parameter 44 - Float 44 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12390 |  | 412391 | Parameters - Custom parameters - Custom parameter 45 - Float 45 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12392 |  | 412393 | Parameters - Custom parameters - Custom parameter 46 - Float 46 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12394 |  | 412395 | Parameters - Custom parameters - Custom parameter 47 - Float 47 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12396 |  | 412397 | Parameters - Custom parameters - Custom parameter 48 - Float 48 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom parameter: Float | 12398 |  | 412399 | Parameters - Custom parameters - Custom parameter 49 - Float 49 | FLOAT | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12400 |  | 412401 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12401 |  | 412402 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12402 |  | 412403 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12403 |  | 412404 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12404 |  | 412405 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12405 |  | 412406 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12406 |  | 412407 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12407 |  | 412408 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12408 |  | 412409 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12409 |  | 412410 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12410 |  | 412411 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12411 |  | 412412 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12412 |  | 412413 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12413 |  | 412414 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12414 |  | 412415 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12415 |  | 412416 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12416 |  | 412417 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12417 |  | 412418 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12418 |  | 412419 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue input | 12419 |  | 412420 | Functions - Analogue input functions - Local - CustomLogic - Inputs - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Breaker priority: Write values | 14000 |  | 414001 | Activate priorities | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14001 |  | 414002 | Priority of breaker 1 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14002 |  | 414003 | Priority of breaker 2 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14003 |  | 414004 | Priority of breaker 3 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14004 |  | 414005 | Priority of breaker 4 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14005 |  | 414006 | Priority of breaker 5 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14006 |  | 414007 | Priority of breaker 6 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14007 |  | 414008 | Priority of breaker 7 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14008 |  | 414009 | Priority of breaker 8 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14009 |  | 414010 | Priority of breaker 9 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14010 |  | 414011 | Priority of breaker 10 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14011 |  | 414012 | Priority of breaker 11 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14012 |  | 414013 | Priority of breaker 12 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14013 |  | 414014 | Priority of breaker 13 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14014 |  | 414015 | Priority of breaker 14 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14015 |  | 414016 | Priority of breaker 15 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14016 |  | 414017 | Priority of breaker 16 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14017 |  | 414018 | Priority of breaker 17 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14018 |  | 414019 | Priority of breaker 18 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14019 |  | 414020 | Priority of breaker 19 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14020 |  | 414021 | Priority of breaker 20 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14021 |  | 414022 | Priority of breaker 21 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14022 |  | 414023 | Priority of breaker 22 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14023 |  | 414024 | Priority of breaker 23 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14024 |  | 414025 | Priority of breaker 24 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14025 |  | 414026 | Priority of breaker 25 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14026 |  | 414027 | Priority of breaker 26 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14027 |  | 414028 | Priority of breaker 27 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14028 |  | 414029 | Priority of breaker 28 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14029 |  | 414030 | Priority of breaker 29 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14030 |  | 414031 | Priority of breaker 30 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14031 |  | 414032 | Priority of breaker 31 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Buffered value | 14032 |  | 414033 | Priority of breaker 32 | INT16 | X * 1 | X * 1 |  | X
Codesys analogue inputs | 16000 |  | 416001 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16001 |  | 416002 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16002 |  | 416003 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16003 |  | 416004 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16004 |  | 416005 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16005 |  | 416006 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16006 |  | 416007 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16007 |  | 416008 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16008 |  | 416009 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16009 |  | 416010 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16010 |  | 416011 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16011 |  | 416012 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16012 |  | 416013 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16013 |  | 416014 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16014 |  | 416015 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16015 |  | 416016 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16016 |  | 416017 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16017 |  | 416018 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16018 |  | 416019 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16019 |  | 416020 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16020 |  | 416021 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16021 |  | 416022 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16022 |  | 416023 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16023 |  | 416024 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16024 |  | 416025 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16025 |  | 416026 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16026 |  | 416027 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16027 |  | 416028 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16028 |  | 416029 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16029 |  | 416030 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16030 |  | 416031 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16031 |  | 416032 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16032 |  | 416033 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16033 |  | 416034 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16034 |  | 416035 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16035 |  | 416036 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16036 |  | 416037 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16037 |  | 416038 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16038 |  | 416039 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16039 |  | 416040 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16040 |  | 416041 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16041 |  | 416042 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16042 |  | 416043 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16043 |  | 416044 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16044 |  | 416045 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16045 |  | 416046 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16046 |  | 416047 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16047 |  | 416048 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16048 |  | 416049 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16049 |  | 416050 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16050 |  | 416051 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16051 |  | 416052 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16052 |  | 416053 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16053 |  | 416054 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16054 |  | 416055 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16055 |  | 416056 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16056 |  | 416057 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16057 |  | 416058 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16058 |  | 416059 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16059 |  | 416060 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16060 |  | 416061 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16061 |  | 416062 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16062 |  | 416063 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16063 |  | 416064 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16064 |  | 416065 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16065 |  | 416066 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16066 |  | 416067 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16067 |  | 416068 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16068 |  | 416069 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16069 |  | 416070 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16070 |  | 416071 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16071 |  | 416072 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16072 |  | 416073 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16073 |  | 416074 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16074 |  | 416075 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16075 |  | 416076 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16076 |  | 416077 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16077 |  | 416078 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16078 |  | 416079 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16079 |  | 416080 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16080 |  | 416081 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16081 |  | 416082 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16082 |  | 416083 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16083 |  | 416084 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16084 |  | 416085 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16085 |  | 416086 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16086 |  | 416087 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16087 |  | 416088 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16088 |  | 416089 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16089 |  | 416090 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16090 |  | 416091 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16091 |  | 416092 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16092 |  | 416093 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16093 |  | 416094 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16094 |  | 416095 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16095 |  | 416096 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16096 |  | 416097 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16097 |  | 416098 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16098 |  | 416099 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue inputs | 16099 |  | 416100 | Functions - Analogue input functions - Local - CODESYS - Custom analogue input | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18000 |  | 418001 | Counters - Engine - Start attempts - Total | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Counter | 18006 |  | 418007 | Counters - Engine - Operation time - Total running hours | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18008 |  | 418009 | Counters - Engine - Operation time - Total running minutes | INT32 | X * 1 | X * 1 | min | X |  | X | X | X
Counter | 18010 |  | 418011 | Counters - Engine - Operation time - Running hours since reset 1 | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18012 |  | 418013 | Counters - Engine - Operation time - Running minutes since reset 1 | INT32 | X * 1 | X * 1 | min | X |  | X | X | X
Counter | 18014 |  | 418015 | Counters - Engine - Operation time - Running hours since reset 2 | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18016 |  | 418017 | Counters - Engine - Operation time - Running minutes since reset 2 | INT32 | X * 1 | X * 1 | min | X |  | X | X | X
Counter | 18018 |  | 418019 | Counters - Engine - Operation time - Running hours since reset 3 | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18020 |  | 418021 | Counters - Engine - Operation time - Running minutes since reset 3 | INT32 | X * 1 | X * 1 | min | X |  | X | X | X
Counter | 18022 |  | 418023 | Counters - Engine - Operation time - Running hours since reset 4 | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18024 |  | 418025 | Counters - Engine - Operation time - Running minutes since reset 4 | INT32 | X * 1 | X * 1 | min | X |  | X | X | X
Counter | 18050 |  | 418051 | Counters - Breakers - Generator breaker - Close operations | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Counter | 18050 |  | 418051 | Counters - Breakers - Bus tie breaker - Close operations | INT32 | X * 1 | X * 1 |  |  | X
Counter | 18050 |  | 418051 | Counters - Breakers - Mains breaker - Close operations | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Counter | 18052 |  | 418053 | Counters - Breakers - Generator breaker - Trips | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Counter | 18052 |  | 418053 | Counters - Breakers - Bus tie breaker - Trips | INT32 | X * 1 | X * 1 |  |  | X
Counter | 18052 |  | 418053 | Counters - Breakers - Mains breaker - Trips | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Counter | 18054 |  | 418055 | Counters - Breakers - Generator breaker - Close operations since reset | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Counter | 18054 |  | 418055 | Counters - Breakers - Bus tie breaker - Close operations since reset | INT32 | X * 1 | X * 1 |  |  | X
Counter | 18054 |  | 418055 | Counters - Breakers - Mains breaker - Close operations since reset | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Counter | 18056 |  | 418057 | Counters - Breakers - Generator breaker - Failed operations | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Counter | 18056 |  | 418057 | Counters - Breakers - Bus tie breaker - Failed operations | INT32 | X * 1 | X * 1 |  |  | X
Counter | 18056 |  | 418057 | Counters - Breakers - Mains breaker - Failed operations | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Counter | 18058 |  | 418059 | Counters - Breakers - Mains breaker - Close operations | INT32 | X * 1 | X * 1 |  |  |  |  | X
Counter | 18058 |  | 418059 | Counters - Breakers - Tie breaker - Close operations | INT32 | X * 1 | X * 1 | [7 empty] | X
Counter | 18060 |  | 418061 | Counters - Breakers - Mains breaker - Trips | INT32 | X * 1 | X * 1 |  |  |  |  | X
Counter | 18060 |  | 418061 | Counters - Breakers - Tie breaker - Trips | INT32 | X * 1 | X * 1 | [7 empty] | X
Counter | 18062 |  | 418063 | Counters - Breakers - Mains breaker - Close operations since reset | INT32 | X * 1 | X * 1 |  |  |  |  | X
Counter | 18062 |  | 418063 | Counters - Breakers - Tie breaker - Close operations since reset | INT32 | X * 1 | X * 1 | [7 empty] | X
Counter | 18064 |  | 418065 | Counters - Breakers - Mains breaker - Failed operations | INT32 | X * 1 | X * 1 |  |  |  |  | X
Counter | 18064 |  | 418065 | Counters - Breakers - Tie breaker - Failed operations | INT32 | X * 1 | X * 1 | [7 empty] | X
Counter | 18066 |  | 418067 | Counters - Generator - Production counters - Active energy export | INT32 | X * 1 | X * 1 | kWh | X |  | X | X | X
Counter | 18066 |  | 418067 | Counters - Busbar A - Production counters - Active energy export | INT32 | X * 1 | X * 1 | kWh |  | X
Counter | 18066 |  | 418067 | Counters - Mains - Production counters - Active energy export | INT32 | X * 1 | X * 1 | kWh | [5 empty] | X | X
Counter | 18068 |  | 418069 | Counters - Generator - Production counters - Reactive energy export | INT32 | X * 1 | X * 1 | kvarh | X |  | X | X | X
Counter | 18068 |  | 418069 | Counters - Busbar A - Production counters - Reactive energy export | INT32 | X * 1 | X * 1 | kvarh |  | X
Counter | 18068 |  | 418069 | Counters - Mains - Production counters - Reactive energy export | INT32 | X * 1 | X * 1 | kvarh | [5 empty] | X | X
Counter | 18070 |  | 418071 | Counters - Busbar A - Production counters - Active energy import | INT32 | X * 1 | X * 1 | kWh |  | X
Counter | 18070 |  | 418071 | Counters - Mains - Production counters - Active energy import | INT32 | X * 1 | X * 1 | kWh | [5 empty] | X | X
Counter | 18072 |  | 418073 | Counters - Busbar A - Production counters - Reactive energy import | INT32 | X * 1 | X * 1 | kvarh |  | X
Counter | 18072 |  | 418073 | Counters - Mains - Production counters - Reactive energy import | INT32 | X * 1 | X * 1 | kvarh | [5 empty] | X | X
Counter | 18074 |  | 418075 | Counters - Busbar A - Production counters - Active energy difference | INT32 | X * 1 | X * 1 | kWh |  | X
Counter | 18074 |  | 418075 | Counters - Mains - Production counters - Active energy difference | INT32 | X * 1 | X * 1 | kWh | [5 empty] | X | X
Counter | 18076 |  | 418077 | Counters - Busbar A - Production counters - Reactive energy difference | INT32 | X * 1 | X * 1 | kvarh |  | X
Counter | 18076 |  | 418077 | Counters - Mains - Production counters - Reactive energy difference | INT32 | X * 1 | X * 1 | kvarh | [5 empty] | X | X
Counter | 18086 |  | 418087 | Counters - Custom counters - Custom counter 0 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18088 |  | 418089 | Counters - Custom counters - Custom counter 1 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18090 |  | 418091 | Counters - Custom counters - Custom counter 2 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18092 |  | 418093 | Counters - Custom counters - Custom counter 3 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18094 |  | 418095 | Counters - Custom counters - Custom counter 4 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18096 |  | 418097 | Counters - Custom counters - Custom counter 5 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18098 |  | 418099 | Counters - Custom counters - Custom counter 6 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18100 |  | 418101 | Counters - Custom counters - Custom counter 7 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18102 |  | 418103 | Counters - Custom counters - Custom counter 8 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18104 |  | 418105 | Counters - Custom counters - Custom counter 9 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18106 |  | 418107 | Counters - Custom counters - Custom counter 10 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18108 |  | 418109 | Counters - Custom counters - Custom counter 11 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18110 |  | 418111 | Counters - Custom counters - Custom counter 12 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18112 |  | 418113 | Counters - Custom counters - Custom counter 13 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18114 |  | 418115 | Counters - Custom counters - Custom counter 14 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18116 |  | 418117 | Counters - Custom counters - Custom counter 15 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18118 |  | 418119 | Counters - Custom counters - Custom counter 16 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18120 |  | 418121 | Counters - Custom counters - Custom counter 17 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18122 |  | 418123 | Counters - Custom counters - Custom counter 18 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18124 |  | 418125 | Counters - Custom counters - Custom counter 19 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18126 |  | 418127 | Counters - Custom counters - Custom counter 20 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18128 |  | 418129 | Counters - Custom counters - Custom counter 21 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18130 |  | 418131 | Counters - Custom counters - Custom counter 22 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18132 |  | 418133 | Counters - Custom counters - Custom counter 23 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18134 |  | 418135 | Counters - Custom counters - Custom counter 24 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18136 |  | 418137 | Counters - Custom counters - Custom counter 25 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18138 |  | 418139 | Counters - Custom counters - Custom counter 26 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18140 |  | 418141 | Counters - Custom counters - Custom counter 27 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18142 |  | 418143 | Counters - Custom counters - Custom counter 28 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18144 |  | 418145 | Counters - Custom counters - Custom counter 29 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18146 |  | 418147 | Counters - Custom counters - Custom counter 30 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18148 |  | 418149 | Counters - Custom counters - Custom counter 31 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18150 |  | 418151 | Counters - Custom counters - Custom counter 32 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18152 |  | 418153 | Counters - Custom counters - Custom counter 33 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18154 |  | 418155 | Counters - Custom counters - Custom counter 34 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18156 |  | 418157 | Counters - Custom counters - Custom counter 35 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18158 |  | 418159 | Counters - Custom counters - Custom counter 36 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18160 |  | 418161 | Counters - Custom counters - Custom counter 37 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18162 |  | 418163 | Counters - Custom counters - Custom counter 38 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18164 |  | 418165 | Counters - Custom counters - Custom counter 39 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18166 |  | 418167 | Counters - Custom counters - Custom counter 40 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18168 |  | 418169 | Counters - Custom counters - Custom counter 41 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18170 |  | 418171 | Counters - Custom counters - Custom counter 42 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18172 |  | 418173 | Counters - Custom counters - Custom counter 43 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18174 |  | 418175 | Counters - Custom counters - Custom counter 44 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18176 |  | 418177 | Counters - Custom counters - Custom counter 45 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18178 |  | 418179 | Counters - Custom counters - Custom counter 46 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18180 |  | 418181 | Counters - Custom counters - Custom counter 47 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18182 |  | 418183 | Counters - Custom counters - Custom counter 48 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18184 |  | 418185 | Counters - Custom counters - Custom counter 49 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18186 |  | 418187 | Counters - Custom counters - Custom counter 50 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18188 |  | 418189 | Counters - Custom counters - Custom counter 51 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18190 |  | 418191 | Counters - Custom counters - Custom counter 52 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18192 |  | 418193 | Counters - Custom counters - Custom counter 53 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18194 |  | 418195 | Counters - Custom counters - Custom counter 54 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18196 |  | 418197 | Counters - Custom counters - Custom counter 55 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18198 |  | 418199 | Counters - Custom counters - Custom counter 56 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18200 |  | 418201 | Counters - Custom counters - Custom counter 57 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18202 |  | 418203 | Counters - Custom counters - Custom counter 58 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18204 |  | 418205 | Counters - Custom counters - Custom counter 59 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18206 |  | 418207 | Counters - Custom counters - Custom counter 60 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18208 |  | 418209 | Counters - Custom counters - Custom counter 61 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18210 |  | 418211 | Counters - Custom counters - Custom counter 62 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18212 |  | 418213 | Counters - Custom counters - Custom counter 63 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18214 |  | 418215 | Counters - Custom counters - Custom counter 64 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18216 |  | 418217 | Counters - Custom counters - Custom counter 65 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18218 |  | 418219 | Counters - Custom counters - Custom counter 66 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18220 |  | 418221 | Counters - Custom counters - Custom counter 67 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18222 |  | 418223 | Counters - Custom counters - Custom counter 68 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18224 |  | 418225 | Counters - Custom counters - Custom counter 69 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18226 |  | 418227 | Counters - Custom counters - Custom counter 70 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18228 |  | 418229 | Counters - Custom counters - Custom counter 71 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18230 |  | 418231 | Counters - Custom counters - Custom counter 72 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18232 |  | 418233 | Counters - Custom counters - Custom counter 73 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18234 |  | 418235 | Counters - Custom counters - Custom counter 74 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18236 |  | 418237 | Counters - Custom counters - Custom counter 75 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18238 |  | 418239 | Counters - Custom counters - Custom counter 76 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18240 |  | 418241 | Counters - Custom counters - Custom counter 77 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18242 |  | 418243 | Counters - Custom counters - Custom counter 78 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18244 |  | 418245 | Counters - Custom counters - Custom counter 79 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18246 |  | 418247 | Counters - Custom counters - Custom counter 80 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18248 |  | 418249 | Counters - Custom counters - Custom counter 81 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18250 |  | 418251 | Counters - Custom counters - Custom counter 82 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18252 |  | 418253 | Counters - Custom counters - Custom counter 83 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18254 |  | 418255 | Counters - Custom counters - Custom counter 84 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18256 |  | 418257 | Counters - Custom counters - Custom counter 85 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18258 |  | 418259 | Counters - Custom counters - Custom counter 86 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18260 |  | 418261 | Counters - Custom counters - Custom counter 87 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18262 |  | 418263 | Counters - Custom counters - Custom counter 88 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18264 |  | 418265 | Counters - Custom counters - Custom counter 89 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18266 |  | 418267 | Counters - Custom counters - Custom counter 90 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18268 |  | 418269 | Counters - Custom counters - Custom counter 91 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18270 |  | 418271 | Counters - Custom counters - Custom counter 92 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18272 |  | 418273 | Counters - Custom counters - Custom counter 93 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18274 |  | 418275 | Counters - Custom counters - Custom counter 94 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18276 |  | 418277 | Counters - Custom counters - Custom counter 95 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18278 |  | 418279 | Counters - Custom counters - Custom counter 96 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18280 |  | 418281 | Counters - Custom counters - Custom counter 97 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18282 |  | 418283 | Counters - Custom counters - Custom counter 98 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18284 |  | 418285 | Counters - Custom counters - Custom counter 99 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18286 |  | 418287 | Counters - Engine - Operation time - Running hours load profiled | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18288 |  | 418289 | Counters - Engine - Operation time - Running days since reset 1 | INT32 | X * 1 | X * 1 | d | X |  | X | X | X
Counter | 18290 |  | 418291 | Counters - Engine - Operation time - Running days since reset 2 | INT32 | X * 1 | X * 1 | d | X |  | X | X | X
Counter | 18292 |  | 418293 | Counters - Engine - Operation time - Running days since reset 3 | INT32 | X * 1 | X * 1 | d | X |  | X | X | X
Counter | 18294 |  | 418295 | Counters - Engine - Operation time - Running days since reset 4 | INT32 | X * 1 | X * 1 | d | X |  | X | X | X
Counter | 18296 |  | 418297 | Counters - Engine - Operation time - Running hours relative | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18298 |  | 418299 | Counters - Engine - Operation time - Automatic priority swap hours | INT32 | X * 1 | X * 1 | h | X | X | X | X | X | X | X
Counter | 18300 |  | 418301 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Active energy export (transducer 1) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18302 |  | 418303 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy export (transducer 1) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18304 |  | 418305 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Active energy import (transducer 1) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18306 |  | 418307 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy import (transducer 1) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18308 |  | 418309 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Active energy difference (transducer 1) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18310 |  | 418311 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy difference (transducer 1) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18312 |  | 418313 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Active energy export (transducer 2) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18314 |  | 418315 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy export (transducer 2) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18316 |  | 418317 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Active energy import (transducer 2) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18318 |  | 418319 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy import (transducer 2) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18320 |  | 418321 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Active energy difference (transducer 2) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18322 |  | 418323 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy difference (transducer 2) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18324 |  | 418325 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Active energy export (transducer 3) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18326 |  | 418327 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy export (transducer 3) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18328 |  | 418329 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Active energy import (transducer 3) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18330 |  | 418331 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy import (transducer 3) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18332 |  | 418333 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Active energy difference (transducer 3) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18334 |  | 418335 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy difference (transducer 3) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18336 |  | 418337 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Active energy export (transducer 4) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18338 |  | 418339 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy export (transducer 4) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18340 |  | 418341 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Active energy import (transducer 4) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18342 |  | 418343 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy import (transducer 4) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18344 |  | 418345 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Active energy difference (transducer 4) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18346 |  | 418347 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy difference (transducer 4) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Alarm parameter: Set point | 20005 |  | 420006 | Parameters - Engine - Start sequence - Crank failure - Configuration - Set point | INT16 | X * 10 | X * 0.1 | RPM | X |  | X | X | X
Alarm parameter: Set point | 20006 |  | 420007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20007 |  | 420008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20008 |  | 420009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20009 |  | 420010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20013 |  | 420014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | bar | X |  | X | X | X
Alarm parameter: Set point | 20014 |  | 420015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | bar | X |  | X | X | X
Alarm parameter: Set point | 20015 |  | 420016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm parameter: Set point | 20016 |  | 420017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm parameter: Set point | 20017 |  | 420018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm parameter: Set point | 20018 |  | 420019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm parameter: Set point | 20019 |  | 420020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm parameter: Set point | 20020 |  | 420021 | Parameters - Engine - Protections - Level - Coolant level 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20021 |  | 420022 | Parameters - Engine - Protections - Level - Coolant level 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20022 |  | 420023 | Parameters - Engine - Protections - Level - Coolant level 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20104 |  | 420105 | Parameters - Mains - Additional protections - Vector shift - Configuration - Set point | INT16 | X * 1 | X * 1 | ° |  |  | X | X
Alarm parameter: Set point | 20104 |  | 420105 | Parameters - Busbar - Additional protections - Vector shift - Configuration - Set point | INT16 | X * 1 | X * 1 | ° | X |  |  |  | X | X | X
Alarm parameter: Set point | 20104 |  | 420105 | Parameters - Busbar B - Additional protections - Vector shift - Configuration - Set point | INT16 | X * 1 | X * 1 | ° |  | X
Alarm parameter: Set point | 20108 |  | 420109 | Parameters - Generator - Additional protections - V< and Q< 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20108 |  | 420109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20108 |  | 420109 | Parameters - Mains - Additional protections - V< and Q< 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20109 |  | 420110 | Parameters - Generator - Additional protections - V< and Q< 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20109 |  | 420110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20109 |  | 420110 | Parameters - Mains - Additional protections - V< and Q< 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20110 |  | 420111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20110 |  | 420111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20110 |  | 420111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20111 |  | 420112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20111 |  | 420112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20111 |  | 420112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20117 |  | 420118 | Parameters - Generator - Current protections - High set differential current - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
Alarm parameter: Set point | 20128 |  | 420129 | Parameters - Custom alarm - Custom alarm 0 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20129 |  | 420130 | Parameters - Custom alarm - Custom alarm 1 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20130 |  | 420131 | Parameters - Custom alarm - Custom alarm 2 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20131 |  | 420132 | Parameters - Custom alarm - Custom alarm 3 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20132 |  | 420133 | Parameters - Custom alarm - Custom alarm 4 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20133 |  | 420134 | Parameters - Custom alarm - Custom alarm 5 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20134 |  | 420135 | Parameters - Custom alarm - Custom alarm 6 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20135 |  | 420136 | Parameters - Custom alarm - Custom alarm 7 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20136 |  | 420137 | Parameters - Custom alarm - Custom alarm 8 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20137 |  | 420138 | Parameters - Custom alarm - Custom alarm 9 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20138 |  | 420139 | Parameters - Custom alarm - Custom alarm 10 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20139 |  | 420140 | Parameters - Custom alarm - Custom alarm 11 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20140 |  | 420141 | Parameters - Custom alarm - Custom alarm 12 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20141 |  | 420142 | Parameters - Custom alarm - Custom alarm 13 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20142 |  | 420143 | Parameters - Custom alarm - Custom alarm 14 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20143 |  | 420144 | Parameters - Custom alarm - Custom alarm 15 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20144 |  | 420145 | Parameters - Custom alarm - Custom alarm 16 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20145 |  | 420146 | Parameters - Custom alarm - Custom alarm 17 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20146 |  | 420147 | Parameters - Custom alarm - Custom alarm 18 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20147 |  | 420148 | Parameters - Custom alarm - Custom alarm 19 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20148 |  | 420149 | Parameters - Custom alarm - Custom alarm 20 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20149 |  | 420150 | Parameters - Custom alarm - Custom alarm 21 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20150 |  | 420151 | Parameters - Custom alarm - Custom alarm 22 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20151 |  | 420152 | Parameters - Custom alarm - Custom alarm 23 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20152 |  | 420153 | Parameters - Custom alarm - Custom alarm 24 - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20153 |  | 420154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20154 |  | 420155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20181 |  | 420182 | Controller temperature too high - Set point | INT16 | X * 1 | X * 1 | °C | X | X | X | X | X | X | X
Alarm parameter: Set point | 20182 |  | 420183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20183 |  | 420184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20184 |  | 420185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20185 |  | 420186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20186 |  | 420187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20187 |  | 420188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20188 |  | 420189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20189 |  | 420190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20190 |  | 420191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20191 |  | 420192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20192 |  | 420193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20193 |  | 420194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20194 |  | 420195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20195 |  | 420196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20196 |  | 420197 | EIM3.1 4 supply voltage high - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20197 |  | 420198 | EIM3.1 4 supply voltage low or missing - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20198 |  | 420199 | EIM3.1 5 supply voltage high - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20199 |  | 420200 | EIM3.1 5 supply voltage low or missing - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20209 |  | 420210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20210 |  | 420211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20211 |  | 420212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20212 |  | 420213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20213 |  | 420214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20214 |  | 420215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20215 |  | 420216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20216 |  | 420217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20217 |  | 420218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20218 |  | 420219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20219 |  | 420220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20220 |  | 420221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20221 |  | 420222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20222 |  | 420223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20223 |  | 420224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20224 |  | 420225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20225 |  | 420226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20226 |  | 420227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Configuration - Set point | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm parameter: Set point | 20228 |  | 420229 | Parameters - System - Monitoring - Duplicate controller ID - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 20471 |  | 420472 | Parameters - Non-essential load trip - Trip 1 - Over-current - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm parameter: Set point | 20472 |  | 420473 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm parameter: Set point | 20473 |  | 420474 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm parameter: Set point | 20474 |  | 420475 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm parameter: Set point | 20475 |  | 420476 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm parameter: Set point | 20476 |  | 420477 | Parameters - Non-essential load trip - Trip 2 - Over-current - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm parameter: Set point | 20477 |  | 420478 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm parameter: Set point | 20478 |  | 420479 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm parameter: Set point | 20479 |  | 420480 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm parameter: Set point | 20480 |  | 420481 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm parameter: Set point | 20481 |  | 420482 | Parameters - Non-essential load trip - Trip 3 - Over-current - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm parameter: Set point | 20482 |  | 420483 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm parameter: Set point | 20483 |  | 420484 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm parameter: Set point | 20484 |  | 420485 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm parameter: Set point | 20485 |  | 420486 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Configuration - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm parameter: Set point | 20615 |  | 420616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20615 |  | 420616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20615 |  | 420616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20616 |  | 420617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20616 |  | 420617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20616 |  | 420617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20617 |  | 420618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20617 |  | 420618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20617 |  | 420618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20618 |  | 420619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20618 |  | 420619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20618 |  | 420619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20619 |  | 420620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20619 |  | 420620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20619 |  | 420620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20620 |  | 420621 | Parameters - Generator - Voltage protections - Voltage unbalance - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20620 |  | 420621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20620 |  | 420621 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20621 |  | 420622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20621 |  | 420622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20621 |  | 420622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20622 |  | 420623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20622 |  | 420623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20622 |  | 420623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20623 |  | 420624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20623 |  | 420624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20623 |  | 420624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20624 |  | 420625 | Parameters - Generator - Current protections - Over-current 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20624 |  | 420625 | Parameters - Busbar A - Current protections - Over-current 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20624 |  | 420625 | Parameters - Mains - Current protections - Over-current 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20625 |  | 420626 | Parameters - Generator - Current protections - Over-current 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20625 |  | 420626 | Parameters - Busbar A - Current protections - Over-current 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20625 |  | 420626 | Parameters - Mains - Current protections - Over-current 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20626 |  | 420627 | Parameters - Generator - Current protections - Over-current 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20626 |  | 420627 | Parameters - Busbar A - Current protections - Over-current 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20626 |  | 420627 | Parameters - Mains - Current protections - Over-current 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20627 |  | 420628 | Parameters - Generator - Current protections - Over-current 4 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20627 |  | 420628 | Parameters - Busbar A - Current protections - Over-current 4 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20627 |  | 420628 | Parameters - Mains - Current protections - Over-current 4 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20628 |  | 420629 | Parameters - Generator - Current protections - Fast over-current 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20628 |  | 420629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20628 |  | 420629 | Parameters - Mains - Current protections - Fast over-current 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20629 |  | 420630 | Parameters - Generator - Current protections - Fast over-current 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20629 |  | 420630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20629 |  | 420630 | Parameters - Mains - Current protections - Fast over-current 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20630 |  | 420631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20630 |  | 420631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20630 |  | 420631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20631 |  | 420632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20631 |  | 420632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20631 |  | 420632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20632 |  | 420633 | Parameters - Generator - Current protections - Directional over-current 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20632 |  | 420633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20632 |  | 420633 | Parameters - Mains - Current protections - Directional over-current 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20633 |  | 420634 | Parameters - Generator - Current protections - Directional over-current 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20633 |  | 420634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20633 |  | 420634 | Parameters - Mains - Current protections - Directional over-current 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20634 |  | 420635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20635 |  | 420636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20636 |  | 420637 | Parameters - Generator - Current protections - Negative sequence current - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20636 |  | 420637 | Parameters - Busbar A - Current protections - Negative sequence current - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20636 |  | 420637 | Parameters - Mains - Current protections - Negative sequence current - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20637 |  | 420638 | Parameters - Generator - Current protections - Zero sequence current - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20637 |  | 420638 | Parameters - Busbar A - Current protections - Zero sequence current - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20637 |  | 420638 | Parameters - Mains - Current protections - Zero sequence current - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20638 |  | 420639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20638 |  | 420639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20638 |  | 420639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20639 |  | 420640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20639 |  | 420640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20639 |  | 420640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20640 |  | 420641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20640 |  | 420641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20640 |  | 420641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20641 |  | 420642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20641 |  | 420642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20641 |  | 420642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20642 |  | 420643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20642 |  | 420643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20642 |  | 420643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20643 |  | 420644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20643 |  | 420644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20643 |  | 420644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20644 |  | 420645 | Parameters - Generator - Power protections - Overload 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20644 |  | 420645 | Parameters - Busbar A - Power protections - Power export 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20644 |  | 420645 | Parameters - Mains - Power protections - Overload 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20645 |  | 420646 | Parameters - Generator - Power protections - Overload 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20645 |  | 420646 | Parameters - Busbar A - Power protections - Power export 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20645 |  | 420646 | Parameters - Mains - Power protections - Overload 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20646 |  | 420647 | Parameters - Generator - Power protections - Overload 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20646 |  | 420647 | Parameters - Busbar A - Power protections - Power export 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20646 |  | 420647 | Parameters - Mains - Power protections - Overload 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20647 |  | 420648 | Parameters - Generator - Power protections - Overload 4 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20647 |  | 420648 | Parameters - Busbar A - Power protections - Power export 4 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20647 |  | 420648 | Parameters - Mains - Power protections - Overload 4 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20648 |  | 420649 | Parameters - Generator - Power protections - Overload 5 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20648 |  | 420649 | Parameters - Busbar A - Power protections - Power export 5 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20648 |  | 420649 | Parameters - Mains - Power protections - Overload 5 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20649 |  | 420650 | Parameters - Generator - Power protections - Reverse power 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20649 |  | 420650 | Parameters - Busbar A - Power protections - Power import 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20649 |  | 420650 | Parameters - Mains - Power protections - Reverse power 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20650 |  | 420651 | Parameters - Generator - Power protections - Reverse power 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20650 |  | 420651 | Parameters - Busbar A - Power protections - Power import 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20650 |  | 420651 | Parameters - Mains - Power protections - Reverse power 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20651 |  | 420652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20651 |  | 420652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20651 |  | 420652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20652 |  | 420653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20652 |  | 420653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20652 |  | 420653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20653 |  | 420654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20653 |  | 420654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20653 |  | 420654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20654 |  | 420655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Set point | 20654 |  | 420655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20654 |  | 420655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Set point | 20655 |  | 420656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20655 |  | 420656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20655 |  | 420656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20656 |  | 420657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20656 |  | 420657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20656 |  | 420657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20657 |  | 420658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20657 |  | 420658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20657 |  | 420658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20658 |  | 420659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20658 |  | 420659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20658 |  | 420659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20659 |  | 420660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20659 |  | 420660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20659 |  | 420660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20660 |  | 420661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20660 |  | 420661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20660 |  | 420661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20661 |  | 420662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20661 |  | 420662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20661 |  | 420662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20662 |  | 420663 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20662 |  | 420663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20662 |  | 420663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20663 |  | 420664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20663 |  | 420664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20663 |  | 420664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20664 |  | 420665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20664 |  | 420665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20664 |  | 420665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20665 |  | 420666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20665 |  | 420666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20665 |  | 420666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20666 |  | 420667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20666 |  | 420667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20666 |  | 420667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20667 |  | 420668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20667 |  | 420668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20667 |  | 420668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20668 |  | 420669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20668 |  | 420669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20668 |  | 420669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20669 |  | 420670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20669 |  | 420670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20669 |  | 420670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20670 |  | 420671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20670 |  | 420671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20670 |  | 420671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20671 |  | 420672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20671 |  | 420672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20671 |  | 420672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20672 |  | 420673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Set point | 20672 |  | 420673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Set point | 20672 |  | 420673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Configuration - Set point | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Set point | 20717 |  | 420718 | Parameters - Engine - Maintenance - Service timer - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Set point | 20718 |  | 420719 | Parameters - Engine - Maintenance - Service timer - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Set point | 20719 |  | 420720 | Parameters - Engine - Maintenance - Service timer - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Set point | 20720 |  | 420721 | Parameters - Engine - Maintenance - Service timer - Configuration - Set point | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Set point | 20854 |  | 420855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Configuration - Set point | INT16 | X * 1 | X * 1 | ° | X |  | X | X | X
Alarm parameter: Set point | 20854 |  | 420855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Configuration - Set point | INT16 | X * 1 | X * 1 | ° |  | X
Alarm parameter: Set point | 20854 |  | 420855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Set point | INT16 | X * 1 | X * 1 | ° | [5 empty] | X | X
Alarm parameter: Set point | 20855 |  | 420856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Set point | INT16 | X * 1 | X * 1 | ° |  |  |  | X
Alarm parameter: Set point | 20855 |  | 420856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Configuration - Set point | INT16 | X * 1 | X * 1 | ° | [6 empty] | X
Alarm parameter: Set point | 20857 |  | 420858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Configuration - Set point | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
Alarm parameter: Set point | 20858 |  | 420859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Configuration - Set point | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
Alarm parameter: Set point | 20859 |  | 420860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Configuration - Set point | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
Alarm parameter: Set point | 20860 |  | 420861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Configuration - Set point | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
Alarm parameter: Set point | 20878 |  | 420879 | Internal issue detected. A restart is required soon! - Set point | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Alarm parameter: Set point | 20880 |  | 420881 | Card issue detected - Set point | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21600 |  | 421601 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21601 |  | 421602 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21602 |  | 421603 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21603 |  | 421604 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21604 |  | 421605 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21605 |  | 421606 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21606 |  | 421607 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21607 |  | 421608 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21608 |  | 421609 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21609 |  | 421610 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21610 |  | 421611 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21611 |  | 421612 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21612 |  | 421613 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21613 |  | 421614 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21614 |  | 421615 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21615 |  | 421616 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21616 |  | 421617 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21617 |  | 421618 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21618 |  | 421619 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21619 |  | 421620 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21620 |  | 421621 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21621 |  | 421622 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21622 |  | 421623 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21623 |  | 421624 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21624 |  | 421625 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21625 |  | 421626 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21626 |  | 421627 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21627 |  | 421628 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21628 |  | 421629 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21629 |  | 421630 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21630 |  | 421631 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21631 |  | 421632 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21632 |  | 421633 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21633 |  | 421634 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21634 |  | 421635 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21635 |  | 421636 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21636 |  | 421637 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21637 |  | 421638 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21638 |  | 421639 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21639 |  | 421640 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21640 |  | 421641 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21641 |  | 421642 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21642 |  | 421643 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21643 |  | 421644 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21644 |  | 421645 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21645 |  | 421646 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21646 |  | 421647 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21647 |  | 421648 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21648 |  | 421649 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21649 |  | 421650 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21650 |  | 421651 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21651 |  | 421652 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21652 |  | 421653 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21653 |  | 421654 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21654 |  | 421655 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21655 |  | 421656 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21656 |  | 421657 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21657 |  | 421658 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21658 |  | 421659 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21659 |  | 421660 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21660 |  | 421661 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21661 |  | 421662 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21662 |  | 421663 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21663 |  | 421664 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21664 |  | 421665 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21665 |  | 421666 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21666 |  | 421667 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21667 |  | 421668 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21668 |  | 421669 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21669 |  | 421670 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21670 |  | 421671 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21671 |  | 421672 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21672 |  | 421673 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21673 |  | 421674 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21674 |  | 421675 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21675 |  | 421676 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21676 |  | 421677 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21677 |  | 421678 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21678 |  | 421679 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21679 |  | 421680 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21680 |  | 421681 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21681 |  | 421682 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21682 |  | 421683 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21683 |  | 421684 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21684 |  | 421685 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21685 |  | 421686 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21686 |  | 421687 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21687 |  | 421688 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21688 |  | 421689 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21689 |  | 421690 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21690 |  | 421691 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21691 |  | 421692 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21692 |  | 421693 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21693 |  | 421694 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21694 |  | 421695 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21695 |  | 421696 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21696 |  | 421697 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21697 |  | 421698 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21698 |  | 421699 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21699 |  | 421700 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21700 |  | 421701 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21701 |  | 421702 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21702 |  | 421703 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21703 |  | 421704 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21704 |  | 421705 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21705 |  | 421706 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21706 |  | 421707 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21707 |  | 421708 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21708 |  | 421709 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21709 |  | 421710 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21710 |  | 421711 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21711 |  | 421712 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21712 |  | 421713 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21713 |  | 421714 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21714 |  | 421715 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21715 |  | 421716 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21716 |  | 421717 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21717 |  | 421718 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21718 |  | 421719 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21719 |  | 421720 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21720 |  | 421721 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21721 |  | 421722 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21722 |  | 421723 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21723 |  | 421724 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21724 |  | 421725 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21725 |  | 421726 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21726 |  | 421727 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21727 |  | 421728 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21728 |  | 421729 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21729 |  | 421730 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21730 |  | 421731 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21731 |  | 421732 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21732 |  | 421733 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21733 |  | 421734 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21734 |  | 421735 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21735 |  | 421736 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21736 |  | 421737 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21737 |  | 421738 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21738 |  | 421739 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21739 |  | 421740 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21740 |  | 421741 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21741 |  | 421742 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21742 |  | 421743 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21743 |  | 421744 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21744 |  | 421745 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21745 |  | 421746 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21746 |  | 421747 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21747 |  | 421748 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21748 |  | 421749 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21749 |  | 421750 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21750 |  | 421751 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21751 |  | 421752 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21752 |  | 421753 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21753 |  | 421754 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21754 |  | 421755 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21755 |  | 421756 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21756 |  | 421757 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21757 |  | 421758 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21758 |  | 421759 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21759 |  | 421760 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21760 |  | 421761 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21761 |  | 421762 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21762 |  | 421763 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21763 |  | 421764 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21764 |  | 421765 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21765 |  | 421766 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21766 |  | 421767 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21767 |  | 421768 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21768 |  | 421769 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21769 |  | 421770 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21770 |  | 421771 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21771 |  | 421772 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21772 |  | 421773 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21773 |  | 421774 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21774 |  | 421775 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21775 |  | 421776 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21776 |  | 421777 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21777 |  | 421778 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21778 |  | 421779 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21779 |  | 421780 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21780 |  | 421781 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21781 |  | 421782 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21782 |  | 421783 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21783 |  | 421784 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21784 |  | 421785 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21785 |  | 421786 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21786 |  | 421787 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21787 |  | 421788 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21788 |  | 421789 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21789 |  | 421790 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21790 |  | 421791 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21791 |  | 421792 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21792 |  | 421793 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21793 |  | 421794 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21794 |  | 421795 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21795 |  | 421796 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21796 |  | 421797 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21797 |  | 421798 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21798 |  | 421799 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Set point | 21799 |  | 421800 | Analogue custom alarm - Set point | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22006 |  | 422007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22007 |  | 422008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22008 |  | 422009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22009 |  | 422010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22013 |  | 422014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | bar | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22014 |  | 422015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | bar | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22015 |  | 422016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22016 |  | 422017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22017 |  | 422018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22018 |  | 422019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22019 |  | 422020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22020 |  | 422021 | Parameters - Engine - Protections - Level - Coolant level 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22021 |  | 422022 | Parameters - Engine - Protections - Level - Coolant level 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22022 |  | 422023 | Parameters - Engine - Protections - Level - Coolant level 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22108 |  | 422109 | Parameters - Generator - Additional protections - V< and Q< 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22108 |  | 422109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22108 |  | 422109 | Parameters - Mains - Additional protections - V< and Q< 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22109 |  | 422110 | Parameters - Generator - Additional protections - V< and Q< 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22109 |  | 422110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22109 |  | 422110 | Parameters - Mains - Additional protections - V< and Q< 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22110 |  | 422111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22110 |  | 422111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22110 |  | 422111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22111 |  | 422112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22111 |  | 422112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22111 |  | 422112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22128 |  | 422129 | Parameters - Custom alarm - Custom alarm 0 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22129 |  | 422130 | Parameters - Custom alarm - Custom alarm 1 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22130 |  | 422131 | Parameters - Custom alarm - Custom alarm 2 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22131 |  | 422132 | Parameters - Custom alarm - Custom alarm 3 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22132 |  | 422133 | Parameters - Custom alarm - Custom alarm 4 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22133 |  | 422134 | Parameters - Custom alarm - Custom alarm 5 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22134 |  | 422135 | Parameters - Custom alarm - Custom alarm 6 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22135 |  | 422136 | Parameters - Custom alarm - Custom alarm 7 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22136 |  | 422137 | Parameters - Custom alarm - Custom alarm 8 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22137 |  | 422138 | Parameters - Custom alarm - Custom alarm 9 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22138 |  | 422139 | Parameters - Custom alarm - Custom alarm 10 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22139 |  | 422140 | Parameters - Custom alarm - Custom alarm 11 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22140 |  | 422141 | Parameters - Custom alarm - Custom alarm 12 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22141 |  | 422142 | Parameters - Custom alarm - Custom alarm 13 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22142 |  | 422143 | Parameters - Custom alarm - Custom alarm 14 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22143 |  | 422144 | Parameters - Custom alarm - Custom alarm 15 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22144 |  | 422145 | Parameters - Custom alarm - Custom alarm 16 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22145 |  | 422146 | Parameters - Custom alarm - Custom alarm 17 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22146 |  | 422147 | Parameters - Custom alarm - Custom alarm 18 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22147 |  | 422148 | Parameters - Custom alarm - Custom alarm 19 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22148 |  | 422149 | Parameters - Custom alarm - Custom alarm 20 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22149 |  | 422150 | Parameters - Custom alarm - Custom alarm 21 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22150 |  | 422151 | Parameters - Custom alarm - Custom alarm 22 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22151 |  | 422152 | Parameters - Custom alarm - Custom alarm 23 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22152 |  | 422153 | Parameters - Custom alarm - Custom alarm 24 - Configuration - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 22615 |  | 422616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22615 |  | 422616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22615 |  | 422616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22616 |  | 422617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22616 |  | 422617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22616 |  | 422617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22617 |  | 422618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22617 |  | 422618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22617 |  | 422618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22618 |  | 422619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22618 |  | 422619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22618 |  | 422619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22619 |  | 422620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22619 |  | 422620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22619 |  | 422620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22620 |  | 422621 | Parameters - Generator - Voltage protections - Voltage unbalance - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22620 |  | 422621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22620 |  | 422621 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22621 |  | 422622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22621 |  | 422622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22621 |  | 422622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22622 |  | 422623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22622 |  | 422623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22622 |  | 422623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22623 |  | 422624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22623 |  | 422624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22623 |  | 422624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22624 |  | 422625 | Parameters - Generator - Current protections - Over-current 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22624 |  | 422625 | Parameters - Busbar A - Current protections - Over-current 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22624 |  | 422625 | Parameters - Mains - Current protections - Over-current 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22625 |  | 422626 | Parameters - Generator - Current protections - Over-current 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22625 |  | 422626 | Parameters - Busbar A - Current protections - Over-current 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22625 |  | 422626 | Parameters - Mains - Current protections - Over-current 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22626 |  | 422627 | Parameters - Generator - Current protections - Over-current 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22626 |  | 422627 | Parameters - Busbar A - Current protections - Over-current 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22626 |  | 422627 | Parameters - Mains - Current protections - Over-current 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22627 |  | 422628 | Parameters - Generator - Current protections - Over-current 4 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22627 |  | 422628 | Parameters - Busbar A - Current protections - Over-current 4 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22627 |  | 422628 | Parameters - Mains - Current protections - Over-current 4 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22628 |  | 422629 | Parameters - Generator - Current protections - Fast over-current 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22628 |  | 422629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22628 |  | 422629 | Parameters - Mains - Current protections - Fast over-current 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22629 |  | 422630 | Parameters - Generator - Current protections - Fast over-current 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22629 |  | 422630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22629 |  | 422630 | Parameters - Mains - Current protections - Fast over-current 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22630 |  | 422631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22630 |  | 422631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22630 |  | 422631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22631 |  | 422632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22631 |  | 422632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22631 |  | 422632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22632 |  | 422633 | Parameters - Generator - Current protections - Directional over-current 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22632 |  | 422633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22632 |  | 422633 | Parameters - Mains - Current protections - Directional over-current 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22633 |  | 422634 | Parameters - Generator - Current protections - Directional over-current 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22633 |  | 422634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22633 |  | 422634 | Parameters - Mains - Current protections - Directional over-current 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22634 |  | 422635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22635 |  | 422636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22636 |  | 422637 | Parameters - Generator - Current protections - Negative sequence current - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22636 |  | 422637 | Parameters - Busbar A - Current protections - Negative sequence current - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22636 |  | 422637 | Parameters - Mains - Current protections - Negative sequence current - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22637 |  | 422638 | Parameters - Generator - Current protections - Zero sequence current - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22637 |  | 422638 | Parameters - Busbar A - Current protections - Zero sequence current - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22637 |  | 422638 | Parameters - Mains - Current protections - Zero sequence current - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22638 |  | 422639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22638 |  | 422639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22638 |  | 422639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22639 |  | 422640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22639 |  | 422640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22639 |  | 422640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22640 |  | 422641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22640 |  | 422641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22640 |  | 422641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22641 |  | 422642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22641 |  | 422642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22641 |  | 422642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22642 |  | 422643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22642 |  | 422643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22642 |  | 422643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22643 |  | 422644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22643 |  | 422644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22643 |  | 422644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22644 |  | 422645 | Parameters - Generator - Power protections - Overload 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22644 |  | 422645 | Parameters - Busbar A - Power protections - Power export 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22644 |  | 422645 | Parameters - Mains - Power protections - Overload 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22645 |  | 422646 | Parameters - Generator - Power protections - Overload 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22645 |  | 422646 | Parameters - Busbar A - Power protections - Power export 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22645 |  | 422646 | Parameters - Mains - Power protections - Overload 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22646 |  | 422647 | Parameters - Generator - Power protections - Overload 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22646 |  | 422647 | Parameters - Busbar A - Power protections - Power export 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22646 |  | 422647 | Parameters - Mains - Power protections - Overload 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22647 |  | 422648 | Parameters - Generator - Power protections - Overload 4 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22647 |  | 422648 | Parameters - Busbar A - Power protections - Power export 4 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22647 |  | 422648 | Parameters - Mains - Power protections - Overload 4 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22648 |  | 422649 | Parameters - Generator - Power protections - Overload 5 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22648 |  | 422649 | Parameters - Busbar A - Power protections - Power export 5 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22648 |  | 422649 | Parameters - Mains - Power protections - Overload 5 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22649 |  | 422650 | Parameters - Generator - Power protections - Reverse power 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22649 |  | 422650 | Parameters - Busbar A - Power protections - Power import 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22649 |  | 422650 | Parameters - Mains - Power protections - Reverse power 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22650 |  | 422651 | Parameters - Generator - Power protections - Reverse power 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22650 |  | 422651 | Parameters - Busbar A - Power protections - Power import 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22650 |  | 422651 | Parameters - Mains - Power protections - Reverse power 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22651 |  | 422652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22651 |  | 422652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22651 |  | 422652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22652 |  | 422653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22652 |  | 422653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22652 |  | 422653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22653 |  | 422654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22653 |  | 422654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22653 |  | 422654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22654 |  | 422655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm parameter: Reset hysteresis | 22654 |  | 422655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22654 |  | 422655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm parameter: Reset hysteresis | 22655 |  | 422656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22655 |  | 422656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22655 |  | 422656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22656 |  | 422657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22656 |  | 422657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22656 |  | 422657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22657 |  | 422658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22657 |  | 422658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22657 |  | 422658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22658 |  | 422659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22658 |  | 422659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22658 |  | 422659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22659 |  | 422660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22659 |  | 422660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22659 |  | 422660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22660 |  | 422661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22660 |  | 422661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22660 |  | 422661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22661 |  | 422662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22661 |  | 422662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22661 |  | 422662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22662 |  | 422663 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22662 |  | 422663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22662 |  | 422663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22663 |  | 422664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22663 |  | 422664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22663 |  | 422664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22664 |  | 422665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22664 |  | 422665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22664 |  | 422665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22665 |  | 422666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22665 |  | 422666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22665 |  | 422666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22666 |  | 422667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22666 |  | 422667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22666 |  | 422667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22667 |  | 422668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22667 |  | 422668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22667 |  | 422668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22668 |  | 422669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22668 |  | 422669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22668 |  | 422669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22669 |  | 422670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22669 |  | 422670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22669 |  | 422670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22670 |  | 422671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22670 |  | 422671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22670 |  | 422671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22671 |  | 422672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22671 |  | 422672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22671 |  | 422672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22672 |  | 422673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm parameter: Reset hysteresis | 22672 |  | 422673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm parameter: Reset hysteresis | 22672 |  | 422673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Configuration - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm parameter: Reset hysteresis | 22878 |  | 422879 | Internal issue detected. A restart is required soon! - Reset hysteresis | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23600 |  | 423601 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23601 |  | 423602 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23602 |  | 423603 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23603 |  | 423604 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23604 |  | 423605 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23605 |  | 423606 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23606 |  | 423607 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23607 |  | 423608 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23608 |  | 423609 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23609 |  | 423610 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23610 |  | 423611 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23611 |  | 423612 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23612 |  | 423613 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23613 |  | 423614 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23614 |  | 423615 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23615 |  | 423616 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23616 |  | 423617 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23617 |  | 423618 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23618 |  | 423619 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23619 |  | 423620 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23620 |  | 423621 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23621 |  | 423622 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23622 |  | 423623 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23623 |  | 423624 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23624 |  | 423625 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23625 |  | 423626 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23626 |  | 423627 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23627 |  | 423628 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23628 |  | 423629 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23629 |  | 423630 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23630 |  | 423631 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23631 |  | 423632 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23632 |  | 423633 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23633 |  | 423634 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23634 |  | 423635 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23635 |  | 423636 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23636 |  | 423637 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23637 |  | 423638 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23638 |  | 423639 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23639 |  | 423640 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23640 |  | 423641 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23641 |  | 423642 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23642 |  | 423643 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23643 |  | 423644 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23644 |  | 423645 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23645 |  | 423646 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23646 |  | 423647 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23647 |  | 423648 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23648 |  | 423649 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23649 |  | 423650 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23650 |  | 423651 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23651 |  | 423652 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23652 |  | 423653 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23653 |  | 423654 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23654 |  | 423655 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23655 |  | 423656 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23656 |  | 423657 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23657 |  | 423658 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23658 |  | 423659 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23659 |  | 423660 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23660 |  | 423661 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23661 |  | 423662 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23662 |  | 423663 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23663 |  | 423664 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23664 |  | 423665 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23665 |  | 423666 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23666 |  | 423667 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23667 |  | 423668 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23668 |  | 423669 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23669 |  | 423670 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23670 |  | 423671 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23671 |  | 423672 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23672 |  | 423673 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23673 |  | 423674 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23674 |  | 423675 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23675 |  | 423676 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23676 |  | 423677 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23677 |  | 423678 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23678 |  | 423679 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23679 |  | 423680 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23680 |  | 423681 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23681 |  | 423682 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23682 |  | 423683 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23683 |  | 423684 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23684 |  | 423685 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23685 |  | 423686 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23686 |  | 423687 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23687 |  | 423688 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23688 |  | 423689 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23689 |  | 423690 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23690 |  | 423691 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23691 |  | 423692 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23692 |  | 423693 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23693 |  | 423694 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23694 |  | 423695 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23695 |  | 423696 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23696 |  | 423697 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23697 |  | 423698 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23698 |  | 423699 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23699 |  | 423700 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23700 |  | 423701 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23701 |  | 423702 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23702 |  | 423703 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23703 |  | 423704 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23704 |  | 423705 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23705 |  | 423706 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23706 |  | 423707 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23707 |  | 423708 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23708 |  | 423709 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23709 |  | 423710 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23710 |  | 423711 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23711 |  | 423712 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23712 |  | 423713 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23713 |  | 423714 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23714 |  | 423715 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23715 |  | 423716 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23716 |  | 423717 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23717 |  | 423718 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23718 |  | 423719 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23719 |  | 423720 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23720 |  | 423721 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23721 |  | 423722 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23722 |  | 423723 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23723 |  | 423724 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23724 |  | 423725 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23725 |  | 423726 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23726 |  | 423727 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23727 |  | 423728 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23728 |  | 423729 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23729 |  | 423730 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23730 |  | 423731 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23731 |  | 423732 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23732 |  | 423733 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23733 |  | 423734 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23734 |  | 423735 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23735 |  | 423736 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23736 |  | 423737 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23737 |  | 423738 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23738 |  | 423739 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23739 |  | 423740 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23740 |  | 423741 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23741 |  | 423742 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23742 |  | 423743 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23743 |  | 423744 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23744 |  | 423745 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23745 |  | 423746 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23746 |  | 423747 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23747 |  | 423748 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23748 |  | 423749 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23749 |  | 423750 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23750 |  | 423751 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23751 |  | 423752 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23752 |  | 423753 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23753 |  | 423754 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23754 |  | 423755 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23755 |  | 423756 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23756 |  | 423757 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23757 |  | 423758 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23758 |  | 423759 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23759 |  | 423760 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23760 |  | 423761 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23761 |  | 423762 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23762 |  | 423763 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23763 |  | 423764 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23764 |  | 423765 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23765 |  | 423766 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23766 |  | 423767 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23767 |  | 423768 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23768 |  | 423769 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23769 |  | 423770 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23770 |  | 423771 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23771 |  | 423772 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23772 |  | 423773 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23773 |  | 423774 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23774 |  | 423775 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23775 |  | 423776 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23776 |  | 423777 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23777 |  | 423778 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23778 |  | 423779 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23779 |  | 423780 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23780 |  | 423781 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23781 |  | 423782 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23782 |  | 423783 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23783 |  | 423784 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23784 |  | 423785 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23785 |  | 423786 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23786 |  | 423787 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23787 |  | 423788 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23788 |  | 423789 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23789 |  | 423790 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23790 |  | 423791 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23791 |  | 423792 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23792 |  | 423793 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23793 |  | 423794 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23794 |  | 423795 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23795 |  | 423796 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23796 |  | 423797 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23797 |  | 423798 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23798 |  | 423799 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Reset hysteresis | 23799 |  | 423800 | Analogue custom alarm - Reset hysteresis | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Delay | 24003 |  | 424004 | Parameters - Engine - Stop sequence - Stop failure - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24005 |  | 424006 | Parameters - Engine - Start sequence - Crank failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24006 |  | 424007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24007 |  | 424008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24008 |  | 424009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24009 |  | 424010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24010 |  | 424011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24013 |  | 424014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24014 |  | 424015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24015 |  | 424016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24016 |  | 424017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24017 |  | 424018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24018 |  | 424019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24019 |  | 424020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24020 |  | 424021 | Parameters - Engine - Protections - Level - Coolant level 1 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24021 |  | 424022 | Parameters - Engine - Protections - Level - Coolant level 2 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24022 |  | 424023 | Parameters - Engine - Protections - Level - Coolant level 3 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24027 |  | 424028 | Parameters - Engine - Running detection - Primary running feedback failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24041 |  | 424042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24041 |  | 424042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24041 |  | 424042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24042 |  | 424043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24042 |  | 424043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24042 |  | 424043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24043 |  | 424044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24043 |  | 424044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24043 |  | 424044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24044 |  | 424045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24044 |  | 424045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24044 |  | 424045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24045 |  | 424046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24045 |  | 424046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24045 |  | 424046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24046 |  | 424047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24046 |  | 424047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24046 |  | 424047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24049 |  | 424050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm parameter: Delay | 24049 |  | 424050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm parameter: Delay | 24050 |  | 424051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm parameter: Delay | 24050 |  | 424051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm parameter: Delay | 24051 |  | 424052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm parameter: Delay | 24051 |  | 424052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm parameter: Delay | 24052 |  | 424053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm parameter: Delay | 24052 |  | 424053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm parameter: Delay | 24053 |  | 424054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm parameter: Delay | 24053 |  | 424054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm parameter: Delay | 24054 |  | 424055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm parameter: Delay | 24054 |  | 424055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm parameter: Delay | 24060 |  | 424061 | Parameters - Mains - AC setup - Phase sequence error - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24060 |  | 424061 | Parameters - Busbar - AC setup - Phase sequence error - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24060 |  | 424061 | Parameters - Busbar B - AC setup - Phase sequence error - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24061 |  | 424062 | Parameters - Generator - AC setup - Phase sequence error - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24061 |  | 424062 | Parameters - Busbar A - AC setup - Phase sequence error - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24061 |  | 424062 | Parameters - Mains - AC setup - Phase sequence error - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24062 |  | 424063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24103 |  | 424104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
Alarm parameter: Delay | 24103 |  | 424104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24103 |  | 424104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24108 |  | 424109 | Parameters - Generator - Additional protections - V< and Q< 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24108 |  | 424109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24108 |  | 424109 | Parameters - Mains - Additional protections - V< and Q< 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24109 |  | 424110 | Parameters - Generator - Additional protections - V< and Q< 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24109 |  | 424110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24109 |  | 424110 | Parameters - Mains - Additional protections - V< and Q< 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24110 |  | 424111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24110 |  | 424111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24110 |  | 424111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24111 |  | 424112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24111 |  | 424112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24111 |  | 424112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24116 |  | 424117 | Parameters - Generator - Current protections - Stabilised differential current - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24117 |  | 424118 | Parameters - Generator - Current protections - High set differential current - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24119 |  | 424120 | Parameters - Local - Mode - Not under remote control - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24128 |  | 424129 | Parameters - Custom alarm - Custom alarm 0 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24129 |  | 424130 | Parameters - Custom alarm - Custom alarm 1 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24130 |  | 424131 | Parameters - Custom alarm - Custom alarm 2 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24131 |  | 424132 | Parameters - Custom alarm - Custom alarm 3 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24132 |  | 424133 | Parameters - Custom alarm - Custom alarm 4 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24133 |  | 424134 | Parameters - Custom alarm - Custom alarm 5 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24134 |  | 424135 | Parameters - Custom alarm - Custom alarm 6 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24135 |  | 424136 | Parameters - Custom alarm - Custom alarm 7 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24136 |  | 424137 | Parameters - Custom alarm - Custom alarm 8 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24137 |  | 424138 | Parameters - Custom alarm - Custom alarm 9 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24138 |  | 424139 | Parameters - Custom alarm - Custom alarm 10 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24139 |  | 424140 | Parameters - Custom alarm - Custom alarm 11 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24140 |  | 424141 | Parameters - Custom alarm - Custom alarm 12 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24141 |  | 424142 | Parameters - Custom alarm - Custom alarm 13 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24142 |  | 424143 | Parameters - Custom alarm - Custom alarm 14 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24143 |  | 424144 | Parameters - Custom alarm - Custom alarm 15 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24144 |  | 424145 | Parameters - Custom alarm - Custom alarm 16 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24145 |  | 424146 | Parameters - Custom alarm - Custom alarm 17 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24146 |  | 424147 | Parameters - Custom alarm - Custom alarm 18 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24147 |  | 424148 | Parameters - Custom alarm - Custom alarm 19 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24148 |  | 424149 | Parameters - Custom alarm - Custom alarm 20 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24149 |  | 424150 | Parameters - Custom alarm - Custom alarm 21 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24150 |  | 424151 | Parameters - Custom alarm - Custom alarm 22 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24151 |  | 424152 | Parameters - Custom alarm - Custom alarm 23 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24152 |  | 424153 | Parameters - Custom alarm - Custom alarm 24 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24153 |  | 424154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24154 |  | 424155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24163 |  | 424164 | Required hardware card(s) not found - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24164 |  | 424165 | Software mismatch on hardware module(s) - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24165 |  | 424166 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  |  | X
Alarm parameter: Delay | 24165 |  | 424166 | Parameters - Busbar - AC setup - Multiple phase wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X
Alarm parameter: Delay | 24165 |  | 424166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24166 |  | 424167 | Parameters - Generator - AC setup - Multiple phase wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X |  | X
Alarm parameter: Delay | 24166 |  | 424167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24166 |  | 424167 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
Alarm parameter: Delay | 24167 |  | 424168 | Parameters - Mains - AC setup - L1 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  |  | X
Alarm parameter: Delay | 24167 |  | 424168 | Parameters - Busbar - AC setup - L1 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X
Alarm parameter: Delay | 24167 |  | 424168 | Parameters - Busbar B - AC setup - L1 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24168 |  | 424169 | Parameters - Mains - AC setup - L2 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  |  | X
Alarm parameter: Delay | 24168 |  | 424169 | Parameters - Busbar - AC setup - L2 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X
Alarm parameter: Delay | 24168 |  | 424169 | Parameters - Busbar B - AC setup - L2 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24169 |  | 424170 | Parameters - Mains - AC setup - L3 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  |  | X
Alarm parameter: Delay | 24169 |  | 424170 | Parameters - Busbar - AC setup - L3 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X
Alarm parameter: Delay | 24169 |  | 424170 | Parameters - Busbar B - AC setup - L3 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24170 |  | 424171 | Parameters - Generator - AC setup - L1 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X |  | X
Alarm parameter: Delay | 24170 |  | 424171 | Parameters - Busbar A - AC setup - L1 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24170 |  | 424171 | Parameters - Mains - AC setup - L1 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
Alarm parameter: Delay | 24171 |  | 424172 | Parameters - Generator - AC setup - L2 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X |  | X
Alarm parameter: Delay | 24171 |  | 424172 | Parameters - Busbar A - AC setup - L2 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24171 |  | 424172 | Parameters - Mains - AC setup - L2 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
Alarm parameter: Delay | 24172 |  | 424173 | Parameters - Generator - AC setup - L3 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X |  | X
Alarm parameter: Delay | 24172 |  | 424173 | Parameters - Busbar A - AC setup - L3 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24172 |  | 424173 | Parameters - Mains - AC setup - L3 wire break - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X
Alarm parameter: Delay | 24179 |  | 424180 | Parameters - Engine - Emergency stop - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24179 |  | 424180 | Parameters - Busbar A - Emergency stop - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24179 |  | 424180 | Parameters - Mains - Emergency stop - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24180 |  | 424181 | Clock battery failure - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24181 |  | 424182 | Controller temperature too high - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24182 |  | 424183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24183 |  | 424184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24184 |  | 424185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24185 |  | 424186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24186 |  | 424187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24187 |  | 424188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24188 |  | 424189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24189 |  | 424190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24190 |  | 424191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24191 |  | 424192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24192 |  | 424193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24193 |  | 424194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24194 |  | 424195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24195 |  | 424196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24196 |  | 424197 | EIM3.1 4 supply voltage high - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24197 |  | 424198 | EIM3.1 4 supply voltage low or missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24198 |  | 424199 | EIM3.1 5 supply voltage high - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24199 |  | 424200 | EIM3.1 5 supply voltage low or missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24200 |  | 424201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24201 |  | 424202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24202 |  | 424203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24203 |  | 424204 | EIM3.1 4 relay 4 wire break - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24204 |  | 424205 | EIM3.1 5 relay 4 wire break - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24205 |  | 424206 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24206 |  | 424207 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24207 |  | 424208 | AC protections not running (differential current) - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24208 |  | 424209 | AC data is missing (differential current) - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24209 |  | 424210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24210 |  | 424211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24211 |  | 424212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24212 |  | 424213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24213 |  | 424214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24214 |  | 424215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24215 |  | 424216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24216 |  | 424217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24217 |  | 424218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24218 |  | 424219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24219 |  | 424220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24220 |  | 424221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24221 |  | 424222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24222 |  | 424223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24223 |  | 424224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24224 |  | 424225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24225 |  | 424226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24226 |  | 424227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24237 |  | 424238 | Blackout detection mismatch - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24240 |  | 424241 | Parameters - Communication - NTP - NTP server 1 not connected - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24242 |  | 424243 | Parameters - Communication - NTP - NTP server 2 not connected - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24245 |  | 424246 | Parameters - Communication - NTP - No NTP server(s) connected - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24297 |  | 424298 | Different single-line configurations - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24299 |  | 424300 | Parameters - Communication - Modbus - Modbus communication timeout - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24301 |  | 424302 | Parameters - CODESYS - Monitoring - Application not OK - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24306 |  | 424307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24316 |  | 424317 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24364 |  | 424365 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24471 |  | 424472 | Parameters - Non-essential load trip - Trip 1 - Over-current - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24472 |  | 424473 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24473 |  | 424474 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24474 |  | 424475 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24475 |  | 424476 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24476 |  | 424477 | Parameters - Non-essential load trip - Trip 2 - Over-current - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24477 |  | 424478 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24478 |  | 424479 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24479 |  | 424480 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24480 |  | 424481 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24481 |  | 424482 | Parameters - Non-essential load trip - Trip 3 - Over-current - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24482 |  | 424483 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24483 |  | 424484 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24484 |  | 424485 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24485 |  | 424486 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24490 |  | 424491 | Parameters - System - Monitoring - Single-line hazard - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24491 |  | 424492 | ID not present - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24492 |  | 424493 | Unsupported application - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24493 |  | 424494 | Application internal CAN protocol conflict - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24495 |  | 424496 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24510 |  | 424511 | Dry mode: Voltage level unexpected - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24541 |  | 424542 | Hardware is not compatible based on module versions - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24615 |  | 424616 | Parameters - Generator - Voltage protections - Under-voltage 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24615 |  | 424616 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24615 |  | 424616 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24616 |  | 424617 | Parameters - Generator - Voltage protections - Under-voltage 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24616 |  | 424617 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24616 |  | 424617 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24617 |  | 424618 | Parameters - Generator - Voltage protections - Under-voltage 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24617 |  | 424618 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24617 |  | 424618 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24618 |  | 424619 | Parameters - Generator - Voltage protections - Over-voltage 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24618 |  | 424619 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24618 |  | 424619 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24619 |  | 424620 | Parameters - Generator - Voltage protections - Over-voltage 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24619 |  | 424620 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24619 |  | 424620 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24620 |  | 424621 | Parameters - Generator - Voltage protections - Voltage unbalance - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24620 |  | 424621 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24620 |  | 424621 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24621 |  | 424622 | Parameters - Generator - Voltage protections - Negative sequence voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24621 |  | 424622 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24621 |  | 424622 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24622 |  | 424623 | Parameters - Generator - Voltage protections - Zero sequence voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24622 |  | 424623 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24622 |  | 424623 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24623 |  | 424624 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24623 |  | 424624 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24623 |  | 424624 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24624 |  | 424625 | Parameters - Generator - Current protections - Over-current 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24624 |  | 424625 | Parameters - Busbar A - Current protections - Over-current 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24624 |  | 424625 | Parameters - Mains - Current protections - Over-current 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24625 |  | 424626 | Parameters - Generator - Current protections - Over-current 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24625 |  | 424626 | Parameters - Busbar A - Current protections - Over-current 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24625 |  | 424626 | Parameters - Mains - Current protections - Over-current 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24626 |  | 424627 | Parameters - Generator - Current protections - Over-current 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24626 |  | 424627 | Parameters - Busbar A - Current protections - Over-current 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24626 |  | 424627 | Parameters - Mains - Current protections - Over-current 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24627 |  | 424628 | Parameters - Generator - Current protections - Over-current 4 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24627 |  | 424628 | Parameters - Busbar A - Current protections - Over-current 4 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24627 |  | 424628 | Parameters - Mains - Current protections - Over-current 4 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24628 |  | 424629 | Parameters - Generator - Current protections - Fast over-current 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24628 |  | 424629 | Parameters - Busbar A - Current protections - Fast over-current 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24628 |  | 424629 | Parameters - Mains - Current protections - Fast over-current 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24629 |  | 424630 | Parameters - Generator - Current protections - Fast over-current 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24629 |  | 424630 | Parameters - Busbar A - Current protections - Fast over-current 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24629 |  | 424630 | Parameters - Mains - Current protections - Fast over-current 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24630 |  | 424631 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24630 |  | 424631 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24630 |  | 424631 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24631 |  | 424632 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24631 |  | 424632 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24631 |  | 424632 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24632 |  | 424633 | Parameters - Generator - Current protections - Directional over-current 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24632 |  | 424633 | Parameters - Busbar A - Current protections - Directional over-current 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24632 |  | 424633 | Parameters - Mains - Current protections - Directional over-current 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24633 |  | 424634 | Parameters - Generator - Current protections - Directional over-current 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24633 |  | 424634 | Parameters - Busbar A - Current protections - Directional over-current 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24633 |  | 424634 | Parameters - Mains - Current protections - Directional over-current 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24634 |  | 424635 | Parameters - Busbar A - Current protections - Directional over-current 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24635 |  | 424636 | Parameters - Busbar A - Current protections - Directional over-current 4 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24636 |  | 424637 | Parameters - Generator - Current protections - Negative sequence current - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24636 |  | 424637 | Parameters - Busbar A - Current protections - Negative sequence current - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24636 |  | 424637 | Parameters - Mains - Current protections - Negative sequence current - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24637 |  | 424638 | Parameters - Generator - Current protections - Zero sequence current - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24637 |  | 424638 | Parameters - Busbar A - Current protections - Zero sequence current - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24637 |  | 424638 | Parameters - Mains - Current protections - Zero sequence current - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24638 |  | 424639 | Parameters - Generator - Frequency protections - Over-frequency 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24638 |  | 424639 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24638 |  | 424639 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24639 |  | 424640 | Parameters - Generator - Frequency protections - Over-frequency 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24639 |  | 424640 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24639 |  | 424640 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24640 |  | 424641 | Parameters - Generator - Frequency protections - Over-frequency 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24640 |  | 424641 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24640 |  | 424641 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24641 |  | 424642 | Parameters - Generator - Frequency protections - Under-frequency 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24641 |  | 424642 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24641 |  | 424642 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24642 |  | 424643 | Parameters - Generator - Frequency protections - Under-frequency 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24642 |  | 424643 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24642 |  | 424643 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24643 |  | 424644 | Parameters - Generator - Frequency protections - Under-frequency 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24643 |  | 424644 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24643 |  | 424644 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24644 |  | 424645 | Parameters - Generator - Power protections - Overload 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24644 |  | 424645 | Parameters - Busbar A - Power protections - Power export 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24644 |  | 424645 | Parameters - Mains - Power protections - Overload 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24645 |  | 424646 | Parameters - Generator - Power protections - Overload 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24645 |  | 424646 | Parameters - Busbar A - Power protections - Power export 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24645 |  | 424646 | Parameters - Mains - Power protections - Overload 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24646 |  | 424647 | Parameters - Generator - Power protections - Overload 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24646 |  | 424647 | Parameters - Busbar A - Power protections - Power export 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24646 |  | 424647 | Parameters - Mains - Power protections - Overload 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24647 |  | 424648 | Parameters - Generator - Power protections - Overload 4 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24647 |  | 424648 | Parameters - Busbar A - Power protections - Power export 4 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24647 |  | 424648 | Parameters - Mains - Power protections - Overload 4 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24648 |  | 424649 | Parameters - Generator - Power protections - Overload 5 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24648 |  | 424649 | Parameters - Busbar A - Power protections - Power export 5 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24648 |  | 424649 | Parameters - Mains - Power protections - Overload 5 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24649 |  | 424650 | Parameters - Generator - Power protections - Reverse power 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24649 |  | 424650 | Parameters - Busbar A - Power protections - Power import 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24649 |  | 424650 | Parameters - Mains - Power protections - Reverse power 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24650 |  | 424651 | Parameters - Generator - Power protections - Reverse power 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24650 |  | 424651 | Parameters - Busbar A - Power protections - Power import 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24650 |  | 424651 | Parameters - Mains - Power protections - Reverse power 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24651 |  | 424652 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24651 |  | 424652 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24651 |  | 424652 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24652 |  | 424653 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24652 |  | 424653 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24652 |  | 424653 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24653 |  | 424654 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24653 |  | 424654 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24653 |  | 424654 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24654 |  | 424655 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24654 |  | 424655 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24654 |  | 424655 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24655 |  | 424656 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24655 |  | 424656 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24655 |  | 424656 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24656 |  | 424657 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24656 |  | 424657 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24656 |  | 424657 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24657 |  | 424658 | Parameters - Mains - Voltage protections - Over-voltage 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24657 |  | 424658 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24657 |  | 424658 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24658 |  | 424659 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24658 |  | 424659 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24658 |  | 424659 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24659 |  | 424660 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24659 |  | 424660 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24659 |  | 424660 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24660 |  | 424661 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24660 |  | 424661 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24660 |  | 424661 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24661 |  | 424662 | Parameters - Mains - Voltage protections - Under-voltage 4 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24661 |  | 424662 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24661 |  | 424662 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24662 |  | 424663 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24662 |  | 424663 | Parameters - Busbar - Voltage protections - Voltage unbalance - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24662 |  | 424663 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24663 |  | 424664 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24663 |  | 424664 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24663 |  | 424664 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24664 |  | 424665 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24664 |  | 424665 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24664 |  | 424665 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24665 |  | 424666 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24665 |  | 424666 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24665 |  | 424666 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24666 |  | 424667 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24666 |  | 424667 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24666 |  | 424667 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24667 |  | 424668 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24667 |  | 424668 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24667 |  | 424668 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24668 |  | 424669 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24668 |  | 424669 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24668 |  | 424669 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24669 |  | 424670 | Parameters - Mains - Frequency protections - Under-frequency 4 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24669 |  | 424670 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24669 |  | 424670 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24670 |  | 424671 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24670 |  | 424671 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24670 |  | 424671 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24671 |  | 424672 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24671 |  | 424672 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24671 |  | 424672 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24672 |  | 424673 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24672 |  | 424673 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm parameter: Delay | 24672 |  | 424673 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm parameter: Delay | 24717 |  | 424718 | External MB open failure - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24718 |  | 424719 | Parameters - Power management rules - Ground relay - Ground relay general failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24719 |  | 424720 | Parameters - Power management rules - Ground relay - Ground relay open failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24720 |  | 424721 | Parameters - Power management rules - Ground relay - Ground relay close failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24721 |  | 424722 | Parameters - Power management rules - Ground relay - Ground relay position failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24722 |  | 424723 | Parameters - Breakers - Close before excitation - CBE rerun failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24723 |  | 424724 | Parameters - Breakers - Close before excitation - CBE failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24724 |  | 424725 | Load too high - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24725 |  | 424726 | ID to run configuration failure - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24726 |  | 424727 | Can ID not available - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24727 |  | 424728 | Duplicated CAN IDs - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24728 |  | 424729 | Parameters - Local power management - Alarms - Busbar blocked - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
Alarm parameter: Delay | 24729 |  | 424730 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24730 |  | 424731 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24731 |  | 424732 | Parameters - System - Monitoring - BTB 33 position failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24732 |  | 424733 | Parameters - System - Monitoring - BTB 34 position failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24733 |  | 424734 | Parameters - System - Monitoring - BTB 35 position failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24734 |  | 424735 | Parameters - System - Monitoring - BTB 36 position failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24735 |  | 424736 | Parameters - System - Monitoring - BTB 37 position failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24736 |  | 424737 | Parameters - System - Monitoring - BTB 38 position failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24737 |  | 424738 | Parameters - System - Monitoring - BTB 39 position failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24738 |  | 424739 | Parameters - System - Monitoring - BTB 40 position failure - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24854 |  | 424855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm parameter: Delay | 24854 |  | 424855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm parameter: Delay | 24854 |  | 424855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm parameter: Delay | 24855 |  | 424856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm parameter: Delay | 24855 |  | 424856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm parameter: Delay | 24857 |  | 424858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24858 |  | 424859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24859 |  | 424860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24860 |  | 424861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Configuration - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24861 |  | 424862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24862 |  | 424863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24863 |  | 424864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24864 |  | 424865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24865 |  | 424866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24866 |  | 424867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24867 |  | 424868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24868 |  | 424869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24869 |  | 424870 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24870 |  | 424871 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24871 |  | 424872 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24872 |  | 424873 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24873 |  | 424874 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24874 |  | 424875 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24875 |  | 424876 | AC protections not running - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24876 |  | 424877 | AC data is missing - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24877 |  | 424878 | Live voltage detected - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24881 |  | 424882 | Card configuration failed - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24883 |  | 424884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24884 |  | 424885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24885 |  | 424886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm parameter: Delay | 24886 |  | 424887 | Licence error - Delay | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 24891 |  | 424892 | Parameters - Grid code - Capability curve - Import protection - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 24892 |  | 424893 | Parameters - Grid code - Capability curve - Export protection - Configuration - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm parameter: Delay | 25500 |  | 425501 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25501 |  | 425502 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25502 |  | 425503 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25503 |  | 425504 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25504 |  | 425505 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25505 |  | 425506 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25506 |  | 425507 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25507 |  | 425508 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25508 |  | 425509 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25509 |  | 425510 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25510 |  | 425511 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25511 |  | 425512 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25512 |  | 425513 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25513 |  | 425514 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25514 |  | 425515 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25515 |  | 425516 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25516 |  | 425517 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25517 |  | 425518 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25518 |  | 425519 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25519 |  | 425520 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25520 |  | 425521 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25521 |  | 425522 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25522 |  | 425523 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25523 |  | 425524 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25524 |  | 425525 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25525 |  | 425526 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25526 |  | 425527 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25527 |  | 425528 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25528 |  | 425529 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25529 |  | 425530 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25530 |  | 425531 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25531 |  | 425532 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25532 |  | 425533 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25533 |  | 425534 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25534 |  | 425535 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25535 |  | 425536 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25536 |  | 425537 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25537 |  | 425538 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25538 |  | 425539 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25539 |  | 425540 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25540 |  | 425541 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25541 |  | 425542 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25542 |  | 425543 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25543 |  | 425544 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25544 |  | 425545 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25545 |  | 425546 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25546 |  | 425547 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25547 |  | 425548 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25548 |  | 425549 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25549 |  | 425550 | Digital custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25600 |  | 425601 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25601 |  | 425602 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25602 |  | 425603 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25603 |  | 425604 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25604 |  | 425605 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25605 |  | 425606 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25606 |  | 425607 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25607 |  | 425608 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25608 |  | 425609 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25609 |  | 425610 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25610 |  | 425611 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25611 |  | 425612 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25612 |  | 425613 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25613 |  | 425614 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25614 |  | 425615 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25615 |  | 425616 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25616 |  | 425617 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25617 |  | 425618 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25618 |  | 425619 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25619 |  | 425620 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25620 |  | 425621 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25621 |  | 425622 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25622 |  | 425623 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25623 |  | 425624 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25624 |  | 425625 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25625 |  | 425626 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25626 |  | 425627 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25627 |  | 425628 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25628 |  | 425629 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25629 |  | 425630 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25630 |  | 425631 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25631 |  | 425632 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25632 |  | 425633 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25633 |  | 425634 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25634 |  | 425635 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25635 |  | 425636 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25636 |  | 425637 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25637 |  | 425638 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25638 |  | 425639 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25639 |  | 425640 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25640 |  | 425641 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25641 |  | 425642 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25642 |  | 425643 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25643 |  | 425644 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25644 |  | 425645 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25645 |  | 425646 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25646 |  | 425647 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25647 |  | 425648 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25648 |  | 425649 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25649 |  | 425650 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25650 |  | 425651 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25651 |  | 425652 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25652 |  | 425653 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25653 |  | 425654 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25654 |  | 425655 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25655 |  | 425656 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25656 |  | 425657 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25657 |  | 425658 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25658 |  | 425659 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25659 |  | 425660 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25660 |  | 425661 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25661 |  | 425662 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25662 |  | 425663 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25663 |  | 425664 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25664 |  | 425665 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25665 |  | 425666 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25666 |  | 425667 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25667 |  | 425668 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25668 |  | 425669 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25669 |  | 425670 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25670 |  | 425671 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25671 |  | 425672 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25672 |  | 425673 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25673 |  | 425674 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25674 |  | 425675 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25675 |  | 425676 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25676 |  | 425677 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25677 |  | 425678 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25678 |  | 425679 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25679 |  | 425680 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25680 |  | 425681 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25681 |  | 425682 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25682 |  | 425683 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25683 |  | 425684 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25684 |  | 425685 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25685 |  | 425686 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25686 |  | 425687 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25687 |  | 425688 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25688 |  | 425689 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25689 |  | 425690 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25690 |  | 425691 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25691 |  | 425692 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25692 |  | 425693 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25693 |  | 425694 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25694 |  | 425695 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25695 |  | 425696 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25696 |  | 425697 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25697 |  | 425698 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25698 |  | 425699 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25699 |  | 425700 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25700 |  | 425701 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25701 |  | 425702 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25702 |  | 425703 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25703 |  | 425704 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25704 |  | 425705 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25705 |  | 425706 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25706 |  | 425707 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25707 |  | 425708 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25708 |  | 425709 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25709 |  | 425710 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25710 |  | 425711 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25711 |  | 425712 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25712 |  | 425713 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25713 |  | 425714 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25714 |  | 425715 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25715 |  | 425716 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25716 |  | 425717 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25717 |  | 425718 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25718 |  | 425719 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25719 |  | 425720 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25720 |  | 425721 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25721 |  | 425722 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25722 |  | 425723 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25723 |  | 425724 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25724 |  | 425725 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25725 |  | 425726 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25726 |  | 425727 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25727 |  | 425728 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25728 |  | 425729 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25729 |  | 425730 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25730 |  | 425731 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25731 |  | 425732 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25732 |  | 425733 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25733 |  | 425734 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25734 |  | 425735 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25735 |  | 425736 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25736 |  | 425737 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25737 |  | 425738 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25738 |  | 425739 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25739 |  | 425740 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25740 |  | 425741 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25741 |  | 425742 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25742 |  | 425743 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25743 |  | 425744 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25744 |  | 425745 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25745 |  | 425746 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25746 |  | 425747 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25747 |  | 425748 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25748 |  | 425749 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25749 |  | 425750 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25750 |  | 425751 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25751 |  | 425752 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25752 |  | 425753 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25753 |  | 425754 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25754 |  | 425755 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25755 |  | 425756 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25756 |  | 425757 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25757 |  | 425758 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25758 |  | 425759 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25759 |  | 425760 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25760 |  | 425761 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25761 |  | 425762 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25762 |  | 425763 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25763 |  | 425764 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25764 |  | 425765 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25765 |  | 425766 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25766 |  | 425767 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25767 |  | 425768 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25768 |  | 425769 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25769 |  | 425770 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25770 |  | 425771 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25771 |  | 425772 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25772 |  | 425773 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25773 |  | 425774 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25774 |  | 425775 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25775 |  | 425776 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25776 |  | 425777 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25777 |  | 425778 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25778 |  | 425779 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25779 |  | 425780 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25780 |  | 425781 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25781 |  | 425782 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25782 |  | 425783 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25783 |  | 425784 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25784 |  | 425785 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25785 |  | 425786 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25786 |  | 425787 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25787 |  | 425788 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25788 |  | 425789 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25789 |  | 425790 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25790 |  | 425791 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25791 |  | 425792 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25792 |  | 425793 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25793 |  | 425794 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25794 |  | 425795 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25795 |  | 425796 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25796 |  | 425797 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25797 |  | 425798 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25798 |  | 425799 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Delay | 25799 |  | 425800 | Analogue custom alarm - Delay | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
Alarm parameter: Action | 26000 |  | 426001 | Application initialisation error - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26001 |  | 426002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26002 |  | 426003 | Preliminary software - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26003 |  | 426004 | Parameters - Engine - Stop sequence - Stop failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26004 |  | 426005 | Parameters - Engine - Start sequence - Start failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26005 |  | 426006 | Parameters - Engine - Start sequence - Crank failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26006 |  | 426007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26007 |  | 426008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26008 |  | 426009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26009 |  | 426010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26010 |  | 426011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26011 |  | 426012 | Parameters - Engine - Stop sequence - Externally stopped - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26013 |  | 426014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26014 |  | 426015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26015 |  | 426016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26016 |  | 426017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26017 |  | 426018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26018 |  | 426019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26019 |  | 426020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26020 |  | 426021 | Parameters - Engine - Protections - Level - Coolant level 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26021 |  | 426022 | Parameters - Engine - Protections - Level - Coolant level 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26022 |  | 426023 | Parameters - Engine - Protections - Level - Coolant level 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26027 |  | 426028 | Parameters - Engine - Running detection - Primary running feedback failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26041 |  | 426042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26041 |  | 426042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26041 |  | 426042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26042 |  | 426043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26042 |  | 426043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26042 |  | 426043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26043 |  | 426044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26043 |  | 426044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26043 |  | 426044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26044 |  | 426045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26044 |  | 426045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26044 |  | 426045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26045 |  | 426046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26045 |  | 426046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26045 |  | 426046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26046 |  | 426047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26046 |  | 426047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26046 |  | 426047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26047 |  | 426048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26047 |  | 426048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26047 |  | 426048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26048 |  | 426049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26048 |  | 426049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26048 |  | 426049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26049 |  | 426050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Action | 26049 |  | 426050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Configuration - Action | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Action | 26050 |  | 426051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Action | 26050 |  | 426051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Configuration - Action | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Action | 26051 |  | 426052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Action | 26051 |  | 426052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Configuration - Action | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Action | 26052 |  | 426053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Action | 26052 |  | 426053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Configuration - Action | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Action | 26053 |  | 426054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Action | 26053 |  | 426054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Configuration - Action | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Action | 26054 |  | 426055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Action | 26054 |  | 426055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Configuration - Action | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Action | 26055 |  | 426056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Action | 26055 |  | 426056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Configuration - Action | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Action | 26056 |  | 426057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Action | 26056 |  | 426057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Configuration - Action | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Action | 26060 |  | 426061 | Parameters - Mains - AC setup - Phase sequence error - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26060 |  | 426061 | Parameters - Busbar - AC setup - Phase sequence error - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26060 |  | 426061 | Parameters - Busbar B - AC setup - Phase sequence error - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26061 |  | 426062 | Parameters - Generator - AC setup - Phase sequence error - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26061 |  | 426062 | Parameters - Busbar A - AC setup - Phase sequence error - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26061 |  | 426062 | Parameters - Mains - AC setup - Phase sequence error - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26062 |  | 426063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26103 |  | 426104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26103 |  | 426104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26103 |  | 426104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26104 |  | 426105 | Parameters - Mains - Additional protections - Vector shift - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26104 |  | 426105 | Parameters - Busbar - Additional protections - Vector shift - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26104 |  | 426105 | Parameters - Busbar B - Additional protections - Vector shift - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26105 |  | 426106 | Parameters - Generator - Current protections - Inverse time over-current - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26105 |  | 426106 | Parameters - Busbar A - Current protections - Inverse time over-current - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26105 |  | 426106 | Parameters - Mains - Current protections - Inverse time over-current - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26106 |  | 426107 | Parameters - Local - 4th current input - Earth inverse time over-current - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26107 |  | 426108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26108 |  | 426109 | Parameters - Generator - Additional protections - V< and Q< 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26108 |  | 426109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26108 |  | 426109 | Parameters - Mains - Additional protections - V< and Q< 1 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26109 |  | 426110 | Parameters - Generator - Additional protections - V< and Q< 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26109 |  | 426110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26109 |  | 426110 | Parameters - Mains - Additional protections - V< and Q< 2 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26110 |  | 426111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26110 |  | 426111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26110 |  | 426111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26111 |  | 426112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26111 |  | 426112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26111 |  | 426112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26115 |  | 426116 | Protection set point out of range - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26116 |  | 426117 | Parameters - Generator - Current protections - Stabilised differential current - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26117 |  | 426118 | Parameters - Generator - Current protections - High set differential current - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26118 |  | 426119 | Protection set point out of range (differential current) - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26119 |  | 426120 | Parameters - Local - Mode - Not under remote control - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26121 |  | 426122 | Parameters - Local - Monitoring - System not OK - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26122 |  | 426123 | Configuration update delayed - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26123 |  | 426124 | Critical process error - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26124 |  | 426125 | Restore error - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26125 |  | 426126 | SD-card format error - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26126 |  | 426127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26127 |  | 426128 | Fieldbus configuration exceeded maximum I/O configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26128 |  | 426129 | Parameters - Custom alarm - Custom alarm 0 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26129 |  | 426130 | Parameters - Custom alarm - Custom alarm 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26130 |  | 426131 | Parameters - Custom alarm - Custom alarm 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26131 |  | 426132 | Parameters - Custom alarm - Custom alarm 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26132 |  | 426133 | Parameters - Custom alarm - Custom alarm 4 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26133 |  | 426134 | Parameters - Custom alarm - Custom alarm 5 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26134 |  | 426135 | Parameters - Custom alarm - Custom alarm 6 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26135 |  | 426136 | Parameters - Custom alarm - Custom alarm 7 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26136 |  | 426137 | Parameters - Custom alarm - Custom alarm 8 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26137 |  | 426138 | Parameters - Custom alarm - Custom alarm 9 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26138 |  | 426139 | Parameters - Custom alarm - Custom alarm 10 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26139 |  | 426140 | Parameters - Custom alarm - Custom alarm 11 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26140 |  | 426141 | Parameters - Custom alarm - Custom alarm 12 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26141 |  | 426142 | Parameters - Custom alarm - Custom alarm 13 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26142 |  | 426143 | Parameters - Custom alarm - Custom alarm 14 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26143 |  | 426144 | Parameters - Custom alarm - Custom alarm 15 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26144 |  | 426145 | Parameters - Custom alarm - Custom alarm 16 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26145 |  | 426146 | Parameters - Custom alarm - Custom alarm 17 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26146 |  | 426147 | Parameters - Custom alarm - Custom alarm 18 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26147 |  | 426148 | Parameters - Custom alarm - Custom alarm 19 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26148 |  | 426149 | Parameters - Custom alarm - Custom alarm 20 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26149 |  | 426150 | Parameters - Custom alarm - Custom alarm 21 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26150 |  | 426151 | Parameters - Custom alarm - Custom alarm 22 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26151 |  | 426152 | Parameters - Custom alarm - Custom alarm 23 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26152 |  | 426153 | Parameters - Custom alarm - Custom alarm 24 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26153 |  | 426154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26154 |  | 426155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26163 |  | 426164 | Required hardware card(s) not found - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26164 |  | 426165 | Software mismatch on hardware module(s) - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26165 |  | 426166 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Action | 26165 |  | 426166 | Parameters - Busbar - AC setup - Multiple phase wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Action | 26165 |  | 426166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26166 |  | 426167 | Parameters - Generator - AC setup - Multiple phase wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Action | 26166 |  | 426167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26166 |  | 426167 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Action | 26167 |  | 426168 | Parameters - Mains - AC setup - L1 wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Action | 26167 |  | 426168 | Parameters - Busbar - AC setup - L1 wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Action | 26167 |  | 426168 | Parameters - Busbar B - AC setup - L1 wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26168 |  | 426169 | Parameters - Mains - AC setup - L2 wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Action | 26168 |  | 426169 | Parameters - Busbar - AC setup - L2 wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Action | 26168 |  | 426169 | Parameters - Busbar B - AC setup - L2 wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26169 |  | 426170 | Parameters - Mains - AC setup - L3 wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Action | 26169 |  | 426170 | Parameters - Busbar - AC setup - L3 wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Action | 26169 |  | 426170 | Parameters - Busbar B - AC setup - L3 wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26170 |  | 426171 | Parameters - Generator - AC setup - L1 wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Action | 26170 |  | 426171 | Parameters - Busbar A - AC setup - L1 wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26170 |  | 426171 | Parameters - Mains - AC setup - L1 wire break - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Action | 26171 |  | 426172 | Parameters - Generator - AC setup - L2 wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Action | 26171 |  | 426172 | Parameters - Busbar A - AC setup - L2 wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26171 |  | 426172 | Parameters - Mains - AC setup - L2 wire break - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Action | 26172 |  | 426173 | Parameters - Generator - AC setup - L3 wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Action | 26172 |  | 426173 | Parameters - Busbar A - AC setup - L3 wire break - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26172 |  | 426173 | Parameters - Mains - AC setup - L3 wire break - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Action | 26178 |  | 426179 | Parameters - Mains - AC setup - Supervision alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X |  | X | X
Alarm parameter: Action | 26179 |  | 426180 | Parameters - Engine - Emergency stop - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26179 |  | 426180 | Parameters - Busbar A - Emergency stop - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26179 |  | 426180 | Parameters - Mains - Emergency stop - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26180 |  | 426181 | Clock battery failure - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26181 |  | 426182 | Controller temperature too high - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26182 |  | 426183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26183 |  | 426184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26184 |  | 426185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26185 |  | 426186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26186 |  | 426187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26187 |  | 426188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26188 |  | 426189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26189 |  | 426190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26190 |  | 426191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26191 |  | 426192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26192 |  | 426193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26193 |  | 426194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26194 |  | 426195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26195 |  | 426196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26196 |  | 426197 | EIM3.1 4 supply voltage high - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26197 |  | 426198 | EIM3.1 4 supply voltage low or missing - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26198 |  | 426199 | EIM3.1 5 supply voltage high - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26199 |  | 426200 | EIM3.1 5 supply voltage low or missing - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26200 |  | 426201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26201 |  | 426202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26202 |  | 426203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26203 |  | 426204 | EIM3.1 4 relay 4 wire break - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26204 |  | 426205 | EIM3.1 5 relay 4 wire break - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26205 |  | 426206 | AC protections not running - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26206 |  | 426207 | AC data is missing - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26207 |  | 426208 | AC protections not running (differential current) - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26208 |  | 426209 | AC data is missing (differential current) - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26209 |  | 426210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26210 |  | 426211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26211 |  | 426212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26212 |  | 426213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26213 |  | 426214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26214 |  | 426215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26215 |  | 426216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26216 |  | 426217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26217 |  | 426218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26218 |  | 426219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26219 |  | 426220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26220 |  | 426221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26221 |  | 426222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26222 |  | 426223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26223 |  | 426224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26224 |  | 426225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26225 |  | 426226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26226 |  | 426227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26228 |  | 426229 | Parameters - System - Monitoring - Duplicate controller ID - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26229 |  | 426230 | Parameters - System - Monitoring - Missing all controllers - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26231 |  | 426232 | Controller ID not configured - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26236 |  | 426237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26237 |  | 426238 | Blackout detection mismatch - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26240 |  | 426241 | Parameters - Communication - NTP - NTP server 1 not connected - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26241 |  | 426242 | Parameters - Communication - NTP - NTP server 1 no response - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26242 |  | 426243 | Parameters - Communication - NTP - NTP server 2 not connected - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26243 |  | 426244 | Parameters - Communication - NTP - NTP server 2 no response - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26244 |  | 426245 | Parameters - Communication - NTP - No NTP server time synchronisation - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26245 |  | 426246 | Parameters - Communication - NTP - No NTP server(s) connected - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26246 |  | 426247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26247 |  | 426248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26296 |  | 426297 | Controller not part of system - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26297 |  | 426298 | Different single-line configurations - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26298 |  | 426299 | Single-line missing/none active - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26299 |  | 426300 | Parameters - Communication - Modbus - Modbus communication timeout - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26300 |  | 426301 | Parameters - CODESYS - Monitoring - I/O config conflict - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26301 |  | 426302 | Parameters - CODESYS - Monitoring - Application not OK - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26302 |  | 426303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26303 |  | 426304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26304 |  | 426305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26305 |  | 426306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26306 |  | 426307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26307 |  | 426308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26308 |  | 426309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26309 |  | 426310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26310 |  | 426311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26311 |  | 426312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26312 |  | 426313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26315 |  | 426316 | Parameters - Local - CustomLogic - Configuration invalid - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26316 |  | 426317 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26317 |  | 426318 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26318 |  | 426319 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26319 |  | 426320 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26320 |  | 426321 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26321 |  | 426322 | Parameters - Generator - Digital AVR - Alarms - Open diode - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26322 |  | 426323 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26323 |  | 426324 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26324 |  | 426325 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26325 |  | 426326 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26326 |  | 426327 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26327 |  | 426328 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26328 |  | 426329 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26329 |  | 426330 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26330 |  | 426331 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26331 |  | 426332 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26332 |  | 426333 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26333 |  | 426334 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26334 |  | 426335 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26335 |  | 426336 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26336 |  | 426337 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26337 |  | 426338 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26338 |  | 426339 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26339 |  | 426340 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26340 |  | 426341 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26341 |  | 426342 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26342 |  | 426343 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26343 |  | 426344 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26344 |  | 426345 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26345 |  | 426346 | Parameters - Generator - Digital AVR - Alarms - Motor start - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26346 |  | 426347 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26347 |  | 426348 | Parameters - Generator - Digital AVR - Alarms - Power supply - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26348 |  | 426349 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26349 |  | 426350 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26350 |  | 426351 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26351 |  | 426352 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26352 |  | 426353 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26353 |  | 426354 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26354 |  | 426355 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26355 |  | 426356 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26356 |  | 426357 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26357 |  | 426358 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26358 |  | 426359 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26359 |  | 426360 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26360 |  | 426361 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26361 |  | 426362 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26362 |  | 426363 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26363 |  | 426364 | DAVR unsupported AC configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26364 |  | 426365 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26365 |  | 426366 | Parameters - Generator - Voltage protections - Under-voltage 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26365 |  | 426366 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26365 |  | 426366 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26366 |  | 426367 | Parameters - Generator - Voltage protections - Under-voltage 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26366 |  | 426367 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26366 |  | 426367 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26367 |  | 426368 | Parameters - Generator - Voltage protections - Under-voltage 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26367 |  | 426368 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26367 |  | 426368 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26368 |  | 426369 | Parameters - Generator - Voltage protections - Over-voltage 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26368 |  | 426369 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26368 |  | 426369 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26369 |  | 426370 | Parameters - Generator - Voltage protections - Over-voltage 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26369 |  | 426370 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26369 |  | 426370 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26370 |  | 426371 | Parameters - Generator - Voltage protections - Voltage unbalance - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26370 |  | 426371 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26370 |  | 426371 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26371 |  | 426372 | Parameters - Generator - Voltage protections - Negative sequence voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26371 |  | 426372 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26371 |  | 426372 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26372 |  | 426373 | Parameters - Generator - Voltage protections - Zero sequence voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26372 |  | 426373 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26372 |  | 426373 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26373 |  | 426374 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26373 |  | 426374 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26373 |  | 426374 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26374 |  | 426375 | Parameters - Generator - Current protections - Over-current 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26374 |  | 426375 | Parameters - Busbar A - Current protections - Over-current 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26374 |  | 426375 | Parameters - Mains - Current protections - Over-current 1 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26375 |  | 426376 | Parameters - Generator - Current protections - Over-current 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26375 |  | 426376 | Parameters - Busbar A - Current protections - Over-current 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26375 |  | 426376 | Parameters - Mains - Current protections - Over-current 2 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26376 |  | 426377 | Parameters - Generator - Current protections - Over-current 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26376 |  | 426377 | Parameters - Busbar A - Current protections - Over-current 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26376 |  | 426377 | Parameters - Mains - Current protections - Over-current 3 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26377 |  | 426378 | Parameters - Generator - Current protections - Over-current 4 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26377 |  | 426378 | Parameters - Busbar A - Current protections - Over-current 4 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26377 |  | 426378 | Parameters - Mains - Current protections - Over-current 4 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26378 |  | 426379 | Parameters - Generator - Current protections - Fast over-current 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26378 |  | 426379 | Parameters - Busbar A - Current protections - Fast over-current 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26378 |  | 426379 | Parameters - Mains - Current protections - Fast over-current 1 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26379 |  | 426380 | Parameters - Generator - Current protections - Fast over-current 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26379 |  | 426380 | Parameters - Busbar A - Current protections - Fast over-current 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26379 |  | 426380 | Parameters - Mains - Current protections - Fast over-current 2 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26380 |  | 426381 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26380 |  | 426381 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26380 |  | 426381 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26381 |  | 426382 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26381 |  | 426382 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26381 |  | 426382 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26382 |  | 426383 | Parameters - Generator - Current protections - Directional over-current 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26382 |  | 426383 | Parameters - Busbar A - Current protections - Directional over-current 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26382 |  | 426383 | Parameters - Mains - Current protections - Directional over-current 1 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26383 |  | 426384 | Parameters - Generator - Current protections - Directional over-current 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26383 |  | 426384 | Parameters - Busbar A - Current protections - Directional over-current 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26383 |  | 426384 | Parameters - Mains - Current protections - Directional over-current 2 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26384 |  | 426385 | Parameters - Busbar A - Current protections - Directional over-current 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26385 |  | 426386 | Parameters - Busbar A - Current protections - Directional over-current 4 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26386 |  | 426387 | Parameters - Generator - Current protections - Negative sequence current - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26386 |  | 426387 | Parameters - Busbar A - Current protections - Negative sequence current - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26386 |  | 426387 | Parameters - Mains - Current protections - Negative sequence current - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26387 |  | 426388 | Parameters - Generator - Current protections - Zero sequence current - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26387 |  | 426388 | Parameters - Busbar A - Current protections - Zero sequence current - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26387 |  | 426388 | Parameters - Mains - Current protections - Zero sequence current - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26388 |  | 426389 | Parameters - Generator - Frequency protections - Over-frequency 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26388 |  | 426389 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26388 |  | 426389 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26389 |  | 426390 | Parameters - Generator - Frequency protections - Over-frequency 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26389 |  | 426390 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26389 |  | 426390 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26390 |  | 426391 | Parameters - Generator - Frequency protections - Over-frequency 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26390 |  | 426391 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26390 |  | 426391 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26391 |  | 426392 | Parameters - Generator - Frequency protections - Under-frequency 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26391 |  | 426392 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26391 |  | 426392 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26392 |  | 426393 | Parameters - Generator - Frequency protections - Under-frequency 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26392 |  | 426393 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26392 |  | 426393 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26393 |  | 426394 | Parameters - Generator - Frequency protections - Under-frequency 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26393 |  | 426394 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26393 |  | 426394 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26394 |  | 426395 | Parameters - Generator - Power protections - Overload 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26394 |  | 426395 | Parameters - Busbar A - Power protections - Power export 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26394 |  | 426395 | Parameters - Mains - Power protections - Overload 1 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26395 |  | 426396 | Parameters - Generator - Power protections - Overload 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26395 |  | 426396 | Parameters - Busbar A - Power protections - Power export 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26395 |  | 426396 | Parameters - Mains - Power protections - Overload 2 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26396 |  | 426397 | Parameters - Generator - Power protections - Overload 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26396 |  | 426397 | Parameters - Busbar A - Power protections - Power export 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26396 |  | 426397 | Parameters - Mains - Power protections - Overload 3 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26397 |  | 426398 | Parameters - Generator - Power protections - Overload 4 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26397 |  | 426398 | Parameters - Busbar A - Power protections - Power export 4 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26397 |  | 426398 | Parameters - Mains - Power protections - Overload 4 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26398 |  | 426399 | Parameters - Generator - Power protections - Overload 5 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26398 |  | 426399 | Parameters - Busbar A - Power protections - Power export 5 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26398 |  | 426399 | Parameters - Mains - Power protections - Overload 5 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26399 |  | 426400 | Parameters - Generator - Power protections - Reverse power 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26399 |  | 426400 | Parameters - Busbar A - Power protections - Power import 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26399 |  | 426400 | Parameters - Mains - Power protections - Reverse power 1 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26400 |  | 426401 | Parameters - Generator - Power protections - Reverse power 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26400 |  | 426401 | Parameters - Busbar A - Power protections - Power import 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26400 |  | 426401 | Parameters - Mains - Power protections - Reverse power 2 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26401 |  | 426402 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26401 |  | 426402 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26401 |  | 426402 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26402 |  | 426403 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26402 |  | 426403 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26402 |  | 426403 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26403 |  | 426404 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26403 |  | 426404 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26403 |  | 426404 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26404 |  | 426405 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26404 |  | 426405 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26404 |  | 426405 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26405 |  | 426406 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26405 |  | 426406 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26405 |  | 426406 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26406 |  | 426407 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26406 |  | 426407 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26406 |  | 426407 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26407 |  | 426408 | Parameters - Mains - Voltage protections - Over-voltage 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26407 |  | 426408 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26407 |  | 426408 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26408 |  | 426409 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26408 |  | 426409 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26408 |  | 426409 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26409 |  | 426410 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26409 |  | 426410 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26409 |  | 426410 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26410 |  | 426411 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26410 |  | 426411 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26410 |  | 426411 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26411 |  | 426412 | Parameters - Mains - Voltage protections - Under-voltage 4 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26411 |  | 426412 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26411 |  | 426412 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26412 |  | 426413 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26412 |  | 426413 | Parameters - Busbar - Voltage protections - Voltage unbalance - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26412 |  | 426413 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26413 |  | 426414 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26413 |  | 426414 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26413 |  | 426414 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26414 |  | 426415 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26414 |  | 426415 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26414 |  | 426415 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26415 |  | 426416 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26415 |  | 426416 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26415 |  | 426416 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26416 |  | 426417 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26416 |  | 426417 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26416 |  | 426417 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26417 |  | 426418 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26417 |  | 426418 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26417 |  | 426418 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26418 |  | 426419 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26418 |  | 426419 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26418 |  | 426419 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26419 |  | 426420 | Parameters - Mains - Frequency protections - Under-frequency 4 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26419 |  | 426420 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26419 |  | 426420 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26420 |  | 426421 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26420 |  | 426421 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26420 |  | 426421 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26421 |  | 426422 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26421 |  | 426422 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26421 |  | 426422 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26422 |  | 426423 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26422 |  | 426423 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Action | 26422 |  | 426423 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26467 |  | 426468 | Parameters - Engine - Maintenance - Service timer - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26468 |  | 426469 | Parameters - Engine - Maintenance - Service timer - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26469 |  | 426470 | Parameters - Engine - Maintenance - Service timer - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26470 |  | 426471 | Parameters - Engine - Maintenance - Service timer - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26471 |  | 426472 | External MB open failure - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26472 |  | 426473 | Parameters - Power management rules - Ground relay - Ground relay general failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26473 |  | 426474 | Parameters - Power management rules - Ground relay - Ground relay open failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26474 |  | 426475 | Parameters - Power management rules - Ground relay - Ground relay close failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26475 |  | 426476 | Parameters - Power management rules - Ground relay - Ground relay position failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26476 |  | 426477 | Parameters - Breakers - Close before excitation - CBE rerun failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26477 |  | 426478 | Parameters - Breakers - Close before excitation - CBE failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26478 |  | 426479 | Load too high - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26479 |  | 426480 | ID to run configuration failure - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26481 |  | 426482 | Parameters - System - Monitoring - Missing any genset controller - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26482 |  | 426483 | Parameters - System - Monitoring - Missing any mains controller - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26483 |  | 426484 | Parameters - System - Monitoring - Missing any bustie controller - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26484 |  | 426485 | Can ID not available - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26485 |  | 426486 | Duplicated CAN IDs - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26486 |  | 426487 | Parameters - Local power management - Alarms - Busbar blocked - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26487 |  | 426488 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26488 |  | 426489 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26489 |  | 426490 | Parameters - System - Monitoring - BTB 33 position failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26490 |  | 426491 | Parameters - System - Monitoring - BTB 34 position failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26491 |  | 426492 | Parameters - System - Monitoring - BTB 35 position failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26492 |  | 426493 | Parameters - System - Monitoring - BTB 36 position failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26493 |  | 426494 | Parameters - System - Monitoring - BTB 37 position failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26494 |  | 426495 | Parameters - System - Monitoring - BTB 38 position failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26495 |  | 426496 | Parameters - System - Monitoring - BTB 39 position failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26496 |  | 426497 | Parameters - System - Monitoring - BTB 40 position failure - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26497 |  | 426498 | Primary CAN missing ID 1 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26498 |  | 426499 | Primary CAN missing ID 2 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26499 |  | 426500 | Primary CAN missing ID 3 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26500 |  | 426501 | Primary CAN missing ID 4 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26501 |  | 426502 | Primary CAN missing ID 5 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26502 |  | 426503 | Primary CAN missing ID 6 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26503 |  | 426504 | Primary CAN missing ID 7 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26504 |  | 426505 | Primary CAN missing ID 8 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26505 |  | 426506 | Primary CAN missing ID 9 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26506 |  | 426507 | Primary CAN missing ID 10 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26507 |  | 426508 | Primary CAN missing ID 11 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26508 |  | 426509 | Primary CAN missing ID 12 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26509 |  | 426510 | Primary CAN missing ID 13 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26510 |  | 426511 | Primary CAN missing ID 14 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26511 |  | 426512 | Primary CAN missing ID 15 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26512 |  | 426513 | Primary CAN missing ID 16 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26513 |  | 426514 | Primary CAN missing ID 17 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26514 |  | 426515 | Primary CAN missing ID 18 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26515 |  | 426516 | Primary CAN missing ID 19 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26516 |  | 426517 | Primary CAN missing ID 20 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26517 |  | 426518 | Primary CAN missing ID 21 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26518 |  | 426519 | Primary CAN missing ID 22 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26519 |  | 426520 | Primary CAN missing ID 23 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26520 |  | 426521 | Primary CAN missing ID 24 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26521 |  | 426522 | Primary CAN missing ID 25 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26522 |  | 426523 | Primary CAN missing ID 26 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26523 |  | 426524 | Primary CAN missing ID 27 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26524 |  | 426525 | Primary CAN missing ID 28 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26525 |  | 426526 | Primary CAN missing ID 29 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26526 |  | 426527 | Primary CAN missing ID 30 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26527 |  | 426528 | Primary CAN missing ID 31 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26528 |  | 426529 | Primary CAN missing ID 32 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26529 |  | 426530 | Primary CAN missing ID 33 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26530 |  | 426531 | Primary CAN missing ID 34 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26531 |  | 426532 | Primary CAN missing ID 35 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26532 |  | 426533 | Primary CAN missing ID 36 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26533 |  | 426534 | Primary CAN missing ID 37 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26534 |  | 426535 | Primary CAN missing ID 38 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26535 |  | 426536 | Primary CAN missing ID 39 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26536 |  | 426537 | Primary CAN missing ID 40 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26537 |  | 426538 | Secondary CAN missing ID 1 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26538 |  | 426539 | Secondary CAN missing ID 2 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26539 |  | 426540 | Secondary CAN missing ID 3 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26540 |  | 426541 | Secondary CAN missing ID 4 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26541 |  | 426542 | Secondary CAN missing ID 5 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26542 |  | 426543 | Secondary CAN missing ID 6 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26543 |  | 426544 | Secondary CAN missing ID 7 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26544 |  | 426545 | Secondary CAN missing ID 8 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26545 |  | 426546 | Secondary CAN missing ID 9 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26546 |  | 426547 | Secondary CAN missing ID 10 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26547 |  | 426548 | Secondary CAN missing ID 11 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26548 |  | 426549 | Secondary CAN missing ID 12 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26549 |  | 426550 | Secondary CAN missing ID 13 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26550 |  | 426551 | Secondary CAN missing ID 14 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26551 |  | 426552 | Secondary CAN missing ID 15 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26552 |  | 426553 | Secondary CAN missing ID 16 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26553 |  | 426554 | Secondary CAN missing ID 17 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26554 |  | 426555 | Secondary CAN missing ID 18 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26555 |  | 426556 | Secondary CAN missing ID 19 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26556 |  | 426557 | Secondary CAN missing ID 20 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26557 |  | 426558 | Secondary CAN missing ID 21 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26558 |  | 426559 | Secondary CAN missing ID 22 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26559 |  | 426560 | Secondary CAN missing ID 23 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26560 |  | 426561 | Secondary CAN missing ID 24 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26561 |  | 426562 | Secondary CAN missing ID 25 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26562 |  | 426563 | Secondary CAN missing ID 26 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26563 |  | 426564 | Secondary CAN missing ID 27 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26564 |  | 426565 | Secondary CAN missing ID 28 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26565 |  | 426566 | Secondary CAN missing ID 29 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26566 |  | 426567 | Secondary CAN missing ID 30 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26567 |  | 426568 | Secondary CAN missing ID 31 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26568 |  | 426569 | Secondary CAN missing ID 32 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26569 |  | 426570 | Secondary CAN missing ID 33 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26570 |  | 426571 | Secondary CAN missing ID 34 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26571 |  | 426572 | Secondary CAN missing ID 35 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26572 |  | 426573 | Secondary CAN missing ID 36 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26573 |  | 426574 | Secondary CAN missing ID 37 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26574 |  | 426575 | Secondary CAN missing ID 38 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26575 |  | 426576 | Secondary CAN missing ID 39 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26576 |  | 426577 | Secondary CAN missing ID 40 - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26577 |  | 426578 | Priority error - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26578 |  | 426579 | Parameters - Non-essential load trip - Trip 1 - Over-current - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26579 |  | 426580 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26580 |  | 426581 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26581 |  | 426582 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26582 |  | 426583 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26583 |  | 426584 | Parameters - Non-essential load trip - Trip 2 - Over-current - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26584 |  | 426585 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26585 |  | 426586 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26586 |  | 426587 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26587 |  | 426588 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26588 |  | 426589 | Parameters - Non-essential load trip - Trip 3 - Over-current - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26589 |  | 426590 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26590 |  | 426591 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26591 |  | 426592 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26592 |  | 426593 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Action | 26593 |  | 426594 | Parameters - System - Monitoring - Single-line hazard - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26594 |  | 426595 | ID not present - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26595 |  | 426596 | Unsupported application - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26596 |  | 426597 | Application internal CAN protocol conflict - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26597 |  | 426598 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26598 |  | 426599 | Dry mode: Voltage level unexpected - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26599 |  | 426600 | Invalid DAVR configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26600 |  | 426601 | Parameters - Communication - DEIF network - DEIF network fork detected - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26602 |  | 426603 | Parameters - Communication - DEIF network - DEIF network has only one connection - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26604 |  | 426605 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26604 |  | 426605 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Configuration - Action | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Action | 26604 |  | 426605 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Action | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Action | 26605 |  | 426606 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Action | 26605 |  | 426606 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Configuration - Action | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Action | 26607 |  | 426608 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26608 |  | 426609 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26609 |  | 426610 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26610 |  | 426611 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26611 |  | 426612 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26612 |  | 426613 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26613 |  | 426614 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26614 |  | 426615 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26615 |  | 426616 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26616 |  | 426617 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26617 |  | 426618 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26618 |  | 426619 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26619 |  | 426620 | AC protections not running - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26620 |  | 426621 | AC data is missing - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26621 |  | 426622 | AC protections not running - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26622 |  | 426623 | AC data is missing - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26623 |  | 426624 | AC protections not running - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26624 |  | 426625 | AC data is missing - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26625 |  | 426626 | AC protections not running - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26626 |  | 426627 | AC data is missing - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26627 |  | 426628 | Live voltage detected - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26628 |  | 426629 | Internal issue detected. A restart is required soon! - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26629 |  | 426630 | Parameters - System - Monitoring - Missing controllers - Configuration - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26630 |  | 426631 | Card issue detected - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26631 |  | 426632 | Card configuration failed - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26632 |  | 426633 | Unknown traffic on DEIF network - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26633 |  | 426634 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26634 |  | 426635 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26635 |  | 426636 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Configuration - Action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Action | 26636 |  | 426637 | Local IO service error - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26637 |  | 426638 | App logging failure - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26638 |  | 426639 | Event logging failure - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26639 |  | 426640 | Licence error - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26640 |  | 426641 | Brightness is dimmed according to temperature - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 26641 |  | 426642 | Parameters - Grid code - Mains sync inhibit - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26642 |  | 426643 | Parameters - Grid code - Capability curve - Import protection - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26643 |  | 426644 | Parameters - Grid code - Capability curve - Export protection - Configuration - Action | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Action | 26644 |  | 426645 | Hardware is not compatible based on module versions - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27500 |  | 427501 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27501 |  | 427502 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27502 |  | 427503 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27503 |  | 427504 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27504 |  | 427505 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27505 |  | 427506 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27506 |  | 427507 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27507 |  | 427508 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27508 |  | 427509 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27509 |  | 427510 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27510 |  | 427511 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27511 |  | 427512 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27512 |  | 427513 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27513 |  | 427514 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27514 |  | 427515 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27515 |  | 427516 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27516 |  | 427517 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27517 |  | 427518 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27518 |  | 427519 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27519 |  | 427520 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27520 |  | 427521 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27521 |  | 427522 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27522 |  | 427523 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27523 |  | 427524 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27524 |  | 427525 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27525 |  | 427526 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27526 |  | 427527 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27527 |  | 427528 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27528 |  | 427529 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27529 |  | 427530 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27530 |  | 427531 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27531 |  | 427532 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27532 |  | 427533 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27533 |  | 427534 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27534 |  | 427535 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27535 |  | 427536 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27536 |  | 427537 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27537 |  | 427538 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27538 |  | 427539 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27539 |  | 427540 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27540 |  | 427541 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27541 |  | 427542 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27542 |  | 427543 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27543 |  | 427544 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27544 |  | 427545 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27545 |  | 427546 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27546 |  | 427547 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27547 |  | 427548 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27548 |  | 427549 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27549 |  | 427550 | Digital custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27600 |  | 427601 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27601 |  | 427602 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27602 |  | 427603 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27603 |  | 427604 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27604 |  | 427605 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27605 |  | 427606 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27606 |  | 427607 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27607 |  | 427608 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27608 |  | 427609 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27609 |  | 427610 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27610 |  | 427611 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27611 |  | 427612 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27612 |  | 427613 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27613 |  | 427614 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27614 |  | 427615 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27615 |  | 427616 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27616 |  | 427617 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27617 |  | 427618 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27618 |  | 427619 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27619 |  | 427620 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27620 |  | 427621 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27621 |  | 427622 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27622 |  | 427623 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27623 |  | 427624 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27624 |  | 427625 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27625 |  | 427626 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27626 |  | 427627 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27627 |  | 427628 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27628 |  | 427629 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27629 |  | 427630 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27630 |  | 427631 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27631 |  | 427632 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27632 |  | 427633 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27633 |  | 427634 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27634 |  | 427635 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27635 |  | 427636 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27636 |  | 427637 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27637 |  | 427638 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27638 |  | 427639 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27639 |  | 427640 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27640 |  | 427641 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27641 |  | 427642 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27642 |  | 427643 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27643 |  | 427644 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27644 |  | 427645 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27645 |  | 427646 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27646 |  | 427647 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27647 |  | 427648 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27648 |  | 427649 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27649 |  | 427650 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27650 |  | 427651 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27651 |  | 427652 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27652 |  | 427653 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27653 |  | 427654 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27654 |  | 427655 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27655 |  | 427656 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27656 |  | 427657 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27657 |  | 427658 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27658 |  | 427659 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27659 |  | 427660 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27660 |  | 427661 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27661 |  | 427662 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27662 |  | 427663 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27663 |  | 427664 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27664 |  | 427665 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27665 |  | 427666 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27666 |  | 427667 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27667 |  | 427668 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27668 |  | 427669 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27669 |  | 427670 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27670 |  | 427671 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27671 |  | 427672 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27672 |  | 427673 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27673 |  | 427674 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27674 |  | 427675 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27675 |  | 427676 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27676 |  | 427677 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27677 |  | 427678 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27678 |  | 427679 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27679 |  | 427680 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27680 |  | 427681 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27681 |  | 427682 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27682 |  | 427683 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27683 |  | 427684 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27684 |  | 427685 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27685 |  | 427686 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27686 |  | 427687 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27687 |  | 427688 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27688 |  | 427689 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27689 |  | 427690 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27690 |  | 427691 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27691 |  | 427692 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27692 |  | 427693 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27693 |  | 427694 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27694 |  | 427695 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27695 |  | 427696 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27696 |  | 427697 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27697 |  | 427698 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27698 |  | 427699 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27699 |  | 427700 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27700 |  | 427701 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27701 |  | 427702 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27702 |  | 427703 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27703 |  | 427704 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27704 |  | 427705 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27705 |  | 427706 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27706 |  | 427707 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27707 |  | 427708 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27708 |  | 427709 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27709 |  | 427710 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27710 |  | 427711 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27711 |  | 427712 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27712 |  | 427713 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27713 |  | 427714 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27714 |  | 427715 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27715 |  | 427716 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27716 |  | 427717 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27717 |  | 427718 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27718 |  | 427719 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27719 |  | 427720 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27720 |  | 427721 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27721 |  | 427722 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27722 |  | 427723 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27723 |  | 427724 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27724 |  | 427725 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27725 |  | 427726 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27726 |  | 427727 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27727 |  | 427728 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27728 |  | 427729 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27729 |  | 427730 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27730 |  | 427731 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27731 |  | 427732 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27732 |  | 427733 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27733 |  | 427734 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27734 |  | 427735 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27735 |  | 427736 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27736 |  | 427737 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27737 |  | 427738 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27738 |  | 427739 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27739 |  | 427740 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27740 |  | 427741 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27741 |  | 427742 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27742 |  | 427743 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27743 |  | 427744 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27744 |  | 427745 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27745 |  | 427746 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27746 |  | 427747 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27747 |  | 427748 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27748 |  | 427749 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27749 |  | 427750 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27750 |  | 427751 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27751 |  | 427752 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27752 |  | 427753 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27753 |  | 427754 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27754 |  | 427755 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27755 |  | 427756 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27756 |  | 427757 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27757 |  | 427758 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27758 |  | 427759 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27759 |  | 427760 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27760 |  | 427761 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27761 |  | 427762 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27762 |  | 427763 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27763 |  | 427764 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27764 |  | 427765 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27765 |  | 427766 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27766 |  | 427767 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27767 |  | 427768 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27768 |  | 427769 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27769 |  | 427770 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27770 |  | 427771 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27771 |  | 427772 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27772 |  | 427773 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27773 |  | 427774 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27774 |  | 427775 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27775 |  | 427776 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27776 |  | 427777 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27777 |  | 427778 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27778 |  | 427779 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27779 |  | 427780 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27780 |  | 427781 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27781 |  | 427782 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27782 |  | 427783 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27783 |  | 427784 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27784 |  | 427785 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27785 |  | 427786 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27786 |  | 427787 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27787 |  | 427788 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27788 |  | 427789 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27789 |  | 427790 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27790 |  | 427791 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27791 |  | 427792 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27792 |  | 427793 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27793 |  | 427794 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27794 |  | 427795 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27795 |  | 427796 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27796 |  | 427797 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27797 |  | 427798 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27798 |  | 427799 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Action | 27799 |  | 427800 | Analogue custom alarm - Action | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28000 |  | 428001 | Application initialisation error - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28001 |  | 428002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28002 |  | 428003 | Preliminary software - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28003 |  | 428004 | Parameters - Engine - Stop sequence - Stop failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28004 |  | 428005 | Parameters - Engine - Start sequence - Start failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28005 |  | 428006 | Parameters - Engine - Start sequence - Crank failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28006 |  | 428007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28007 |  | 428008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28008 |  | 428009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28009 |  | 428010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28010 |  | 428011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28011 |  | 428012 | Parameters - Engine - Stop sequence - Externally stopped - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28013 |  | 428014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28014 |  | 428015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28015 |  | 428016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28016 |  | 428017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28017 |  | 428018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28018 |  | 428019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28019 |  | 428020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28020 |  | 428021 | Parameters - Engine - Protections - Level - Coolant level 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28021 |  | 428022 | Parameters - Engine - Protections - Level - Coolant level 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28022 |  | 428023 | Parameters - Engine - Protections - Level - Coolant level 3 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28027 |  | 428028 | Parameters - Engine - Running detection - Primary running feedback failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28041 |  | 428042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28041 |  | 428042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28041 |  | 428042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28042 |  | 428043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28042 |  | 428043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28042 |  | 428043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28043 |  | 428044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28043 |  | 428044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28043 |  | 428044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28044 |  | 428045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28044 |  | 428045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28044 |  | 428045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28045 |  | 428046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28045 |  | 428046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28045 |  | 428046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28046 |  | 428047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28046 |  | 428047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28046 |  | 428047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28047 |  | 428048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28047 |  | 428048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28047 |  | 428048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28048 |  | 428049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28048 |  | 428049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28048 |  | 428049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28049 |  | 428050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Configuration | 28049 |  | 428050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Configuration | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Configuration | 28050 |  | 428051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Configuration | 28050 |  | 428051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Configuration | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Configuration | 28051 |  | 428052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Configuration | 28051 |  | 428052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Configuration | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Configuration | 28052 |  | 428053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Configuration | 28052 |  | 428053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Configuration | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Configuration | 28053 |  | 428054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Configuration | 28053 |  | 428054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Configuration | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Configuration | 28054 |  | 428055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Configuration | 28054 |  | 428055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Configuration | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Configuration | 28055 |  | 428056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Configuration | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Configuration | 28055 |  | 428056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Configuration | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Configuration | 28056 |  | 428057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Configuration | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Configuration | 28056 |  | 428057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Configuration | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Configuration | 28060 |  | 428061 | Parameters - Mains - AC setup - Phase sequence error - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28060 |  | 428061 | Parameters - Busbar - AC setup - Phase sequence error - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28060 |  | 428061 | Parameters - Busbar B - AC setup - Phase sequence error - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28061 |  | 428062 | Parameters - Generator - AC setup - Phase sequence error - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28061 |  | 428062 | Parameters - Busbar A - AC setup - Phase sequence error - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28061 |  | 428062 | Parameters - Mains - AC setup - Phase sequence error - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28062 |  | 428063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28103 |  | 428104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28103 |  | 428104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28103 |  | 428104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28104 |  | 428105 | Parameters - Mains - Additional protections - Vector shift - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28104 |  | 428105 | Parameters - Busbar - Additional protections - Vector shift - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28104 |  | 428105 | Parameters - Busbar B - Additional protections - Vector shift - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28105 |  | 428106 | Parameters - Generator - Current protections - Inverse time over-current - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28105 |  | 428106 | Parameters - Busbar A - Current protections - Inverse time over-current - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28105 |  | 428106 | Parameters - Mains - Current protections - Inverse time over-current - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28106 |  | 428107 | Parameters - Local - 4th current input - Earth inverse time over-current - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28107 |  | 428108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28108 |  | 428109 | Parameters - Generator - Additional protections - V< and Q< 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28108 |  | 428109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28108 |  | 428109 | Parameters - Mains - Additional protections - V< and Q< 1 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28109 |  | 428110 | Parameters - Generator - Additional protections - V< and Q< 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28109 |  | 428110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28109 |  | 428110 | Parameters - Mains - Additional protections - V< and Q< 2 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28110 |  | 428111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28110 |  | 428111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28110 |  | 428111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28111 |  | 428112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28111 |  | 428112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28111 |  | 428112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28115 |  | 428116 | Protection set point out of range - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28116 |  | 428117 | Parameters - Generator - Current protections - Stabilised differential current - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28117 |  | 428118 | Parameters - Generator - Current protections - High set differential current - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28118 |  | 428119 | Protection set point out of range (differential current) - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28119 |  | 428120 | Parameters - Local - Mode - Not under remote control - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28121 |  | 428122 | Parameters - Local - Monitoring - System not OK - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28122 |  | 428123 | Configuration update delayed - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28123 |  | 428124 | Critical process error - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28124 |  | 428125 | Restore error - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28125 |  | 428126 | SD-card format error - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28126 |  | 428127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28127 |  | 428128 | Fieldbus configuration exceeded maximum I/O configuration - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28128 |  | 428129 | Parameters - Custom alarm - Custom alarm 0 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28129 |  | 428130 | Parameters - Custom alarm - Custom alarm 1 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28130 |  | 428131 | Parameters - Custom alarm - Custom alarm 2 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28131 |  | 428132 | Parameters - Custom alarm - Custom alarm 3 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28132 |  | 428133 | Parameters - Custom alarm - Custom alarm 4 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28133 |  | 428134 | Parameters - Custom alarm - Custom alarm 5 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28134 |  | 428135 | Parameters - Custom alarm - Custom alarm 6 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28135 |  | 428136 | Parameters - Custom alarm - Custom alarm 7 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28136 |  | 428137 | Parameters - Custom alarm - Custom alarm 8 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28137 |  | 428138 | Parameters - Custom alarm - Custom alarm 9 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28138 |  | 428139 | Parameters - Custom alarm - Custom alarm 10 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28139 |  | 428140 | Parameters - Custom alarm - Custom alarm 11 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28140 |  | 428141 | Parameters - Custom alarm - Custom alarm 12 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28141 |  | 428142 | Parameters - Custom alarm - Custom alarm 13 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28142 |  | 428143 | Parameters - Custom alarm - Custom alarm 14 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28143 |  | 428144 | Parameters - Custom alarm - Custom alarm 15 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28144 |  | 428145 | Parameters - Custom alarm - Custom alarm 16 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28145 |  | 428146 | Parameters - Custom alarm - Custom alarm 17 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28146 |  | 428147 | Parameters - Custom alarm - Custom alarm 18 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28147 |  | 428148 | Parameters - Custom alarm - Custom alarm 19 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28148 |  | 428149 | Parameters - Custom alarm - Custom alarm 20 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28149 |  | 428150 | Parameters - Custom alarm - Custom alarm 21 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28150 |  | 428151 | Parameters - Custom alarm - Custom alarm 22 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28151 |  | 428152 | Parameters - Custom alarm - Custom alarm 23 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28152 |  | 428153 | Parameters - Custom alarm - Custom alarm 24 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28153 |  | 428154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28154 |  | 428155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28163 |  | 428164 | Required hardware card(s) not found - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28164 |  | 428165 | Software mismatch on hardware module(s) - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28165 |  | 428166 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Configuration | 28165 |  | 428166 | Parameters - Busbar - AC setup - Multiple phase wire break - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Configuration | 28165 |  | 428166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28166 |  | 428167 | Parameters - Generator - AC setup - Multiple phase wire break - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Configuration | 28166 |  | 428167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28166 |  | 428167 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Configuration | 28167 |  | 428168 | Parameters - Mains - AC setup - L1 wire break - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Configuration | 28167 |  | 428168 | Parameters - Busbar - AC setup - L1 wire break - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Configuration | 28167 |  | 428168 | Parameters - Busbar B - AC setup - L1 wire break - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28168 |  | 428169 | Parameters - Mains - AC setup - L2 wire break - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Configuration | 28168 |  | 428169 | Parameters - Busbar - AC setup - L2 wire break - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Configuration | 28168 |  | 428169 | Parameters - Busbar B - AC setup - L2 wire break - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28169 |  | 428170 | Parameters - Mains - AC setup - L3 wire break - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Configuration | 28169 |  | 428170 | Parameters - Busbar - AC setup - L3 wire break - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Configuration | 28169 |  | 428170 | Parameters - Busbar B - AC setup - L3 wire break - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28170 |  | 428171 | Parameters - Generator - AC setup - L1 wire break - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Configuration | 28170 |  | 428171 | Parameters - Busbar A - AC setup - L1 wire break - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28170 |  | 428171 | Parameters - Mains - AC setup - L1 wire break - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Configuration | 28171 |  | 428172 | Parameters - Generator - AC setup - L2 wire break - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Configuration | 28171 |  | 428172 | Parameters - Busbar A - AC setup - L2 wire break - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28171 |  | 428172 | Parameters - Mains - AC setup - L2 wire break - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Configuration | 28172 |  | 428173 | Parameters - Generator - AC setup - L3 wire break - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Configuration | 28172 |  | 428173 | Parameters - Busbar A - AC setup - L3 wire break - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28172 |  | 428173 | Parameters - Mains - AC setup - L3 wire break - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Configuration | 28178 |  | 428179 | Parameters - Mains - AC setup - Supervision alarm - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X |  | X | X
Alarm parameter: Configuration | 28179 |  | 428180 | Parameters - Engine - Emergency stop - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28179 |  | 428180 | Parameters - Busbar A - Emergency stop - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28179 |  | 428180 | Parameters - Mains - Emergency stop - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28180 |  | 428181 | Clock battery failure - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28181 |  | 428182 | Controller temperature too high - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28182 |  | 428183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28183 |  | 428184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28184 |  | 428185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28185 |  | 428186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28186 |  | 428187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28187 |  | 428188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28188 |  | 428189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28189 |  | 428190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28190 |  | 428191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28191 |  | 428192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28192 |  | 428193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28193 |  | 428194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28194 |  | 428195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28195 |  | 428196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28196 |  | 428197 | EIM3.1 4 supply voltage high - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28197 |  | 428198 | EIM3.1 4 supply voltage low or missing - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28198 |  | 428199 | EIM3.1 5 supply voltage high - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28199 |  | 428200 | EIM3.1 5 supply voltage low or missing - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28200 |  | 428201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28201 |  | 428202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28202 |  | 428203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28203 |  | 428204 | EIM3.1 4 relay 4 wire break - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28204 |  | 428205 | EIM3.1 5 relay 4 wire break - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28205 |  | 428206 | AC protections not running - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28206 |  | 428207 | AC data is missing - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28207 |  | 428208 | AC protections not running (differential current) - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28208 |  | 428209 | AC data is missing (differential current) - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28209 |  | 428210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28210 |  | 428211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28211 |  | 428212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28212 |  | 428213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28213 |  | 428214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28214 |  | 428215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28215 |  | 428216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28216 |  | 428217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28217 |  | 428218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28218 |  | 428219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28219 |  | 428220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28220 |  | 428221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28221 |  | 428222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28222 |  | 428223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28223 |  | 428224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28224 |  | 428225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28225 |  | 428226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28226 |  | 428227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28228 |  | 428229 | Parameters - System - Monitoring - Duplicate controller ID - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28229 |  | 428230 | Parameters - System - Monitoring - Missing all controllers - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28231 |  | 428232 | Controller ID not configured - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28236 |  | 428237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28237 |  | 428238 | Blackout detection mismatch - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28240 |  | 428241 | Parameters - Communication - NTP - NTP server 1 not connected - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28241 |  | 428242 | Parameters - Communication - NTP - NTP server 1 no response - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28242 |  | 428243 | Parameters - Communication - NTP - NTP server 2 not connected - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28243 |  | 428244 | Parameters - Communication - NTP - NTP server 2 no response - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28244 |  | 428245 | Parameters - Communication - NTP - No NTP server time synchronisation - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28245 |  | 428246 | Parameters - Communication - NTP - No NTP server(s) connected - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28246 |  | 428247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28247 |  | 428248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28296 |  | 428297 | Controller not part of system - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28297 |  | 428298 | Different single-line configurations - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28298 |  | 428299 | Single-line missing/none active - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28299 |  | 428300 | Parameters - Communication - Modbus - Modbus communication timeout - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28300 |  | 428301 | Parameters - CODESYS - Monitoring - I/O config conflict - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28301 |  | 428302 | Parameters - CODESYS - Monitoring - Application not OK - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28302 |  | 428303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28303 |  | 428304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28304 |  | 428305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28305 |  | 428306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28306 |  | 428307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28307 |  | 428308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28308 |  | 428309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28309 |  | 428310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28310 |  | 428311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28311 |  | 428312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28312 |  | 428313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28315 |  | 428316 | Parameters - Local - CustomLogic - Configuration invalid - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28316 |  | 428317 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28317 |  | 428318 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28318 |  | 428319 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28319 |  | 428320 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28320 |  | 428321 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28321 |  | 428322 | Parameters - Generator - Digital AVR - Alarms - Open diode - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28322 |  | 428323 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28323 |  | 428324 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28324 |  | 428325 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28325 |  | 428326 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28326 |  | 428327 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28327 |  | 428328 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28328 |  | 428329 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28329 |  | 428330 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28330 |  | 428331 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28331 |  | 428332 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28332 |  | 428333 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28333 |  | 428334 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28334 |  | 428335 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28335 |  | 428336 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28336 |  | 428337 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28337 |  | 428338 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28338 |  | 428339 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28339 |  | 428340 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28340 |  | 428341 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28341 |  | 428342 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28342 |  | 428343 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28343 |  | 428344 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28344 |  | 428345 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28345 |  | 428346 | Parameters - Generator - Digital AVR - Alarms - Motor start - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28346 |  | 428347 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28347 |  | 428348 | Parameters - Generator - Digital AVR - Alarms - Power supply - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28348 |  | 428349 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28349 |  | 428350 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28350 |  | 428351 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28351 |  | 428352 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28352 |  | 428353 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28353 |  | 428354 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28354 |  | 428355 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28355 |  | 428356 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28356 |  | 428357 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28357 |  | 428358 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28358 |  | 428359 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28359 |  | 428360 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28360 |  | 428361 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28361 |  | 428362 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28362 |  | 428363 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28363 |  | 428364 | DAVR unsupported AC configuration - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28364 |  | 428365 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28365 |  | 428366 | Parameters - Generator - Voltage protections - Under-voltage 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28365 |  | 428366 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28365 |  | 428366 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28366 |  | 428367 | Parameters - Generator - Voltage protections - Under-voltage 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28366 |  | 428367 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28366 |  | 428367 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28367 |  | 428368 | Parameters - Generator - Voltage protections - Under-voltage 3 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28367 |  | 428368 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28367 |  | 428368 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28368 |  | 428369 | Parameters - Generator - Voltage protections - Over-voltage 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28368 |  | 428369 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28368 |  | 428369 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28369 |  | 428370 | Parameters - Generator - Voltage protections - Over-voltage 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28369 |  | 428370 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28369 |  | 428370 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28370 |  | 428371 | Parameters - Generator - Voltage protections - Voltage unbalance - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28370 |  | 428371 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28370 |  | 428371 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28371 |  | 428372 | Parameters - Generator - Voltage protections - Negative sequence voltage - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28371 |  | 428372 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28371 |  | 428372 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28372 |  | 428373 | Parameters - Generator - Voltage protections - Zero sequence voltage - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28372 |  | 428373 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28372 |  | 428373 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28373 |  | 428374 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28373 |  | 428374 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28373 |  | 428374 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28374 |  | 428375 | Parameters - Generator - Current protections - Over-current 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28374 |  | 428375 | Parameters - Busbar A - Current protections - Over-current 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28374 |  | 428375 | Parameters - Mains - Current protections - Over-current 1 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28375 |  | 428376 | Parameters - Generator - Current protections - Over-current 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28375 |  | 428376 | Parameters - Busbar A - Current protections - Over-current 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28375 |  | 428376 | Parameters - Mains - Current protections - Over-current 2 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28376 |  | 428377 | Parameters - Generator - Current protections - Over-current 3 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28376 |  | 428377 | Parameters - Busbar A - Current protections - Over-current 3 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28376 |  | 428377 | Parameters - Mains - Current protections - Over-current 3 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28377 |  | 428378 | Parameters - Generator - Current protections - Over-current 4 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28377 |  | 428378 | Parameters - Busbar A - Current protections - Over-current 4 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28377 |  | 428378 | Parameters - Mains - Current protections - Over-current 4 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28378 |  | 428379 | Parameters - Generator - Current protections - Fast over-current 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28378 |  | 428379 | Parameters - Busbar A - Current protections - Fast over-current 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28378 |  | 428379 | Parameters - Mains - Current protections - Fast over-current 1 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28379 |  | 428380 | Parameters - Generator - Current protections - Fast over-current 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28379 |  | 428380 | Parameters - Busbar A - Current protections - Fast over-current 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28379 |  | 428380 | Parameters - Mains - Current protections - Fast over-current 2 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28380 |  | 428381 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28380 |  | 428381 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28380 |  | 428381 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28381 |  | 428382 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28381 |  | 428382 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28381 |  | 428382 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28382 |  | 428383 | Parameters - Generator - Current protections - Directional over-current 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28382 |  | 428383 | Parameters - Busbar A - Current protections - Directional over-current 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28382 |  | 428383 | Parameters - Mains - Current protections - Directional over-current 1 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28383 |  | 428384 | Parameters - Generator - Current protections - Directional over-current 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28383 |  | 428384 | Parameters - Busbar A - Current protections - Directional over-current 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28383 |  | 428384 | Parameters - Mains - Current protections - Directional over-current 2 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28384 |  | 428385 | Parameters - Busbar A - Current protections - Directional over-current 3 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28385 |  | 428386 | Parameters - Busbar A - Current protections - Directional over-current 4 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28386 |  | 428387 | Parameters - Generator - Current protections - Negative sequence current - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28386 |  | 428387 | Parameters - Busbar A - Current protections - Negative sequence current - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28386 |  | 428387 | Parameters - Mains - Current protections - Negative sequence current - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28387 |  | 428388 | Parameters - Generator - Current protections - Zero sequence current - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28387 |  | 428388 | Parameters - Busbar A - Current protections - Zero sequence current - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28387 |  | 428388 | Parameters - Mains - Current protections - Zero sequence current - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28388 |  | 428389 | Parameters - Generator - Frequency protections - Over-frequency 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28388 |  | 428389 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28388 |  | 428389 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28389 |  | 428390 | Parameters - Generator - Frequency protections - Over-frequency 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28389 |  | 428390 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28389 |  | 428390 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28390 |  | 428391 | Parameters - Generator - Frequency protections - Over-frequency 3 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28390 |  | 428391 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28390 |  | 428391 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28391 |  | 428392 | Parameters - Generator - Frequency protections - Under-frequency 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28391 |  | 428392 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28391 |  | 428392 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28392 |  | 428393 | Parameters - Generator - Frequency protections - Under-frequency 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28392 |  | 428393 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28392 |  | 428393 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28393 |  | 428394 | Parameters - Generator - Frequency protections - Under-frequency 3 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28393 |  | 428394 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28393 |  | 428394 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28394 |  | 428395 | Parameters - Generator - Power protections - Overload 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28394 |  | 428395 | Parameters - Busbar A - Power protections - Power export 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28394 |  | 428395 | Parameters - Mains - Power protections - Overload 1 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28395 |  | 428396 | Parameters - Generator - Power protections - Overload 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28395 |  | 428396 | Parameters - Busbar A - Power protections - Power export 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28395 |  | 428396 | Parameters - Mains - Power protections - Overload 2 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28396 |  | 428397 | Parameters - Generator - Power protections - Overload 3 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28396 |  | 428397 | Parameters - Busbar A - Power protections - Power export 3 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28396 |  | 428397 | Parameters - Mains - Power protections - Overload 3 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28397 |  | 428398 | Parameters - Generator - Power protections - Overload 4 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28397 |  | 428398 | Parameters - Busbar A - Power protections - Power export 4 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28397 |  | 428398 | Parameters - Mains - Power protections - Overload 4 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28398 |  | 428399 | Parameters - Generator - Power protections - Overload 5 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28398 |  | 428399 | Parameters - Busbar A - Power protections - Power export 5 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28398 |  | 428399 | Parameters - Mains - Power protections - Overload 5 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28399 |  | 428400 | Parameters - Generator - Power protections - Reverse power 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28399 |  | 428400 | Parameters - Busbar A - Power protections - Power import 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28399 |  | 428400 | Parameters - Mains - Power protections - Reverse power 1 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28400 |  | 428401 | Parameters - Generator - Power protections - Reverse power 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28400 |  | 428401 | Parameters - Busbar A - Power protections - Power import 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28400 |  | 428401 | Parameters - Mains - Power protections - Reverse power 2 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28401 |  | 428402 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28401 |  | 428402 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28401 |  | 428402 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28402 |  | 428403 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28402 |  | 428403 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28402 |  | 428403 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28403 |  | 428404 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28403 |  | 428404 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28403 |  | 428404 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28404 |  | 428405 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28404 |  | 428405 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28404 |  | 428405 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28405 |  | 428406 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28405 |  | 428406 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28405 |  | 428406 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28406 |  | 428407 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28406 |  | 428407 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28406 |  | 428407 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28407 |  | 428408 | Parameters - Mains - Voltage protections - Over-voltage 3 - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28407 |  | 428408 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28407 |  | 428408 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28408 |  | 428409 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28408 |  | 428409 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28408 |  | 428409 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28409 |  | 428410 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28409 |  | 428410 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28409 |  | 428410 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28410 |  | 428411 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28410 |  | 428411 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28410 |  | 428411 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28411 |  | 428412 | Parameters - Mains - Voltage protections - Under-voltage 4 - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28411 |  | 428412 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28411 |  | 428412 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28412 |  | 428413 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28412 |  | 428413 | Parameters - Busbar - Voltage protections - Voltage unbalance - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28412 |  | 428413 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28413 |  | 428414 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28413 |  | 428414 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28413 |  | 428414 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28414 |  | 428415 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28414 |  | 428415 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28414 |  | 428415 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28415 |  | 428416 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28415 |  | 428416 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28415 |  | 428416 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28416 |  | 428417 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28416 |  | 428417 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28416 |  | 428417 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28417 |  | 428418 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28417 |  | 428418 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28417 |  | 428418 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28418 |  | 428419 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28418 |  | 428419 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28418 |  | 428419 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28419 |  | 428420 | Parameters - Mains - Frequency protections - Under-frequency 4 - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28419 |  | 428420 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28419 |  | 428420 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28420 |  | 428421 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28420 |  | 428421 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28420 |  | 428421 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28421 |  | 428422 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28421 |  | 428422 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28421 |  | 428422 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28422 |  | 428423 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28422 |  | 428423 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Configuration | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Configuration | 28422 |  | 428423 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28467 |  | 428468 | Parameters - Engine - Maintenance - Service timer - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28468 |  | 428469 | Parameters - Engine - Maintenance - Service timer - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28469 |  | 428470 | Parameters - Engine - Maintenance - Service timer - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28470 |  | 428471 | Parameters - Engine - Maintenance - Service timer - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28471 |  | 428472 | External MB open failure - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28472 |  | 428473 | Parameters - Power management rules - Ground relay - Ground relay general failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28473 |  | 428474 | Parameters - Power management rules - Ground relay - Ground relay open failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28474 |  | 428475 | Parameters - Power management rules - Ground relay - Ground relay close failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28475 |  | 428476 | Parameters - Power management rules - Ground relay - Ground relay position failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28476 |  | 428477 | Parameters - Breakers - Close before excitation - CBE rerun failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28477 |  | 428478 | Parameters - Breakers - Close before excitation - CBE failure - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28478 |  | 428479 | Load too high - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28479 |  | 428480 | ID to run configuration failure - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28481 |  | 428482 | Parameters - System - Monitoring - Missing any genset controller - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28482 |  | 428483 | Parameters - System - Monitoring - Missing any mains controller - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28483 |  | 428484 | Parameters - System - Monitoring - Missing any bustie controller - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28484 |  | 428485 | Can ID not available - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28485 |  | 428486 | Duplicated CAN IDs - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28486 |  | 428487 | Parameters - Local power management - Alarms - Busbar blocked - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28487 |  | 428488 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28488 |  | 428489 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28489 |  | 428490 | Parameters - System - Monitoring - BTB 33 position failure - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28490 |  | 428491 | Parameters - System - Monitoring - BTB 34 position failure - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28491 |  | 428492 | Parameters - System - Monitoring - BTB 35 position failure - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28492 |  | 428493 | Parameters - System - Monitoring - BTB 36 position failure - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28493 |  | 428494 | Parameters - System - Monitoring - BTB 37 position failure - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28494 |  | 428495 | Parameters - System - Monitoring - BTB 38 position failure - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28495 |  | 428496 | Parameters - System - Monitoring - BTB 39 position failure - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28496 |  | 428497 | Parameters - System - Monitoring - BTB 40 position failure - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28497 |  | 428498 | Primary CAN missing ID 1 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28498 |  | 428499 | Primary CAN missing ID 2 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28499 |  | 428500 | Primary CAN missing ID 3 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28500 |  | 428501 | Primary CAN missing ID 4 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28501 |  | 428502 | Primary CAN missing ID 5 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28502 |  | 428503 | Primary CAN missing ID 6 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28503 |  | 428504 | Primary CAN missing ID 7 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28504 |  | 428505 | Primary CAN missing ID 8 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28505 |  | 428506 | Primary CAN missing ID 9 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28506 |  | 428507 | Primary CAN missing ID 10 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28507 |  | 428508 | Primary CAN missing ID 11 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28508 |  | 428509 | Primary CAN missing ID 12 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28509 |  | 428510 | Primary CAN missing ID 13 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28510 |  | 428511 | Primary CAN missing ID 14 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28511 |  | 428512 | Primary CAN missing ID 15 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28512 |  | 428513 | Primary CAN missing ID 16 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28513 |  | 428514 | Primary CAN missing ID 17 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28514 |  | 428515 | Primary CAN missing ID 18 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28515 |  | 428516 | Primary CAN missing ID 19 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28516 |  | 428517 | Primary CAN missing ID 20 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28517 |  | 428518 | Primary CAN missing ID 21 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28518 |  | 428519 | Primary CAN missing ID 22 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28519 |  | 428520 | Primary CAN missing ID 23 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28520 |  | 428521 | Primary CAN missing ID 24 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28521 |  | 428522 | Primary CAN missing ID 25 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28522 |  | 428523 | Primary CAN missing ID 26 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28523 |  | 428524 | Primary CAN missing ID 27 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28524 |  | 428525 | Primary CAN missing ID 28 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28525 |  | 428526 | Primary CAN missing ID 29 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28526 |  | 428527 | Primary CAN missing ID 30 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28527 |  | 428528 | Primary CAN missing ID 31 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28528 |  | 428529 | Primary CAN missing ID 32 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28529 |  | 428530 | Primary CAN missing ID 33 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28530 |  | 428531 | Primary CAN missing ID 34 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28531 |  | 428532 | Primary CAN missing ID 35 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28532 |  | 428533 | Primary CAN missing ID 36 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28533 |  | 428534 | Primary CAN missing ID 37 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28534 |  | 428535 | Primary CAN missing ID 38 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28535 |  | 428536 | Primary CAN missing ID 39 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28536 |  | 428537 | Primary CAN missing ID 40 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28537 |  | 428538 | Secondary CAN missing ID 1 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28538 |  | 428539 | Secondary CAN missing ID 2 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28539 |  | 428540 | Secondary CAN missing ID 3 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28540 |  | 428541 | Secondary CAN missing ID 4 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28541 |  | 428542 | Secondary CAN missing ID 5 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28542 |  | 428543 | Secondary CAN missing ID 6 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28543 |  | 428544 | Secondary CAN missing ID 7 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28544 |  | 428545 | Secondary CAN missing ID 8 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28545 |  | 428546 | Secondary CAN missing ID 9 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28546 |  | 428547 | Secondary CAN missing ID 10 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28547 |  | 428548 | Secondary CAN missing ID 11 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28548 |  | 428549 | Secondary CAN missing ID 12 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28549 |  | 428550 | Secondary CAN missing ID 13 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28550 |  | 428551 | Secondary CAN missing ID 14 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28551 |  | 428552 | Secondary CAN missing ID 15 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28552 |  | 428553 | Secondary CAN missing ID 16 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28553 |  | 428554 | Secondary CAN missing ID 17 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28554 |  | 428555 | Secondary CAN missing ID 18 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28555 |  | 428556 | Secondary CAN missing ID 19 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28556 |  | 428557 | Secondary CAN missing ID 20 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28557 |  | 428558 | Secondary CAN missing ID 21 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28558 |  | 428559 | Secondary CAN missing ID 22 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28559 |  | 428560 | Secondary CAN missing ID 23 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28560 |  | 428561 | Secondary CAN missing ID 24 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28561 |  | 428562 | Secondary CAN missing ID 25 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28562 |  | 428563 | Secondary CAN missing ID 26 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28563 |  | 428564 | Secondary CAN missing ID 27 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28564 |  | 428565 | Secondary CAN missing ID 28 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28565 |  | 428566 | Secondary CAN missing ID 29 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28566 |  | 428567 | Secondary CAN missing ID 30 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28567 |  | 428568 | Secondary CAN missing ID 31 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28568 |  | 428569 | Secondary CAN missing ID 32 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28569 |  | 428570 | Secondary CAN missing ID 33 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28570 |  | 428571 | Secondary CAN missing ID 34 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28571 |  | 428572 | Secondary CAN missing ID 35 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28572 |  | 428573 | Secondary CAN missing ID 36 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28573 |  | 428574 | Secondary CAN missing ID 37 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28574 |  | 428575 | Secondary CAN missing ID 38 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28575 |  | 428576 | Secondary CAN missing ID 39 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28576 |  | 428577 | Secondary CAN missing ID 40 - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28577 |  | 428578 | Priority error - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28578 |  | 428579 | Parameters - Non-essential load trip - Trip 1 - Over-current - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28579 |  | 428580 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28580 |  | 428581 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28581 |  | 428582 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28582 |  | 428583 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28583 |  | 428584 | Parameters - Non-essential load trip - Trip 2 - Over-current - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28584 |  | 428585 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28585 |  | 428586 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28586 |  | 428587 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28587 |  | 428588 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28588 |  | 428589 | Parameters - Non-essential load trip - Trip 3 - Over-current - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28589 |  | 428590 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28590 |  | 428591 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28591 |  | 428592 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28592 |  | 428593 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Configuration | 28593 |  | 428594 | Parameters - System - Monitoring - Single-line hazard - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28594 |  | 428595 | ID not present - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28595 |  | 428596 | Unsupported application - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28596 |  | 428597 | Application internal CAN protocol conflict - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28597 |  | 428598 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28598 |  | 428599 | Dry mode: Voltage level unexpected - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28599 |  | 428600 | Invalid DAVR configuration - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28600 |  | 428601 | Parameters - Communication - DEIF network - DEIF network fork detected - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28602 |  | 428603 | Parameters - Communication - DEIF network - DEIF network has only one connection - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28604 |  | 428605 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28604 |  | 428605 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Configuration | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Configuration | 28604 |  | 428605 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Configuration | 28605 |  | 428606 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Configuration | 28605 |  | 428606 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Configuration | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Configuration | 28607 |  | 428608 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28608 |  | 428609 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28609 |  | 428610 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28610 |  | 428611 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28611 |  | 428612 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28612 |  | 428613 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28613 |  | 428614 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28614 |  | 428615 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28615 |  | 428616 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28616 |  | 428617 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28617 |  | 428618 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28618 |  | 428619 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28619 |  | 428620 | AC protections not running - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28620 |  | 428621 | AC data is missing - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28621 |  | 428622 | AC protections not running - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28622 |  | 428623 | AC data is missing - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28623 |  | 428624 | AC protections not running - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28624 |  | 428625 | AC data is missing - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28625 |  | 428626 | AC protections not running - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28626 |  | 428627 | AC data is missing - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28627 |  | 428628 | Live voltage detected - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28628 |  | 428629 | Internal issue detected. A restart is required soon! - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28629 |  | 428630 | Parameters - System - Monitoring - Missing controllers - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28630 |  | 428631 | Card issue detected - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28631 |  | 428632 | Card configuration failed - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28632 |  | 428633 | Unknown traffic on DEIF network - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28633 |  | 428634 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28634 |  | 428635 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28635 |  | 428636 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Configuration | 28636 |  | 428637 | Local IO service error - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28637 |  | 428638 | App logging failure - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28638 |  | 428639 | Event logging failure - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28639 |  | 428640 | Licence error - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28640 |  | 428641 | Brightness is dimmed according to temperature - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 28641 |  | 428642 | Parameters - Grid code - Mains sync inhibit - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28642 |  | 428643 | Parameters - Grid code - Capability curve - Import protection - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28643 |  | 428644 | Parameters - Grid code - Capability curve - Export protection - Configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Configuration | 28644 |  | 428645 | Hardware is not compatible based on module versions - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29500 |  | 429501 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29501 |  | 429502 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29502 |  | 429503 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29503 |  | 429504 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29504 |  | 429505 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29505 |  | 429506 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29506 |  | 429507 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29507 |  | 429508 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29508 |  | 429509 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29509 |  | 429510 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29510 |  | 429511 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29511 |  | 429512 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29512 |  | 429513 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29513 |  | 429514 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29514 |  | 429515 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29515 |  | 429516 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29516 |  | 429517 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29517 |  | 429518 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29518 |  | 429519 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29519 |  | 429520 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29520 |  | 429521 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29521 |  | 429522 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29522 |  | 429523 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29523 |  | 429524 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29524 |  | 429525 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29525 |  | 429526 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29526 |  | 429527 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29527 |  | 429528 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29528 |  | 429529 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29529 |  | 429530 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29530 |  | 429531 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29531 |  | 429532 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29532 |  | 429533 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29533 |  | 429534 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29534 |  | 429535 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29535 |  | 429536 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29536 |  | 429537 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29537 |  | 429538 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29538 |  | 429539 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29539 |  | 429540 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29540 |  | 429541 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29541 |  | 429542 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29542 |  | 429543 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29543 |  | 429544 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29544 |  | 429545 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29545 |  | 429546 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29546 |  | 429547 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29547 |  | 429548 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29548 |  | 429549 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29549 |  | 429550 | Digital custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29600 |  | 429601 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29601 |  | 429602 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29602 |  | 429603 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29603 |  | 429604 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29604 |  | 429605 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29605 |  | 429606 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29606 |  | 429607 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29607 |  | 429608 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29608 |  | 429609 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29609 |  | 429610 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29610 |  | 429611 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29611 |  | 429612 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29612 |  | 429613 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29613 |  | 429614 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29614 |  | 429615 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29615 |  | 429616 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29616 |  | 429617 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29617 |  | 429618 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29618 |  | 429619 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29619 |  | 429620 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29620 |  | 429621 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29621 |  | 429622 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29622 |  | 429623 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29623 |  | 429624 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29624 |  | 429625 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29625 |  | 429626 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29626 |  | 429627 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29627 |  | 429628 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29628 |  | 429629 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29629 |  | 429630 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29630 |  | 429631 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29631 |  | 429632 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29632 |  | 429633 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29633 |  | 429634 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29634 |  | 429635 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29635 |  | 429636 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29636 |  | 429637 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29637 |  | 429638 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29638 |  | 429639 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29639 |  | 429640 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29640 |  | 429641 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29641 |  | 429642 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29642 |  | 429643 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29643 |  | 429644 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29644 |  | 429645 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29645 |  | 429646 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29646 |  | 429647 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29647 |  | 429648 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29648 |  | 429649 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29649 |  | 429650 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29650 |  | 429651 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29651 |  | 429652 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29652 |  | 429653 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29653 |  | 429654 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29654 |  | 429655 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29655 |  | 429656 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29656 |  | 429657 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29657 |  | 429658 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29658 |  | 429659 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29659 |  | 429660 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29660 |  | 429661 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29661 |  | 429662 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29662 |  | 429663 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29663 |  | 429664 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29664 |  | 429665 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29665 |  | 429666 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29666 |  | 429667 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29667 |  | 429668 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29668 |  | 429669 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29669 |  | 429670 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29670 |  | 429671 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29671 |  | 429672 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29672 |  | 429673 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29673 |  | 429674 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29674 |  | 429675 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29675 |  | 429676 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29676 |  | 429677 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29677 |  | 429678 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29678 |  | 429679 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29679 |  | 429680 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29680 |  | 429681 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29681 |  | 429682 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29682 |  | 429683 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29683 |  | 429684 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29684 |  | 429685 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29685 |  | 429686 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29686 |  | 429687 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29687 |  | 429688 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29688 |  | 429689 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29689 |  | 429690 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29690 |  | 429691 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29691 |  | 429692 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29692 |  | 429693 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29693 |  | 429694 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29694 |  | 429695 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29695 |  | 429696 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29696 |  | 429697 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29697 |  | 429698 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29698 |  | 429699 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29699 |  | 429700 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29700 |  | 429701 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29701 |  | 429702 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29702 |  | 429703 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29703 |  | 429704 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29704 |  | 429705 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29705 |  | 429706 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29706 |  | 429707 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29707 |  | 429708 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29708 |  | 429709 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29709 |  | 429710 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29710 |  | 429711 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29711 |  | 429712 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29712 |  | 429713 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29713 |  | 429714 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29714 |  | 429715 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29715 |  | 429716 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29716 |  | 429717 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29717 |  | 429718 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29718 |  | 429719 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29719 |  | 429720 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29720 |  | 429721 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29721 |  | 429722 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29722 |  | 429723 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29723 |  | 429724 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29724 |  | 429725 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29725 |  | 429726 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29726 |  | 429727 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29727 |  | 429728 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29728 |  | 429729 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29729 |  | 429730 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29730 |  | 429731 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29731 |  | 429732 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29732 |  | 429733 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29733 |  | 429734 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29734 |  | 429735 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29735 |  | 429736 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29736 |  | 429737 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29737 |  | 429738 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29738 |  | 429739 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29739 |  | 429740 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29740 |  | 429741 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29741 |  | 429742 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29742 |  | 429743 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29743 |  | 429744 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29744 |  | 429745 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29745 |  | 429746 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29746 |  | 429747 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29747 |  | 429748 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29748 |  | 429749 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29749 |  | 429750 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29750 |  | 429751 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29751 |  | 429752 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29752 |  | 429753 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29753 |  | 429754 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29754 |  | 429755 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29755 |  | 429756 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29756 |  | 429757 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29757 |  | 429758 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29758 |  | 429759 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29759 |  | 429760 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29760 |  | 429761 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29761 |  | 429762 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29762 |  | 429763 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29763 |  | 429764 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29764 |  | 429765 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29765 |  | 429766 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29766 |  | 429767 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29767 |  | 429768 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29768 |  | 429769 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29769 |  | 429770 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29770 |  | 429771 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29771 |  | 429772 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29772 |  | 429773 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29773 |  | 429774 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29774 |  | 429775 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29775 |  | 429776 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29776 |  | 429777 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29777 |  | 429778 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29778 |  | 429779 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29779 |  | 429780 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29780 |  | 429781 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29781 |  | 429782 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29782 |  | 429783 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29783 |  | 429784 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29784 |  | 429785 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29785 |  | 429786 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29786 |  | 429787 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29787 |  | 429788 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29788 |  | 429789 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29789 |  | 429790 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29790 |  | 429791 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29791 |  | 429792 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29792 |  | 429793 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29793 |  | 429794 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29794 |  | 429795 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29795 |  | 429796 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29796 |  | 429797 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29797 |  | 429798 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29798 |  | 429799 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Configuration | 29799 |  | 429800 | Analogue custom alarm - Configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30000 |  | 430001 | Application initialisation error - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30002 |  | 430003 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30004 |  | 430005 | Preliminary software - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30006 |  | 430007 | Parameters - Engine - Stop sequence - Stop failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30008 |  | 430009 | Parameters - Engine - Start sequence - Start failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30010 |  | 430011 | Parameters - Engine - Start sequence - Crank failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30012 |  | 430013 | Parameters - Engine - Protections - Speed - Overspeed 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30014 |  | 430015 | Parameters - Engine - Protections - Speed - Overspeed 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30016 |  | 430017 | Parameters - Engine - Protections - Speed - Under-speed 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30018 |  | 430019 | Parameters - Engine - Protections - Speed - Under-speed 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30020 |  | 430021 | Parameters - Engine - Running detection - Magnetic pickup wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30022 |  | 430023 | Parameters - Engine - Stop sequence - Externally stopped - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30026 |  | 430027 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30028 |  | 430029 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30030 |  | 430031 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30032 |  | 430033 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30034 |  | 430035 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30036 |  | 430037 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30038 |  | 430039 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30040 |  | 430041 | Parameters - Engine - Protections - Level - Coolant level 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30042 |  | 430043 | Parameters - Engine - Protections - Level - Coolant level 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30044 |  | 430045 | Parameters - Engine - Protections - Level - Coolant level 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30054 |  | 430055 | Parameters - Engine - Running detection - Primary running feedback failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30082 |  | 430083 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30082 |  | 430083 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30082 |  | 430083 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30084 |  | 430085 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30084 |  | 430085 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30084 |  | 430085 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30086 |  | 430087 | Parameters - Breakers - Generator breaker monitoring - Position failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30086 |  | 430087 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30086 |  | 430087 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30088 |  | 430089 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30088 |  | 430089 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30088 |  | 430089 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30090 |  | 430091 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30090 |  | 430091 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30090 |  | 430091 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30092 |  | 430093 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30092 |  | 430093 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30092 |  | 430093 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30094 |  | 430095 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30094 |  | 430095 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30094 |  | 430095 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30096 |  | 430097 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30096 |  | 430097 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30096 |  | 430097 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30098 |  | 430099 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Inhibit | 30098 |  | 430099 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Inhibit | 30100 |  | 430101 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Inhibit | 30100 |  | 430101 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Inhibit | 30102 |  | 430103 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Inhibit | 30102 |  | 430103 | Parameters - Breakers - Tie breaker monitoring - Position failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Inhibit | 30104 |  | 430105 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Inhibit | 30104 |  | 430105 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Inhibit | 30106 |  | 430107 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Inhibit | 30106 |  | 430107 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Inhibit | 30108 |  | 430109 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Inhibit | 30108 |  | 430109 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Inhibit | 30110 |  | 430111 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Inhibit | 30110 |  | 430111 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Inhibit | 30112 |  | 430113 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Inhibit | 30112 |  | 430113 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Inhibit | 30120 |  | 430121 | Parameters - Mains - AC setup - Phase sequence error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30120 |  | 430121 | Parameters - Busbar - AC setup - Phase sequence error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30120 |  | 430121 | Parameters - Busbar B - AC setup - Phase sequence error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30122 |  | 430123 | Parameters - Generator - AC setup - Phase sequence error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30122 |  | 430123 | Parameters - Busbar A - AC setup - Phase sequence error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30122 |  | 430123 | Parameters - Mains - AC setup - Phase sequence error - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30124 |  | 430125 | Parameters - Generator - AC setup - Voltage or frequency not OK - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30206 |  | 430207 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30206 |  | 430207 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30206 |  | 430207 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30208 |  | 430209 | Parameters - Mains - Additional protections - Vector shift - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30208 |  | 430209 | Parameters - Busbar - Additional protections - Vector shift - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30208 |  | 430209 | Parameters - Busbar B - Additional protections - Vector shift - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30210 |  | 430211 | Parameters - Generator - Current protections - Inverse time over-current - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30210 |  | 430211 | Parameters - Busbar A - Current protections - Inverse time over-current - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30210 |  | 430211 | Parameters - Mains - Current protections - Inverse time over-current - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30212 |  | 430213 | Parameters - Local - 4th current input - Earth inverse time over-current - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30214 |  | 430215 | Parameters - Local - 4th current input - Neutral inverse time over-current - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30216 |  | 430217 | Parameters - Generator - Additional protections - V< and Q< 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30216 |  | 430217 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30216 |  | 430217 | Parameters - Mains - Additional protections - V< and Q< 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30218 |  | 430219 | Parameters - Generator - Additional protections - V< and Q< 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30218 |  | 430219 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30218 |  | 430219 | Parameters - Mains - Additional protections - V< and Q< 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30220 |  | 430221 | Parameters - Generator - Additional protections - Average over-voltage 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30220 |  | 430221 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30220 |  | 430221 | Parameters - Mains - Additional protections - Average over-voltage 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30222 |  | 430223 | Parameters - Generator - Additional protections - Average over-voltage 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30222 |  | 430223 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30222 |  | 430223 | Parameters - Mains - Additional protections - Average over-voltage 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30230 |  | 430231 | Protection set point out of range - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30232 |  | 430233 | Parameters - Generator - Current protections - Stabilised differential current - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30234 |  | 430235 | Parameters - Generator - Current protections - High set differential current - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30236 |  | 430237 | Protection set point out of range (differential current) - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30238 |  | 430239 | Parameters - Local - Mode - Not under remote control - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30242 |  | 430243 | Parameters - Local - Monitoring - System not OK - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30244 |  | 430245 | Configuration update delayed - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30246 |  | 430247 | Critical process error - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30248 |  | 430249 | Restore error - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30250 |  | 430251 | SD-card format error - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30252 |  | 430253 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30254 |  | 430255 | Fieldbus configuration exceeded maximum I/O configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30256 |  | 430257 | Parameters - Custom alarm - Custom alarm 0 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30258 |  | 430259 | Parameters - Custom alarm - Custom alarm 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30260 |  | 430261 | Parameters - Custom alarm - Custom alarm 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30262 |  | 430263 | Parameters - Custom alarm - Custom alarm 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30264 |  | 430265 | Parameters - Custom alarm - Custom alarm 4 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30266 |  | 430267 | Parameters - Custom alarm - Custom alarm 5 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30268 |  | 430269 | Parameters - Custom alarm - Custom alarm 6 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30270 |  | 430271 | Parameters - Custom alarm - Custom alarm 7 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30272 |  | 430273 | Parameters - Custom alarm - Custom alarm 8 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30274 |  | 430275 | Parameters - Custom alarm - Custom alarm 9 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30276 |  | 430277 | Parameters - Custom alarm - Custom alarm 10 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30278 |  | 430279 | Parameters - Custom alarm - Custom alarm 11 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30280 |  | 430281 | Parameters - Custom alarm - Custom alarm 12 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30282 |  | 430283 | Parameters - Custom alarm - Custom alarm 13 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30284 |  | 430285 | Parameters - Custom alarm - Custom alarm 14 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30286 |  | 430287 | Parameters - Custom alarm - Custom alarm 15 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30288 |  | 430289 | Parameters - Custom alarm - Custom alarm 16 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30290 |  | 430291 | Parameters - Custom alarm - Custom alarm 17 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30292 |  | 430293 | Parameters - Custom alarm - Custom alarm 18 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30294 |  | 430295 | Parameters - Custom alarm - Custom alarm 19 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30296 |  | 430297 | Parameters - Custom alarm - Custom alarm 20 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30298 |  | 430299 | Parameters - Custom alarm - Custom alarm 21 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30300 |  | 430301 | Parameters - Custom alarm - Custom alarm 22 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30302 |  | 430303 | Parameters - Custom alarm - Custom alarm 23 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30304 |  | 430305 | Parameters - Custom alarm - Custom alarm 24 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30306 |  | 430307 | Parameters - Regulators - GOV - Monitoring - Regulation error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30308 |  | 430309 | Parameters - Regulators - AVR - Monitoring - Regulation error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30326 |  | 430327 | Required hardware card(s) not found - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30328 |  | 430329 | Software mismatch on hardware module(s) - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30330 |  | 430331 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Inhibit | 30330 |  | 430331 | Parameters - Busbar - AC setup - Multiple phase wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Inhibit | 30330 |  | 430331 | Parameters - Busbar B - AC setup - Multiple phase wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30332 |  | 430333 | Parameters - Generator - AC setup - Multiple phase wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Inhibit | 30332 |  | 430333 | Parameters - Busbar A - AC setup - Multiple phase wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30332 |  | 430333 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Inhibit | 30334 |  | 430335 | Parameters - Mains - AC setup - L1 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Inhibit | 30334 |  | 430335 | Parameters - Busbar - AC setup - L1 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Inhibit | 30334 |  | 430335 | Parameters - Busbar B - AC setup - L1 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30336 |  | 430337 | Parameters - Mains - AC setup - L2 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Inhibit | 30336 |  | 430337 | Parameters - Busbar - AC setup - L2 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Inhibit | 30336 |  | 430337 | Parameters - Busbar B - AC setup - L2 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30338 |  | 430339 | Parameters - Mains - AC setup - L3 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Inhibit | 30338 |  | 430339 | Parameters - Busbar - AC setup - L3 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Inhibit | 30338 |  | 430339 | Parameters - Busbar B - AC setup - L3 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30340 |  | 430341 | Parameters - Generator - AC setup - L1 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Inhibit | 30340 |  | 430341 | Parameters - Busbar A - AC setup - L1 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30340 |  | 430341 | Parameters - Mains - AC setup - L1 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Inhibit | 30342 |  | 430343 | Parameters - Generator - AC setup - L2 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Inhibit | 30342 |  | 430343 | Parameters - Busbar A - AC setup - L2 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30342 |  | 430343 | Parameters - Mains - AC setup - L2 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Inhibit | 30344 |  | 430345 | Parameters - Generator - AC setup - L3 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Inhibit | 30344 |  | 430345 | Parameters - Busbar A - AC setup - L3 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30344 |  | 430345 | Parameters - Mains - AC setup - L3 wire break - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Inhibit | 30356 |  | 430357 | Parameters - Mains - AC setup - Supervision alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X |  | X | X
Alarm parameter: Inhibit | 30358 |  | 430359 | Parameters - Engine - Emergency stop - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30358 |  | 430359 | Parameters - Busbar A - Emergency stop - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30358 |  | 430359 | Parameters - Mains - Emergency stop - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30360 |  | 430361 | Clock battery failure - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30362 |  | 430363 | Controller temperature too high - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30364 |  | 430365 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30366 |  | 430367 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30368 |  | 430369 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30370 |  | 430371 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30372 |  | 430373 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30374 |  | 430375 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30376 |  | 430377 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30378 |  | 430379 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30380 |  | 430381 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30382 |  | 430383 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30384 |  | 430385 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30386 |  | 430387 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30388 |  | 430389 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30390 |  | 430391 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30392 |  | 430393 | EIM3.1 4 supply voltage high - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30394 |  | 430395 | EIM3.1 4 supply voltage low or missing - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30396 |  | 430397 | EIM3.1 5 supply voltage high - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30398 |  | 430399 | EIM3.1 5 supply voltage low or missing - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30400 |  | 430401 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30402 |  | 430403 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30404 |  | 430405 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30406 |  | 430407 | EIM3.1 4 relay 4 wire break - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30408 |  | 430409 | EIM3.1 5 relay 4 wire break - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30410 |  | 430411 | AC protections not running - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30412 |  | 430413 | AC data is missing - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30414 |  | 430415 | AC protections not running (differential current) - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30416 |  | 430417 | AC data is missing (differential current) - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30418 |  | 430419 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30420 |  | 430421 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30422 |  | 430423 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30424 |  | 430425 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30426 |  | 430427 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30428 |  | 430429 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30430 |  | 430431 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30432 |  | 430433 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30434 |  | 430435 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30436 |  | 430437 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30438 |  | 430439 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30440 |  | 430441 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30442 |  | 430443 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30444 |  | 430445 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30446 |  | 430447 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30448 |  | 430449 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30450 |  | 430451 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30452 |  | 430453 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30456 |  | 430457 | Parameters - System - Monitoring - Duplicate controller ID - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30458 |  | 430459 | Parameters - System - Monitoring - Missing all controllers - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30462 |  | 430463 | Controller ID not configured - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30472 |  | 430473 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30474 |  | 430475 | Blackout detection mismatch - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30480 |  | 430481 | Parameters - Communication - NTP - NTP server 1 not connected - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30482 |  | 430483 | Parameters - Communication - NTP - NTP server 1 no response - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30484 |  | 430485 | Parameters - Communication - NTP - NTP server 2 not connected - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30486 |  | 430487 | Parameters - Communication - NTP - NTP server 2 no response - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30488 |  | 430489 | Parameters - Communication - NTP - No NTP server time synchronisation - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30490 |  | 430491 | Parameters - Communication - NTP - No NTP server(s) connected - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30492 |  | 430493 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30494 |  | 430495 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30592 |  | 430593 | Controller not part of system - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30594 |  | 430595 | Different single-line configurations - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30596 |  | 430597 | Single-line missing/none active - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30598 |  | 430599 | Parameters - Communication - Modbus - Modbus communication timeout - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30600 |  | 430601 | Parameters - CODESYS - Monitoring - I/O config conflict - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30602 |  | 430603 | Parameters - CODESYS - Monitoring - Application not OK - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30604 |  | 430605 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30606 |  | 430607 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30608 |  | 430609 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30610 |  | 430611 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30612 |  | 430613 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30614 |  | 430615 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30616 |  | 430617 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30618 |  | 430619 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30620 |  | 430621 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30622 |  | 430623 | Parameters - Communication - Fieldbus - Fieldbus conflict - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30624 |  | 430625 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30630 |  | 430631 | Parameters - Local - CustomLogic - Configuration invalid - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30632 |  | 430633 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30634 |  | 430635 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30636 |  | 430637 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30638 |  | 430639 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30640 |  | 430641 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30642 |  | 430643 | Parameters - Generator - Digital AVR - Alarms - Open diode - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30644 |  | 430645 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30646 |  | 430647 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30648 |  | 430649 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30650 |  | 430651 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30652 |  | 430653 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30654 |  | 430655 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30656 |  | 430657 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30658 |  | 430659 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30660 |  | 430661 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30662 |  | 430663 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30664 |  | 430665 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30666 |  | 430667 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30668 |  | 430669 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30670 |  | 430671 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30672 |  | 430673 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30674 |  | 430675 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30676 |  | 430677 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30678 |  | 430679 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30680 |  | 430681 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30682 |  | 430683 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30684 |  | 430685 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30686 |  | 430687 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30688 |  | 430689 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30690 |  | 430691 | Parameters - Generator - Digital AVR - Alarms - Motor start - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30692 |  | 430693 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30694 |  | 430695 | Parameters - Generator - Digital AVR - Alarms - Power supply - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30696 |  | 430697 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30698 |  | 430699 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30700 |  | 430701 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30702 |  | 430703 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30704 |  | 430705 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30706 |  | 430707 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30708 |  | 430709 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30710 |  | 430711 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30712 |  | 430713 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30714 |  | 430715 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30716 |  | 430717 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30718 |  | 430719 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30720 |  | 430721 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30722 |  | 430723 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30724 |  | 430725 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30726 |  | 430727 | DAVR unsupported AC configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30728 |  | 430729 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30730 |  | 430731 | Parameters - Generator - Voltage protections - Under-voltage 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30730 |  | 430731 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30730 |  | 430731 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30732 |  | 430733 | Parameters - Generator - Voltage protections - Under-voltage 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30732 |  | 430733 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30732 |  | 430733 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30734 |  | 430735 | Parameters - Generator - Voltage protections - Under-voltage 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30734 |  | 430735 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30734 |  | 430735 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30736 |  | 430737 | Parameters - Generator - Voltage protections - Over-voltage 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30736 |  | 430737 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30736 |  | 430737 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30738 |  | 430739 | Parameters - Generator - Voltage protections - Over-voltage 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30738 |  | 430739 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30738 |  | 430739 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30740 |  | 430741 | Parameters - Generator - Voltage protections - Voltage unbalance - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30740 |  | 430741 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30740 |  | 430741 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30742 |  | 430743 | Parameters - Generator - Voltage protections - Negative sequence voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30742 |  | 430743 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30742 |  | 430743 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30744 |  | 430745 | Parameters - Generator - Voltage protections - Zero sequence voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30744 |  | 430745 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30744 |  | 430745 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30746 |  | 430747 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30746 |  | 430747 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30746 |  | 430747 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30748 |  | 430749 | Parameters - Generator - Current protections - Over-current 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30748 |  | 430749 | Parameters - Busbar A - Current protections - Over-current 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30748 |  | 430749 | Parameters - Mains - Current protections - Over-current 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30750 |  | 430751 | Parameters - Generator - Current protections - Over-current 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30750 |  | 430751 | Parameters - Busbar A - Current protections - Over-current 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30750 |  | 430751 | Parameters - Mains - Current protections - Over-current 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30752 |  | 430753 | Parameters - Generator - Current protections - Over-current 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30752 |  | 430753 | Parameters - Busbar A - Current protections - Over-current 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30752 |  | 430753 | Parameters - Mains - Current protections - Over-current 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30754 |  | 430755 | Parameters - Generator - Current protections - Over-current 4 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30754 |  | 430755 | Parameters - Busbar A - Current protections - Over-current 4 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30754 |  | 430755 | Parameters - Mains - Current protections - Over-current 4 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30756 |  | 430757 | Parameters - Generator - Current protections - Fast over-current 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30756 |  | 430757 | Parameters - Busbar A - Current protections - Fast over-current 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30756 |  | 430757 | Parameters - Mains - Current protections - Fast over-current 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30758 |  | 430759 | Parameters - Generator - Current protections - Fast over-current 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30758 |  | 430759 | Parameters - Busbar A - Current protections - Fast over-current 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30758 |  | 430759 | Parameters - Mains - Current protections - Fast over-current 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30760 |  | 430761 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30760 |  | 430761 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30760 |  | 430761 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30762 |  | 430763 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30762 |  | 430763 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30762 |  | 430763 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30764 |  | 430765 | Parameters - Generator - Current protections - Directional over-current 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30764 |  | 430765 | Parameters - Busbar A - Current protections - Directional over-current 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30764 |  | 430765 | Parameters - Mains - Current protections - Directional over-current 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30766 |  | 430767 | Parameters - Generator - Current protections - Directional over-current 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30766 |  | 430767 | Parameters - Busbar A - Current protections - Directional over-current 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30766 |  | 430767 | Parameters - Mains - Current protections - Directional over-current 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30768 |  | 430769 | Parameters - Busbar A - Current protections - Directional over-current 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30770 |  | 430771 | Parameters - Busbar A - Current protections - Directional over-current 4 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30772 |  | 430773 | Parameters - Generator - Current protections - Negative sequence current - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30772 |  | 430773 | Parameters - Busbar A - Current protections - Negative sequence current - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30772 |  | 430773 | Parameters - Mains - Current protections - Negative sequence current - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30774 |  | 430775 | Parameters - Generator - Current protections - Zero sequence current - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30774 |  | 430775 | Parameters - Busbar A - Current protections - Zero sequence current - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30774 |  | 430775 | Parameters - Mains - Current protections - Zero sequence current - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30776 |  | 430777 | Parameters - Generator - Frequency protections - Over-frequency 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30776 |  | 430777 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30776 |  | 430777 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30778 |  | 430779 | Parameters - Generator - Frequency protections - Over-frequency 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30778 |  | 430779 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30778 |  | 430779 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30780 |  | 430781 | Parameters - Generator - Frequency protections - Over-frequency 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30780 |  | 430781 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30780 |  | 430781 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30782 |  | 430783 | Parameters - Generator - Frequency protections - Under-frequency 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30782 |  | 430783 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30782 |  | 430783 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30784 |  | 430785 | Parameters - Generator - Frequency protections - Under-frequency 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30784 |  | 430785 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30784 |  | 430785 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30786 |  | 430787 | Parameters - Generator - Frequency protections - Under-frequency 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30786 |  | 430787 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30786 |  | 430787 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30788 |  | 430789 | Parameters - Generator - Power protections - Overload 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30788 |  | 430789 | Parameters - Busbar A - Power protections - Power export 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30788 |  | 430789 | Parameters - Mains - Power protections - Overload 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30790 |  | 430791 | Parameters - Generator - Power protections - Overload 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30790 |  | 430791 | Parameters - Busbar A - Power protections - Power export 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30790 |  | 430791 | Parameters - Mains - Power protections - Overload 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30792 |  | 430793 | Parameters - Generator - Power protections - Overload 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30792 |  | 430793 | Parameters - Busbar A - Power protections - Power export 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30792 |  | 430793 | Parameters - Mains - Power protections - Overload 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30794 |  | 430795 | Parameters - Generator - Power protections - Overload 4 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30794 |  | 430795 | Parameters - Busbar A - Power protections - Power export 4 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30794 |  | 430795 | Parameters - Mains - Power protections - Overload 4 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30796 |  | 430797 | Parameters - Generator - Power protections - Overload 5 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30796 |  | 430797 | Parameters - Busbar A - Power protections - Power export 5 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30796 |  | 430797 | Parameters - Mains - Power protections - Overload 5 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30798 |  | 430799 | Parameters - Generator - Power protections - Reverse power 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30798 |  | 430799 | Parameters - Busbar A - Power protections - Power import 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30798 |  | 430799 | Parameters - Mains - Power protections - Reverse power 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30800 |  | 430801 | Parameters - Generator - Power protections - Reverse power 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30800 |  | 430801 | Parameters - Busbar A - Power protections - Power import 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30800 |  | 430801 | Parameters - Mains - Power protections - Reverse power 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30802 |  | 430803 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30802 |  | 430803 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30802 |  | 430803 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30804 |  | 430805 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30804 |  | 430805 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30804 |  | 430805 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30806 |  | 430807 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30806 |  | 430807 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30806 |  | 430807 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30808 |  | 430809 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30808 |  | 430809 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30808 |  | 430809 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30810 |  | 430811 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30810 |  | 430811 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30810 |  | 430811 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30812 |  | 430813 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30812 |  | 430813 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30812 |  | 430813 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30814 |  | 430815 | Parameters - Mains - Voltage protections - Over-voltage 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30814 |  | 430815 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30814 |  | 430815 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30816 |  | 430817 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30816 |  | 430817 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30816 |  | 430817 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30818 |  | 430819 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30818 |  | 430819 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30818 |  | 430819 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30820 |  | 430821 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30820 |  | 430821 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30820 |  | 430821 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30822 |  | 430823 | Parameters - Mains - Voltage protections - Under-voltage 4 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30822 |  | 430823 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30822 |  | 430823 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30824 |  | 430825 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30824 |  | 430825 | Parameters - Busbar - Voltage protections - Voltage unbalance - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30824 |  | 430825 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30826 |  | 430827 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30826 |  | 430827 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30826 |  | 430827 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30828 |  | 430829 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30828 |  | 430829 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30828 |  | 430829 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30830 |  | 430831 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30830 |  | 430831 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30830 |  | 430831 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30832 |  | 430833 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30832 |  | 430833 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30832 |  | 430833 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30834 |  | 430835 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30834 |  | 430835 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30834 |  | 430835 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30836 |  | 430837 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30836 |  | 430837 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30836 |  | 430837 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30838 |  | 430839 | Parameters - Mains - Frequency protections - Under-frequency 4 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30838 |  | 430839 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30838 |  | 430839 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30840 |  | 430841 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30840 |  | 430841 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30840 |  | 430841 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30842 |  | 430843 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30842 |  | 430843 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30842 |  | 430843 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30844 |  | 430845 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 30844 |  | 430845 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Inhibit | 30844 |  | 430845 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30934 |  | 430935 | Parameters - Engine - Maintenance - Service timer - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30936 |  | 430937 | Parameters - Engine - Maintenance - Service timer - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30938 |  | 430939 | Parameters - Engine - Maintenance - Service timer - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30940 |  | 430941 | Parameters - Engine - Maintenance - Service timer - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30942 |  | 430943 | External MB open failure - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30944 |  | 430945 | Parameters - Power management rules - Ground relay - Ground relay general failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30946 |  | 430947 | Parameters - Power management rules - Ground relay - Ground relay open failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30948 |  | 430949 | Parameters - Power management rules - Ground relay - Ground relay close failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30950 |  | 430951 | Parameters - Power management rules - Ground relay - Ground relay position failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30952 |  | 430953 | Parameters - Breakers - Close before excitation - CBE rerun failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30954 |  | 430955 | Parameters - Breakers - Close before excitation - CBE failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 30956 |  | 430957 | Load too high - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30958 |  | 430959 | ID to run configuration failure - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 30962 |  | 430963 | Parameters - System - Monitoring - Missing any genset controller - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30964 |  | 430965 | Parameters - System - Monitoring - Missing any mains controller - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30966 |  | 430967 | Parameters - System - Monitoring - Missing any bustie controller - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30968 |  | 430969 | Can ID not available - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30970 |  | 430971 | Duplicated CAN IDs - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30972 |  | 430973 | Parameters - Local power management - Alarms - Busbar blocked - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 30974 |  | 430975 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30976 |  | 430977 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 30978 |  | 430979 | Parameters - System - Monitoring - BTB 33 position failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30980 |  | 430981 | Parameters - System - Monitoring - BTB 34 position failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30982 |  | 430983 | Parameters - System - Monitoring - BTB 35 position failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30984 |  | 430985 | Parameters - System - Monitoring - BTB 36 position failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30986 |  | 430987 | Parameters - System - Monitoring - BTB 37 position failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30988 |  | 430989 | Parameters - System - Monitoring - BTB 38 position failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30990 |  | 430991 | Parameters - System - Monitoring - BTB 39 position failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30992 |  | 430993 | Parameters - System - Monitoring - BTB 40 position failure - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30994 |  | 430995 | Primary CAN missing ID 1 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30996 |  | 430997 | Primary CAN missing ID 2 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 30998 |  | 430999 | Primary CAN missing ID 3 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31000 |  | 431001 | Primary CAN missing ID 4 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31002 |  | 431003 | Primary CAN missing ID 5 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31004 |  | 431005 | Primary CAN missing ID 6 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31006 |  | 431007 | Primary CAN missing ID 7 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31008 |  | 431009 | Primary CAN missing ID 8 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31010 |  | 431011 | Primary CAN missing ID 9 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31012 |  | 431013 | Primary CAN missing ID 10 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31014 |  | 431015 | Primary CAN missing ID 11 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31016 |  | 431017 | Primary CAN missing ID 12 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31018 |  | 431019 | Primary CAN missing ID 13 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31020 |  | 431021 | Primary CAN missing ID 14 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31022 |  | 431023 | Primary CAN missing ID 15 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31024 |  | 431025 | Primary CAN missing ID 16 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31026 |  | 431027 | Primary CAN missing ID 17 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31028 |  | 431029 | Primary CAN missing ID 18 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31030 |  | 431031 | Primary CAN missing ID 19 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31032 |  | 431033 | Primary CAN missing ID 20 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31034 |  | 431035 | Primary CAN missing ID 21 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31036 |  | 431037 | Primary CAN missing ID 22 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31038 |  | 431039 | Primary CAN missing ID 23 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31040 |  | 431041 | Primary CAN missing ID 24 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31042 |  | 431043 | Primary CAN missing ID 25 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31044 |  | 431045 | Primary CAN missing ID 26 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31046 |  | 431047 | Primary CAN missing ID 27 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31048 |  | 431049 | Primary CAN missing ID 28 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31050 |  | 431051 | Primary CAN missing ID 29 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31052 |  | 431053 | Primary CAN missing ID 30 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31054 |  | 431055 | Primary CAN missing ID 31 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31056 |  | 431057 | Primary CAN missing ID 32 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31058 |  | 431059 | Primary CAN missing ID 33 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31060 |  | 431061 | Primary CAN missing ID 34 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31062 |  | 431063 | Primary CAN missing ID 35 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31064 |  | 431065 | Primary CAN missing ID 36 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31066 |  | 431067 | Primary CAN missing ID 37 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31068 |  | 431069 | Primary CAN missing ID 38 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31070 |  | 431071 | Primary CAN missing ID 39 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31072 |  | 431073 | Primary CAN missing ID 40 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31074 |  | 431075 | Secondary CAN missing ID 1 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31076 |  | 431077 | Secondary CAN missing ID 2 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31078 |  | 431079 | Secondary CAN missing ID 3 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31080 |  | 431081 | Secondary CAN missing ID 4 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31082 |  | 431083 | Secondary CAN missing ID 5 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31084 |  | 431085 | Secondary CAN missing ID 6 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31086 |  | 431087 | Secondary CAN missing ID 7 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31088 |  | 431089 | Secondary CAN missing ID 8 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31090 |  | 431091 | Secondary CAN missing ID 9 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31092 |  | 431093 | Secondary CAN missing ID 10 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31094 |  | 431095 | Secondary CAN missing ID 11 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31096 |  | 431097 | Secondary CAN missing ID 12 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31098 |  | 431099 | Secondary CAN missing ID 13 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31100 |  | 431101 | Secondary CAN missing ID 14 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31102 |  | 431103 | Secondary CAN missing ID 15 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31104 |  | 431105 | Secondary CAN missing ID 16 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31106 |  | 431107 | Secondary CAN missing ID 17 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31108 |  | 431109 | Secondary CAN missing ID 18 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31110 |  | 431111 | Secondary CAN missing ID 19 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31112 |  | 431113 | Secondary CAN missing ID 20 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31114 |  | 431115 | Secondary CAN missing ID 21 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31116 |  | 431117 | Secondary CAN missing ID 22 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31118 |  | 431119 | Secondary CAN missing ID 23 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31120 |  | 431121 | Secondary CAN missing ID 24 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31122 |  | 431123 | Secondary CAN missing ID 25 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31124 |  | 431125 | Secondary CAN missing ID 26 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31126 |  | 431127 | Secondary CAN missing ID 27 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31128 |  | 431129 | Secondary CAN missing ID 28 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31130 |  | 431131 | Secondary CAN missing ID 29 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31132 |  | 431133 | Secondary CAN missing ID 30 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31134 |  | 431135 | Secondary CAN missing ID 31 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31136 |  | 431137 | Secondary CAN missing ID 32 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31138 |  | 431139 | Secondary CAN missing ID 33 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31140 |  | 431141 | Secondary CAN missing ID 34 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31142 |  | 431143 | Secondary CAN missing ID 35 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31144 |  | 431145 | Secondary CAN missing ID 36 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31146 |  | 431147 | Secondary CAN missing ID 37 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31148 |  | 431149 | Secondary CAN missing ID 38 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31150 |  | 431151 | Secondary CAN missing ID 39 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31152 |  | 431153 | Secondary CAN missing ID 40 - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31154 |  | 431155 | Priority error - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31156 |  | 431157 | Parameters - Non-essential load trip - Trip 1 - Over-current - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 31158 |  | 431159 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 31160 |  | 431161 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 31162 |  | 431163 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 31164 |  | 431165 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 31166 |  | 431167 | Parameters - Non-essential load trip - Trip 2 - Over-current - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 31168 |  | 431169 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 31170 |  | 431171 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 31172 |  | 431173 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 31174 |  | 431175 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 31176 |  | 431177 | Parameters - Non-essential load trip - Trip 3 - Over-current - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 31178 |  | 431179 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 31180 |  | 431181 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 31182 |  | 431183 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 31184 |  | 431185 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Inhibit | 31186 |  | 431187 | Parameters - System - Monitoring - Single-line hazard - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31188 |  | 431189 | ID not present - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31190 |  | 431191 | Unsupported application - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31192 |  | 431193 | Application internal CAN protocol conflict - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31194 |  | 431195 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31196 |  | 431197 | Dry mode: Voltage level unexpected - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 31198 |  | 431199 | Invalid DAVR configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 31200 |  | 431201 | Parameters - Communication - DEIF network - DEIF network fork detected - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31204 |  | 431205 | Parameters - Communication - DEIF network - DEIF network has only one connection - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31208 |  | 431209 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 31208 |  | 431209 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  | X
Alarm parameter: Inhibit | 31208 |  | 431209 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Inhibit | 31210 |  | 431211 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Inhibit | 31210 |  | 431211 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Configuration - Inhibit | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Inhibit | 31214 |  | 431215 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31216 |  | 431217 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31218 |  | 431219 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31220 |  | 431221 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31222 |  | 431223 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31224 |  | 431225 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31226 |  | 431227 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31228 |  | 431229 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31230 |  | 431231 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31232 |  | 431233 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31234 |  | 431235 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31236 |  | 431237 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31238 |  | 431239 | AC protections not running - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31240 |  | 431241 | AC data is missing - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31242 |  | 431243 | AC protections not running - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31244 |  | 431245 | AC data is missing - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31246 |  | 431247 | AC protections not running - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31248 |  | 431249 | AC data is missing - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31250 |  | 431251 | AC protections not running - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31252 |  | 431253 | AC data is missing - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31254 |  | 431255 | Live voltage detected - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31256 |  | 431257 | Internal issue detected. A restart is required soon! - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31258 |  | 431259 | Parameters - System - Monitoring - Missing controllers - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31260 |  | 431261 | Card issue detected - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31262 |  | 431263 | Card configuration failed - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31264 |  | 431265 | Unknown traffic on DEIF network - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31266 |  | 431267 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 31268 |  | 431269 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 31270 |  | 431271 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Inhibit | 31272 |  | 431273 | Local IO service error - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31274 |  | 431275 | App logging failure - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31276 |  | 431277 | Event logging failure - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31278 |  | 431279 | Licence error - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31280 |  | 431281 | Brightness is dimmed according to temperature - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 31282 |  | 431283 | Parameters - Grid code - Mains sync inhibit - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 31284 |  | 431285 | Parameters - Grid code - Capability curve - Import protection - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 31286 |  | 431287 | Parameters - Grid code - Capability curve - Export protection - Configuration - Inhibit | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Inhibit | 31288 |  | 431289 | Hardware is not compatible based on module versions - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33000 |  | 433001 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33002 |  | 433003 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33004 |  | 433005 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33006 |  | 433007 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33008 |  | 433009 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33010 |  | 433011 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33012 |  | 433013 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33014 |  | 433015 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33016 |  | 433017 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33018 |  | 433019 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33020 |  | 433021 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33022 |  | 433023 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33024 |  | 433025 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33026 |  | 433027 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33028 |  | 433029 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33030 |  | 433031 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33032 |  | 433033 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33034 |  | 433035 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33036 |  | 433037 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33038 |  | 433039 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33040 |  | 433041 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33042 |  | 433043 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33044 |  | 433045 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33046 |  | 433047 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33048 |  | 433049 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33050 |  | 433051 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33052 |  | 433053 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33054 |  | 433055 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33056 |  | 433057 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33058 |  | 433059 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33060 |  | 433061 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33062 |  | 433063 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33064 |  | 433065 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33066 |  | 433067 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33068 |  | 433069 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33070 |  | 433071 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33072 |  | 433073 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33074 |  | 433075 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33076 |  | 433077 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33078 |  | 433079 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33080 |  | 433081 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33082 |  | 433083 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33084 |  | 433085 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33086 |  | 433087 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33088 |  | 433089 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33090 |  | 433091 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33092 |  | 433093 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33094 |  | 433095 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33096 |  | 433097 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33098 |  | 433099 | Digital custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33200 |  | 433201 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33202 |  | 433203 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33204 |  | 433205 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33206 |  | 433207 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33208 |  | 433209 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33210 |  | 433211 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33212 |  | 433213 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33214 |  | 433215 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33216 |  | 433217 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33218 |  | 433219 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33220 |  | 433221 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33222 |  | 433223 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33224 |  | 433225 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33226 |  | 433227 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33228 |  | 433229 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33230 |  | 433231 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33232 |  | 433233 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33234 |  | 433235 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33236 |  | 433237 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33238 |  | 433239 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33240 |  | 433241 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33242 |  | 433243 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33244 |  | 433245 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33246 |  | 433247 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33248 |  | 433249 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33250 |  | 433251 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33252 |  | 433253 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33254 |  | 433255 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33256 |  | 433257 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33258 |  | 433259 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33260 |  | 433261 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33262 |  | 433263 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33264 |  | 433265 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33266 |  | 433267 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33268 |  | 433269 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33270 |  | 433271 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33272 |  | 433273 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33274 |  | 433275 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33276 |  | 433277 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33278 |  | 433279 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33280 |  | 433281 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33282 |  | 433283 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33284 |  | 433285 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33286 |  | 433287 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33288 |  | 433289 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33290 |  | 433291 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33292 |  | 433293 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33294 |  | 433295 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33296 |  | 433297 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33298 |  | 433299 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33300 |  | 433301 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33302 |  | 433303 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33304 |  | 433305 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33306 |  | 433307 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33308 |  | 433309 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33310 |  | 433311 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33312 |  | 433313 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33314 |  | 433315 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33316 |  | 433317 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33318 |  | 433319 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33320 |  | 433321 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33322 |  | 433323 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33324 |  | 433325 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33326 |  | 433327 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33328 |  | 433329 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33330 |  | 433331 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33332 |  | 433333 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33334 |  | 433335 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33336 |  | 433337 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33338 |  | 433339 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33340 |  | 433341 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33342 |  | 433343 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33344 |  | 433345 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33346 |  | 433347 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33348 |  | 433349 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33350 |  | 433351 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33352 |  | 433353 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33354 |  | 433355 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33356 |  | 433357 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33358 |  | 433359 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33360 |  | 433361 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33362 |  | 433363 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33364 |  | 433365 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33366 |  | 433367 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33368 |  | 433369 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33370 |  | 433371 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33372 |  | 433373 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33374 |  | 433375 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33376 |  | 433377 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33378 |  | 433379 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33380 |  | 433381 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33382 |  | 433383 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33384 |  | 433385 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33386 |  | 433387 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33388 |  | 433389 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33390 |  | 433391 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33392 |  | 433393 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33394 |  | 433395 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33396 |  | 433397 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33398 |  | 433399 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33400 |  | 433401 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33402 |  | 433403 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33404 |  | 433405 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33406 |  | 433407 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33408 |  | 433409 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33410 |  | 433411 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33412 |  | 433413 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33414 |  | 433415 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33416 |  | 433417 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33418 |  | 433419 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33420 |  | 433421 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33422 |  | 433423 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33424 |  | 433425 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33426 |  | 433427 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33428 |  | 433429 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33430 |  | 433431 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33432 |  | 433433 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33434 |  | 433435 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33436 |  | 433437 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33438 |  | 433439 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33440 |  | 433441 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33442 |  | 433443 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33444 |  | 433445 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33446 |  | 433447 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33448 |  | 433449 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33450 |  | 433451 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33452 |  | 433453 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33454 |  | 433455 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33456 |  | 433457 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33458 |  | 433459 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33460 |  | 433461 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33462 |  | 433463 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33464 |  | 433465 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33466 |  | 433467 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33468 |  | 433469 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33470 |  | 433471 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33472 |  | 433473 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33474 |  | 433475 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33476 |  | 433477 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33478 |  | 433479 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33480 |  | 433481 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33482 |  | 433483 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33484 |  | 433485 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33486 |  | 433487 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33488 |  | 433489 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33490 |  | 433491 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33492 |  | 433493 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33494 |  | 433495 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33496 |  | 433497 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33498 |  | 433499 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33500 |  | 433501 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33502 |  | 433503 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33504 |  | 433505 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33506 |  | 433507 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33508 |  | 433509 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33510 |  | 433511 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33512 |  | 433513 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33514 |  | 433515 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33516 |  | 433517 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33518 |  | 433519 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33520 |  | 433521 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33522 |  | 433523 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33524 |  | 433525 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33526 |  | 433527 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33528 |  | 433529 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33530 |  | 433531 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33532 |  | 433533 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33534 |  | 433535 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33536 |  | 433537 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33538 |  | 433539 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33540 |  | 433541 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33542 |  | 433543 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33544 |  | 433545 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33546 |  | 433547 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33548 |  | 433549 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33550 |  | 433551 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33552 |  | 433553 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33554 |  | 433555 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33556 |  | 433557 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33558 |  | 433559 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33560 |  | 433561 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33562 |  | 433563 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33564 |  | 433565 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33566 |  | 433567 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33568 |  | 433569 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33570 |  | 433571 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33572 |  | 433573 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33574 |  | 433575 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33576 |  | 433577 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33578 |  | 433579 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33580 |  | 433581 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33582 |  | 433583 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33584 |  | 433585 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33586 |  | 433587 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33588 |  | 433589 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33590 |  | 433591 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33592 |  | 433593 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33594 |  | 433595 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33596 |  | 433597 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Inhibit | 33598 |  | 433599 | Analogue custom alarm - Inhibit | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34000 |  | 434001 | Application initialisation error - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34002 |  | 434003 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34004 |  | 434005 | Preliminary software - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34006 |  | 434007 | Parameters - Engine - Stop sequence - Stop failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34008 |  | 434009 | Parameters - Engine - Start sequence - Start failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34010 |  | 434011 | Parameters - Engine - Start sequence - Crank failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34012 |  | 434013 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34014 |  | 434015 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34016 |  | 434017 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34018 |  | 434019 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34020 |  | 434021 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34022 |  | 434023 | Parameters - Engine - Stop sequence - Externally stopped - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34026 |  | 434027 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34028 |  | 434029 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34030 |  | 434031 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34032 |  | 434033 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34034 |  | 434035 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34036 |  | 434037 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34038 |  | 434039 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34040 |  | 434041 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34042 |  | 434043 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34044 |  | 434045 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34054 |  | 434055 | Parameters - Engine - Running detection - Primary running feedback failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34082 |  | 434083 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34082 |  | 434083 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34082 |  | 434083 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34084 |  | 434085 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34084 |  | 434085 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34084 |  | 434085 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34086 |  | 434087 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34086 |  | 434087 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34086 |  | 434087 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34088 |  | 434089 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34088 |  | 434089 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34088 |  | 434089 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34090 |  | 434091 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34090 |  | 434091 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34090 |  | 434091 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34092 |  | 434093 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34092 |  | 434093 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34092 |  | 434093 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34094 |  | 434095 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34094 |  | 434095 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34094 |  | 434095 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34096 |  | 434097 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34096 |  | 434097 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34096 |  | 434097 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34098 |  | 434099 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Shelve time | 34098 |  | 434099 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - UTC shelved | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Shelve time | 34100 |  | 434101 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Shelve time | 34100 |  | 434101 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - UTC shelved | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Shelve time | 34102 |  | 434103 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Shelve time | 34102 |  | 434103 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - UTC shelved | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Shelve time | 34104 |  | 434105 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Shelve time | 34104 |  | 434105 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - UTC shelved | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Shelve time | 34106 |  | 434107 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Shelve time | 34106 |  | 434107 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - UTC shelved | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Shelve time | 34108 |  | 434109 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Shelve time | 34108 |  | 434109 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - UTC shelved | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Shelve time | 34110 |  | 434111 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Shelve time | 34110 |  | 434111 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - UTC shelved | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Shelve time | 34112 |  | 434113 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Shelve time | 34112 |  | 434113 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - UTC shelved | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Shelve time | 34120 |  | 434121 | Parameters - Mains - AC setup - Phase sequence error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34120 |  | 434121 | Parameters - Busbar - AC setup - Phase sequence error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34120 |  | 434121 | Parameters - Busbar B - AC setup - Phase sequence error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34122 |  | 434123 | Parameters - Generator - AC setup - Phase sequence error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34122 |  | 434123 | Parameters - Busbar A - AC setup - Phase sequence error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34122 |  | 434123 | Parameters - Mains - AC setup - Phase sequence error - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34124 |  | 434125 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34206 |  | 434207 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34206 |  | 434207 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34206 |  | 434207 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34208 |  | 434209 | Parameters - Mains - Additional protections - Vector shift - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34208 |  | 434209 | Parameters - Busbar - Additional protections - Vector shift - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34208 |  | 434209 | Parameters - Busbar B - Additional protections - Vector shift - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34210 |  | 434211 | Parameters - Generator - Current protections - Inverse time over-current - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34210 |  | 434211 | Parameters - Busbar A - Current protections - Inverse time over-current - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34210 |  | 434211 | Parameters - Mains - Current protections - Inverse time over-current - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34212 |  | 434213 | Parameters - Local - 4th current input - Earth inverse time over-current - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34214 |  | 434215 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34216 |  | 434217 | Parameters - Generator - Additional protections - V< and Q< 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34216 |  | 434217 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34216 |  | 434217 | Parameters - Mains - Additional protections - V< and Q< 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34218 |  | 434219 | Parameters - Generator - Additional protections - V< and Q< 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34218 |  | 434219 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34218 |  | 434219 | Parameters - Mains - Additional protections - V< and Q< 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34220 |  | 434221 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34220 |  | 434221 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34220 |  | 434221 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34222 |  | 434223 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34222 |  | 434223 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34222 |  | 434223 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34230 |  | 434231 | Protection set point out of range - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34232 |  | 434233 | Parameters - Generator - Current protections - Stabilised differential current - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34234 |  | 434235 | Parameters - Generator - Current protections - High set differential current - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34236 |  | 434237 | Protection set point out of range (differential current) - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34238 |  | 434239 | Parameters - Local - Mode - Not under remote control - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34242 |  | 434243 | Parameters - Local - Monitoring - System not OK - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34244 |  | 434245 | Configuration update delayed - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34246 |  | 434247 | Critical process error - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34248 |  | 434249 | Restore error - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34250 |  | 434251 | SD-card format error - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34252 |  | 434253 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34254 |  | 434255 | Fieldbus configuration exceeded maximum I/O configuration - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34256 |  | 434257 | Parameters - Custom alarm - Custom alarm 0 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34258 |  | 434259 | Parameters - Custom alarm - Custom alarm 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34260 |  | 434261 | Parameters - Custom alarm - Custom alarm 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34262 |  | 434263 | Parameters - Custom alarm - Custom alarm 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34264 |  | 434265 | Parameters - Custom alarm - Custom alarm 4 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34266 |  | 434267 | Parameters - Custom alarm - Custom alarm 5 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34268 |  | 434269 | Parameters - Custom alarm - Custom alarm 6 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34270 |  | 434271 | Parameters - Custom alarm - Custom alarm 7 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34272 |  | 434273 | Parameters - Custom alarm - Custom alarm 8 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34274 |  | 434275 | Parameters - Custom alarm - Custom alarm 9 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34276 |  | 434277 | Parameters - Custom alarm - Custom alarm 10 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34278 |  | 434279 | Parameters - Custom alarm - Custom alarm 11 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34280 |  | 434281 | Parameters - Custom alarm - Custom alarm 12 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34282 |  | 434283 | Parameters - Custom alarm - Custom alarm 13 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34284 |  | 434285 | Parameters - Custom alarm - Custom alarm 14 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34286 |  | 434287 | Parameters - Custom alarm - Custom alarm 15 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34288 |  | 434289 | Parameters - Custom alarm - Custom alarm 16 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34290 |  | 434291 | Parameters - Custom alarm - Custom alarm 17 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34292 |  | 434293 | Parameters - Custom alarm - Custom alarm 18 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34294 |  | 434295 | Parameters - Custom alarm - Custom alarm 19 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34296 |  | 434297 | Parameters - Custom alarm - Custom alarm 20 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34298 |  | 434299 | Parameters - Custom alarm - Custom alarm 21 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34300 |  | 434301 | Parameters - Custom alarm - Custom alarm 22 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34302 |  | 434303 | Parameters - Custom alarm - Custom alarm 23 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34304 |  | 434305 | Parameters - Custom alarm - Custom alarm 24 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34306 |  | 434307 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34308 |  | 434309 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34326 |  | 434327 | Required hardware card(s) not found - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34328 |  | 434329 | Software mismatch on hardware module(s) - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34330 |  | 434331 | Parameters - Mains - AC setup - Multiple phase wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X
Alarm status: Shelve time | 34330 |  | 434331 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Shelve time | 34330 |  | 434331 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34332 |  | 434333 | Parameters - Generator - AC setup - Multiple phase wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Shelve time | 34332 |  | 434333 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34332 |  | 434333 | Parameters - Mains - AC setup - Multiple phase wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Shelve time | 34334 |  | 434335 | Parameters - Mains - AC setup - L1 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X
Alarm status: Shelve time | 34334 |  | 434335 | Parameters - Busbar - AC setup - L1 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Shelve time | 34334 |  | 434335 | Parameters - Busbar B - AC setup - L1 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34336 |  | 434337 | Parameters - Mains - AC setup - L2 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X
Alarm status: Shelve time | 34336 |  | 434337 | Parameters - Busbar - AC setup - L2 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Shelve time | 34336 |  | 434337 | Parameters - Busbar B - AC setup - L2 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34338 |  | 434339 | Parameters - Mains - AC setup - L3 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X
Alarm status: Shelve time | 34338 |  | 434339 | Parameters - Busbar - AC setup - L3 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Shelve time | 34338 |  | 434339 | Parameters - Busbar B - AC setup - L3 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34340 |  | 434341 | Parameters - Generator - AC setup - L1 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Shelve time | 34340 |  | 434341 | Parameters - Busbar A - AC setup - L1 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34340 |  | 434341 | Parameters - Mains - AC setup - L1 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Shelve time | 34342 |  | 434343 | Parameters - Generator - AC setup - L2 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Shelve time | 34342 |  | 434343 | Parameters - Busbar A - AC setup - L2 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34342 |  | 434343 | Parameters - Mains - AC setup - L2 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Shelve time | 34344 |  | 434345 | Parameters - Generator - AC setup - L3 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Shelve time | 34344 |  | 434345 | Parameters - Busbar A - AC setup - L3 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34344 |  | 434345 | Parameters - Mains - AC setup - L3 wire break - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Shelve time | 34356 |  | 434357 | Parameters - Mains - AC setup - Supervision alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X |  | X | X
Alarm status: Shelve time | 34358 |  | 434359 | Parameters - Engine - Emergency stop - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34358 |  | 434359 | Parameters - Busbar A - Emergency stop - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34358 |  | 434359 | Parameters - Mains - Emergency stop - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34360 |  | 434361 | Clock battery failure - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34362 |  | 434363 | Controller temperature too high - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34364 |  | 434365 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34366 |  | 434367 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34368 |  | 434369 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34370 |  | 434371 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34372 |  | 434373 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34374 |  | 434375 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34376 |  | 434377 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34378 |  | 434379 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34380 |  | 434381 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34382 |  | 434383 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34384 |  | 434385 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34386 |  | 434387 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34388 |  | 434389 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34390 |  | 434391 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34392 |  | 434393 | EIM3.1 4 supply voltage high - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34394 |  | 434395 | EIM3.1 4 supply voltage low or missing - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34396 |  | 434397 | EIM3.1 5 supply voltage high - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34398 |  | 434399 | EIM3.1 5 supply voltage low or missing - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34400 |  | 434401 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34402 |  | 434403 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34404 |  | 434405 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34406 |  | 434407 | EIM3.1 4 relay 4 wire break - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34408 |  | 434409 | EIM3.1 5 relay 4 wire break - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34410 |  | 434411 | AC protections not running - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34412 |  | 434413 | AC data is missing - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34414 |  | 434415 | AC protections not running (differential current) - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34416 |  | 434417 | AC data is missing (differential current) - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34418 |  | 434419 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34420 |  | 434421 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34422 |  | 434423 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34424 |  | 434425 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34426 |  | 434427 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34428 |  | 434429 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34430 |  | 434431 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34432 |  | 434433 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34434 |  | 434435 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34436 |  | 434437 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34438 |  | 434439 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34440 |  | 434441 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34442 |  | 434443 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34444 |  | 434445 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34446 |  | 434447 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34448 |  | 434449 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34450 |  | 434451 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34452 |  | 434453 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34456 |  | 434457 | Parameters - System - Monitoring - Duplicate controller ID - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34458 |  | 434459 | Parameters - System - Monitoring - Missing all controllers - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34462 |  | 434463 | Controller ID not configured - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34472 |  | 434473 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34474 |  | 434475 | Blackout detection mismatch - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34480 |  | 434481 | Parameters - Communication - NTP - NTP server 1 not connected - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34482 |  | 434483 | Parameters - Communication - NTP - NTP server 1 no response - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34484 |  | 434485 | Parameters - Communication - NTP - NTP server 2 not connected - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34486 |  | 434487 | Parameters - Communication - NTP - NTP server 2 no response - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34488 |  | 434489 | Parameters - Communication - NTP - No NTP server time synchronisation - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34490 |  | 434491 | Parameters - Communication - NTP - No NTP server(s) connected - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34492 |  | 434493 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34494 |  | 434495 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34592 |  | 434593 | Controller not part of system - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34594 |  | 434595 | Different single-line configurations - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34596 |  | 434597 | Single-line missing/none active - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34598 |  | 434599 | Parameters - Communication - Modbus - Modbus communication timeout - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34600 |  | 434601 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34602 |  | 434603 | Parameters - CODESYS - Monitoring - Application not OK - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34604 |  | 434605 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34606 |  | 434607 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34608 |  | 434609 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34610 |  | 434611 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34612 |  | 434613 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34614 |  | 434615 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34616 |  | 434617 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34618 |  | 434619 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34620 |  | 434621 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34622 |  | 434623 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34624 |  | 434625 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34630 |  | 434631 | Parameters - Local - CustomLogic - Configuration invalid - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34632 |  | 434633 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34634 |  | 434635 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34636 |  | 434637 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34638 |  | 434639 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34640 |  | 434641 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34642 |  | 434643 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34644 |  | 434645 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34646 |  | 434647 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34648 |  | 434649 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34650 |  | 434651 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34652 |  | 434653 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34654 |  | 434655 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34656 |  | 434657 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34658 |  | 434659 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34660 |  | 434661 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34662 |  | 434663 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34664 |  | 434665 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34666 |  | 434667 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34668 |  | 434669 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34670 |  | 434671 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34672 |  | 434673 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34674 |  | 434675 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34676 |  | 434677 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34678 |  | 434679 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34680 |  | 434681 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34682 |  | 434683 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34684 |  | 434685 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34686 |  | 434687 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34688 |  | 434689 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34690 |  | 434691 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34692 |  | 434693 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34694 |  | 434695 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34696 |  | 434697 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34698 |  | 434699 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34700 |  | 434701 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34702 |  | 434703 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34704 |  | 434705 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34706 |  | 434707 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34708 |  | 434709 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34710 |  | 434711 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34712 |  | 434713 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34714 |  | 434715 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34716 |  | 434717 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34718 |  | 434719 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34720 |  | 434721 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34722 |  | 434723 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34724 |  | 434725 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34726 |  | 434727 | DAVR unsupported AC configuration - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34728 |  | 434729 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34730 |  | 434731 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34730 |  | 434731 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34730 |  | 434731 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34732 |  | 434733 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34732 |  | 434733 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34732 |  | 434733 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34734 |  | 434735 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34734 |  | 434735 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34734 |  | 434735 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34736 |  | 434737 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34736 |  | 434737 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34736 |  | 434737 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34738 |  | 434739 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34738 |  | 434739 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34738 |  | 434739 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34740 |  | 434741 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34740 |  | 434741 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34740 |  | 434741 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34742 |  | 434743 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34742 |  | 434743 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34742 |  | 434743 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34744 |  | 434745 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34744 |  | 434745 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34744 |  | 434745 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34746 |  | 434747 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34746 |  | 434747 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34746 |  | 434747 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34748 |  | 434749 | Parameters - Generator - Current protections - Over-current 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34748 |  | 434749 | Parameters - Busbar A - Current protections - Over-current 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34748 |  | 434749 | Parameters - Mains - Current protections - Over-current 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34750 |  | 434751 | Parameters - Generator - Current protections - Over-current 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34750 |  | 434751 | Parameters - Busbar A - Current protections - Over-current 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34750 |  | 434751 | Parameters - Mains - Current protections - Over-current 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34752 |  | 434753 | Parameters - Generator - Current protections - Over-current 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34752 |  | 434753 | Parameters - Busbar A - Current protections - Over-current 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34752 |  | 434753 | Parameters - Mains - Current protections - Over-current 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34754 |  | 434755 | Parameters - Generator - Current protections - Over-current 4 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34754 |  | 434755 | Parameters - Busbar A - Current protections - Over-current 4 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34754 |  | 434755 | Parameters - Mains - Current protections - Over-current 4 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34756 |  | 434757 | Parameters - Generator - Current protections - Fast over-current 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34756 |  | 434757 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34756 |  | 434757 | Parameters - Mains - Current protections - Fast over-current 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34758 |  | 434759 | Parameters - Generator - Current protections - Fast over-current 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34758 |  | 434759 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34758 |  | 434759 | Parameters - Mains - Current protections - Fast over-current 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34760 |  | 434761 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34760 |  | 434761 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34760 |  | 434761 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34762 |  | 434763 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34762 |  | 434763 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34762 |  | 434763 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34764 |  | 434765 | Parameters - Generator - Current protections - Directional over-current 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34764 |  | 434765 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34764 |  | 434765 | Parameters - Mains - Current protections - Directional over-current 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34766 |  | 434767 | Parameters - Generator - Current protections - Directional over-current 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34766 |  | 434767 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34766 |  | 434767 | Parameters - Mains - Current protections - Directional over-current 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34768 |  | 434769 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34770 |  | 434771 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34772 |  | 434773 | Parameters - Generator - Current protections - Negative sequence current - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34772 |  | 434773 | Parameters - Busbar A - Current protections - Negative sequence current - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34772 |  | 434773 | Parameters - Mains - Current protections - Negative sequence current - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34774 |  | 434775 | Parameters - Generator - Current protections - Zero sequence current - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34774 |  | 434775 | Parameters - Busbar A - Current protections - Zero sequence current - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34774 |  | 434775 | Parameters - Mains - Current protections - Zero sequence current - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34776 |  | 434777 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34776 |  | 434777 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34776 |  | 434777 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34778 |  | 434779 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34778 |  | 434779 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34778 |  | 434779 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34780 |  | 434781 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34780 |  | 434781 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34780 |  | 434781 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34782 |  | 434783 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34782 |  | 434783 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34782 |  | 434783 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34784 |  | 434785 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34784 |  | 434785 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34784 |  | 434785 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34786 |  | 434787 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34786 |  | 434787 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34786 |  | 434787 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34788 |  | 434789 | Parameters - Generator - Power protections - Overload 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34788 |  | 434789 | Parameters - Busbar A - Power protections - Power export 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34788 |  | 434789 | Parameters - Mains - Power protections - Overload 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34790 |  | 434791 | Parameters - Generator - Power protections - Overload 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34790 |  | 434791 | Parameters - Busbar A - Power protections - Power export 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34790 |  | 434791 | Parameters - Mains - Power protections - Overload 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34792 |  | 434793 | Parameters - Generator - Power protections - Overload 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34792 |  | 434793 | Parameters - Busbar A - Power protections - Power export 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34792 |  | 434793 | Parameters - Mains - Power protections - Overload 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34794 |  | 434795 | Parameters - Generator - Power protections - Overload 4 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34794 |  | 434795 | Parameters - Busbar A - Power protections - Power export 4 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34794 |  | 434795 | Parameters - Mains - Power protections - Overload 4 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34796 |  | 434797 | Parameters - Generator - Power protections - Overload 5 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34796 |  | 434797 | Parameters - Busbar A - Power protections - Power export 5 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34796 |  | 434797 | Parameters - Mains - Power protections - Overload 5 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34798 |  | 434799 | Parameters - Generator - Power protections - Reverse power 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34798 |  | 434799 | Parameters - Busbar A - Power protections - Power import 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34798 |  | 434799 | Parameters - Mains - Power protections - Reverse power 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34800 |  | 434801 | Parameters - Generator - Power protections - Reverse power 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34800 |  | 434801 | Parameters - Busbar A - Power protections - Power import 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34800 |  | 434801 | Parameters - Mains - Power protections - Reverse power 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34802 |  | 434803 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34802 |  | 434803 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34802 |  | 434803 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34804 |  | 434805 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34804 |  | 434805 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34804 |  | 434805 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34806 |  | 434807 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34806 |  | 434807 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34806 |  | 434807 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34808 |  | 434809 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34808 |  | 434809 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34808 |  | 434809 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34810 |  | 434811 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34810 |  | 434811 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34810 |  | 434811 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34812 |  | 434813 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34812 |  | 434813 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34812 |  | 434813 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34814 |  | 434815 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34814 |  | 434815 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34814 |  | 434815 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34816 |  | 434817 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34816 |  | 434817 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34816 |  | 434817 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34818 |  | 434819 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34818 |  | 434819 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34818 |  | 434819 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34820 |  | 434821 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34820 |  | 434821 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34820 |  | 434821 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34822 |  | 434823 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34822 |  | 434823 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34822 |  | 434823 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34824 |  | 434825 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34824 |  | 434825 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34824 |  | 434825 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34826 |  | 434827 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34826 |  | 434827 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34826 |  | 434827 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34828 |  | 434829 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34828 |  | 434829 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34828 |  | 434829 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34830 |  | 434831 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34830 |  | 434831 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34830 |  | 434831 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34832 |  | 434833 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34832 |  | 434833 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34832 |  | 434833 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34834 |  | 434835 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34834 |  | 434835 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34834 |  | 434835 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34836 |  | 434837 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34836 |  | 434837 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34836 |  | 434837 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34838 |  | 434839 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34838 |  | 434839 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34838 |  | 434839 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34840 |  | 434841 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34840 |  | 434841 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34840 |  | 434841 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34842 |  | 434843 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34842 |  | 434843 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34842 |  | 434843 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34844 |  | 434845 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 34844 |  | 434845 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Shelve time | 34844 |  | 434845 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34934 |  | 434935 | Parameters - Engine - Maintenance - Service timer - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34936 |  | 434937 | Parameters - Engine - Maintenance - Service timer - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34938 |  | 434939 | Parameters - Engine - Maintenance - Service timer - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34940 |  | 434941 | Parameters - Engine - Maintenance - Service timer - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34942 |  | 434943 | External MB open failure - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34944 |  | 434945 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34946 |  | 434947 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34948 |  | 434949 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34950 |  | 434951 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34952 |  | 434953 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34954 |  | 434955 | Parameters - Breakers - Close before excitation - CBE failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 34956 |  | 434957 | Load too high - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34958 |  | 434959 | ID to run configuration failure - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 34962 |  | 434963 | Parameters - System - Monitoring - Missing any genset controller - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34964 |  | 434965 | Parameters - System - Monitoring - Missing any mains controller - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34966 |  | 434967 | Parameters - System - Monitoring - Missing any bustie controller - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34968 |  | 434969 | Can ID not available - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34970 |  | 434971 | Duplicated CAN IDs - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34972 |  | 434973 | Parameters - Local power management - Alarms - Busbar blocked - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 34974 |  | 434975 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34976 |  | 434977 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 34978 |  | 434979 | Parameters - System - Monitoring - BTB 33 position failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34980 |  | 434981 | Parameters - System - Monitoring - BTB 34 position failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34982 |  | 434983 | Parameters - System - Monitoring - BTB 35 position failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34984 |  | 434985 | Parameters - System - Monitoring - BTB 36 position failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34986 |  | 434987 | Parameters - System - Monitoring - BTB 37 position failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34988 |  | 434989 | Parameters - System - Monitoring - BTB 38 position failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34990 |  | 434991 | Parameters - System - Monitoring - BTB 39 position failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34992 |  | 434993 | Parameters - System - Monitoring - BTB 40 position failure - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34994 |  | 434995 | Primary CAN missing ID 1 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34996 |  | 434997 | Primary CAN missing ID 2 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 34998 |  | 434999 | Primary CAN missing ID 3 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35000 |  | 435001 | Primary CAN missing ID 4 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35002 |  | 435003 | Primary CAN missing ID 5 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35004 |  | 435005 | Primary CAN missing ID 6 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35006 |  | 435007 | Primary CAN missing ID 7 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35008 |  | 435009 | Primary CAN missing ID 8 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35010 |  | 435011 | Primary CAN missing ID 9 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35012 |  | 435013 | Primary CAN missing ID 10 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35014 |  | 435015 | Primary CAN missing ID 11 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35016 |  | 435017 | Primary CAN missing ID 12 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35018 |  | 435019 | Primary CAN missing ID 13 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35020 |  | 435021 | Primary CAN missing ID 14 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35022 |  | 435023 | Primary CAN missing ID 15 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35024 |  | 435025 | Primary CAN missing ID 16 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35026 |  | 435027 | Primary CAN missing ID 17 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35028 |  | 435029 | Primary CAN missing ID 18 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35030 |  | 435031 | Primary CAN missing ID 19 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35032 |  | 435033 | Primary CAN missing ID 20 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35034 |  | 435035 | Primary CAN missing ID 21 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35036 |  | 435037 | Primary CAN missing ID 22 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35038 |  | 435039 | Primary CAN missing ID 23 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35040 |  | 435041 | Primary CAN missing ID 24 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35042 |  | 435043 | Primary CAN missing ID 25 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35044 |  | 435045 | Primary CAN missing ID 26 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35046 |  | 435047 | Primary CAN missing ID 27 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35048 |  | 435049 | Primary CAN missing ID 28 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35050 |  | 435051 | Primary CAN missing ID 29 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35052 |  | 435053 | Primary CAN missing ID 30 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35054 |  | 435055 | Primary CAN missing ID 31 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35056 |  | 435057 | Primary CAN missing ID 32 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35058 |  | 435059 | Primary CAN missing ID 33 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35060 |  | 435061 | Primary CAN missing ID 34 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35062 |  | 435063 | Primary CAN missing ID 35 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35064 |  | 435065 | Primary CAN missing ID 36 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35066 |  | 435067 | Primary CAN missing ID 37 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35068 |  | 435069 | Primary CAN missing ID 38 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35070 |  | 435071 | Primary CAN missing ID 39 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35072 |  | 435073 | Primary CAN missing ID 40 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35074 |  | 435075 | Secondary CAN missing ID 1 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35076 |  | 435077 | Secondary CAN missing ID 2 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35078 |  | 435079 | Secondary CAN missing ID 3 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35080 |  | 435081 | Secondary CAN missing ID 4 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35082 |  | 435083 | Secondary CAN missing ID 5 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35084 |  | 435085 | Secondary CAN missing ID 6 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35086 |  | 435087 | Secondary CAN missing ID 7 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35088 |  | 435089 | Secondary CAN missing ID 8 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35090 |  | 435091 | Secondary CAN missing ID 9 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35092 |  | 435093 | Secondary CAN missing ID 10 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35094 |  | 435095 | Secondary CAN missing ID 11 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35096 |  | 435097 | Secondary CAN missing ID 12 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35098 |  | 435099 | Secondary CAN missing ID 13 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35100 |  | 435101 | Secondary CAN missing ID 14 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35102 |  | 435103 | Secondary CAN missing ID 15 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35104 |  | 435105 | Secondary CAN missing ID 16 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35106 |  | 435107 | Secondary CAN missing ID 17 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35108 |  | 435109 | Secondary CAN missing ID 18 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35110 |  | 435111 | Secondary CAN missing ID 19 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35112 |  | 435113 | Secondary CAN missing ID 20 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35114 |  | 435115 | Secondary CAN missing ID 21 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35116 |  | 435117 | Secondary CAN missing ID 22 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35118 |  | 435119 | Secondary CAN missing ID 23 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35120 |  | 435121 | Secondary CAN missing ID 24 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35122 |  | 435123 | Secondary CAN missing ID 25 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35124 |  | 435125 | Secondary CAN missing ID 26 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35126 |  | 435127 | Secondary CAN missing ID 27 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35128 |  | 435129 | Secondary CAN missing ID 28 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35130 |  | 435131 | Secondary CAN missing ID 29 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35132 |  | 435133 | Secondary CAN missing ID 30 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35134 |  | 435135 | Secondary CAN missing ID 31 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35136 |  | 435137 | Secondary CAN missing ID 32 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35138 |  | 435139 | Secondary CAN missing ID 33 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35140 |  | 435141 | Secondary CAN missing ID 34 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35142 |  | 435143 | Secondary CAN missing ID 35 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35144 |  | 435145 | Secondary CAN missing ID 36 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35146 |  | 435147 | Secondary CAN missing ID 37 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35148 |  | 435149 | Secondary CAN missing ID 38 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35150 |  | 435151 | Secondary CAN missing ID 39 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35152 |  | 435153 | Secondary CAN missing ID 40 - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35154 |  | 435155 | Priority error - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35156 |  | 435157 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 35158 |  | 435159 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 35160 |  | 435161 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 35162 |  | 435163 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 35164 |  | 435165 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 35166 |  | 435167 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 35168 |  | 435169 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 35170 |  | 435171 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 35172 |  | 435173 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 35174 |  | 435175 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 35176 |  | 435177 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 35178 |  | 435179 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 35180 |  | 435181 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 35182 |  | 435183 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 35184 |  | 435185 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Shelve time | 35186 |  | 435187 | Parameters - System - Monitoring - Single-line hazard - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35188 |  | 435189 | ID not present - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35190 |  | 435191 | Unsupported application - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35192 |  | 435193 | Application internal CAN protocol conflict - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35194 |  | 435195 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35196 |  | 435197 | Dry mode: Voltage level unexpected - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 35198 |  | 435199 | Invalid DAVR configuration - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 35200 |  | 435201 | Parameters - Communication - DEIF network - DEIF network fork detected - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35204 |  | 435205 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35208 |  | 435209 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 35208 |  | 435209 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  | X
Alarm status: Shelve time | 35208 |  | 435209 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - UTC shelved | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Shelve time | 35210 |  | 435211 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Shelve time | 35210 |  | 435211 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - UTC shelved | INT32 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Shelve time | 35214 |  | 435215 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35216 |  | 435217 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35218 |  | 435219 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35220 |  | 435221 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35222 |  | 435223 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35224 |  | 435225 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35226 |  | 435227 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35228 |  | 435229 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35230 |  | 435231 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35232 |  | 435233 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35234 |  | 435235 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35236 |  | 435237 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35238 |  | 435239 | AC protections not running - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35240 |  | 435241 | AC data is missing - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35242 |  | 435243 | AC protections not running - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35244 |  | 435245 | AC data is missing - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35246 |  | 435247 | AC protections not running - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35248 |  | 435249 | AC data is missing - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35250 |  | 435251 | AC protections not running - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35252 |  | 435253 | AC data is missing - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35254 |  | 435255 | Live voltage detected - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35256 |  | 435257 | Internal issue detected. A restart is required soon! - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35258 |  | 435259 | Parameters - System - Monitoring - Missing controllers - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35260 |  | 435261 | Card issue detected - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35262 |  | 435263 | Card configuration failed - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35264 |  | 435265 | Unknown traffic on DEIF network - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35266 |  | 435267 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 35268 |  | 435269 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 35270 |  | 435271 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - UTC shelved | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Shelve time | 35272 |  | 435273 | Local IO service error - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35274 |  | 435275 | App logging failure - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35276 |  | 435277 | Event logging failure - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35278 |  | 435279 | Licence error - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35280 |  | 435281 | Brightness is dimmed according to temperature - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 35282 |  | 435283 | Parameters - Grid code - Mains sync inhibit - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 35284 |  | 435285 | Parameters - Grid code - Capability curve - Import protection - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 35286 |  | 435287 | Parameters - Grid code - Capability curve - Export protection - Information - UTC shelved | INT32 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Shelve time | 35288 |  | 435289 | Hardware is not compatible based on module versions - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37000 |  | 437001 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37002 |  | 437003 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37004 |  | 437005 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37006 |  | 437007 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37008 |  | 437009 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37010 |  | 437011 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37012 |  | 437013 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37014 |  | 437015 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37016 |  | 437017 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37018 |  | 437019 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37020 |  | 437021 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37022 |  | 437023 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37024 |  | 437025 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37026 |  | 437027 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37028 |  | 437029 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37030 |  | 437031 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37032 |  | 437033 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37034 |  | 437035 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37036 |  | 437037 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37038 |  | 437039 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37040 |  | 437041 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37042 |  | 437043 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37044 |  | 437045 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37046 |  | 437047 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37048 |  | 437049 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37050 |  | 437051 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37052 |  | 437053 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37054 |  | 437055 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37056 |  | 437057 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37058 |  | 437059 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37060 |  | 437061 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37062 |  | 437063 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37064 |  | 437065 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37066 |  | 437067 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37068 |  | 437069 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37070 |  | 437071 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37072 |  | 437073 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37074 |  | 437075 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37076 |  | 437077 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37078 |  | 437079 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37080 |  | 437081 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37082 |  | 437083 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37084 |  | 437085 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37086 |  | 437087 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37088 |  | 437089 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37090 |  | 437091 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37092 |  | 437093 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37094 |  | 437095 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37096 |  | 437097 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37098 |  | 437099 | Digital custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37200 |  | 437201 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37202 |  | 437203 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37204 |  | 437205 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37206 |  | 437207 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37208 |  | 437209 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37210 |  | 437211 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37212 |  | 437213 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37214 |  | 437215 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37216 |  | 437217 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37218 |  | 437219 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37220 |  | 437221 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37222 |  | 437223 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37224 |  | 437225 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37226 |  | 437227 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37228 |  | 437229 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37230 |  | 437231 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37232 |  | 437233 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37234 |  | 437235 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37236 |  | 437237 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37238 |  | 437239 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37240 |  | 437241 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37242 |  | 437243 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37244 |  | 437245 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37246 |  | 437247 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37248 |  | 437249 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37250 |  | 437251 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37252 |  | 437253 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37254 |  | 437255 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37256 |  | 437257 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37258 |  | 437259 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37260 |  | 437261 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37262 |  | 437263 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37264 |  | 437265 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37266 |  | 437267 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37268 |  | 437269 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37270 |  | 437271 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37272 |  | 437273 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37274 |  | 437275 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37276 |  | 437277 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37278 |  | 437279 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37280 |  | 437281 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37282 |  | 437283 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37284 |  | 437285 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37286 |  | 437287 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37288 |  | 437289 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37290 |  | 437291 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37292 |  | 437293 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37294 |  | 437295 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37296 |  | 437297 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37298 |  | 437299 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37300 |  | 437301 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37302 |  | 437303 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37304 |  | 437305 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37306 |  | 437307 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37308 |  | 437309 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37310 |  | 437311 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37312 |  | 437313 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37314 |  | 437315 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37316 |  | 437317 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37318 |  | 437319 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37320 |  | 437321 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37322 |  | 437323 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37324 |  | 437325 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37326 |  | 437327 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37328 |  | 437329 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37330 |  | 437331 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37332 |  | 437333 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37334 |  | 437335 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37336 |  | 437337 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37338 |  | 437339 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37340 |  | 437341 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37342 |  | 437343 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37344 |  | 437345 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37346 |  | 437347 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37348 |  | 437349 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37350 |  | 437351 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37352 |  | 437353 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37354 |  | 437355 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37356 |  | 437357 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37358 |  | 437359 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37360 |  | 437361 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37362 |  | 437363 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37364 |  | 437365 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37366 |  | 437367 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37368 |  | 437369 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37370 |  | 437371 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37372 |  | 437373 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37374 |  | 437375 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37376 |  | 437377 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37378 |  | 437379 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37380 |  | 437381 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37382 |  | 437383 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37384 |  | 437385 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37386 |  | 437387 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37388 |  | 437389 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37390 |  | 437391 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37392 |  | 437393 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37394 |  | 437395 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37396 |  | 437397 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37398 |  | 437399 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37400 |  | 437401 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37402 |  | 437403 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37404 |  | 437405 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37406 |  | 437407 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37408 |  | 437409 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37410 |  | 437411 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37412 |  | 437413 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37414 |  | 437415 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37416 |  | 437417 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37418 |  | 437419 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37420 |  | 437421 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37422 |  | 437423 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37424 |  | 437425 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37426 |  | 437427 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37428 |  | 437429 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37430 |  | 437431 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37432 |  | 437433 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37434 |  | 437435 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37436 |  | 437437 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37438 |  | 437439 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37440 |  | 437441 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37442 |  | 437443 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37444 |  | 437445 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37446 |  | 437447 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37448 |  | 437449 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37450 |  | 437451 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37452 |  | 437453 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37454 |  | 437455 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37456 |  | 437457 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37458 |  | 437459 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37460 |  | 437461 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37462 |  | 437463 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37464 |  | 437465 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37466 |  | 437467 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37468 |  | 437469 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37470 |  | 437471 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37472 |  | 437473 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37474 |  | 437475 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37476 |  | 437477 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37478 |  | 437479 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37480 |  | 437481 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37482 |  | 437483 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37484 |  | 437485 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37486 |  | 437487 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37488 |  | 437489 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37490 |  | 437491 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37492 |  | 437493 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37494 |  | 437495 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37496 |  | 437497 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37498 |  | 437499 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37500 |  | 437501 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37502 |  | 437503 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37504 |  | 437505 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37506 |  | 437507 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37508 |  | 437509 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37510 |  | 437511 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37512 |  | 437513 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37514 |  | 437515 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37516 |  | 437517 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37518 |  | 437519 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37520 |  | 437521 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37522 |  | 437523 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37524 |  | 437525 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37526 |  | 437527 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37528 |  | 437529 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37530 |  | 437531 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37532 |  | 437533 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37534 |  | 437535 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37536 |  | 437537 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37538 |  | 437539 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37540 |  | 437541 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37542 |  | 437543 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37544 |  | 437545 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37546 |  | 437547 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37548 |  | 437549 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37550 |  | 437551 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37552 |  | 437553 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37554 |  | 437555 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37556 |  | 437557 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37558 |  | 437559 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37560 |  | 437561 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37562 |  | 437563 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37564 |  | 437565 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37566 |  | 437567 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37568 |  | 437569 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37570 |  | 437571 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37572 |  | 437573 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37574 |  | 437575 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37576 |  | 437577 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37578 |  | 437579 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37580 |  | 437581 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37582 |  | 437583 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37584 |  | 437585 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37586 |  | 437587 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37588 |  | 437589 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37590 |  | 437591 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37592 |  | 437593 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37594 |  | 437595 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37596 |  | 437597 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Shelve time | 37598 |  | 437599 | Analogue custom alarm - UTC shelved | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38000 |  | 438001 | Application initialisation error - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38001 |  | 438002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38002 |  | 438003 | Preliminary software - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38003 |  | 438004 | Parameters - Engine - Stop sequence - Stop failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38004 |  | 438005 | Parameters - Engine - Start sequence - Start failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38005 |  | 438006 | Parameters - Engine - Start sequence - Crank failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38006 |  | 438007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38007 |  | 438008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38008 |  | 438009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38009 |  | 438010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38010 |  | 438011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38011 |  | 438012 | Parameters - Engine - Stop sequence - Externally stopped - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38013 |  | 438014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38014 |  | 438015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38015 |  | 438016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38016 |  | 438017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38017 |  | 438018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38018 |  | 438019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38019 |  | 438020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38020 |  | 438021 | Parameters - Engine - Protections - Level - Coolant level 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38021 |  | 438022 | Parameters - Engine - Protections - Level - Coolant level 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38022 |  | 438023 | Parameters - Engine - Protections - Level - Coolant level 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38027 |  | 438028 | Parameters - Engine - Running detection - Primary running feedback failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38041 |  | 438042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38041 |  | 438042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38041 |  | 438042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38042 |  | 438043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38042 |  | 438043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38042 |  | 438043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38043 |  | 438044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38043 |  | 438044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38043 |  | 438044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38044 |  | 438045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38044 |  | 438045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38044 |  | 438045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38045 |  | 438046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38045 |  | 438046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38045 |  | 438046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38046 |  | 438047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38046 |  | 438047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38046 |  | 438047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38047 |  | 438048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38047 |  | 438048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38047 |  | 438048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38048 |  | 438049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38048 |  | 438049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38048 |  | 438049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38049 |  | 438050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Severity | 38049 |  | 438050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Configuration - Severity | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Severity | 38050 |  | 438051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Severity | 38050 |  | 438051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Configuration - Severity | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Severity | 38051 |  | 438052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Severity | 38051 |  | 438052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Configuration - Severity | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Severity | 38052 |  | 438053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Severity | 38052 |  | 438053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Configuration - Severity | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Severity | 38053 |  | 438054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Severity | 38053 |  | 438054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Configuration - Severity | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Severity | 38054 |  | 438055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Severity | 38054 |  | 438055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Configuration - Severity | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Severity | 38055 |  | 438056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Severity | 38055 |  | 438056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Configuration - Severity | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Severity | 38056 |  | 438057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Severity | 38056 |  | 438057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Configuration - Severity | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Severity | 38060 |  | 438061 | Parameters - Mains - AC setup - Phase sequence error - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38060 |  | 438061 | Parameters - Busbar - AC setup - Phase sequence error - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38060 |  | 438061 | Parameters - Busbar B - AC setup - Phase sequence error - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38061 |  | 438062 | Parameters - Generator - AC setup - Phase sequence error - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38061 |  | 438062 | Parameters - Busbar A - AC setup - Phase sequence error - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38061 |  | 438062 | Parameters - Mains - AC setup - Phase sequence error - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38062 |  | 438063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38103 |  | 438104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38103 |  | 438104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38103 |  | 438104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38104 |  | 438105 | Parameters - Mains - Additional protections - Vector shift - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38104 |  | 438105 | Parameters - Busbar - Additional protections - Vector shift - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38104 |  | 438105 | Parameters - Busbar B - Additional protections - Vector shift - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38105 |  | 438106 | Parameters - Generator - Current protections - Inverse time over-current - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38105 |  | 438106 | Parameters - Busbar A - Current protections - Inverse time over-current - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38105 |  | 438106 | Parameters - Mains - Current protections - Inverse time over-current - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38106 |  | 438107 | Parameters - Local - 4th current input - Earth inverse time over-current - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38107 |  | 438108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38108 |  | 438109 | Parameters - Generator - Additional protections - V< and Q< 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38108 |  | 438109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38108 |  | 438109 | Parameters - Mains - Additional protections - V< and Q< 1 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38109 |  | 438110 | Parameters - Generator - Additional protections - V< and Q< 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38109 |  | 438110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38109 |  | 438110 | Parameters - Mains - Additional protections - V< and Q< 2 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38110 |  | 438111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38110 |  | 438111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38110 |  | 438111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38111 |  | 438112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38111 |  | 438112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38111 |  | 438112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38115 |  | 438116 | Protection set point out of range - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38116 |  | 438117 | Parameters - Generator - Current protections - Stabilised differential current - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38117 |  | 438118 | Parameters - Generator - Current protections - High set differential current - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38118 |  | 438119 | Protection set point out of range (differential current) - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38119 |  | 438120 | Parameters - Local - Mode - Not under remote control - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38121 |  | 438122 | Parameters - Local - Monitoring - System not OK - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38122 |  | 438123 | Configuration update delayed - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38123 |  | 438124 | Critical process error - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38124 |  | 438125 | Restore error - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38125 |  | 438126 | SD-card format error - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38126 |  | 438127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38127 |  | 438128 | Fieldbus configuration exceeded maximum I/O configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38128 |  | 438129 | Parameters - Custom alarm - Custom alarm 0 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38129 |  | 438130 | Parameters - Custom alarm - Custom alarm 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38130 |  | 438131 | Parameters - Custom alarm - Custom alarm 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38131 |  | 438132 | Parameters - Custom alarm - Custom alarm 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38132 |  | 438133 | Parameters - Custom alarm - Custom alarm 4 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38133 |  | 438134 | Parameters - Custom alarm - Custom alarm 5 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38134 |  | 438135 | Parameters - Custom alarm - Custom alarm 6 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38135 |  | 438136 | Parameters - Custom alarm - Custom alarm 7 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38136 |  | 438137 | Parameters - Custom alarm - Custom alarm 8 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38137 |  | 438138 | Parameters - Custom alarm - Custom alarm 9 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38138 |  | 438139 | Parameters - Custom alarm - Custom alarm 10 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38139 |  | 438140 | Parameters - Custom alarm - Custom alarm 11 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38140 |  | 438141 | Parameters - Custom alarm - Custom alarm 12 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38141 |  | 438142 | Parameters - Custom alarm - Custom alarm 13 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38142 |  | 438143 | Parameters - Custom alarm - Custom alarm 14 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38143 |  | 438144 | Parameters - Custom alarm - Custom alarm 15 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38144 |  | 438145 | Parameters - Custom alarm - Custom alarm 16 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38145 |  | 438146 | Parameters - Custom alarm - Custom alarm 17 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38146 |  | 438147 | Parameters - Custom alarm - Custom alarm 18 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38147 |  | 438148 | Parameters - Custom alarm - Custom alarm 19 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38148 |  | 438149 | Parameters - Custom alarm - Custom alarm 20 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38149 |  | 438150 | Parameters - Custom alarm - Custom alarm 21 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38150 |  | 438151 | Parameters - Custom alarm - Custom alarm 22 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38151 |  | 438152 | Parameters - Custom alarm - Custom alarm 23 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38152 |  | 438153 | Parameters - Custom alarm - Custom alarm 24 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38153 |  | 438154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38154 |  | 438155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38163 |  | 438164 | Required hardware card(s) not found - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38164 |  | 438165 | Software mismatch on hardware module(s) - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38165 |  | 438166 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Severity | 38165 |  | 438166 | Parameters - Busbar - AC setup - Multiple phase wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Severity | 38165 |  | 438166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38166 |  | 438167 | Parameters - Generator - AC setup - Multiple phase wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Severity | 38166 |  | 438167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38166 |  | 438167 | Parameters - Mains - AC setup - Multiple phase wire break - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Severity | 38167 |  | 438168 | Parameters - Mains - AC setup - L1 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Severity | 38167 |  | 438168 | Parameters - Busbar - AC setup - L1 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Severity | 38167 |  | 438168 | Parameters - Busbar B - AC setup - L1 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38168 |  | 438169 | Parameters - Mains - AC setup - L2 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Severity | 38168 |  | 438169 | Parameters - Busbar - AC setup - L2 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Severity | 38168 |  | 438169 | Parameters - Busbar B - AC setup - L2 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38169 |  | 438170 | Parameters - Mains - AC setup - L3 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm parameter: Severity | 38169 |  | 438170 | Parameters - Busbar - AC setup - L3 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm parameter: Severity | 38169 |  | 438170 | Parameters - Busbar B - AC setup - L3 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38170 |  | 438171 | Parameters - Generator - AC setup - L1 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Severity | 38170 |  | 438171 | Parameters - Busbar A - AC setup - L1 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38170 |  | 438171 | Parameters - Mains - AC setup - L1 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Severity | 38171 |  | 438172 | Parameters - Generator - AC setup - L2 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Severity | 38171 |  | 438172 | Parameters - Busbar A - AC setup - L2 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38171 |  | 438172 | Parameters - Mains - AC setup - L2 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Severity | 38172 |  | 438173 | Parameters - Generator - AC setup - L3 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm parameter: Severity | 38172 |  | 438173 | Parameters - Busbar A - AC setup - L3 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38172 |  | 438173 | Parameters - Mains - AC setup - L3 wire break - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm parameter: Severity | 38178 |  | 438179 | Parameters - Mains - AC setup - Supervision alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X |  | X | X
Alarm parameter: Severity | 38179 |  | 438180 | Parameters - Engine - Emergency stop - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38179 |  | 438180 | Parameters - Busbar A - Emergency stop - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38179 |  | 438180 | Parameters - Mains - Emergency stop - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38180 |  | 438181 | Clock battery failure - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38181 |  | 438182 | Controller temperature too high - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38182 |  | 438183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38183 |  | 438184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38184 |  | 438185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38185 |  | 438186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38186 |  | 438187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38187 |  | 438188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38188 |  | 438189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38189 |  | 438190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38190 |  | 438191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38191 |  | 438192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38192 |  | 438193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38193 |  | 438194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38194 |  | 438195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38195 |  | 438196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38196 |  | 438197 | EIM3.1 4 supply voltage high - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38197 |  | 438198 | EIM3.1 4 supply voltage low or missing - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38198 |  | 438199 | EIM3.1 5 supply voltage high - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38199 |  | 438200 | EIM3.1 5 supply voltage low or missing - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38200 |  | 438201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38201 |  | 438202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38202 |  | 438203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38203 |  | 438204 | EIM3.1 4 relay 4 wire break - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38204 |  | 438205 | EIM3.1 5 relay 4 wire break - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38205 |  | 438206 | AC protections not running - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38206 |  | 438207 | AC data is missing - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38207 |  | 438208 | AC protections not running (differential current) - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38208 |  | 438209 | AC data is missing (differential current) - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38209 |  | 438210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38210 |  | 438211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38211 |  | 438212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38212 |  | 438213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38213 |  | 438214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38214 |  | 438215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38215 |  | 438216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38216 |  | 438217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38217 |  | 438218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38218 |  | 438219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38219 |  | 438220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38220 |  | 438221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38221 |  | 438222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38222 |  | 438223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38223 |  | 438224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38224 |  | 438225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38225 |  | 438226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38226 |  | 438227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38228 |  | 438229 | Parameters - System - Monitoring - Duplicate controller ID - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38229 |  | 438230 | Parameters - System - Monitoring - Missing all controllers - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38231 |  | 438232 | Controller ID not configured - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38236 |  | 438237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38237 |  | 438238 | Blackout detection mismatch - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38240 |  | 438241 | Parameters - Communication - NTP - NTP server 1 not connected - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38241 |  | 438242 | Parameters - Communication - NTP - NTP server 1 no response - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38242 |  | 438243 | Parameters - Communication - NTP - NTP server 2 not connected - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38243 |  | 438244 | Parameters - Communication - NTP - NTP server 2 no response - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38244 |  | 438245 | Parameters - Communication - NTP - No NTP server time synchronisation - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38245 |  | 438246 | Parameters - Communication - NTP - No NTP server(s) connected - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38246 |  | 438247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38247 |  | 438248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38296 |  | 438297 | Controller not part of system - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38297 |  | 438298 | Different single-line configurations - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38298 |  | 438299 | Single-line missing/none active - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38299 |  | 438300 | Parameters - Communication - Modbus - Modbus communication timeout - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38300 |  | 438301 | Parameters - CODESYS - Monitoring - I/O config conflict - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38301 |  | 438302 | Parameters - CODESYS - Monitoring - Application not OK - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38302 |  | 438303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38303 |  | 438304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38304 |  | 438305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38305 |  | 438306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38306 |  | 438307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38307 |  | 438308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38308 |  | 438309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38309 |  | 438310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38310 |  | 438311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38311 |  | 438312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38312 |  | 438313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38315 |  | 438316 | Parameters - Local - CustomLogic - Configuration invalid - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38316 |  | 438317 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38317 |  | 438318 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38318 |  | 438319 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38319 |  | 438320 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38320 |  | 438321 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38321 |  | 438322 | Parameters - Generator - Digital AVR - Alarms - Open diode - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38322 |  | 438323 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38323 |  | 438324 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38324 |  | 438325 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38325 |  | 438326 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38326 |  | 438327 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38327 |  | 438328 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38328 |  | 438329 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38329 |  | 438330 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38330 |  | 438331 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38331 |  | 438332 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38332 |  | 438333 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38333 |  | 438334 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38334 |  | 438335 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38335 |  | 438336 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38336 |  | 438337 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38337 |  | 438338 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38338 |  | 438339 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38339 |  | 438340 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38340 |  | 438341 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38341 |  | 438342 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38342 |  | 438343 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38343 |  | 438344 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38344 |  | 438345 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38345 |  | 438346 | Parameters - Generator - Digital AVR - Alarms - Motor start - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38346 |  | 438347 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38347 |  | 438348 | Parameters - Generator - Digital AVR - Alarms - Power supply - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38348 |  | 438349 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38349 |  | 438350 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38350 |  | 438351 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38351 |  | 438352 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38352 |  | 438353 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38353 |  | 438354 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38354 |  | 438355 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38355 |  | 438356 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38356 |  | 438357 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38357 |  | 438358 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38358 |  | 438359 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38359 |  | 438360 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38360 |  | 438361 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38361 |  | 438362 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38362 |  | 438363 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38363 |  | 438364 | DAVR unsupported AC configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38364 |  | 438365 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38365 |  | 438366 | Parameters - Generator - Voltage protections - Under-voltage 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38365 |  | 438366 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38365 |  | 438366 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38366 |  | 438367 | Parameters - Generator - Voltage protections - Under-voltage 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38366 |  | 438367 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38366 |  | 438367 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38367 |  | 438368 | Parameters - Generator - Voltage protections - Under-voltage 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38367 |  | 438368 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38367 |  | 438368 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38368 |  | 438369 | Parameters - Generator - Voltage protections - Over-voltage 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38368 |  | 438369 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38368 |  | 438369 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38369 |  | 438370 | Parameters - Generator - Voltage protections - Over-voltage 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38369 |  | 438370 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38369 |  | 438370 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38370 |  | 438371 | Parameters - Generator - Voltage protections - Voltage unbalance - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38370 |  | 438371 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38370 |  | 438371 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38371 |  | 438372 | Parameters - Generator - Voltage protections - Negative sequence voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38371 |  | 438372 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38371 |  | 438372 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38372 |  | 438373 | Parameters - Generator - Voltage protections - Zero sequence voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38372 |  | 438373 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38372 |  | 438373 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38373 |  | 438374 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38373 |  | 438374 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38373 |  | 438374 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38374 |  | 438375 | Parameters - Generator - Current protections - Over-current 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38374 |  | 438375 | Parameters - Busbar A - Current protections - Over-current 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38374 |  | 438375 | Parameters - Mains - Current protections - Over-current 1 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38375 |  | 438376 | Parameters - Generator - Current protections - Over-current 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38375 |  | 438376 | Parameters - Busbar A - Current protections - Over-current 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38375 |  | 438376 | Parameters - Mains - Current protections - Over-current 2 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38376 |  | 438377 | Parameters - Generator - Current protections - Over-current 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38376 |  | 438377 | Parameters - Busbar A - Current protections - Over-current 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38376 |  | 438377 | Parameters - Mains - Current protections - Over-current 3 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38377 |  | 438378 | Parameters - Generator - Current protections - Over-current 4 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38377 |  | 438378 | Parameters - Busbar A - Current protections - Over-current 4 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38377 |  | 438378 | Parameters - Mains - Current protections - Over-current 4 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38378 |  | 438379 | Parameters - Generator - Current protections - Fast over-current 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38378 |  | 438379 | Parameters - Busbar A - Current protections - Fast over-current 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38378 |  | 438379 | Parameters - Mains - Current protections - Fast over-current 1 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38379 |  | 438380 | Parameters - Generator - Current protections - Fast over-current 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38379 |  | 438380 | Parameters - Busbar A - Current protections - Fast over-current 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38379 |  | 438380 | Parameters - Mains - Current protections - Fast over-current 2 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38380 |  | 438381 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38380 |  | 438381 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38380 |  | 438381 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38381 |  | 438382 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38381 |  | 438382 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38381 |  | 438382 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38382 |  | 438383 | Parameters - Generator - Current protections - Directional over-current 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38382 |  | 438383 | Parameters - Busbar A - Current protections - Directional over-current 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38382 |  | 438383 | Parameters - Mains - Current protections - Directional over-current 1 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38383 |  | 438384 | Parameters - Generator - Current protections - Directional over-current 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38383 |  | 438384 | Parameters - Busbar A - Current protections - Directional over-current 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38383 |  | 438384 | Parameters - Mains - Current protections - Directional over-current 2 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38384 |  | 438385 | Parameters - Busbar A - Current protections - Directional over-current 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38385 |  | 438386 | Parameters - Busbar A - Current protections - Directional over-current 4 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38386 |  | 438387 | Parameters - Generator - Current protections - Negative sequence current - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38386 |  | 438387 | Parameters - Busbar A - Current protections - Negative sequence current - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38386 |  | 438387 | Parameters - Mains - Current protections - Negative sequence current - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38387 |  | 438388 | Parameters - Generator - Current protections - Zero sequence current - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38387 |  | 438388 | Parameters - Busbar A - Current protections - Zero sequence current - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38387 |  | 438388 | Parameters - Mains - Current protections - Zero sequence current - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38388 |  | 438389 | Parameters - Generator - Frequency protections - Over-frequency 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38388 |  | 438389 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38388 |  | 438389 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38389 |  | 438390 | Parameters - Generator - Frequency protections - Over-frequency 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38389 |  | 438390 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38389 |  | 438390 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38390 |  | 438391 | Parameters - Generator - Frequency protections - Over-frequency 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38390 |  | 438391 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38390 |  | 438391 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38391 |  | 438392 | Parameters - Generator - Frequency protections - Under-frequency 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38391 |  | 438392 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38391 |  | 438392 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38392 |  | 438393 | Parameters - Generator - Frequency protections - Under-frequency 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38392 |  | 438393 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38392 |  | 438393 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38393 |  | 438394 | Parameters - Generator - Frequency protections - Under-frequency 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38393 |  | 438394 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38393 |  | 438394 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38394 |  | 438395 | Parameters - Generator - Power protections - Overload 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38394 |  | 438395 | Parameters - Busbar A - Power protections - Power export 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38394 |  | 438395 | Parameters - Mains - Power protections - Overload 1 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38395 |  | 438396 | Parameters - Generator - Power protections - Overload 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38395 |  | 438396 | Parameters - Busbar A - Power protections - Power export 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38395 |  | 438396 | Parameters - Mains - Power protections - Overload 2 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38396 |  | 438397 | Parameters - Generator - Power protections - Overload 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38396 |  | 438397 | Parameters - Busbar A - Power protections - Power export 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38396 |  | 438397 | Parameters - Mains - Power protections - Overload 3 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38397 |  | 438398 | Parameters - Generator - Power protections - Overload 4 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38397 |  | 438398 | Parameters - Busbar A - Power protections - Power export 4 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38397 |  | 438398 | Parameters - Mains - Power protections - Overload 4 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38398 |  | 438399 | Parameters - Generator - Power protections - Overload 5 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38398 |  | 438399 | Parameters - Busbar A - Power protections - Power export 5 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38398 |  | 438399 | Parameters - Mains - Power protections - Overload 5 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38399 |  | 438400 | Parameters - Generator - Power protections - Reverse power 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38399 |  | 438400 | Parameters - Busbar A - Power protections - Power import 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38399 |  | 438400 | Parameters - Mains - Power protections - Reverse power 1 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38400 |  | 438401 | Parameters - Generator - Power protections - Reverse power 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38400 |  | 438401 | Parameters - Busbar A - Power protections - Power import 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38400 |  | 438401 | Parameters - Mains - Power protections - Reverse power 2 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38401 |  | 438402 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38401 |  | 438402 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38401 |  | 438402 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38402 |  | 438403 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38402 |  | 438403 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38402 |  | 438403 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38403 |  | 438404 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38403 |  | 438404 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38403 |  | 438404 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38404 |  | 438405 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38404 |  | 438405 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38404 |  | 438405 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38405 |  | 438406 | Parameters - Mains - Voltage protections - Over-voltage 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38405 |  | 438406 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38405 |  | 438406 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38406 |  | 438407 | Parameters - Mains - Voltage protections - Over-voltage 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38406 |  | 438407 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38406 |  | 438407 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38407 |  | 438408 | Parameters - Mains - Voltage protections - Over-voltage 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38407 |  | 438408 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38407 |  | 438408 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38408 |  | 438409 | Parameters - Mains - Voltage protections - Under-voltage 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38408 |  | 438409 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38408 |  | 438409 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38409 |  | 438410 | Parameters - Mains - Voltage protections - Under-voltage 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38409 |  | 438410 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38409 |  | 438410 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38410 |  | 438411 | Parameters - Mains - Voltage protections - Under-voltage 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38410 |  | 438411 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38410 |  | 438411 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38411 |  | 438412 | Parameters - Mains - Voltage protections - Under-voltage 4 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38411 |  | 438412 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38411 |  | 438412 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38412 |  | 438413 | Parameters - Mains - Voltage protections - Voltage unbalance - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38412 |  | 438413 | Parameters - Busbar - Voltage protections - Voltage unbalance - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38412 |  | 438413 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38413 |  | 438414 | Parameters - Mains - Frequency protections - Over-frequency 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38413 |  | 438414 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38413 |  | 438414 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38414 |  | 438415 | Parameters - Mains - Frequency protections - Over-frequency 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38414 |  | 438415 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38414 |  | 438415 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38415 |  | 438416 | Parameters - Mains - Frequency protections - Over-frequency 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38415 |  | 438416 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38415 |  | 438416 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38416 |  | 438417 | Parameters - Mains - Frequency protections - Under-frequency 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38416 |  | 438417 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38416 |  | 438417 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38417 |  | 438418 | Parameters - Mains - Frequency protections - Under-frequency 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38417 |  | 438418 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38417 |  | 438418 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38418 |  | 438419 | Parameters - Mains - Frequency protections - Under-frequency 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38418 |  | 438419 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38418 |  | 438419 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38419 |  | 438420 | Parameters - Mains - Frequency protections - Under-frequency 4 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38419 |  | 438420 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38419 |  | 438420 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38420 |  | 438421 | Parameters - Mains - Voltage protections - Negative sequence voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38420 |  | 438421 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38420 |  | 438421 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38421 |  | 438422 | Parameters - Mains - Voltage protections - Zero sequence voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38421 |  | 438422 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38421 |  | 438422 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38422 |  | 438423 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38422 |  | 438423 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm parameter: Severity | 38422 |  | 438423 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38471 |  | 438472 | Parameters - Non-essential load trip - Trip 1 - Over-current - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38472 |  | 438473 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38473 |  | 438474 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38474 |  | 438475 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38475 |  | 438476 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38476 |  | 438477 | Parameters - Non-essential load trip - Trip 2 - Over-current - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38477 |  | 438478 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38478 |  | 438479 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38479 |  | 438480 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38480 |  | 438481 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38481 |  | 438482 | Parameters - Non-essential load trip - Trip 3 - Over-current - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38482 |  | 438483 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38483 |  | 438484 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38484 |  | 438485 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38485 |  | 438486 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38490 |  | 438491 | Parameters - System - Monitoring - Single-line hazard - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38491 |  | 438492 | ID not present - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38492 |  | 438493 | Unsupported application - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38493 |  | 438494 | Application internal CAN protocol conflict - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38495 |  | 438496 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38510 |  | 438511 | Dry mode: Voltage level unexpected - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38541 |  | 438542 | Hardware is not compatible based on module versions - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38559 |  | 438560 | Invalid DAVR configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38717 |  | 438718 | Parameters - Engine - Maintenance - Service timer - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38718 |  | 438719 | Parameters - Engine - Maintenance - Service timer - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38719 |  | 438720 | Parameters - Engine - Maintenance - Service timer - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38720 |  | 438721 | Parameters - Engine - Maintenance - Service timer - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38721 |  | 438722 | External MB open failure - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38722 |  | 438723 | Parameters - Power management rules - Ground relay - Ground relay general failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38723 |  | 438724 | Parameters - Power management rules - Ground relay - Ground relay open failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38724 |  | 438725 | Parameters - Power management rules - Ground relay - Ground relay close failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38725 |  | 438726 | Parameters - Power management rules - Ground relay - Ground relay position failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38726 |  | 438727 | Parameters - Breakers - Close before excitation - CBE rerun failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38727 |  | 438728 | Parameters - Breakers - Close before excitation - CBE failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38728 |  | 438729 | Load too high - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38729 |  | 438730 | ID to run configuration failure - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38731 |  | 438732 | Parameters - System - Monitoring - Missing any genset controller - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38732 |  | 438733 | Parameters - System - Monitoring - Missing any mains controller - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38733 |  | 438734 | Parameters - System - Monitoring - Missing any bustie controller - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38734 |  | 438735 | Can ID not available - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38735 |  | 438736 | Duplicated CAN IDs - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38736 |  | 438737 | Parameters - Local power management - Alarms - Busbar blocked - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm parameter: Severity | 38737 |  | 438738 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38738 |  | 438739 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38739 |  | 438740 | Parameters - System - Monitoring - BTB 33 position failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38740 |  | 438741 | Parameters - System - Monitoring - BTB 34 position failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38741 |  | 438742 | Parameters - System - Monitoring - BTB 35 position failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38742 |  | 438743 | Parameters - System - Monitoring - BTB 36 position failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38743 |  | 438744 | Parameters - System - Monitoring - BTB 37 position failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38744 |  | 438745 | Parameters - System - Monitoring - BTB 38 position failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38745 |  | 438746 | Parameters - System - Monitoring - BTB 39 position failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38746 |  | 438747 | Parameters - System - Monitoring - BTB 40 position failure - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38747 |  | 438748 | Primary CAN missing ID 1 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38748 |  | 438749 | Primary CAN missing ID 2 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38749 |  | 438750 | Primary CAN missing ID 3 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38750 |  | 438751 | Primary CAN missing ID 4 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38751 |  | 438752 | Primary CAN missing ID 5 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38752 |  | 438753 | Primary CAN missing ID 6 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38753 |  | 438754 | Primary CAN missing ID 7 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38754 |  | 438755 | Primary CAN missing ID 8 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38755 |  | 438756 | Primary CAN missing ID 9 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38756 |  | 438757 | Primary CAN missing ID 10 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38757 |  | 438758 | Primary CAN missing ID 11 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38758 |  | 438759 | Primary CAN missing ID 12 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38759 |  | 438760 | Primary CAN missing ID 13 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38760 |  | 438761 | Primary CAN missing ID 14 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38761 |  | 438762 | Primary CAN missing ID 15 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38762 |  | 438763 | Primary CAN missing ID 16 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38763 |  | 438764 | Primary CAN missing ID 17 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38764 |  | 438765 | Primary CAN missing ID 18 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38765 |  | 438766 | Primary CAN missing ID 19 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38766 |  | 438767 | Primary CAN missing ID 20 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38767 |  | 438768 | Primary CAN missing ID 21 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38768 |  | 438769 | Primary CAN missing ID 22 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38769 |  | 438770 | Primary CAN missing ID 23 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38770 |  | 438771 | Primary CAN missing ID 24 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38771 |  | 438772 | Primary CAN missing ID 25 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38772 |  | 438773 | Primary CAN missing ID 26 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38773 |  | 438774 | Primary CAN missing ID 27 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38774 |  | 438775 | Primary CAN missing ID 28 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38775 |  | 438776 | Primary CAN missing ID 29 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38776 |  | 438777 | Primary CAN missing ID 30 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38777 |  | 438778 | Primary CAN missing ID 31 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38778 |  | 438779 | Primary CAN missing ID 32 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38779 |  | 438780 | Primary CAN missing ID 33 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38780 |  | 438781 | Primary CAN missing ID 34 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38781 |  | 438782 | Primary CAN missing ID 35 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38782 |  | 438783 | Primary CAN missing ID 36 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38783 |  | 438784 | Primary CAN missing ID 37 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38784 |  | 438785 | Primary CAN missing ID 38 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38785 |  | 438786 | Primary CAN missing ID 39 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38786 |  | 438787 | Primary CAN missing ID 40 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38787 |  | 438788 | Secondary CAN missing ID 1 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38788 |  | 438789 | Secondary CAN missing ID 2 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38789 |  | 438790 | Secondary CAN missing ID 3 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38790 |  | 438791 | Secondary CAN missing ID 4 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38791 |  | 438792 | Secondary CAN missing ID 5 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38792 |  | 438793 | Secondary CAN missing ID 6 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38793 |  | 438794 | Secondary CAN missing ID 7 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38794 |  | 438795 | Secondary CAN missing ID 8 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38795 |  | 438796 | Secondary CAN missing ID 9 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38796 |  | 438797 | Secondary CAN missing ID 10 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38797 |  | 438798 | Secondary CAN missing ID 11 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38798 |  | 438799 | Secondary CAN missing ID 12 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38799 |  | 438800 | Secondary CAN missing ID 13 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38800 |  | 438801 | Secondary CAN missing ID 14 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38801 |  | 438802 | Secondary CAN missing ID 15 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38802 |  | 438803 | Secondary CAN missing ID 16 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38803 |  | 438804 | Secondary CAN missing ID 17 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38804 |  | 438805 | Secondary CAN missing ID 18 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38805 |  | 438806 | Secondary CAN missing ID 19 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38806 |  | 438807 | Secondary CAN missing ID 20 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38807 |  | 438808 | Secondary CAN missing ID 21 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38808 |  | 438809 | Secondary CAN missing ID 22 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38809 |  | 438810 | Secondary CAN missing ID 23 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38810 |  | 438811 | Secondary CAN missing ID 24 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38811 |  | 438812 | Secondary CAN missing ID 25 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38812 |  | 438813 | Secondary CAN missing ID 26 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38813 |  | 438814 | Secondary CAN missing ID 27 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38814 |  | 438815 | Secondary CAN missing ID 28 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38815 |  | 438816 | Secondary CAN missing ID 29 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38816 |  | 438817 | Secondary CAN missing ID 30 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38817 |  | 438818 | Secondary CAN missing ID 31 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38818 |  | 438819 | Secondary CAN missing ID 32 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38819 |  | 438820 | Secondary CAN missing ID 33 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38820 |  | 438821 | Secondary CAN missing ID 34 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38821 |  | 438822 | Secondary CAN missing ID 35 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38822 |  | 438823 | Secondary CAN missing ID 36 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38823 |  | 438824 | Secondary CAN missing ID 37 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38824 |  | 438825 | Secondary CAN missing ID 38 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38825 |  | 438826 | Secondary CAN missing ID 39 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38826 |  | 438827 | Secondary CAN missing ID 40 - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38827 |  | 438828 | Priority error - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38850 |  | 438851 | Parameters - Communication - DEIF network - DEIF network fork detected - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38852 |  | 438853 | Parameters - Communication - DEIF network - DEIF network has only one connection - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38854 |  | 438855 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38854 |  | 438855 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  | X
Alarm parameter: Severity | 38854 |  | 438855 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Severity | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm parameter: Severity | 38855 |  | 438856 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm parameter: Severity | 38855 |  | 438856 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Configuration - Severity | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm parameter: Severity | 38857 |  | 438858 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38858 |  | 438859 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38859 |  | 438860 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38860 |  | 438861 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38861 |  | 438862 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38862 |  | 438863 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38863 |  | 438864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38864 |  | 438865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38865 |  | 438866 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38866 |  | 438867 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38867 |  | 438868 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38868 |  | 438869 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38869 |  | 438870 | AC protections not running - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38870 |  | 438871 | AC data is missing - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38871 |  | 438872 | AC protections not running - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38872 |  | 438873 | AC data is missing - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38873 |  | 438874 | AC protections not running - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38874 |  | 438875 | AC data is missing - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38875 |  | 438876 | AC protections not running - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38876 |  | 438877 | AC data is missing - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38877 |  | 438878 | Live voltage detected - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38878 |  | 438879 | Internal issue detected. A restart is required soon! - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38879 |  | 438880 | Parameters - System - Monitoring - Missing controllers - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38880 |  | 438881 | Card issue detected - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38881 |  | 438882 | Card configuration failed - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38882 |  | 438883 | Unknown traffic on DEIF network - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38883 |  | 438884 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38884 |  | 438885 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38885 |  | 438886 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Configuration - Severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm parameter: Severity | 38886 |  | 438887 | Local IO service error - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38887 |  | 438888 | App logging failure - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38888 |  | 438889 | Event logging failure - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38889 |  | 438890 | Licence error - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38890 |  | 438891 | Brightness is dimmed according to temperature - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 38891 |  | 438892 | Parameters - Grid code - Mains sync inhibit - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38892 |  | 438893 | Parameters - Grid code - Capability curve - Import protection - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 38893 |  | 438894 | Parameters - Grid code - Capability curve - Export protection - Configuration - Severity | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm parameter: Severity | 39500 |  | 439501 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39501 |  | 439502 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39502 |  | 439503 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39503 |  | 439504 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39504 |  | 439505 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39505 |  | 439506 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39506 |  | 439507 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39507 |  | 439508 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39508 |  | 439509 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39509 |  | 439510 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39510 |  | 439511 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39511 |  | 439512 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39512 |  | 439513 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39513 |  | 439514 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39514 |  | 439515 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39515 |  | 439516 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39516 |  | 439517 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39517 |  | 439518 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39518 |  | 439519 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39519 |  | 439520 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39520 |  | 439521 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39521 |  | 439522 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39522 |  | 439523 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39523 |  | 439524 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39524 |  | 439525 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39525 |  | 439526 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39526 |  | 439527 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39527 |  | 439528 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39528 |  | 439529 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39529 |  | 439530 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39530 |  | 439531 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39531 |  | 439532 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39532 |  | 439533 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39533 |  | 439534 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39534 |  | 439535 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39535 |  | 439536 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39536 |  | 439537 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39537 |  | 439538 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39538 |  | 439539 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39539 |  | 439540 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39540 |  | 439541 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39541 |  | 439542 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39542 |  | 439543 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39543 |  | 439544 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39544 |  | 439545 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39545 |  | 439546 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39546 |  | 439547 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39547 |  | 439548 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39548 |  | 439549 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39549 |  | 439550 | Digital custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39600 |  | 439601 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39601 |  | 439602 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39602 |  | 439603 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39603 |  | 439604 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39604 |  | 439605 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39605 |  | 439606 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39606 |  | 439607 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39607 |  | 439608 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39608 |  | 439609 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39609 |  | 439610 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39610 |  | 439611 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39611 |  | 439612 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39612 |  | 439613 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39613 |  | 439614 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39614 |  | 439615 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39615 |  | 439616 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39616 |  | 439617 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39617 |  | 439618 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39618 |  | 439619 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39619 |  | 439620 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39620 |  | 439621 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39621 |  | 439622 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39622 |  | 439623 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39623 |  | 439624 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39624 |  | 439625 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39625 |  | 439626 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39626 |  | 439627 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39627 |  | 439628 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39628 |  | 439629 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39629 |  | 439630 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39630 |  | 439631 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39631 |  | 439632 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39632 |  | 439633 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39633 |  | 439634 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39634 |  | 439635 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39635 |  | 439636 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39636 |  | 439637 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39637 |  | 439638 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39638 |  | 439639 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39639 |  | 439640 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39640 |  | 439641 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39641 |  | 439642 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39642 |  | 439643 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39643 |  | 439644 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39644 |  | 439645 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39645 |  | 439646 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39646 |  | 439647 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39647 |  | 439648 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39648 |  | 439649 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39649 |  | 439650 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39650 |  | 439651 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39651 |  | 439652 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39652 |  | 439653 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39653 |  | 439654 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39654 |  | 439655 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39655 |  | 439656 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39656 |  | 439657 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39657 |  | 439658 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39658 |  | 439659 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39659 |  | 439660 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39660 |  | 439661 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39661 |  | 439662 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39662 |  | 439663 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39663 |  | 439664 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39664 |  | 439665 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39665 |  | 439666 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39666 |  | 439667 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39667 |  | 439668 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39668 |  | 439669 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39669 |  | 439670 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39670 |  | 439671 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39671 |  | 439672 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39672 |  | 439673 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39673 |  | 439674 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39674 |  | 439675 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39675 |  | 439676 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39676 |  | 439677 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39677 |  | 439678 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39678 |  | 439679 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39679 |  | 439680 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39680 |  | 439681 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39681 |  | 439682 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39682 |  | 439683 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39683 |  | 439684 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39684 |  | 439685 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39685 |  | 439686 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39686 |  | 439687 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39687 |  | 439688 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39688 |  | 439689 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39689 |  | 439690 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39690 |  | 439691 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39691 |  | 439692 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39692 |  | 439693 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39693 |  | 439694 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39694 |  | 439695 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39695 |  | 439696 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39696 |  | 439697 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39697 |  | 439698 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39698 |  | 439699 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39699 |  | 439700 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39700 |  | 439701 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39701 |  | 439702 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39702 |  | 439703 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39703 |  | 439704 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39704 |  | 439705 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39705 |  | 439706 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39706 |  | 439707 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39707 |  | 439708 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39708 |  | 439709 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39709 |  | 439710 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39710 |  | 439711 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39711 |  | 439712 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39712 |  | 439713 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39713 |  | 439714 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39714 |  | 439715 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39715 |  | 439716 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39716 |  | 439717 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39717 |  | 439718 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39718 |  | 439719 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39719 |  | 439720 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39720 |  | 439721 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39721 |  | 439722 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39722 |  | 439723 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39723 |  | 439724 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39724 |  | 439725 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39725 |  | 439726 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39726 |  | 439727 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39727 |  | 439728 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39728 |  | 439729 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39729 |  | 439730 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39730 |  | 439731 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39731 |  | 439732 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39732 |  | 439733 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39733 |  | 439734 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39734 |  | 439735 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39735 |  | 439736 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39736 |  | 439737 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39737 |  | 439738 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39738 |  | 439739 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39739 |  | 439740 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39740 |  | 439741 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39741 |  | 439742 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39742 |  | 439743 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39743 |  | 439744 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39744 |  | 439745 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39745 |  | 439746 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39746 |  | 439747 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39747 |  | 439748 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39748 |  | 439749 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39749 |  | 439750 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39750 |  | 439751 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39751 |  | 439752 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39752 |  | 439753 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39753 |  | 439754 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39754 |  | 439755 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39755 |  | 439756 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39756 |  | 439757 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39757 |  | 439758 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39758 |  | 439759 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39759 |  | 439760 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39760 |  | 439761 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39761 |  | 439762 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39762 |  | 439763 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39763 |  | 439764 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39764 |  | 439765 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39765 |  | 439766 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39766 |  | 439767 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39767 |  | 439768 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39768 |  | 439769 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39769 |  | 439770 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39770 |  | 439771 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39771 |  | 439772 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39772 |  | 439773 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39773 |  | 439774 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39774 |  | 439775 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39775 |  | 439776 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39776 |  | 439777 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39777 |  | 439778 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39778 |  | 439779 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39779 |  | 439780 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39780 |  | 439781 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39781 |  | 439782 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39782 |  | 439783 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39783 |  | 439784 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39784 |  | 439785 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39785 |  | 439786 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39786 |  | 439787 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39787 |  | 439788 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39788 |  | 439789 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39789 |  | 439790 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39790 |  | 439791 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39791 |  | 439792 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39792 |  | 439793 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39793 |  | 439794 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39794 |  | 439795 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39795 |  | 439796 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39796 |  | 439797 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39797 |  | 439798 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39798 |  | 439799 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm parameter: Severity | 39799 |  | 439800 | Analogue custom alarm - Severity | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46000 |  | 446001 | Parameters - Engine - Start sequence - Start prepare - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46001 |  | 446002 | Parameters - Engine - Start sequence - Crank - Crank on - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46002 |  | 446003 | Parameters - Engine - Start sequence - Crank - Crank off - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46003 |  | 446004 | Parameters - Engine - Start sequence - Run coil - Run coil before crank - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46004 |  | 446005 | Parameters - Engine - Start sequence - Run coil - During start attempts | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46005 |  | 446006 | Parameters - Engine - Start sequence - Start prepare - Extended start prepare - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46006 |  | 446007 | Parameters - Engine - Stop sequence - Cooldown - Cooldown time - Configuration | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General timer: Settings | 46008 |  | 446009 | Parameters - Engine - Stop sequence - Extended stop - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46010 |  | 446011 | Parameters - Engine - Start sequence - Start attempts - Normal | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46011 |  | 446012 | Parameters - Engine - Start sequence - Start attempts - Suppress alarm action | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46015 |  | 446016 | Parameters - Engine - Idle run start - Idle run - Enable | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46017 |  | 446018 | Parameters - Engine - Idle run start - Minimum - Use | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46018 |  | 446019 | Parameters - Engine - Idle run start - Minimum - Delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46026 |  | 446027 | Parameters - Engine - Idle run stop - Minimum - Use | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46027 |  | 446028 | Parameters - Engine - Idle run stop - Minimum - Delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46033 |  | 446034 | Parameters - Engine - Idle run start - Idle run - Extended inhibit - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46034 |  | 446035 | Parameters - Engine - Running detection - RPM running detection - RPM | INT16 | X * 10 | X * 0.1 | RPM | X |  | X | X | X
General timer: Settings | 46035 |  | 446036 | Parameters - Engine - Running detection - Frequency running detection - Frequency | INT16 | X * 10 | X * 0.1 | Hz | X |  | X | X | X
General timer: Settings | 46036 |  | 446037 | Parameters - Engine - Running detection - Oil pressure running detection - Oil pressure | INT16 | X * 10 | X * 0.1 | bar | X |  | X | X | X
General timer: Settings | 46037 |  | 446038 | Parameters - Engine - Running detection - Feedback type - Primary running feedback | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46038 |  | 446039 | Parameters - Engine - Running detection - Engine ready - Delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46039 |  | 446040 | Parameters - Engine - Start sequence - Crank - Disengage crank | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
General timer: Settings | 46040 |  | 446041 | Parameters - Engine - Running detection - MPU setup - Number of MPU teeth | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46042 |  | 446043 | Parameters - Engine - Running detection - Oil pressure running detection - Use oil pressure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46043 |  | 446044 | Parameters - Engine - Running detection - RPM running detection - Use engine speed | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46047 |  | 446048 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump ON set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 46048 |  | 446049 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump OFF set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 46049 |  | 446050 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump OFF delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46050 |  | 446051 | Parameters - Auxiliary - Pump logic 1 - Source selection - Pump source select | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
General timer: Settings | 46051 |  | 446052 | Breaker type | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46052 |  | 446053 | Parameters - Breakers - Generator breaker configuration - Configuration - Pulse time ON | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46052 |  | 446053 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Pulse time ON | INT16 | X * 10 | X * 0.1 | s |  | X
General timer: Settings | 46052 |  | 446053 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time ON | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General timer: Settings | 46053 |  | 446054 | Parameters - Breakers - Generator breaker configuration - Configuration - Pulse time OFF | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46053 |  | 446054 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Pulse time OFF | INT16 | X * 10 | X * 0.1 | s |  | X
General timer: Settings | 46053 |  | 446054 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time OFF | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General timer: Settings | 46054 |  | 446055 | Parameters - Breakers - Generator breaker configuration - Configuration - Spring load time | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46054 |  | 446055 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Spring load time | INT16 | X * 10 | X * 0.1 | s |  | X
General timer: Settings | 46054 |  | 446055 | Parameters - Breakers - Mains breaker configuration - Configuration - Spring-load time | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General timer: Settings | 46055 |  | 446056 | Parameters - Breakers - Generator breaker configuration - Configuration - Open point (de-loading) | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46055 |  | 446056 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Open point (de-loading) | INT16 | X * 10 | X * 0.1 | % |  | X
General timer: Settings | 46055 |  | 446056 | Parameters - Breakers - Mains breaker configuration - Configuration - Open point (de-loading) | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
General timer: Settings | 46056 |  | 446057 | Breaker type | INT16 | X * 1 | X * 1 |  |  |  |  | X |  |  | X
General timer: Settings | 46057 |  | 446058 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time ON | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General timer: Settings | 46057 |  | 446058 | Parameters - Breakers - Tie breaker configuration - Configuration - Pulse time ON | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
General timer: Settings | 46058 |  | 446059 | Parameters - Breakers - Mains breaker configuration - Configuration - Pulse time OFF | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General timer: Settings | 46058 |  | 446059 | Parameters - Breakers - Tie breaker configuration - Configuration - Pulse time OFF | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
General timer: Settings | 46059 |  | 446060 | Parameters - Breakers - Mains breaker configuration - Configuration - Spring-load time | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General timer: Settings | 46059 |  | 446060 | Parameters - Breakers - Tie breaker configuration - Configuration - Spring-load time | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
General timer: Settings | 46060 |  | 446061 | Open point (de-loading) | INT16 | X * 10 | X * 0.1 | % |  |  |  | X |  |  | X
General timer: Settings | 46062 |  | 446063 | Parameters - Regulators - GOV - Relay configuration - Frequency droop - Droop | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 46063 |  | 446064 | Parameters - Regulators - GOV - Analogue - Frequency droop - Droop | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46064 |  | 446065 | Parameters - Regulators - AVR - Relay configuration - Voltage droop - Droop | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46065 |  | 446066 | Parameters - Regulators - AVR - Analogue - Voltage droop - Droop | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46093 |  | 446094 | Parameters - Local - Nominal settings - Controller nominal setting - Selection | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46094 |  | 446095 | Parameters - Local - Nominal settings - Controller nominal setting - Source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46095 |  | 446096 | Parameters - Mains - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V |  |  | X | X
General timer: Settings | 46095 |  | 446096 | Parameters - Busbar - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X |  |  |  | X | X | X
General timer: Settings | 46095 |  | 446096 | Parameters - Busbar B - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 46097 |  | 446098 | Parameters - Mains - Nominal settings - Nominal settings 1 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW |  |  | X | X
General timer: Settings | 46097 |  | 446098 | Parameters - Busbar - Nominal settings - Nominal settings 1 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | [6 empty] | X
General timer: Settings | 46098 |  | 446099 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW |  |  | X | X |  |  | X
General timer: Settings | 46099 |  | 446100 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar |  |  | X | X |  |  | X
General timer: Settings | 46100 |  | 446101 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA |  |  | X | X |  |  | X
General timer: Settings | 46101 |  | 446102 | Parameters - Mains - Nominal settings - Nominal settings 1 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA |  |  | X | X
General timer: Settings | 46101 |  | 446102 | Parameters - Busbar - Nominal settings - Nominal settings 1 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | [6 empty] | X
General timer: Settings | 46102 |  | 446103 | Parameters - Mains - Nominal settings - Nominal settings 1 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  |  |  | X | X
General timer: Settings | 46102 |  | 446103 | Parameters - Busbar - Nominal settings - Nominal settings 1 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 | [7 empty] | X
General timer: Settings | 46103 |  | 446104 | Parameters - Mains - Nominal settings - Nominal settings 1 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46103 |  | 446104 | Parameters - Busbar - Nominal settings - Nominal settings 1 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 | [7 empty] | X
General timer: Settings | 46104 |  | 446105 | Parameters - Mains - Nominal settings - Nominal settings 1 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46104 |  | 446105 | Parameters - Busbar - Nominal settings - Nominal settings 1 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 | [7 empty] | X
General timer: Settings | 46105 |  | 446106 | Parameters - Mains - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46105 |  | 446106 | Parameters - Busbar - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 46105 |  | 446106 | Parameters - Busbar B - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46106 |  | 446107 | Parameters - Generator - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X
General timer: Settings | 46106 |  | 446107 | Parameters - Busbar A - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 46106 |  | 446107 | Parameters - Mains - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | [5 empty] | X | X
General timer: Settings | 46107 |  | 446108 | Parameters - Generator - Nominal settings - Nominal settings 1 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
General timer: Settings | 46107 |  | 446108 | Parameters - Busbar A - Nominal settings - Nominal settings 1 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz |  | X
General timer: Settings | 46107 |  | 446108 | Parameters - Mains - Nominal settings - Nominal settings 1 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
General timer: Settings | 46108 |  | 446109 | Parameters - Generator - Nominal settings - Nominal settings 1 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X |  | X | X | X
General timer: Settings | 46108 |  | 446109 | Parameters - Busbar A - Nominal settings - Nominal settings 1 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A |  | X
General timer: Settings | 46108 |  | 446109 | Parameters - Mains - Nominal settings - Nominal settings 1 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | [5 empty] | X | X
General timer: Settings | 46109 |  | 446110 | Parameters - Generator - Nominal settings - Nominal settings 1 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X |  | X | X | X
General timer: Settings | 46109 |  | 446110 | Parameters - Busbar A - Nominal settings - Nominal settings 1 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW |  | X
General timer: Settings | 46109 |  | 446110 | Parameters - Mains - Nominal settings - Nominal settings 1 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | [5 empty] | X | X
General timer: Settings | 46110 |  | 446111 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 46111 |  | 446112 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 46112 |  | 446113 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 46113 |  | 446114 | Parameters - Generator - Nominal settings - Nominal settings 1 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X |  | X | X | X
General timer: Settings | 46113 |  | 446114 | Parameters - Busbar A - Nominal settings - Nominal settings 1 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA |  | X
General timer: Settings | 46113 |  | 446114 | Parameters - Mains - Nominal settings - Nominal settings 1 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | [5 empty] | X | X
General timer: Settings | 46114 |  | 446115 | Parameters - Generator - Nominal settings - Nominal settings 1 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X |  | X | X | X
General timer: Settings | 46114 |  | 446115 | Parameters - Busbar A - Nominal settings - Nominal settings 1 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  |  | X
General timer: Settings | 46114 |  | 446115 | Parameters - Mains - Nominal settings - Nominal settings 1 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 | [6 empty] | X | X
General timer: Settings | 46115 |  | 446116 | Parameters - Generator - Nominal settings - Nominal settings 1 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46115 |  | 446116 | Parameters - Busbar A - Nominal settings - Nominal settings 1 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46115 |  | 446116 | Parameters - Mains - Nominal settings - Nominal settings 1 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 46116 |  | 446117 | Parameters - Generator - Nominal settings - Nominal settings 1 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46116 |  | 446117 | Parameters - Busbar A - Nominal settings - Nominal settings 1 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46116 |  | 446117 | Parameters - Mains - Nominal settings - Nominal settings 1 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 46117 |  | 446118 | Parameters - Engine - Nominal settings - Nominal settings 1 - Nominal RPM - Nominal | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
General timer: Settings | 46118 |  | 446119 | Parameters - Regulators - GOV - Analogue - Offset - GOV output offset 1 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46119 |  | 446120 | Parameters - Regulators - AVR - Analogue - Offset - AVR output offset 1 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46120 |  | 446121 | Parameters - Local - 4th current input - Nominal settings - Nominal settings 1 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 46121 |  | 446122 | Parameters - Mains - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V |  |  | X | X
General timer: Settings | 46121 |  | 446122 | Parameters - Busbar - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X |  |  |  | X | X | X
General timer: Settings | 46121 |  | 446122 | Parameters - Busbar B - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 46123 |  | 446124 | Parameters - Mains - Nominal settings - Nominal settings 2 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW |  |  | X | X
General timer: Settings | 46123 |  | 446124 | Parameters - Busbar - Nominal settings - Nominal settings 2 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | [6 empty] | X
General timer: Settings | 46124 |  | 446125 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW |  |  | X | X |  |  | X
General timer: Settings | 46125 |  | 446126 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar |  |  | X | X |  |  | X
General timer: Settings | 46126 |  | 446127 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA |  |  | X | X |  |  | X
General timer: Settings | 46127 |  | 446128 | Parameters - Mains - Nominal settings - Nominal settings 2 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA |  |  | X | X
General timer: Settings | 46127 |  | 446128 | Parameters - Busbar - Nominal settings - Nominal settings 2 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | [6 empty] | X
General timer: Settings | 46128 |  | 446129 | Parameters - Mains - Nominal settings - Nominal settings 2 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  |  |  | X | X
General timer: Settings | 46128 |  | 446129 | Parameters - Busbar - Nominal settings - Nominal settings 2 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 | [7 empty] | X
General timer: Settings | 46129 |  | 446130 | Parameters - Mains - Nominal settings - Nominal settings 2 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46129 |  | 446130 | Parameters - Busbar - Nominal settings - Nominal settings 2 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 | [7 empty] | X
General timer: Settings | 46130 |  | 446131 | Parameters - Mains - Nominal settings - Nominal settings 2 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46130 |  | 446131 | Parameters - Busbar - Nominal settings - Nominal settings 2 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 | [7 empty] | X
General timer: Settings | 46131 |  | 446132 | Parameters - Mains - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46131 |  | 446132 | Parameters - Busbar - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 46131 |  | 446132 | Parameters - Busbar B - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46132 |  | 446133 | Parameters - Mains - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V |  |  | X | X
General timer: Settings | 46132 |  | 446133 | Parameters - Busbar - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X |  |  |  | X | X | X
General timer: Settings | 46132 |  | 446133 | Parameters - Busbar B - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 46134 |  | 446135 | Parameters - Mains - Nominal settings - Nominal settings 3 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW |  |  | X | X
General timer: Settings | 46134 |  | 446135 | Parameters - Busbar - Nominal settings - Nominal settings 3 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | [6 empty] | X
General timer: Settings | 46135 |  | 446136 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW |  |  | X | X |  |  | X
General timer: Settings | 46136 |  | 446137 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar |  |  | X | X |  |  | X
General timer: Settings | 46137 |  | 446138 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA |  |  | X | X |  |  | X
General timer: Settings | 46138 |  | 446139 | Parameters - Mains - Nominal settings - Nominal settings 3 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA |  |  | X | X
General timer: Settings | 46138 |  | 446139 | Parameters - Busbar - Nominal settings - Nominal settings 3 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | [6 empty] | X
General timer: Settings | 46139 |  | 446140 | Parameters - Mains - Nominal settings - Nominal settings 3 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  |  |  | X | X
General timer: Settings | 46139 |  | 446140 | Parameters - Busbar - Nominal settings - Nominal settings 3 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 | [7 empty] | X
General timer: Settings | 46140 |  | 446141 | Parameters - Mains - Nominal settings - Nominal settings 3 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46140 |  | 446141 | Parameters - Busbar - Nominal settings - Nominal settings 3 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 | [7 empty] | X
General timer: Settings | 46141 |  | 446142 | Parameters - Mains - Nominal settings - Nominal settings 3 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46141 |  | 446142 | Parameters - Busbar - Nominal settings - Nominal settings 3 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 | [7 empty] | X
General timer: Settings | 46142 |  | 446143 | Parameters - Mains - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46142 |  | 446143 | Parameters - Busbar - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 46142 |  | 446143 | Parameters - Busbar B - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46143 |  | 446144 | Parameters - Mains - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V |  |  | X | X
General timer: Settings | 46143 |  | 446144 | Parameters - Busbar - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X |  |  |  | X | X | X
General timer: Settings | 46143 |  | 446144 | Parameters - Busbar B - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 46145 |  | 446146 | Parameters - Mains - Nominal settings - Nominal settings 4 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW |  |  | X | X
General timer: Settings | 46145 |  | 446146 | Parameters - Busbar - Nominal settings - Nominal settings 4 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | [6 empty] | X
General timer: Settings | 46146 |  | 446147 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW |  |  | X | X |  |  | X
General timer: Settings | 46147 |  | 446148 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar |  |  | X | X |  |  | X
General timer: Settings | 46148 |  | 446149 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA |  |  | X | X |  |  | X
General timer: Settings | 46149 |  | 446150 | Parameters - Mains - Nominal settings - Nominal settings 4 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA |  |  | X | X
General timer: Settings | 46149 |  | 446150 | Parameters - Busbar - Nominal settings - Nominal settings 4 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | [6 empty] | X
General timer: Settings | 46150 |  | 446151 | Parameters - Mains - Nominal settings - Nominal settings 4 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  |  |  | X | X
General timer: Settings | 46150 |  | 446151 | Parameters - Busbar - Nominal settings - Nominal settings 4 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 | [7 empty] | X
General timer: Settings | 46151 |  | 446152 | Parameters - Mains - Nominal settings - Nominal settings 4 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46151 |  | 446152 | Parameters - Busbar - Nominal settings - Nominal settings 4 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 | [7 empty] | X
General timer: Settings | 46152 |  | 446153 | Parameters - Mains - Nominal settings - Nominal settings 4 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46152 |  | 446153 | Parameters - Busbar - Nominal settings - Nominal settings 4 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 | [7 empty] | X
General timer: Settings | 46153 |  | 446154 | Parameters - Mains - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46153 |  | 446154 | Parameters - Busbar - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 46153 |  | 446154 | Parameters - Busbar B - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46154 |  | 446155 | Parameters - Generator - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X
General timer: Settings | 46154 |  | 446155 | Parameters - Busbar A - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 46154 |  | 446155 | Parameters - Mains - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | [5 empty] | X | X
General timer: Settings | 46155 |  | 446156 | Parameters - Generator - Nominal settings - Nominal settings 2 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
General timer: Settings | 46155 |  | 446156 | Parameters - Busbar A - Nominal settings - Nominal settings 2 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz |  | X
General timer: Settings | 46155 |  | 446156 | Parameters - Mains - Nominal settings - Nominal settings 2 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
General timer: Settings | 46156 |  | 446157 | Parameters - Generator - Nominal settings - Nominal settings 2 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X |  | X | X | X
General timer: Settings | 46156 |  | 446157 | Parameters - Busbar A - Nominal settings - Nominal settings 2 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A |  | X
General timer: Settings | 46156 |  | 446157 | Parameters - Mains - Nominal settings - Nominal settings 2 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | [5 empty] | X | X
General timer: Settings | 46157 |  | 446158 | Parameters - Generator - Nominal settings - Nominal settings 2 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X |  | X | X | X
General timer: Settings | 46157 |  | 446158 | Parameters - Busbar A - Nominal settings - Nominal settings 2 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW |  | X
General timer: Settings | 46157 |  | 446158 | Parameters - Mains - Nominal settings - Nominal settings 2 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | [5 empty] | X | X
General timer: Settings | 46158 |  | 446159 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 46159 |  | 446160 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 46160 |  | 446161 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 46161 |  | 446162 | Parameters - Generator - Nominal settings - Nominal settings 2 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X |  | X | X | X
General timer: Settings | 46161 |  | 446162 | Parameters - Busbar A - Nominal settings - Nominal settings 2 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA |  | X
General timer: Settings | 46161 |  | 446162 | Parameters - Mains - Nominal settings - Nominal settings 2 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | [5 empty] | X | X
General timer: Settings | 46162 |  | 446163 | Parameters - Generator - Nominal settings - Nominal settings 2 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X |  | X | X | X
General timer: Settings | 46162 |  | 446163 | Parameters - Busbar A - Nominal settings - Nominal settings 2 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  |  | X
General timer: Settings | 46162 |  | 446163 | Parameters - Mains - Nominal settings - Nominal settings 2 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 | [6 empty] | X | X
General timer: Settings | 46163 |  | 446164 | Parameters - Generator - Nominal settings - Nominal settings 2 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46163 |  | 446164 | Parameters - Busbar A - Nominal settings - Nominal settings 2 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46163 |  | 446164 | Parameters - Mains - Nominal settings - Nominal settings 2 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 46164 |  | 446165 | Parameters - Generator - Nominal settings - Nominal settings 2 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46164 |  | 446165 | Parameters - Busbar A - Nominal settings - Nominal settings 2 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46164 |  | 446165 | Parameters - Mains - Nominal settings - Nominal settings 2 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 46165 |  | 446166 | Parameters - Engine - Nominal settings - Nominal settings 2 - Nominal RPM - Nominal | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
General timer: Settings | 46166 |  | 446167 | Parameters - Regulators - GOV - Analogue - Offset - GOV output offset 2 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46167 |  | 446168 | Parameters - Regulators - AVR - Analogue - Offset - AVR output offset 2 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46168 |  | 446169 | Parameters - Generator - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X
General timer: Settings | 46168 |  | 446169 | Parameters - Busbar A - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 46168 |  | 446169 | Parameters - Mains - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | [5 empty] | X | X
General timer: Settings | 46169 |  | 446170 | Parameters - Generator - Nominal settings - Nominal settings 3 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
General timer: Settings | 46169 |  | 446170 | Parameters - Busbar A - Nominal settings - Nominal settings 3 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz |  | X
General timer: Settings | 46169 |  | 446170 | Parameters - Mains - Nominal settings - Nominal settings 3 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
General timer: Settings | 46170 |  | 446171 | Parameters - Generator - Nominal settings - Nominal settings 3 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X |  | X | X | X
General timer: Settings | 46170 |  | 446171 | Parameters - Busbar A - Nominal settings - Nominal settings 3 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A |  | X
General timer: Settings | 46170 |  | 446171 | Parameters - Mains - Nominal settings - Nominal settings 3 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | [5 empty] | X | X
General timer: Settings | 46171 |  | 446172 | Parameters - Generator - Nominal settings - Nominal settings 3 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X |  | X | X | X
General timer: Settings | 46171 |  | 446172 | Parameters - Busbar A - Nominal settings - Nominal settings 3 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW |  | X
General timer: Settings | 46171 |  | 446172 | Parameters - Mains - Nominal settings - Nominal settings 3 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | [5 empty] | X | X
General timer: Settings | 46172 |  | 446173 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 46173 |  | 446174 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 46174 |  | 446175 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 46175 |  | 446176 | Parameters - Generator - Nominal settings - Nominal settings 3 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X |  | X | X | X
General timer: Settings | 46175 |  | 446176 | Parameters - Busbar A - Nominal settings - Nominal settings 3 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA |  | X
General timer: Settings | 46175 |  | 446176 | Parameters - Mains - Nominal settings - Nominal settings 3 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | [5 empty] | X | X
General timer: Settings | 46176 |  | 446177 | Parameters - Generator - Nominal settings - Nominal settings 3 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X |  | X | X | X
General timer: Settings | 46176 |  | 446177 | Parameters - Busbar A - Nominal settings - Nominal settings 3 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  |  | X
General timer: Settings | 46176 |  | 446177 | Parameters - Mains - Nominal settings - Nominal settings 3 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 | [6 empty] | X | X
General timer: Settings | 46177 |  | 446178 | Parameters - Generator - Nominal settings - Nominal settings 3 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46177 |  | 446178 | Parameters - Busbar A - Nominal settings - Nominal settings 3 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46177 |  | 446178 | Parameters - Mains - Nominal settings - Nominal settings 3 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 46178 |  | 446179 | Parameters - Generator - Nominal settings - Nominal settings 3 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46178 |  | 446179 | Parameters - Busbar A - Nominal settings - Nominal settings 3 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46178 |  | 446179 | Parameters - Mains - Nominal settings - Nominal settings 3 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 46179 |  | 446180 | Parameters - Engine - Nominal settings - Nominal settings 3 - Nominal RPM - Nominal | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
General timer: Settings | 46180 |  | 446181 | Parameters - Regulators - GOV - Analogue - Offset - GOV output offset 3 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46181 |  | 446182 | Parameters - Regulators - AVR - Analogue - Offset - AVR output offset 3 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46182 |  | 446183 | Parameters - Generator - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X
General timer: Settings | 46182 |  | 446183 | Parameters - Busbar A - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 46182 |  | 446183 | Parameters - Mains - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | [5 empty] | X | X
General timer: Settings | 46183 |  | 446184 | Parameters - Generator - Nominal settings - Nominal settings 4 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
General timer: Settings | 46183 |  | 446184 | Parameters - Busbar A - Nominal settings - Nominal settings 4 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz |  | X
General timer: Settings | 46183 |  | 446184 | Parameters - Mains - Nominal settings - Nominal settings 4 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
General timer: Settings | 46184 |  | 446185 | Parameters - Generator - Nominal settings - Nominal settings 4 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X |  | X | X | X
General timer: Settings | 46184 |  | 446185 | Parameters - Busbar A - Nominal settings - Nominal settings 4 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A |  | X
General timer: Settings | 46184 |  | 446185 | Parameters - Mains - Nominal settings - Nominal settings 4 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | [5 empty] | X | X
General timer: Settings | 46185 |  | 446186 | Parameters - Generator - Nominal settings - Nominal settings 4 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X |  | X | X | X
General timer: Settings | 46185 |  | 446186 | Parameters - Busbar A - Nominal settings - Nominal settings 4 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW |  | X
General timer: Settings | 46185 |  | 446186 | Parameters - Mains - Nominal settings - Nominal settings 4 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | [5 empty] | X | X
General timer: Settings | 46186 |  | 446187 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 46187 |  | 446188 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 46188 |  | 446189 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 46189 |  | 446190 | Parameters - Generator - Nominal settings - Nominal settings 4 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X |  | X | X | X
General timer: Settings | 46189 |  | 446190 | Parameters - Busbar A - Nominal settings - Nominal settings 4 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA |  | X
General timer: Settings | 46189 |  | 446190 | Parameters - Mains - Nominal settings - Nominal settings 4 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | [5 empty] | X | X
General timer: Settings | 46190 |  | 446191 | Parameters - Generator - Nominal settings - Nominal settings 4 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X |  | X | X | X
General timer: Settings | 46190 |  | 446191 | Parameters - Busbar A - Nominal settings - Nominal settings 4 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  |  | X
General timer: Settings | 46190 |  | 446191 | Parameters - Mains - Nominal settings - Nominal settings 4 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 | [6 empty] | X | X
General timer: Settings | 46191 |  | 446192 | Parameters - Generator - Nominal settings - Nominal settings 4 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46191 |  | 446192 | Parameters - Busbar A - Nominal settings - Nominal settings 4 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46191 |  | 446192 | Parameters - Mains - Nominal settings - Nominal settings 4 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 46192 |  | 446193 | Parameters - Generator - Nominal settings - Nominal settings 4 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46192 |  | 446193 | Parameters - Busbar A - Nominal settings - Nominal settings 4 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46192 |  | 446193 | Parameters - Mains - Nominal settings - Nominal settings 4 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 46193 |  | 446194 | Parameters - Engine - Nominal settings - Nominal settings 4 - Nominal RPM - Nominal | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
General timer: Settings | 46194 |  | 446195 | Parameters - Regulators - GOV - Analogue - Offset - GOV output offset 4 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46195 |  | 446196 | Parameters - Regulators - AVR - Analogue - Offset - AVR output offset 4 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46196 |  | 446197 | Parameters - Local - 4th current input - Nominal settings - Nominal settings 2 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 46197 |  | 446198 | Parameters - Local - 4th current input - Nominal settings - Nominal settings 3 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 46198 |  | 446199 | Parameters - Local - 4th current input - Nominal settings - Nominal settings 4 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 46199 |  | 446200 | Parameters - Generator - Production counters - Active energy export - Pulse every | INT16 | X * 1 | X * 1 | kWh | X |  | X | X | X
General timer: Settings | 46199 |  | 446200 | Parameters - Busbar A - Production counters - Active energy export - Pulse every | INT16 | X * 1 | X * 1 | kWh |  | X
General timer: Settings | 46199 |  | 446200 | Parameters - Mains - Production counters - Active energy export - Pulse every | INT16 | X * 1 | X * 1 | kWh | [5 empty] | X | X
General timer: Settings | 46200 |  | 446201 | Parameters - Generator - Production counters - Active energy export - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46200 |  | 446201 | Parameters - Busbar A - Production counters - Active energy export - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s |  | X
General timer: Settings | 46200 |  | 446201 | Parameters - Mains - Production counters - Active energy export - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General timer: Settings | 46201 |  | 446202 | Parameters - Generator - Production counters - Reactive energy export - Pulse every | INT16 | X * 1 | X * 1 | kvarh | X |  | X | X | X
General timer: Settings | 46201 |  | 446202 | Parameters - Busbar A - Production counters - Reactive energy export - Pulse every | INT16 | X * 1 | X * 1 | kvarh |  | X
General timer: Settings | 46201 |  | 446202 | Parameters - Mains - Production counters - Reactive energy export - Pulse every | INT16 | X * 1 | X * 1 | kvarh | [5 empty] | X | X
General timer: Settings | 46202 |  | 446203 | Parameters - Generator - Production counters - Reactive energy export - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46202 |  | 446203 | Parameters - Busbar A - Production counters - Reactive energy export - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s |  | X
General timer: Settings | 46202 |  | 446203 | Parameters - Mains - Production counters - Reactive energy export - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General timer: Settings | 46203 |  | 446204 | Parameters - Busbar A - Production counters - Active energy import - Pulse every | INT16 | X * 1 | X * 1 | kWh |  | X
General timer: Settings | 46203 |  | 446204 | Parameters - Mains - Production counters - Active energy import - Pulse every | INT16 | X * 1 | X * 1 | kWh | [5 empty] | X | X
General timer: Settings | 46204 |  | 446205 | Parameters - Busbar A - Production counters - Active energy import - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s |  | X
General timer: Settings | 46204 |  | 446205 | Parameters - Mains - Production counters - Active energy import - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General timer: Settings | 46205 |  | 446206 | Parameters - Busbar A - Production counters - Reactive energy import - Pulse every | INT16 | X * 1 | X * 1 | kvarh |  | X
General timer: Settings | 46205 |  | 446206 | Parameters - Mains - Production counters - Reactive energy import - Pulse every | INT16 | X * 1 | X * 1 | kvarh | [5 empty] | X | X
General timer: Settings | 46206 |  | 446207 | Parameters - Busbar A - Production counters - Reactive energy import - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s |  | X
General timer: Settings | 46206 |  | 446207 | Parameters - Mains - Production counters - Reactive energy import - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General timer: Settings | 46207 |  | 446208 | Parameters - Busbar A - Production counters - Active energy difference - Pulse every | INT16 | X * 1 | X * 1 | kWh |  | X
General timer: Settings | 46207 |  | 446208 | Parameters - Mains - Production counters - Active energy difference - Pulse every | INT16 | X * 1 | X * 1 | kWh | [5 empty] | X | X
General timer: Settings | 46208 |  | 446209 | Parameters - Busbar A - Production counters - Active energy difference - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s |  | X
General timer: Settings | 46208 |  | 446209 | Parameters - Mains - Production counters - Active energy difference - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General timer: Settings | 46209 |  | 446210 | Parameters - Busbar A - Production counters - Reactive energy difference - Pulse every | INT16 | X * 1 | X * 1 | kvarh |  | X
General timer: Settings | 46209 |  | 446210 | Parameters - Mains - Production counters - Reactive energy difference - Pulse every | INT16 | X * 1 | X * 1 | kvarh | [5 empty] | X | X
General timer: Settings | 46210 |  | 446211 | Parameters - Busbar A - Production counters - Reactive energy difference - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s |  | X
General timer: Settings | 46210 |  | 446211 | Parameters - Mains - Production counters - Reactive energy difference - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General timer: Settings | 46211 |  | 446212 | Parameters - Mains - AC setup - Voltage transformer - Primary | INT16 | X * 1 | X * 1 | V |  |  | X | X
General timer: Settings | 46211 |  | 446212 | Parameters - Busbar - AC setup - Voltage transformer - Primary | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
General timer: Settings | 46211 |  | 446212 | Parameters - Busbar B - AC setup - Voltage transformer - Primary | INT16 | X * 1 | X * 1 | V |  | X
General timer: Settings | 46212 |  | 446213 | Parameters - Mains - AC setup - Voltage transformer - Secondary | INT16 | X * 1 | X * 1 | V |  |  | X | X
General timer: Settings | 46212 |  | 446213 | Parameters - Busbar - AC setup - Voltage transformer - Secondary | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
General timer: Settings | 46212 |  | 446213 | Parameters - Busbar B - AC setup - Voltage transformer - Secondary | INT16 | X * 1 | X * 1 | V |  | X
General timer: Settings | 46213 |  | 446214 | Parameters - Generator - AC setup - Voltage transformer - Primary | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
General timer: Settings | 46213 |  | 446214 | Parameters - Busbar A - AC setup - Voltage transformer - Primary | INT16 | X * 1 | X * 1 | V |  | X
General timer: Settings | 46213 |  | 446214 | Parameters - Mains - AC setup - Voltage transformer - Primary | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
General timer: Settings | 46214 |  | 446215 | Parameters - Generator - AC setup - Voltage transformer - Secondary | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
General timer: Settings | 46214 |  | 446215 | Parameters - Busbar A - AC setup - Voltage transformer - Secondary | INT16 | X * 1 | X * 1 | V |  | X
General timer: Settings | 46214 |  | 446215 | Parameters - Mains - AC setup - Voltage transformer - Secondary | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
General timer: Settings | 46215 |  | 446216 | Parameters - Generator - AC setup - Current transformer - Primary | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
General timer: Settings | 46215 |  | 446216 | Parameters - Busbar A - AC setup - Current transformer - Primary | INT16 | X * 1 | X * 1 | A |  | X
General timer: Settings | 46215 |  | 446216 | Parameters - Mains - AC setup - Current transformer - Primary | INT16 | X * 1 | X * 1 | A | [5 empty] | X | X
General timer: Settings | 46216 |  | 446217 | Parameters - Generator - AC setup - Current transformer - Secondary | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
General timer: Settings | 46216 |  | 446217 | Parameters - Busbar A - AC setup - Current transformer - Secondary | INT16 | X * 1 | X * 1 | A |  | X
General timer: Settings | 46216 |  | 446217 | Parameters - Mains - AC setup - Current transformer - Secondary | INT16 | X * 1 | X * 1 | A | [5 empty] | X | X
General timer: Settings | 46217 |  | 446218 | Parameters - Local - 4th current input - Current transformer (I4) - Primary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 46218 |  | 446219 | Parameters - Local - 4th current input - Current transformer (I4) - Secondary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 46219 |  | 446220 | Parameters - Generator - AC setup - CT - ACM3.2 - Consumer side - Primary | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
General timer: Settings | 46220 |  | 446221 | Parameters - Generator - AC setup - CT - ACM3.2 - Consumer side - Secondary | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
General timer: Settings | 46221 |  | 446222 | Parameters - Generator - AC setup - CT - ACM3.2 - Neutral side - Primary | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
General timer: Settings | 46222 |  | 446223 | Parameters - Generator - AC setup - CT - ACM3.2 - Neutral side - Secondary | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
General timer: Settings | 46223 |  | 446224 | Parameters - Generator - AC setup - CT - ACM3.2 - Consumer side - Current reference dir. | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46224 |  | 446225 | Parameters - Generator - AC setup - CT - ACM3.2 - Neutral side - Current reference dir. | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46225 |  | 446226 | Parameters - Mains - AC setup - Voltage and frequency OK - Configuration | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 46225 |  | 446226 | Parameters - Busbar - AC setup - Voltage and frequency OK - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X | X
General timer: Settings | 46225 |  | 446226 | Parameters - Busbar B - AC setup - Voltage and frequency OK - Configuration | INT16 | X * 10 | X * 0.1 | s |  | X
General timer: Settings | 46226 |  | 446227 | Parameters - Mains - AC setup - Voltage and frequency OK - Minimum OK voltage | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 46226 |  | 446227 | Parameters - Busbar - AC setup - Voltage and frequency OK - Minimum OK voltage | INT16 | X * 1 | X * 1 | % | X |  |  |  | X | X | X
General timer: Settings | 46226 |  | 446227 | Parameters - Busbar B - AC setup - Voltage and frequency OK - Minimum OK voltage | INT16 | X * 1 | X * 1 | % |  | X
General timer: Settings | 46227 |  | 446228 | Parameters - Mains - AC setup - Voltage and frequency OK - Maximum OK voltage | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 46227 |  | 446228 | Parameters - Busbar - AC setup - Voltage and frequency OK - Maximum OK voltage | INT16 | X * 1 | X * 1 | % | X |  |  |  | X | X | X
General timer: Settings | 46227 |  | 446228 | Parameters - Busbar B - AC setup - Voltage and frequency OK - Maximum OK voltage | INT16 | X * 1 | X * 1 | % |  | X
General timer: Settings | 46228 |  | 446229 | Parameters - Mains - AC setup - Voltage and frequency OK - Minimum OK frequency | INT16 | X * 100 | X * 0.01 | % |  |  | X | X
General timer: Settings | 46228 |  | 446229 | Parameters - Busbar - AC setup - Voltage and frequency OK - Minimum OK frequency | INT16 | X * 100 | X * 0.01 | % | X |  |  |  | X | X | X
General timer: Settings | 46228 |  | 446229 | Parameters - Busbar B - AC setup - Voltage and frequency OK - Minimum OK frequency | INT16 | X * 100 | X * 0.01 | % |  | X
General timer: Settings | 46229 |  | 446230 | Parameters - Mains - AC setup - Voltage and frequency OK - Maximum OK frequency | INT16 | X * 100 | X * 0.01 | % |  |  | X | X
General timer: Settings | 46229 |  | 446230 | Parameters - Busbar - AC setup - Voltage and frequency OK - Maximum OK frequency | INT16 | X * 100 | X * 0.01 | % | X |  |  |  | X | X | X
General timer: Settings | 46229 |  | 446230 | Parameters - Busbar B - AC setup - Voltage and frequency OK - Maximum OK frequency | INT16 | X * 100 | X * 0.01 | % |  | X
General timer: Settings | 46230 |  | 446231 | Maximum voltage balance deviation | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 46231 |  | 446232 | Maximum phase deviation | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
General timer: Settings | 46232 |  | 446233 | Parameters - Mains - AC setup - Phase sequence error - Detection voltage | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 46232 |  | 446233 | Parameters - Busbar - AC setup - Phase sequence error - Detection voltage | INT16 | X * 1 | X * 1 | % | X |  |  |  | X | X | X
General timer: Settings | 46232 |  | 446233 | Parameters - Busbar B - AC setup - Phase sequence error - Detection voltage | INT16 | X * 1 | X * 1 | % |  | X
General timer: Settings | 46233 |  | 446234 | Blackout delay | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 46233 |  | 446234 | Parameters - Busbar - AC setup - Blackout detection - Blackout delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  |  |  | X | X | X
General timer: Settings | 46233 |  | 446234 | Parameters - Busbar B - AC setup - Blackout detection - Blackout delay - Configuration | INT16 | X * 10 | X * 0.1 | s |  | X
General timer: Settings | 46234 |  | 446235 | Parameters - Generator - AC setup - Voltage and frequency OK - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46234 |  | 446235 | Parameters - Busbar A - AC setup - Voltage and frequency OK - Configuration | INT16 | X * 10 | X * 0.1 | s |  | X
General timer: Settings | 46234 |  | 446235 | Parameters - Mains - AC setup - Voltage and frequency OK - Configuration | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General timer: Settings | 46235 |  | 446236 | Parameters - Generator - AC setup - Voltage and frequency OK - Minimum OK voltage | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 46235 |  | 446236 | Parameters - Busbar A - AC setup - Voltage and frequency OK - Minimum OK voltage | INT16 | X * 1 | X * 1 | % |  | X
General timer: Settings | 46235 |  | 446236 | Parameters - Mains - AC setup - Voltage and frequency OK - Minimum OK voltage | INT16 | X * 1 | X * 1 | % | [5 empty] | X | X
General timer: Settings | 46236 |  | 446237 | Parameters - Generator - AC setup - Voltage and frequency OK - Maximum OK voltage | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 46236 |  | 446237 | Parameters - Busbar A - AC setup - Voltage and frequency OK - Maximum OK voltage | INT16 | X * 1 | X * 1 | % |  | X
General timer: Settings | 46236 |  | 446237 | Parameters - Mains - AC setup - Voltage and frequency OK - Maximum OK voltage | INT16 | X * 1 | X * 1 | % | [5 empty] | X | X
General timer: Settings | 46237 |  | 446238 | Parameters - Generator - AC setup - Voltage and frequency OK - Minimum OK frequency | INT16 | X * 100 | X * 0.01 | % | X |  | X | X | X
General timer: Settings | 46237 |  | 446238 | Parameters - Busbar A - AC setup - Voltage and frequency OK - Minimum OK frequency | INT16 | X * 100 | X * 0.01 | % |  | X
General timer: Settings | 46237 |  | 446238 | Parameters - Mains - AC setup - Voltage and frequency OK - Minimum OK frequency | INT16 | X * 100 | X * 0.01 | % | [5 empty] | X | X
General timer: Settings | 46238 |  | 446239 | Parameters - Generator - AC setup - Voltage and frequency OK - Maximum OK frequency | INT16 | X * 100 | X * 0.01 | % | X |  | X | X | X
General timer: Settings | 46238 |  | 446239 | Parameters - Busbar A - AC setup - Voltage and frequency OK - Maximum OK frequency | INT16 | X * 100 | X * 0.01 | % |  | X
General timer: Settings | 46238 |  | 446239 | Parameters - Mains - AC setup - Voltage and frequency OK - Maximum OK frequency | INT16 | X * 100 | X * 0.01 | % | [5 empty] | X | X
General timer: Settings | 46239 |  | 446240 | Maximum voltage balance deviation | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 46240 |  | 446241 | Maximum phase deviation | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
General timer: Settings | 46241 |  | 446242 | Parameters - Generator - AC setup - Phase sequence error - Detection voltage | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 46241 |  | 446242 | Parameters - Busbar A - AC setup - Phase sequence error - Detection voltage | INT16 | X * 1 | X * 1 | % |  | X
General timer: Settings | 46241 |  | 446242 | Parameters - Mains - AC setup - Phase sequence error - Detection voltage | INT16 | X * 1 | X * 1 | % | [5 empty] | X | X
General timer: Settings | 46242 |  | 446243 | Blackout delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
General timer: Settings | 46242 |  | 446243 | Parameters - Busbar A - AC setup - Blackout detection - Blackout delay - Configuration | INT16 | X * 10 | X * 0.1 | s |  | X
General timer: Settings | 46243 |  | 446244 | Parameters - Generator - AC setup - Voltage and frequency OK (blackout) - Voltage and frequency OK - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 46244 |  | 446245 | Parameters - Generator - AC setup - Voltage and frequency OK (blackout) - Minimum OK voltage | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 46245 |  | 446246 | Parameters - Generator - AC setup - Voltage and frequency OK (blackout) - Maximum OK voltage | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 46246 |  | 446247 | Parameters - Generator - AC setup - Voltage and frequency OK (blackout) - Minimum OK frequency | INT16 | X * 100 | X * 0.01 | % | X |  | X | X | X
General timer: Settings | 46247 |  | 446248 | Parameters - Generator - AC setup - Voltage and frequency OK (blackout) - Maximum OK frequency | INT16 | X * 100 | X * 0.01 | % | X |  | X | X | X
General timer: Settings | 46248 |  | 446249 | Parameters - Generator - AC setup - Phase configuration - AC configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46248 |  | 446249 | Parameters - Busbar A - AC setup - Phase configuration - AC configuration | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46248 |  | 446249 | Parameters - Mains - AC setup - Phase configuration - AC configuration | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 46249 |  | 446250 | Parameters - Generator - AC setup - Phase direction | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46249 |  | 446250 | Parameters - Busbar A - AC setup - Phase direction | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46249 |  | 446250 | Parameters - Mains - AC setup - Phase direction | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 46250 |  | 446251 | AC phase rotation | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46251 |  | 446252 | Parameters - Mains - AC setup - Mains power measurement - Source | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46251 |  | 446252 | Parameters - Busbar - AC setup - Power measurement - Source | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 46251 |  | 446252 | Parameters - Busbar B - AC setup - Power measurement - Source | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46252 |  | 446253 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46253 |  | 446254 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46254 |  | 446255 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46255 |  | 446256 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46256 |  | 446257 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46257 |  | 446258 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46258 |  | 446259 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46259 |  | 446260 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46260 |  | 446261 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46261 |  | 446262 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46262 |  | 446263 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46263 |  | 446264 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46264 |  | 446265 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46265 |  | 446266 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46266 |  | 446267 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46267 |  | 446268 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46268 |  | 446269 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46269 |  | 446270 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46270 |  | 446271 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46271 |  | 446272 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46272 |  | 446273 | Parameters - Engine - Power derate - Temperature - Derate 1 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46273 |  | 446274 | Parameters - Engine - Power derate - Temperature - Derate 1 - Enable - Enable derate | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46274 |  | 446275 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46275 |  | 446276 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46276 |  | 446277 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46277 |  | 446278 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46278 |  | 446279 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46279 |  | 446280 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46280 |  | 446281 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46281 |  | 446282 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46282 |  | 446283 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46283 |  | 446284 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46284 |  | 446285 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46285 |  | 446286 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46286 |  | 446287 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46287 |  | 446288 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46288 |  | 446289 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46289 |  | 446290 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46290 |  | 446291 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46291 |  | 446292 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46292 |  | 446293 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46293 |  | 446294 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46294 |  | 446295 | Parameters - Engine - Power derate - Temperature - Derate 2 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46295 |  | 446296 | Parameters - Engine - Power derate - Temperature - Derate 2 - Enable - Enable derate | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46296 |  | 446297 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46297 |  | 446298 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46298 |  | 446299 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46299 |  | 446300 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46300 |  | 446301 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46301 |  | 446302 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46302 |  | 446303 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46303 |  | 446304 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46304 |  | 446305 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46305 |  | 446306 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46306 |  | 446307 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46307 |  | 446308 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46308 |  | 446309 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46309 |  | 446310 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46310 |  | 446311 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46311 |  | 446312 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46312 |  | 446313 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46313 |  | 446314 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46314 |  | 446315 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46315 |  | 446316 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
General timer: Settings | 46316 |  | 446317 | Parameters - Engine - Power derate - Temperature - Derate 3 - Setup - Derate curve | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46317 |  | 446318 | Parameters - Engine - Power derate - Temperature - Derate 3 - Enable - Enable derate | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46318 |  | 446319 | Parameters - Engine - Power derate - Percentage - Derate 1 - Enable - Enable derate | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46319 |  | 446320 | Parameters - Local - AC measurement filters - Primary AC measurements - Voltage | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46320 |  | 446321 | Parameters - Local - AC measurement filters - Primary AC measurements - Current | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46321 |  | 446322 | Parameters - Local - AC measurement filters - Primary AC measurements - Active power | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46322 |  | 446323 | Parameters - Local - AC measurement filters - Primary AC measurements - Reactive power | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46323 |  | 446324 | Parameters - Local - AC measurement filters - Primary AC measurements - Apparent power | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46324 |  | 446325 | Parameters - Local - AC measurement filters - Primary AC measurements - Power factor and cos phi | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46325 |  | 446326 | Parameters - Local - AC measurement filters - Primary AC measurements - Frequency from voltage | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46326 |  | 446327 | Parameters - Local - AC measurement filters - Primary AC measurements - Frequency from current | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46370 |  | 446371 | Parameters - Generator - Additional protections - Average over-voltage 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46370 |  | 446371 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46370 |  | 446371 | Parameters - Mains - Additional protections - Average over-voltage 1 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 46371 |  | 446372 | Parameters - Generator - Additional protections - Average over-voltage 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46371 |  | 446372 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46371 |  | 446372 | Parameters - Mains - Additional protections - Average over-voltage 2 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 46372 |  | 446373 | Parameters - Mains - Additional protections - ROCOF (df/dt) - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46372 |  | 446373 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 46372 |  | 446373 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46373 |  | 446374 | Parameters - Mains - Additional protections - Vector shift - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46373 |  | 446374 | Parameters - Busbar - Additional protections - Vector shift - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 46373 |  | 446374 | Parameters - Busbar B - Additional protections - Vector shift - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46374 |  | 446375 | Parameters - Generator - Additional protections - V< and Q< 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46374 |  | 446375 | Parameters - Busbar A - Additional protections - V< and Q< 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46374 |  | 446375 | Parameters - Mains - Additional protections - V< and Q< 1 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 46375 |  | 446376 | Parameters - Generator - Additional protections - V< and Q< 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46375 |  | 446376 | Parameters - Busbar A - Additional protections - V< and Q< 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46375 |  | 446376 | Parameters - Mains - Additional protections - V< and Q< 2 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 46376 |  | 446377 | Parameters - Mains - Additional protections - Vector shift - Vector shift select | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46376 |  | 446377 | Parameters - Busbar - Additional protections - Vector shift - Vector shift select | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 46376 |  | 446377 | Parameters - Busbar B - Additional protections - Vector shift - Vector shift select | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46377 |  | 446378 | Parameters - Generator - Current protections - Inverse time over-current - Curve | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46377 |  | 446378 | Parameters - Busbar A - Current protections - Inverse time over-current - Curve | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46377 |  | 446378 | Parameters - Mains - Current protections - Inverse time over-current - Curve | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 46378 |  | 446379 | Parameters - Generator - Current protections - Inverse time over-current - Limit | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46378 |  | 446379 | Parameters - Busbar A - Current protections - Inverse time over-current - Limit | INT16 | X * 10 | X * 0.1 | % |  | X
General timer: Settings | 46378 |  | 446379 | Parameters - Mains - Current protections - Inverse time over-current - Limit | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
General timer: Settings | 46379 |  | 446380 | Parameters - Generator - Current protections - Inverse time over-current - Time multiplier setting | INT16 | X * 100 | X * 0.01 |  | X |  | X | X | X
General timer: Settings | 46379 |  | 446380 | Parameters - Busbar A - Current protections - Inverse time over-current - Time multiplier setting | INT16 | X * 100 | X * 0.01 |  |  | X
General timer: Settings | 46379 |  | 446380 | Parameters - Mains - Current protections - Inverse time over-current - Time multiplier setting | INT16 | X * 100 | X * 0.01 | [6 empty] | X | X
General timer: Settings | 46380 |  | 446381 | Parameters - Generator - Current protections - Inverse time over-current - k | INT16 | X * 1000 | X * 0.001 | s | X |  | X | X | X
General timer: Settings | 46380 |  | 446381 | Parameters - Busbar A - Current protections - Inverse time over-current - k | INT16 | X * 1000 | X * 0.001 | s |  | X
General timer: Settings | 46380 |  | 446381 | Parameters - Mains - Current protections - Inverse time over-current - k | INT16 | X * 1000 | X * 0.001 | s | [5 empty] | X | X
General timer: Settings | 46381 |  | 446382 | Parameters - Generator - Current protections - Inverse time over-current - c | INT16 | X * 1000 | X * 0.001 | s | X |  | X | X | X
General timer: Settings | 46381 |  | 446382 | Parameters - Busbar A - Current protections - Inverse time over-current - c | INT16 | X * 1000 | X * 0.001 | s |  | X
General timer: Settings | 46381 |  | 446382 | Parameters - Mains - Current protections - Inverse time over-current - c | INT16 | X * 1000 | X * 0.001 | s | [5 empty] | X | X
General timer: Settings | 46382 |  | 446383 | Parameters - Generator - Current protections - Inverse time over-current - alpha | INT16 | X * 1000 | X * 0.001 | s | X |  | X | X | X
General timer: Settings | 46382 |  | 446383 | Parameters - Busbar A - Current protections - Inverse time over-current - alpha | INT16 | X * 1000 | X * 0.001 | s |  | X
General timer: Settings | 46382 |  | 446383 | Parameters - Mains - Current protections - Inverse time over-current - alpha | INT16 | X * 1000 | X * 0.001 | s | [5 empty] | X | X
General timer: Settings | 46383 |  | 446384 | Parameters - Local - 4th current input - Earth inverse time over-current - Curve | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46384 |  | 446385 | Parameters - Local - 4th current input - Earth inverse time over-current - Limit | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 46385 |  | 446386 | Parameters - Local - 4th current input - Earth inverse time over-current - Time multiplier setting | INT16 | X * 100 | X * 0.01 |  | X | X | X | X | X | X | X
General timer: Settings | 46386 |  | 446387 | Parameters - Local - 4th current input - Earth inverse time over-current - k | INT16 | X * 1000 | X * 0.001 | s | X | X | X | X | X | X | X
General timer: Settings | 46387 |  | 446388 | Parameters - Local - 4th current input - Earth inverse time over-current - c | INT16 | X * 1000 | X * 0.001 | s | X | X | X | X | X | X | X
General timer: Settings | 46388 |  | 446389 | Parameters - Local - 4th current input - Earth inverse time over-current - alpha | INT16 | X * 1000 | X * 0.001 | s | X | X | X | X | X | X | X
General timer: Settings | 46389 |  | 446390 | Parameters - Local - 4th current input - Neutral inverse time over-current - Curve | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46390 |  | 446391 | Parameters - Local - 4th current input - Neutral inverse time over-current - Limit | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 46391 |  | 446392 | Parameters - Local - 4th current input - Neutral inverse time over-current - Time multiplier setting | INT16 | X * 100 | X * 0.01 |  | X | X | X | X | X | X | X
General timer: Settings | 46392 |  | 446393 | Parameters - Local - 4th current input - Neutral inverse time over-current - k | INT16 | X * 1000 | X * 0.001 | s | X | X | X | X | X | X | X
General timer: Settings | 46393 |  | 446394 | Parameters - Local - 4th current input - Neutral inverse time over-current - c | INT16 | X * 1000 | X * 0.001 | s | X | X | X | X | X | X | X
General timer: Settings | 46394 |  | 446395 | Parameters - Local - 4th current input - Neutral inverse time over-current - alpha | INT16 | X * 1000 | X * 0.001 | s | X | X | X | X | X | X | X
General timer: Settings | 46395 |  | 446396 | Parameters - Generator - Current protections - Inverse time over-current - Threshold | INT16 | X * 1000 | X * 0.001 |  | X |  | X | X | X
General timer: Settings | 46395 |  | 446396 | Parameters - Busbar A - Current protections - Inverse time over-current - Threshold | INT16 | X * 1000 | X * 0.001 |  |  | X
General timer: Settings | 46395 |  | 446396 | Parameters - Mains - Current protections - Inverse time over-current - Threshold | INT16 | X * 1000 | X * 0.001 | [6 empty] | X | X
General timer: Settings | 46396 |  | 446397 | Parameters - Local - 4th current input - Earth inverse time over-current - Threshold | INT16 | X * 1000 | X * 0.001 |  | X | X | X | X | X | X | X
General timer: Settings | 46397 |  | 446398 | Parameters - Local - 4th current input - Neutral inverse time over-current - Threshold | INT16 | X * 1000 | X * 0.001 |  | X | X | X | X | X | X | X
General timer: Settings | 46398 |  | 446399 | Parameters - Generator - Additional protections - V< and Q< 1 - I min. | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46398 |  | 446399 | Parameters - Busbar A - Additional protections - V< and Q< 1 - I min. | INT16 | X * 10 | X * 0.1 | % |  | X
General timer: Settings | 46398 |  | 446399 | Parameters - Mains - Additional protections - V< and Q< 1 - I min. | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
General timer: Settings | 46399 |  | 446400 | Parameters - Generator - Additional protections - V< and Q< 1 - Angle min. | INT16 | X * 100 | X * 0.01 | ° | X |  | X | X | X
General timer: Settings | 46399 |  | 446400 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Angle min. | INT16 | X * 100 | X * 0.01 | ° |  | X
General timer: Settings | 46399 |  | 446400 | Parameters - Mains - Additional protections - V< and Q< 1 - Angle min. | INT16 | X * 100 | X * 0.01 | ° | [5 empty] | X | X
General timer: Settings | 46400 |  | 446401 | Parameters - Generator - Additional protections - V< and Q< 2 - I min. | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46400 |  | 446401 | Parameters - Busbar A - Additional protections - V< and Q< 2 - I min. | INT16 | X * 10 | X * 0.1 | % |  | X
General timer: Settings | 46400 |  | 446401 | Parameters - Mains - Additional protections - V< and Q< 2 - I min. | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
General timer: Settings | 46401 |  | 446402 | Parameters - Generator - Additional protections - V< and Q< 2 - Angle min. | INT16 | X * 100 | X * 0.01 | ° | X |  | X | X | X
General timer: Settings | 46401 |  | 446402 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Angle min. | INT16 | X * 100 | X * 0.01 | ° |  | X
General timer: Settings | 46401 |  | 446402 | Parameters - Mains - Additional protections - V< and Q< 2 - Angle min. | INT16 | X * 100 | X * 0.01 | ° | [5 empty] | X | X
General timer: Settings | 46402 |  | 446403 | Parameters - Generator - Additional protections - Average over-voltage 1 - V> aggregate time | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General timer: Settings | 46402 |  | 446403 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - V> aggregate time | INT16 | X * 1 | X * 1 | s |  | X
General timer: Settings | 46402 |  | 446403 | Parameters - Mains - Additional protections - Average over-voltage 1 - V> aggregate time | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
General timer: Settings | 46403 |  | 446404 | Parameters - Generator - Additional protections - Average over-voltage 2 - V> aggregate time | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General timer: Settings | 46403 |  | 446404 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - V> aggregate time | INT16 | X * 1 | X * 1 | s |  | X
General timer: Settings | 46403 |  | 446404 | Parameters - Mains - Additional protections - Average over-voltage 2 - V> aggregate time | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
General timer: Settings | 46404 |  | 446405 | Parameters - Mains - Additional protections - ROCOF (df/dt) - ROCOF (df/dt) measurement half period | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 46404 |  | 446405 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - ROCOF (df/dt) measurement half period | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 46404 |  | 446405 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - ROCOF (df/dt) measurement half period | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 46405 |  | 446406 | Parameters - Mains - Additional protections - ROCOF (df/dt) - ROCOF (df/dt) positive set point | INT16 | X * 1000 | X * 0.001 | Hz/s |  |  | X | X
General timer: Settings | 46405 |  | 446406 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - ROCOF (df/dt) positive set point | INT16 | X * 1000 | X * 0.001 | Hz/s | X |  |  |  | X | X | X
General timer: Settings | 46405 |  | 446406 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - ROCOF (df/dt) positive set point | INT16 | X * 1000 | X * 0.001 | Hz/s |  | X
General timer: Settings | 46406 |  | 446407 | Parameters - Mains - Additional protections - ROCOF (df/dt) - ROCOF (df/dt) negative set point | INT16 | X * 1000 | X * 0.001 | Hz/s |  |  | X | X
General timer: Settings | 46406 |  | 446407 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - ROCOF (df/dt) negative set point | INT16 | X * 1000 | X * 0.001 | Hz/s | X |  |  |  | X | X | X
General timer: Settings | 46406 |  | 446407 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - ROCOF (df/dt) negative set point | INT16 | X * 1000 | X * 0.001 | Hz/s |  | X
General timer: Settings | 46621 |  | 446622 | Stabilised differential | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46622 |  | 446623 | Parameters - Generator - Current protections - Stabilised differential current - Stabilised differential - I diff. min. | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 46623 |  | 446624 | Parameters - Generator - Current protections - Stabilised differential current - Stabilised differential - Region 1: End | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 46624 |  | 446625 | Parameters - Generator - Current protections - Stabilised differential current - Stabilised differential - Region 2: Slope | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 46625 |  | 446626 | Parameters - Generator - Current protections - Stabilised differential current - Stabilised differential - Region 2: End | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 46626 |  | 446627 | Parameters - Generator - Current protections - Stabilised differential current - Stabilised differential - Region 3: Slope | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 46627 |  | 446628 | Parameters - Local - Command sources - Active local sources - PICUS commands | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46628 |  | 446629 | Parameters - Local - Command sources - Active local sources - Modbus commands | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46629 |  | 446630 | Parameters - Local - Command sources - Active local sources - I/O commands | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46630 |  | 446631 | Parameters - Local - Command sources - Active local sources - CustomLogic commands | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46631 |  | 446632 | Parameters - Local - Command sources - Active local sources - CODESYS commands | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46632 |  | 446633 | Parameters - Local - Command sources - Active local sources - Display commands | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46633 |  | 446634 | Parameters - Local - Command sources - Active remote sources - PICUS commands | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46634 |  | 446635 | Parameters - Local - Command sources - Active remote sources - Modbus commands | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46635 |  | 446636 | Parameters - Local - Command sources - Active remote sources - I/O commands | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46636 |  | 446637 | Parameters - Local - Command sources - Active remote sources - CustomLogic commands | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46637 |  | 446638 | Parameters - Local - Command sources - Active remote sources - CODESYS commands | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46638 |  | 446639 | Parameters - Local - Command sources - Active remote sources - Display commands | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46639 |  | 446640 | Parameters - Local - Alarm horn - Horn 1 - De-energise when all alarms are acknowledged | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46640 |  | 446641 | Parameters - Local - Alarm horn - Horn 1 - Reset when new alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46641 |  | 446642 | Parameters - Local - Alarm horn - Horn 1 - Minimum down time - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 46642 |  | 446643 | Parameters - Local - Alarm horn - Horn 1 - Minimum up time - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 46643 |  | 446644 | Parameters - Local - Alarm horn - Horn 2 - De-energise when all alarms are acknowledged | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46644 |  | 446645 | Parameters - Local - Alarm horn - Horn 2 - Reset when new alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46645 |  | 446646 | Parameters - Local - Alarm horn - Horn 2 - Minimum down time - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 46646 |  | 446647 | Parameters - Local - Alarm horn - Horn 2 - Minimum up time - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 46647 |  | 446648 | Parameters - Local - Alarm horn - Horn 3 - De-energise when all alarms are acknowledged | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46648 |  | 446649 | Parameters - Local - Alarm horn - Horn 3 - Reset when new alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46649 |  | 446650 | Parameters - Local - Alarm horn - Horn 3 - Minimum down time - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 46650 |  | 446651 | Parameters - Local - Alarm horn - Horn 3 - Minimum up time - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 46651 |  | 446652 | Parameters - Local - Alive - Alive configuration - Duty cycle | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 46652 |  | 446653 | Parameters - Local - Alive - Alive configuration - Period - Configuration | INT16 | X * 100 | X * 0.01 | s | X | X | X | X | X | X | X
General timer: Settings | 46653 |  | 446654 | Parameters - Local - CustomLogic - Configuration - Enable | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46654 |  | 446655 | Parameters - Regulators - GOV - Relay configuration - Automatic configuration - Period time | INT16 | X * 1 | X * 1 | ms | X |  | X | X | X
General timer: Settings | 46655 |  | 446656 | Parameters - Regulators - GOV - Relay configuration - Automatic configuration - Minimum ON time | INT16 | X * 1 | X * 1 | ms | X |  | X | X | X
General timer: Settings | 46656 |  | 446657 | Parameters - Regulators - AVR - Relay configuration - Automatic configuration - Period time | INT16 | X * 1 | X * 1 | ms | X |  | X | X | X
General timer: Settings | 46657 |  | 446658 | Parameters - Regulators - AVR - Relay configuration - Automatic configuration - Minimum ON time | INT16 | X * 1 | X * 1 | ms | X |  | X | X | X
General timer: Settings | 46658 |  | 446659 | Parameters - Regulators - GOV - Analogue - Frequency synchronisation - Kp | INT16 | X * 100 | X * 0.01 |  | X |  | X | X | X
General timer: Settings | 46659 |  | 446660 | Parameters - Regulators - GOV - Analogue - Frequency synchronisation - Ti | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46660 |  | 446661 | Parameters - Regulators - GOV - Analogue - Frequency synchronisation - Td | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46661 |  | 446662 | Parameters - Regulators - GOV - Analogue - Phase synchronisation - Kp | INT16 | X * 100 | X * 0.01 |  | X |  | X | X | X
General timer: Settings | 46662 |  | 446663 | Parameters - Regulators - GOV - Analogue - Phase synchronisation - Ti | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46663 |  | 446664 | Parameters - Regulators - GOV - Analogue - Phase synchronisation - Td | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46664 |  | 446665 | Parameters - Regulators - GOV - Analogue - Frequency regulation - Kp | INT16 | X * 100 | X * 0.01 |  | X |  | X | X | X
General timer: Settings | 46665 |  | 446666 | Parameters - Regulators - GOV - Analogue - Frequency regulation - Ti | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46666 |  | 446667 | Parameters - Regulators - GOV - Analogue - Frequency regulation - Td | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46667 |  | 446668 | Parameters - Regulators - GOV - Analogue - Power load sharing regulation - Kp | INT16 | X * 100 | X * 0.01 |  | X |  | X | X | X
General timer: Settings | 46668 |  | 446669 | Parameters - Regulators - GOV - Analogue - Power load sharing regulation - Ti | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46669 |  | 446670 | Parameters - Regulators - GOV - Analogue - Power load sharing regulation - Td | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46670 |  | 446671 | Parameters - Regulators - GOV - Analogue - Power load sharing regulation - P weight | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46671 |  | 446672 | Parameters - Regulators - AVR - Analogue - Reactive power load sharing regulation - Q weight | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46672 |  | 446673 | Parameters - Regulators - GOV - Analogue - Power regulation - Kp | INT16 | X * 100 | X * 0.01 |  | X |  | X | X | X
General timer: Settings | 46673 |  | 446674 | Parameters - Regulators - GOV - Analogue - Power regulation - Ti | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46674 |  | 446675 | Parameters - Regulators - GOV - Analogue - Power regulation - Td | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46675 |  | 446676 | Parameters - Regulators - GOV - Relay configuration - Frequency synchronisation - Kp | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
General timer: Settings | 46676 |  | 446677 | Parameters - Regulators - GOV - Relay configuration - Phase synchronisation - Kp | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
General timer: Settings | 46677 |  | 446678 | Parameters - Regulators - GOV - Relay configuration - Frequency regulation - Kp | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
General timer: Settings | 46678 |  | 446679 | Parameters - Regulators - GOV - Relay configuration - Frequency regulation - Deadband | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 46679 |  | 446680 | Parameters - Regulators - GOV - Relay configuration - Power regulation - Kp | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
General timer: Settings | 46680 |  | 446681 | Parameters - Regulators - GOV - Relay configuration - Power regulation - Deadband | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 46681 |  | 446682 | Parameters - Regulators - GOV - Relay configuration - Power load sharing regulation - Kp | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
General timer: Settings | 46682 |  | 446683 | Parameters - Regulators - GOV - Relay configuration - Power load sharing regulation - f deadband | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 46683 |  | 446684 | Parameters - Regulators - GOV - Relay configuration - Power load sharing regulation - P deadband | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 46684 |  | 446685 | Parameters - Regulators - GOV - Relay configuration - Power load sharing regulation - P weight | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 46685 |  | 446686 | Parameters - Regulators - AVR - Relay configuration - Reactive power load sharing regulation - Q weight | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46686 |  | 446687 | Parameters - Regulators - AVR - Analogue - Reactive power load sharing regulation - Kp | INT16 | X * 100 | X * 0.01 |  | X |  | X | X | X
General timer: Settings | 46687 |  | 446688 | Parameters - Regulators - AVR - Analogue - Reactive power load sharing regulation - Ti | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46688 |  | 446689 | Parameters - Regulators - AVR - Analogue - Reactive power load sharing regulation - Td | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46689 |  | 446690 | Parameters - Regulators - AVR - Analogue - Voltage regulation - Kp | INT16 | X * 100 | X * 0.01 |  | X |  | X | X | X
General timer: Settings | 46690 |  | 446691 | Parameters - Regulators - AVR - Analogue - Voltage regulation - Ti | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46691 |  | 446692 | Parameters - Regulators - AVR - Analogue - Voltage regulation - Td | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46692 |  | 446693 | Parameters - Regulators - AVR - Analogue - Reactive power regulation - Kp | INT16 | X * 100 | X * 0.01 |  | X |  | X | X | X
General timer: Settings | 46693 |  | 446694 | Parameters - Regulators - AVR - Analogue - Reactive power regulation - Ti | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46694 |  | 446695 | Parameters - Regulators - AVR - Analogue - Reactive power regulation - Td | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X
General timer: Settings | 46695 |  | 446696 | Parameters - Regulators - AVR - Relay configuration - Voltage regulation - Kp | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
General timer: Settings | 46696 |  | 446697 | Parameters - Regulators - AVR - Relay configuration - Voltage regulation - Deadband | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46697 |  | 446698 | Parameters - Regulators - AVR - Relay configuration - Reactive power load sharing regulation - Kp | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
General timer: Settings | 46698 |  | 446699 | Parameters - Regulators - AVR - Relay configuration - Reactive power load sharing regulation - V deadband | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46699 |  | 446700 | Parameters - Regulators - AVR - Relay configuration - Reactive power regulation - Kp | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
General timer: Settings | 46700 |  | 446701 | Parameters - Regulators - AVR - Relay configuration - Reactive power regulation - Deadband | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46701 |  | 446702 | Parameters - Regulators - AVR - Relay configuration - Reactive power load sharing regulation - Q deadband | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 46705 |  | 446706 | Parameters - Regulators - GOV - General configuration - Regulation delay - Regulator delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 46706 |  | 446707 | Parameters - Regulators - AVR - General configuration - Regulator output - Output type | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 46707 |  | 446708 | Parameters - Regulators - GOV - General configuration - Regulator output - Output type | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 46745 |  | 446746 | Parameters - Regulators - GOV - Relay configuration - Manual configuration - Period time | INT16 | X * 1 | X * 1 | ms | X | X | X | X | X | X | X
General timer: Settings | 46748 |  | 446749 | Parameters - Regulators - AVR - Relay configuration - Manual configuration - Period time | INT16 | X * 1 | X * 1 | ms | X |  | X | X | X
General timer: Settings | 47039 |  | 447040 | Parameters - Breakers - Generator breaker configuration - Synchronisation setting - Delta speed min. | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 47040 |  | 447041 | Parameters - Breakers - Generator breaker configuration - Synchronisation setting - Delta speed max. | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 47041 |  | 447042 | Parameters - Mains - AC setup - Supervision selector - Recovery selector time - Configuration | INT16 | X * 10 | X * 0.1 | s |  |  | X | X |  | X | X
General timer: Settings | 47042 |  | 447043 | Parameters - Mains - AC setup - Supervision selector - Recovery time fast - Configuration | INT16 | X * 10 | X * 0.1 | s |  |  | X | X |  | X | X
General timer: Settings | 47043 |  | 447044 | Parameters - Mains - AC setup - Supervision selector - Recovery time slow - Configuration | INT16 | X * 10 | X * 0.1 | s |  |  | X | X |  | X | X
General timer: Settings | 47044 |  | 447045 | Parameters - Mains - AC setup - Supervision selector - Voltage low | INT16 | X * 10 | X * 0.1 | % |  |  | X | X |  | X | X
General timer: Settings | 47045 |  | 447046 | Parameters - Mains - AC setup - Supervision selector - Voltage high | INT16 | X * 10 | X * 0.1 | % |  |  | X | X |  | X | X
General timer: Settings | 47046 |  | 447047 | Parameters - Mains - AC setup - Supervision selector - Frequency low | INT16 | X * 10 | X * 0.1 | % |  |  | X | X |  | X | X
General timer: Settings | 47047 |  | 447048 | Parameters - Mains - AC setup - Supervision selector - Frequency high | INT16 | X * 10 | X * 0.1 | % |  |  | X | X |  | X | X
General timer: Settings | 47048 |  | 447049 | Parameters - Mains - AC setup - Supervision selector - Enable supervision | INT16 | X * 1 | X * 1 |  |  |  | X | X |  | X | X
General timer: Settings | 47049 |  | 447050 | Parameters - Hardware - PSM3.1 1 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47050 |  | 447051 | Parameters - Hardware - PSM3.2 1 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47051 |  | 447052 | Parameters - Hardware - PSM3.2 2 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47052 |  | 447053 | Parameters - Hardware - PSM3.2 3 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47053 |  | 447054 | Parameters - Hardware - EIM3.1 1 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47054 |  | 447055 | Parameters - Hardware - EIM3.1 2 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47055 |  | 447056 | Parameters - Hardware - EIM3.1 3 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47056 |  | 447057 | Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47057 |  | 447058 | Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47058 |  | 447059 | Parameters - Hardware - GAM3.2 1 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47059 |  | 447060 | Parameters - Hardware - GAM3.2 2 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47060 |  | 447061 | Parameters - Hardware - GAM3.2 3 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47061 |  | 447062 | Parameters - Hardware - PSM3.2 4 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47062 |  | 447063 | Parameters - Hardware - PSM3.2 5 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47063 |  | 447064 | Parameters - Hardware - PSM3.2 6 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47064 |  | 447065 | Parameters - Hardware - PSM3.2 7 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47065 |  | 447066 | Parameters - Hardware - PSM3.2 8 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47066 |  | 447067 | Parameters - Hardware - PSM3.2 9 - Diode compensation - Diode offset | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47069 |  | 447070 | Parameters - Test functions - Lamp test - Activate | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47070 |  | 447071 | Parameters - Test functions - Lamp test - Duration - Configuration | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
General timer: Settings | 47071 |  | 447072 | Parameters - Test functions - Lamp test - Colour cycle time - Configuration | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
General timer: Settings | 47072 |  | 447073 | Parameters - System - Plant - Active application | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47073 |  | 447074 | Parameters - CODESYS - Monitoring - Application not OK - Startup time - Configuration | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
General timer: Settings | 47074 |  | 447075 | Parameters - CODESYS - Configuration - Enable | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47075 |  | 447076 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Power configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47076 |  | 447077 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU powerup time - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47077 |  | 447078 | Parameters - Engine - ECU - Controls - Speed control (TSC1 / Custom) - Enable | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47078 |  | 447079 | Parameters - Engine - ECU - Controls - Speed control (TSC1 / Custom) - Source address | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47079 |  | 447080 | Parameters - Engine - ECU - Controls - Generator control (GC1 / Custom) - Enable | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47080 |  | 447081 | Parameters - Engine - ECU - Controls - Generator control (GC1 / Custom) - Source address | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47081 |  | 447082 | Parameters - Engine - ECU - Controls - Cab message (CM1 / Custom) - Source address | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47082 |  | 447083 | EIC derate | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47083 |  | 447084 | Parameters - Engine - ECU - Controls - Speed control (TSC1 / Custom) - Use nominal RPM as reference | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47084 |  | 447085 | Parameters - Engine - ECU - Controls - CAN controls - Enable | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47085 |  | 447086 | Parameters - Engine - ECU - DPF controls - Controls - Aftertreatment Regeneration Inhibit Switch | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47086 |  | 447087 | Parameters - Engine - ECU - DPF controls - Controls - Aftertreatment Regeneration Force Switch | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47087 |  | 447088 | Parameters - Engine - ECU - Controls - Droop - Droop settings | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47088 |  | 447089 | Parameters - Engine - ECU - Controls - Droop - Droop value | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 47089 |  | 447090 | Parameters - Power transformer - Nominal settings 1 - Busbar side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X | X | X
General timer: Settings | 47089 |  | 447090 | Parameters - Power transformer - Nominal settings 1 - Busbar A side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 47090 |  | 447091 | Parameters - Power transformer - Nominal settings 1 - Generator side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X
General timer: Settings | 47090 |  | 447091 | Parameters - Power transformer - Nominal settings 1 - Busbar B side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 47090 |  | 447091 | Parameters - Power transformer - Nominal settings 1 - Mains side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V | [5 empty] | X | X
General timer: Settings | 47091 |  | 447092 | Parameters - Power transformer - Nominal settings 1 - Phase shift | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47092 |  | 447093 | Parameters - Power transformer - Nominal settings 1 - Winding nominal voltage source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47093 |  | 447094 | Parameters - Power transformer - Nominal settings 2 - Busbar side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X | X | X
General timer: Settings | 47093 |  | 447094 | Parameters - Power transformer - Nominal settings 2 - Busbar A side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 47094 |  | 447095 | Parameters - Power transformer - Nominal settings 2 - Generator side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X
General timer: Settings | 47094 |  | 447095 | Parameters - Power transformer - Nominal settings 2 - Busbar B side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 47094 |  | 447095 | Parameters - Power transformer - Nominal settings 2 - Mains side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V | [5 empty] | X | X
General timer: Settings | 47095 |  | 447096 | Parameters - Power transformer - Nominal settings 2 - Phase shift | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47096 |  | 447097 | Parameters - Power transformer - Nominal settings 2 - Winding nominal voltage source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47097 |  | 447098 | Parameters - Power transformer - Nominal settings 3 - Busbar side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X | X | X
General timer: Settings | 47097 |  | 447098 | Parameters - Power transformer - Nominal settings 3 - Busbar A side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 47098 |  | 447099 | Parameters - Power transformer - Nominal settings 3 - Generator side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X
General timer: Settings | 47098 |  | 447099 | Parameters - Power transformer - Nominal settings 3 - Busbar B side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 47098 |  | 447099 | Parameters - Power transformer - Nominal settings 3 - Mains side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V | [5 empty] | X | X
General timer: Settings | 47099 |  | 447100 | Parameters - Power transformer - Nominal settings 3 - Phase shift | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47100 |  | 447101 | Parameters - Power transformer - Nominal settings 3 - Winding nominal voltage source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47101 |  | 447102 | Parameters - Power transformer - Nominal settings 4 - Busbar side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X | X | X
General timer: Settings | 47101 |  | 447102 | Parameters - Power transformer - Nominal settings 4 - Busbar A side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 47102 |  | 447103 | Parameters - Power transformer - Nominal settings 4 - Generator side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X
General timer: Settings | 47102 |  | 447103 | Parameters - Power transformer - Nominal settings 4 - Busbar B side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V |  | X
General timer: Settings | 47102 |  | 447103 | Parameters - Power transformer - Nominal settings 4 - Mains side winding nominal voltage | INT16 | X * 10 | X * 0.1 | V | [5 empty] | X | X
General timer: Settings | 47103 |  | 447104 | Parameters - Power transformer - Nominal settings 4 - Phase shift | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47104 |  | 447105 | Parameters - Power transformer - Nominal settings 4 - Winding nominal voltage source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47105 |  | 447106 | Parameters - Test functions - Emulation - Emulation active | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47106 |  | 447107 | Parameters - Engine - ECU - Controls - Reset - Power off timer - Configuration | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General timer: Settings | 47117 |  | 447118 | Parameters - Generator - Digital AVR - AC setup - Primary | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X
General timer: Settings | 47118 |  | 447119 | Parameters - Generator - Digital AVR - AC setup - Secondary | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X
General timer: Settings | 47119 |  | 447120 | Parameters - Generator - Digital AVR - AC setup - Busbar - Primary | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X
General timer: Settings | 47120 |  | 447121 | Parameters - Generator - Digital AVR - AC setup - Busbar - Secondary | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X
General timer: Settings | 47121 |  | 447122 | Parameters - Generator - Digital AVR - AC setup - Voltage transformer - Enable VT | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47122 |  | 447123 | Parameters - Generator - Digital AVR - Settings - Start on threshold - Start on threshold PWM | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 47123 |  | 447124 | Parameters - Generator - Digital AVR - Settings - Start on threshold - Start on threshold activation | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 47124 |  | 447125 | Parameters - Generator - Digital AVR - Settings - Soft start - Soft-start ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47125 |  | 447126 | Parameters - Generator - Digital AVR - Operation modes - U/f variable slope - Knee set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 47126 |  | 447127 | Parameters - Generator - Digital AVR - Operation modes - U/f variable slope | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
General timer: Settings | 47127 |  | 447128 | Parameters - Generator - Digital AVR - Operation modes - Soft voltage recovery | INT16 | X * 100 | X * 0.01 | s/% | X |  | X | X | X
General timer: Settings | 47128 |  | 447129 | Parameters - Generator - Digital AVR - Operation modes - Load acceptance module - Adjust LAM | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 47129 |  | 447130 | Parameters - Generator - Digital AVR - Settings - Droop - Reactive droop compensation | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 47130 |  | 447131 | Parameters - Generator - Digital AVR - Settings - Droop - Voltage droop compensation | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 47131 |  | 447132 | Parameters - Generator - Digital AVR - Settings - Droop - Droop type | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47132 |  | 447133 | Parameters - Generator - Digital AVR - Current limitation - Magnetisation - Current limitation transformer | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 47133 |  | 447134 | Parameters - Generator - Digital AVR - Current limitation - Inductive motor starting - Current limitation induction motor | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 47134 |  | 447135 | Parameters - Generator - Digital AVR - Current limitation - Selection - Current limitation type | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47135 |  | 447136 | Parameters - Generator - Digital AVR - Settings - PID - PID gain factor | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X
General timer: Settings | 47136 |  | 447137 | Parameters - Generator - Digital AVR - Settings - Controls - Write all settings | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47137 |  | 447138 | Parameters - Generator - Digital AVR - Settings - Bias - Bias scale | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 47138 |  | 447139 | Parameters - Generator - Digital AVR - Settings - Controls | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47139 |  | 447140 | Parameters - Generator - Digital AVR - Settings - Bias - Analogue bias input type | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47140 |  | 447141 | Parameters - Generator - Digital AVR - AC setup - Selection - AC configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47141 |  | 447142 | Parameters - Generator - Digital AVR - Settings - Reset soft start - Minimum frequency threshold | INT16 | X * 10 | X * 0.1 | Hz | X |  | X | X | X
General timer: Settings | 47142 |  | 447143 | Parameters - Generator - Digital AVR - Settings - Reset soft start - Minimum VBus threshold | INT16 | X * 10 | X * 0.1 | V | X |  | X | X | X
General timer: Settings | 47143 |  | 447144 | Parameters - Generator - Digital AVR - Operation modes - Selection - SVR and LAM configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47144 |  | 447145 | Parameters - Generator - Digital AVR - Operation modes - Load acceptance module - LAM duration | INT16 | X * 10 | X * 0.1 | ms | X |  | X | X | X
General timer: Settings | 47145 |  | 447146 | Parameters - Generator - Digital AVR - Settings - Controls - Reset all DVC alarms | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47146 |  | 447147 | Parameters - Generator - Digital AVR - Settings - Bias - Regulation selection | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47147 |  | 447148 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Power-up time - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47148 |  | 447149 | Parameters - Generator - Voltage protections - Under-voltage 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47148 |  | 447149 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47148 |  | 447149 | Parameters - Mains - Voltage protections - Under-voltage 1 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47149 |  | 447150 | Parameters - Generator - Voltage protections - Under-voltage 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47149 |  | 447150 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47149 |  | 447150 | Parameters - Mains - Voltage protections - Under-voltage 2 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47150 |  | 447151 | Parameters - Generator - Voltage protections - Under-voltage 3 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47150 |  | 447151 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47150 |  | 447151 | Parameters - Mains - Voltage protections - Under-voltage 3 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47151 |  | 447152 | Parameters - Generator - Voltage protections - Over-voltage 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47151 |  | 447152 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47151 |  | 447152 | Parameters - Mains - Voltage protections - Over-voltage 1 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47152 |  | 447153 | Parameters - Generator - Voltage protections - Over-voltage 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47152 |  | 447153 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47152 |  | 447153 | Parameters - Mains - Voltage protections - Over-voltage 2 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47153 |  | 447154 | Parameters - Generator - Voltage protections - Voltage unbalance - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47153 |  | 447154 | Parameters - Busbar A - Voltage protections - Voltage unbalance - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47153 |  | 447154 | Parameters - Mains - Voltage protections - Voltage unbalance - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47154 |  | 447155 | Parameters - Generator - Voltage protections - Negative sequence voltage - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47154 |  | 447155 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47154 |  | 447155 | Parameters - Mains - Voltage protections - Negative sequence voltage - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47155 |  | 447156 | Parameters - Generator - Voltage protections - Zero sequence voltage - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47155 |  | 447156 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47155 |  | 447156 | Parameters - Mains - Voltage protections - Zero sequence voltage - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47156 |  | 447157 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47156 |  | 447157 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47156 |  | 447157 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47157 |  | 447158 | Parameters - Generator - Current protections - Over-current 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47157 |  | 447158 | Parameters - Busbar A - Current protections - Over-current 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47157 |  | 447158 | Parameters - Mains - Current protections - Over-current 1 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47158 |  | 447159 | Parameters - Generator - Current protections - Over-current 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47158 |  | 447159 | Parameters - Busbar A - Current protections - Over-current 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47158 |  | 447159 | Parameters - Mains - Current protections - Over-current 2 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47159 |  | 447160 | Parameters - Generator - Current protections - Over-current 3 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47159 |  | 447160 | Parameters - Busbar A - Current protections - Over-current 3 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47159 |  | 447160 | Parameters - Mains - Current protections - Over-current 3 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47160 |  | 447161 | Parameters - Generator - Current protections - Over-current 4 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47160 |  | 447161 | Parameters - Busbar A - Current protections - Over-current 4 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47160 |  | 447161 | Parameters - Mains - Current protections - Over-current 4 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47161 |  | 447162 | Parameters - Generator - Current protections - Fast over-current 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47161 |  | 447162 | Parameters - Busbar A - Current protections - Fast over-current 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47161 |  | 447162 | Parameters - Mains - Current protections - Fast over-current 1 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47162 |  | 447163 | Parameters - Generator - Current protections - Fast over-current 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47162 |  | 447163 | Parameters - Busbar A - Current protections - Fast over-current 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47162 |  | 447163 | Parameters - Mains - Current protections - Fast over-current 2 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47163 |  | 447164 | Parameters - Generator - Current protections - Current unbalance (average calc.) - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47163 |  | 447164 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47163 |  | 447164 | Parameters - Mains - Current protections - Current unbalance (average calc.) - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47164 |  | 447165 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47164 |  | 447165 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47164 |  | 447165 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47165 |  | 447166 | Parameters - Generator - Current protections - Directional over-current 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47165 |  | 447166 | Parameters - Busbar A - Current protections - Directional over-current 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47165 |  | 447166 | Parameters - Mains - Current protections - Directional over-current 1 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47166 |  | 447167 | Parameters - Generator - Current protections - Directional over-current 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47166 |  | 447167 | Parameters - Busbar A - Current protections - Directional over-current 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47166 |  | 447167 | Parameters - Mains - Current protections - Directional over-current 2 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47167 |  | 447168 | Parameters - Busbar A - Current protections - Directional over-current 3 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47168 |  | 447169 | Parameters - Busbar A - Current protections - Directional over-current 4 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47169 |  | 447170 | Parameters - Generator - Current protections - Negative sequence current - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47169 |  | 447170 | Parameters - Busbar A - Current protections - Negative sequence current - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47169 |  | 447170 | Parameters - Mains - Current protections - Negative sequence current - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47170 |  | 447171 | Parameters - Generator - Current protections - Zero sequence current - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47170 |  | 447171 | Parameters - Busbar A - Current protections - Zero sequence current - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47170 |  | 447171 | Parameters - Mains - Current protections - Zero sequence current - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47171 |  | 447172 | Parameters - Generator - Frequency protections - Over-frequency 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47171 |  | 447172 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47171 |  | 447172 | Parameters - Mains - Frequency protections - Over-frequency 1 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47172 |  | 447173 | Parameters - Generator - Frequency protections - Over-frequency 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47172 |  | 447173 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47172 |  | 447173 | Parameters - Mains - Frequency protections - Over-frequency 2 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47173 |  | 447174 | Parameters - Generator - Frequency protections - Over-frequency 3 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47173 |  | 447174 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47173 |  | 447174 | Parameters - Mains - Frequency protections - Over-frequency 3 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47174 |  | 447175 | Parameters - Generator - Frequency protections - Under-frequency 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47174 |  | 447175 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47174 |  | 447175 | Parameters - Mains - Frequency protections - Under-frequency 1 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47175 |  | 447176 | Parameters - Generator - Frequency protections - Under-frequency 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47175 |  | 447176 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47175 |  | 447176 | Parameters - Mains - Frequency protections - Under-frequency 2 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47176 |  | 447177 | Parameters - Generator - Frequency protections - Under-frequency 3 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47176 |  | 447177 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47176 |  | 447177 | Parameters - Mains - Frequency protections - Under-frequency 3 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47177 |  | 447178 | Parameters - Generator - Power protections - Overload 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47177 |  | 447178 | Parameters - Busbar A - Power protections - Power export 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47177 |  | 447178 | Parameters - Mains - Power protections - Overload 1 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47178 |  | 447179 | Parameters - Generator - Power protections - Overload 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47178 |  | 447179 | Parameters - Busbar A - Power protections - Power export 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47178 |  | 447179 | Parameters - Mains - Power protections - Overload 2 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47179 |  | 447180 | Parameters - Generator - Power protections - Overload 3 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47179 |  | 447180 | Parameters - Busbar A - Power protections - Power export 3 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47179 |  | 447180 | Parameters - Mains - Power protections - Overload 3 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47180 |  | 447181 | Parameters - Generator - Power protections - Overload 4 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47180 |  | 447181 | Parameters - Busbar A - Power protections - Power export 4 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47180 |  | 447181 | Parameters - Mains - Power protections - Overload 4 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47181 |  | 447182 | Parameters - Generator - Power protections - Overload 5 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47181 |  | 447182 | Parameters - Busbar A - Power protections - Power export 5 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47181 |  | 447182 | Parameters - Mains - Power protections - Overload 5 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47182 |  | 447183 | Parameters - Generator - Power protections - Reverse power 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47182 |  | 447183 | Parameters - Busbar A - Power protections - Power import 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47182 |  | 447183 | Parameters - Mains - Power protections - Reverse power 1 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47183 |  | 447184 | Parameters - Generator - Power protections - Reverse power 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47183 |  | 447184 | Parameters - Busbar A - Power protections - Power import 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47183 |  | 447184 | Parameters - Mains - Power protections - Reverse power 2 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47184 |  | 447185 | Parameters - Generator - Reactive power protections - Reactive power export 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47184 |  | 447185 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47184 |  | 447185 | Parameters - Mains - Reactive power protections - Reactive power export 1 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47185 |  | 447186 | Parameters - Generator - Reactive power protections - Reactive power export 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47185 |  | 447186 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47185 |  | 447186 | Parameters - Mains - Reactive power protections - Reactive power export 2 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47186 |  | 447187 | Parameters - Generator - Reactive power protections - Reactive power import 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47186 |  | 447187 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47186 |  | 447187 | Parameters - Mains - Reactive power protections - Reactive power import 1 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47187 |  | 447188 | Parameters - Generator - Reactive power protections - Reactive power import 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47187 |  | 447188 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47187 |  | 447188 | Parameters - Mains - Reactive power protections - Reactive power import 2 - AC setup | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47188 |  | 447189 | Parameters - Mains - Voltage protections - Over-voltage 1 - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47188 |  | 447189 | Parameters - Busbar - Voltage protections - Over-voltage 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47188 |  | 447189 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47189 |  | 447190 | Parameters - Mains - Voltage protections - Over-voltage 2 - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47189 |  | 447190 | Parameters - Busbar - Voltage protections - Over-voltage 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47189 |  | 447190 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47190 |  | 447191 | Parameters - Mains - Voltage protections - Over-voltage 3 - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47190 |  | 447191 | Parameters - Busbar - Voltage protections - Over-voltage 3 - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47190 |  | 447191 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47191 |  | 447192 | Parameters - Mains - Voltage protections - Under-voltage 1 - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47191 |  | 447192 | Parameters - Busbar - Voltage protections - Under-voltage 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47191 |  | 447192 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47192 |  | 447193 | Parameters - Mains - Voltage protections - Under-voltage 2 - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47192 |  | 447193 | Parameters - Busbar - Voltage protections - Under-voltage 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47192 |  | 447193 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47193 |  | 447194 | Parameters - Mains - Voltage protections - Under-voltage 3 - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47193 |  | 447194 | Parameters - Busbar - Voltage protections - Under-voltage 3 - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47193 |  | 447194 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47194 |  | 447195 | Parameters - Mains - Voltage protections - Under-voltage 4 - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47194 |  | 447195 | Parameters - Busbar - Voltage protections - Under-voltage 4 - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47194 |  | 447195 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47195 |  | 447196 | Parameters - Mains - Voltage protections - Voltage unbalance - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47195 |  | 447196 | Parameters - Busbar - Voltage protections - Voltage unbalance - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47195 |  | 447196 | Parameters - Busbar B - Voltage protections - Voltage unbalance - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47196 |  | 447197 | Parameters - Mains - Frequency protections - Over-frequency 1 - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47196 |  | 447197 | Parameters - Busbar - Frequency protections - Over-frequency 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47196 |  | 447197 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47197 |  | 447198 | Parameters - Mains - Frequency protections - Over-frequency 2 - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47197 |  | 447198 | Parameters - Busbar - Frequency protections - Over-frequency 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47197 |  | 447198 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47198 |  | 447199 | Parameters - Mains - Frequency protections - Over-frequency 3 - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47198 |  | 447199 | Parameters - Busbar - Frequency protections - Over-frequency 3 - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47198 |  | 447199 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47199 |  | 447200 | Parameters - Mains - Frequency protections - Under-frequency 1 - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47199 |  | 447200 | Parameters - Busbar - Frequency protections - Under-frequency 1 - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47199 |  | 447200 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47200 |  | 447201 | Parameters - Mains - Frequency protections - Under-frequency 2 - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47200 |  | 447201 | Parameters - Busbar - Frequency protections - Under-frequency 2 - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47200 |  | 447201 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47201 |  | 447202 | Parameters - Mains - Frequency protections - Under-frequency 3 - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47201 |  | 447202 | Parameters - Busbar - Frequency protections - Under-frequency 3 - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47201 |  | 447202 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47202 |  | 447203 | Parameters - Mains - Frequency protections - Under-frequency 4 - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47202 |  | 447203 | Parameters - Busbar - Frequency protections - Under-frequency 4 - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47202 |  | 447203 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47203 |  | 447204 | Parameters - Mains - Voltage protections - Negative sequence voltage - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47203 |  | 447204 | Parameters - Busbar - Voltage protections - Negative sequence voltage - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47203 |  | 447204 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47204 |  | 447205 | Parameters - Mains - Voltage protections - Zero sequence voltage - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47204 |  | 447205 | Parameters - Busbar - Voltage protections - Zero sequence voltage - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47204 |  | 447205 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47205 |  | 447206 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - AC setup | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 47205 |  | 447206 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - AC setup | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47205 |  | 447206 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - AC setup | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47206 |  | 447207 | Parameters - Engine - Stop sequence - Externally stopped - Configuration - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General timer: Settings | 47209 |  | 447210 | Parameters - Engine - Start sequence - Run detection not reached - Configuration | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General timer: Settings | 47210 |  | 447211 | Parameters - Breakers - Generator breaker configuration - Configuration - Delay after Hz/V OK before close | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47211 |  | 447212 | Parameters - Local power management - Mains configuration - Mains breaker configuration - MB close delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
General timer: Settings | 47212 |  | 447213 | Parameters - Breakers - Bus tie breaker configuration - Configuration - BTB supply | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47213 |  | 447214 | Parameters - Breakers - Short-time parallel - Configuration - Overlap | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
General timer: Settings | 47215 |  | 447216 | Parameters - Breakers - Bus tie breaker configuration - Configuration - Tie breaker normally open/closed | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47215 |  | 447216 | Parameters - Breakers - Tie breaker configuration - Configuration - Tie breaker normally open/closed | INT16 | X * 1 | X * 1 | [7 empty] | X
General timer: Settings | 47216 |  | 447217 | Parameters - Power management rules - Ground relay - Ground relay configuration - Relay type | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47217 |  | 447218 | Parameters - Power management rules - Ground relay - Ground relay configuration - Close configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47218 |  | 447219 | Parameters - Power management rules - Ground relay - Ground relay configuration - Open configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47219 |  | 447220 | Parameters - Power management rules - Ground relay - Enable | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47220 |  | 447221 | Parameters - Power management rules - Ground relay - Ground relay configuration - RPM level | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
General timer: Settings | 47221 |  | 447222 | Parameters - Breakers - Close before excitation - Configuration - Breaker close set point | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X | X | X
General timer: Settings | 47223 |  | 447224 | Parameters - Breakers - Close before excitation - Configuration - Timer crank release to AVR on | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47224 |  | 447225 | Parameters - Breakers - Close before excitation - Configuration - Breakers to close | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47225 |  | 447226 | Parameters - Breakers - Close before excitation - Configuration - Soft-start timer | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47226 |  | 447227 | Parameters - Breakers - Close before excitation - Configuration - Minimum RPM for excitation | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
General timer: Settings | 47227 |  | 447228 | Parameters - Breakers - Close before excitation - Configuration - Voltage discharge timer for GB close | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47228 |  | 447229 | Parameters - Breakers - Close before excitation - Configuration - Maximum rerun voltage for GB close | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47229 |  | 447230 | Parameters - Breakers - Close before excitation - Configuration - Excitation control during cooldown | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47230 |  | 447231 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Low voltage hysteresis | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
General timer: Settings | 47231 |  | 447232 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - High voltage hysteresis | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
General timer: Settings | 47232 |  | 447233 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Low frequency hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X | X | X
General timer: Settings | 47233 |  | 447234 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - High frequency hysteresis | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X | X | X
General timer: Settings | 47234 |  | 447235 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Voltage failure delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
General timer: Settings | 47235 |  | 447236 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Voltage OK delay - Configuration | INT16 | X * 1 | X * 1 | s | X |  | X | X | X | X | X
General timer: Settings | 47236 |  | 447237 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Low voltage | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
General timer: Settings | 47237 |  | 447238 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - High voltage | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
General timer: Settings | 47238 |  | 447239 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Voltage failure sequence | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
General timer: Settings | 47239 |  | 447240 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Unbalance voltage | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
General timer: Settings | 47240 |  | 447241 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Frequency failure delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X | X | X
General timer: Settings | 47241 |  | 447242 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Frequency OK delay - Configuration | INT16 | X * 1 | X * 1 | s | X |  | X | X | X | X | X
General timer: Settings | 47242 |  | 447243 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - Low frequency | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X | X | X
General timer: Settings | 47243 |  | 447244 | Parameters - Local power management - Mains configuration - Voltage and frequency OK - High frequency | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X | X | X
General timer: Settings | 47244 |  | 447245 | Current PMS mode | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47245 |  | 447246 | Previous PMS mode | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47248 |  | 447249 | Parameters - Regulators - GOV - Regulation set points - Active power ramp configuration - Warm up set point | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 47249 |  | 447250 | Parameters - Regulators - GOV - Regulation set points - Active power ramp configuration - Island ramping | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47250 |  | 447251 | Parameters - Regulators - GOV - Regulation set points - Base load - Return mode | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47255 |  | 447256 | Parameters - Local power management - Mains configuration - Tie breaker configuration - TB de-load before GB | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47256 |  | 447257 | Parameters - Local power management - Non-connected genset - Stop timer - Delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47258 |  | 447259 | Breaker type | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47259 |  | 447260 | MB breaker type | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
General timer: Settings | 47260 |  | 447261 | Parameters - Mains - AC setup - Voltage and frequency OK - Measurement configuration | INT16 | X * 1 | X * 1 |  |  |  | X | X |  | X | X
General timer: Settings | 47261 |  | 447262 | Parameters - System - Monitoring - Mode while controller missing - Mode | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47262 |  | 447263 | Parameters - System - Monitoring - Missing controllers | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47263 |  | 447264 | Internal CAN protocol | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47264 |  | 447265 | Parameters - Power management rules - Mains power - Peak shaving - Start generator | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47266 |  | 447267 | Parameters - Power management rules - Mains power - Peak shaving - Minimum load | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47267 |  | 447268 | Parameters - Power management rules - Mains power - Peak shaving - Stop generator | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47269 |  | 447270 | Parameters - Local - Mode - Command mode - Selection | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
General timer: Settings | 47270 |  | 447271 | Parameters - Power management rules - Mains power - Common power factor control - Set point | INT16 | X * 1000 | X * 0.001 |  | X |  | X | X | X | X | X
General timer: Settings | 47271 |  | 447272 | Parameters - Power management rules - Mains power - Common power factor control - Type | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
General timer: Settings | 47272 |  | 447273 | Parameters - Power management rules - Mains power - Common power factor control - Usage | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47273 |  | 447274 | Parameters - Power management rules - Mains power - Common power factor control - Controller settings Q | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47274 |  | 447275 | Parameters - Power management rules - Mains power - Common power factor control - Controller settings cos phi or Q | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47275 |  | 447276 | Parameters - Power management rules - Load-dependent start/stop - Configuration - Minimum load | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47276 |  | 447277 | Parameters - Power management rules - Mains power - Peak shaving - Start delay - Configuration | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General timer: Settings | 47277 |  | 447278 | Parameters - Power management rules - Mains power - Active power - Offset 1 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X | X | X
General timer: Settings | 47278 |  | 447279 | Parameters - Power management rules - Mains power - Active power - Offset 2 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X | X | X
General timer: Settings | 47279 |  | 447280 | Parameters - Power management rules - Mains power - Active power - Offset 3 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X | X | X
General timer: Settings | 47280 |  | 447281 | Parameters - Power management rules - Mains power - Fixed cos phi offset - Offset 1 | INT16 | X * 10000 | X * 0.0001 |  | X |  | X | X | X | X | X
General timer: Settings | 47281 |  | 447282 | Parameters - Power management rules - Mains power - Fixed cos phi offset - Offset 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
General timer: Settings | 47282 |  | 447283 | Parameters - Power management rules - Mains power - Fixed cos phi offset - Offset 2 | INT16 | X * 10000 | X * 0.0001 |  | X |  | X | X | X | X | X
General timer: Settings | 47283 |  | 447284 | Parameters - Power management rules - Mains power - Fixed cos phi offset - Offset 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
General timer: Settings | 47284 |  | 447285 | Parameters - Power management rules - Mains power - Fixed cos phi offset - Offset 3 | INT16 | X * 10000 | X * 0.0001 |  | X |  | X | X | X | X | X
General timer: Settings | 47285 |  | 447286 | Parameters - Power management rules - Mains power - Fixed cos phi offset - Offset 3 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
General timer: Settings | 47286 |  | 447287 | Parameters - Power management rules - Mains power - External set points - Fixed power | INT16 | X * 1 | X * 1 | kW | X |  | X | X |  | X | X
General timer: Settings | 47287 |  | 447288 | Parameters - Power management rules - Mains power - External set points - Percent of nominal | INT16 | X * 1 | X * 1 | % | X |  | X | X |  | X | X
General timer: Settings | 47288 |  | 447289 | Parameters - Power management rules - Mains power - External set points - Selection | INT16 | X * 1 | X * 1 |  | X |  | X | X |  | X | X
General timer: Settings | 47289 |  | 447290 | Parameters - System power management - Bus tie breaker - Closed ring - Ring close allowed | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47290 |  | 447291 | Parameters - Power management rules - Plant/genset mode - Modes - Genset mode | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47291 |  | 447292 | Plant mode | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47291 |  | 447292 | Parameters - Power management rules - Plant/genset mode - Modes - Plant mode | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47292 |  | 447293 | Parameters - System power management - Store common settings - Settings | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
General timer: Settings | 47293 |  | 447294 | Parameters - Local power management - Mains configuration - Mains breaker configuration - Back synchronising | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
General timer: Settings | 47294 |  | 447295 | Parameters - Local power management - Mains configuration - Mains breaker configuration - Synchronisation to mains | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
General timer: Settings | 47295 |  | 447296 | Parallel | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47295 |  | 447296 | Parameters - Local power management - Mains configuration - Mains breaker configuration - Parallel | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47296 |  | 447297 | No break transfer | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47296 |  | 447297 | Parameters - Local power management - Mains configuration - Mains breaker configuration - No break transfer | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47297 |  | 447298 | Parameters - Local power management - Mains configuration - Controls - Auto switch | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47298 |  | 447299 | Parameters - Local power management - Mains configuration - Controls - Run type | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47299 |  | 447300 | Parameters - Local power management - Mains configuration - Controls - ID to run | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47300 |  | 447301 | Parameters - Local power management - Mains configuration - Controls - MB failure start | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47301 |  | 447302 | Parameters - Local power management - Mains configuration - Tie breaker configuration - TB open point | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47303 |  | 447304 | Parameters - Local power management - Mains configuration - Tie breaker configuration - Power capacity set point | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47305 |  | 447306 | Parameters - Local power management - Mains configuration - Tie breaker configuration - Power capacity overrule delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47306 |  | 447307 | Parameters - Local power management - Mains configuration - Tie breaker configuration - Power capacity overrule enable | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47307 |  | 447308 | Parameters - Local power management - Mains configuration - Controls - Exclude run all | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47308 |  | 447309 | Parameters - System power management - Priority - Selection - Method | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47309 |  | 447310 | Parameters - System power management - Priority - Running hours - Activate priority update | INT16 | X * 1 | X * 1 | h | X |  | X | X | X
General timer: Settings | 47310 |  | 447311 | Parameters - System power management - Priority - Running hours - Method | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47312 |  | 447313 | Parameters - System power management - Priority - Selection - Transmit | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47313 |  | 447314 | Priority 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47314 |  | 447315 | Priority 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47315 |  | 447316 | Priority 3 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47316 |  | 447317 | Priority 4 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47317 |  | 447318 | Priority 5 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47318 |  | 447319 | Priority 6 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47319 |  | 447320 | Priority 7 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47320 |  | 447321 | Priority 8 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47321 |  | 447322 | Priority 9 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47322 |  | 447323 | Priority 10 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47323 |  | 447324 | Priority 11 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47324 |  | 447325 | Priority 12 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47325 |  | 447326 | Priority 13 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47326 |  | 447327 | Priority 14 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47327 |  | 447328 | Priority 15 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47328 |  | 447329 | Priority 16 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47329 |  | 447330 | Priority 17 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47330 |  | 447331 | Priority 18 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47331 |  | 447332 | Priority 19 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47332 |  | 447333 | Priority 20 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47333 |  | 447334 | Priority 21 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47334 |  | 447335 | Priority 22 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47335 |  | 447336 | Priority 23 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47336 |  | 447337 | Priority 24 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47337 |  | 447338 | Priority 25 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47338 |  | 447339 | Priority 26 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47339 |  | 447340 | Priority 27 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47340 |  | 447341 | Priority 28 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47341 |  | 447342 | Priority 29 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47342 |  | 447343 | Priority 30 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47343 |  | 447344 | Priority 31 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47344 |  | 447345 | Priority 32 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47345 |  | 447346 | Parameters - Non-essential load trip - Trip 1 - Settings - Trip when breaker trips | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
General timer: Settings | 47346 |  | 447347 | Parameters - Non-essential load trip - Trip 2 - Settings - Trip when breaker trips | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
General timer: Settings | 47347 |  | 447348 | Parameters - Non-essential load trip - Trip 3 - Settings - Trip when breaker trips | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
General timer: Settings | 47349 |  | 447350 | Parameters - System - Plant - Update - Broadcast application | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47350 |  | 447351 | Parameters - System - Plant - Update - Application to broadcast | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47351 |  | 447352 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Section P> | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47352 |  | 447353 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Section P> factor | INT16 | X * 10 | X * 0.1 |  | X |  | X | X | X | X | X
General timer: Settings | 47353 |  | 447354 | Parameters - Power management rules - Plant/genset mode - Modes - Mode shift | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
General timer: Settings | 47354 |  | 447355 | Parameters - Power management rules - Power reservation - N+X - N + X setup | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47355 |  | 447356 | Parameters - Power management rules - Load-dependent start/stop - Start 1 - P available limit | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47356 |  | 447357 | Parameters - Power management rules - Load-dependent start/stop - Start 1 - S available limit | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47357 |  | 447358 | Parameters - Power management rules - Load-dependent start/stop - Start 1 - Load limit | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47358 |  | 447359 | Parameters - Power management rules - Load-dependent start/stop - Start 1 - Delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47359 |  | 447360 | Parameters - Power management rules - Load-dependent start/stop - Stop 1 - P available limit | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47360 |  | 447361 | Parameters - Power management rules - Load-dependent start/stop - Stop 1 - S available limit | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47361 |  | 447362 | Parameters - Power management rules - Load-dependent start/stop - Stop 1 - Load limit | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47362 |  | 447363 | Parameters - Power management rules - Load-dependent start/stop - Stop 1 - Delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47363 |  | 447364 | Parameters - Power management rules - Load-dependent start/stop - Configuration - Power selection | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47364 |  | 447365 | Parameters - Power management rules - Load-dependent start/stop - Configuration - Method | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47365 |  | 447366 | Parameters - Power management rules - Load-dependent start/stop - Start 2 - P available limit | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47366 |  | 447367 | Parameters - Power management rules - Load-dependent start/stop - Start 2 - S available limit | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47367 |  | 447368 | Parameters - Power management rules - Load-dependent start/stop - Start 2 - Load limit | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47368 |  | 447369 | Parameters - Power management rules - Load-dependent start/stop - Start 2 - Delay - Configuration | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
General timer: Settings | 47370 |  | 447371 | Parameters - Power management rules - Load-dependent start/stop - Stop 2 - P available limit | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47371 |  | 447372 | Parameters - Power management rules - Load-dependent start/stop - Stop 2 - S available limit | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47372 |  | 447373 | Parameters - Power management rules - Load-dependent start/stop - Stop 2 - Load limit | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47373 |  | 447374 | Parameters - Power management rules - Load-dependent start/stop - Stop 2 - Delay - Configuration | INT16 | X * 1 | X * 1 | s | X | X | X | X | X | X | X
General timer: Settings | 47377 |  | 447378 | Parameters - Power management rules - Power reservation - Reserved power - Set point | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X
General timer: Settings | 47379 |  | 447380 | Parameters - Power management rules - Number of gensets connected - Minimum set 1 - Set point | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47380 |  | 447381 | Parameters - Power management rules - Number of gensets connected - Minimum set 2 - Set point | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47381 |  | 447382 | Parameters - Power management rules - Number of gensets connected - Automatic start - Multi-start set 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47382 |  | 447383 | Parameters - Power management rules - Number of gensets connected - Automatic start - Multi-start set 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47383 |  | 447384 | Parameters - Power management rules - Number of gensets connected - Selection - Multi-start selection | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47384 |  | 447385 | Multi-start set during AMF | INT16 | X * 1 | X * 1 |  | X
General timer: Settings | 47385 |  | 447386 | Parameters - Generator - Digital AVR - Settings - Dry alternator - Excitation reference for dry alternator | INT16 | X * 10 | X * 0.1 | A | X |  | X | X | X
General timer: Settings | 47386 |  | 447387 | Parameters - Generator - Digital AVR - Settings - Controls - Digital AVR modes | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47387 |  | 447388 | Parameters - Regulators - GOV - Regulation set points - Active power ramp configuration - Enter operation ramp enable | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47388 |  | 447389 | Parameters - Regulators - GOV - Regulation set points - Active power ramp configuration - Deload ramp enable | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47389 |  | 447390 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47390 |  | 447391 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47391 |  | 447392 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47392 |  | 447393 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47393 |  | 447394 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47394 |  | 447395 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47395 |  | 447396 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47396 |  | 447397 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47397 |  | 447398 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47398 |  | 447399 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47399 |  | 447400 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47400 |  | 447401 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47401 |  | 447402 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47402 |  | 447403 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47403 |  | 447404 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47404 |  | 447405 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47405 |  | 447406 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47406 |  | 447407 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47407 |  | 447408 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47408 |  | 447409 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47409 |  | 447410 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47410 |  | 447411 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47411 |  | 447412 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47412 |  | 447413 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47413 |  | 447414 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47414 |  | 447415 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47415 |  | 447416 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47416 |  | 447417 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47417 |  | 447418 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47418 |  | 447419 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47419 |  | 447420 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47420 |  | 447421 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47421 |  | 447422 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47422 |  | 447423 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47423 |  | 447424 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47424 |  | 447425 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47425 |  | 447426 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47426 |  | 447427 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47427 |  | 447428 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47428 |  | 447429 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47429 |  | 447430 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47430 |  | 447431 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47431 |  | 447432 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47432 |  | 447433 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47433 |  | 447434 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47434 |  | 447435 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47435 |  | 447436 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47436 |  | 447437 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47437 |  | 447438 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47438 |  | 447439 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47439 |  | 447440 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47440 |  | 447441 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47441 |  | 447442 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47442 |  | 447443 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47443 |  | 447444 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47444 |  | 447445 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47445 |  | 447446 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47446 |  | 447447 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47447 |  | 447448 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47448 |  | 447449 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47449 |  | 447450 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47450 |  | 447451 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47451 |  | 447452 | Parameters - Regulators - GOV - Regulation set points - Active power enter operation ramp - Enter operation ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47452 |  | 447453 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47453 |  | 447454 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47454 |  | 447455 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47455 |  | 447456 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47456 |  | 447457 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47457 |  | 447458 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47458 |  | 447459 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47459 |  | 447460 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47460 |  | 447461 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47461 |  | 447462 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47462 |  | 447463 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47463 |  | 447464 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47464 |  | 447465 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47465 |  | 447466 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47466 |  | 447467 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47467 |  | 447468 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47468 |  | 447469 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47469 |  | 447470 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47470 |  | 447471 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47471 |  | 447472 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47472 |  | 447473 | Parameters - Regulators - GOV - Regulation set points - Active power deload ramp - Deload ramp | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47473 |  | 447474 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47474 |  | 447475 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47475 |  | 447476 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47476 |  | 447477 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47477 |  | 447478 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47478 |  | 447479 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47479 |  | 447480 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47480 |  | 447481 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47481 |  | 447482 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47482 |  | 447483 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47483 |  | 447484 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47484 |  | 447485 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47485 |  | 447486 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47486 |  | 447487 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47487 |  | 447488 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47488 |  | 447489 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47489 |  | 447490 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47490 |  | 447491 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47491 |  | 447492 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47492 |  | 447493 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47493 |  | 447494 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp up - Operation ramp up | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47494 |  | 447495 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47495 |  | 447496 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47496 |  | 447497 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47497 |  | 447498 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47498 |  | 447499 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47499 |  | 447500 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47500 |  | 447501 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47501 |  | 447502 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47502 |  | 447503 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47503 |  | 447504 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47504 |  | 447505 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47505 |  | 447506 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47506 |  | 447507 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47507 |  | 447508 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47508 |  | 447509 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47509 |  | 447510 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47510 |  | 447511 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47511 |  | 447512 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47512 |  | 447513 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47513 |  | 447514 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47514 |  | 447515 | Parameters - Regulators - AVR - Regulation set points - Reactive power ramp down - Operation ramp down | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47515 |  | 447516 | Parameters - Breakers - Generator breaker configuration - Synchronisation setting - Delta frequency min. | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
General timer: Settings | 47515 |  | 447516 | Parameters - Breakers - Bus tie breaker configuration - Synchronisation setting - Delta frequency min. | INT16 | X * 100 | X * 0.01 | Hz |  | X
General timer: Settings | 47515 |  | 447516 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Delta frequency min. | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
General timer: Settings | 47516 |  | 447517 | Parameters - Breakers - Generator breaker configuration - Synchronisation setting - Delta frequency max. | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
General timer: Settings | 47516 |  | 447517 | Parameters - Breakers - Bus tie breaker configuration - Synchronisation setting - Delta frequency max. | INT16 | X * 100 | X * 0.01 | Hz |  | X
General timer: Settings | 47516 |  | 447517 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Delta frequency max. | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
General timer: Settings | 47517 |  | 447518 | Parameters - Breakers - Generator breaker configuration - Synchronisation setting - Delta voltage min. | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 47517 |  | 447518 | Parameters - Breakers - Bus tie breaker configuration - Synchronisation setting - Delta voltage min. | INT16 | X * 10 | X * 0.1 | % |  | X
General timer: Settings | 47517 |  | 447518 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Delta voltage min. | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
General timer: Settings | 47518 |  | 447519 | Parameters - Breakers - Generator breaker configuration - Synchronisation setting - Delta voltage max. | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 47518 |  | 447519 | Parameters - Breakers - Bus tie breaker configuration - Synchronisation setting - Delta voltage max. | INT16 | X * 10 | X * 0.1 | % |  | X
General timer: Settings | 47518 |  | 447519 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Delta voltage max. | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
General timer: Settings | 47519 |  | 447520 | Parameters - Breakers - Generator breaker configuration - Synchronisation setting - Breaker close time | INT16 | X * 1000 | X * 0.001 | s | X |  | X | X | X
General timer: Settings | 47519 |  | 447520 | Parameters - Breakers - Bus tie breaker configuration - Synchronisation setting - Breaker close time | INT16 | X * 1000 | X * 0.001 | s |  | X
General timer: Settings | 47519 |  | 447520 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Breaker close time | INT16 | X * 1000 | X * 0.001 | s | [5 empty] | X | X
General timer: Settings | 47520 |  | 447521 | Parameters - Breakers - Generator breaker configuration - Synchronisation setting - Phase window | INT16 | X * 10 | X * 0.1 | ° | X |  | X | X | X
General timer: Settings | 47520 |  | 447521 | Parameters - Breakers - Bus tie breaker configuration - Synchronisation setting - Phase window | INT16 | X * 10 | X * 0.1 | ° |  | X
General timer: Settings | 47520 |  | 447521 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Phase window | INT16 | X * 10 | X * 0.1 | ° | [5 empty] | X | X
General timer: Settings | 47521 |  | 447522 | Parameters - Breakers - Generator breaker configuration - Synchronisation setting - Minimum time in phase window | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47521 |  | 447522 | Parameters - Breakers - Bus tie breaker configuration - Synchronisation setting - Minimum time in phase window | INT16 | X * 10 | X * 0.1 | s |  | X
General timer: Settings | 47521 |  | 447522 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Minimum time in phase window | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
General timer: Settings | 47522 |  | 447523 | Parameters - Breakers - Generator breaker configuration - Synchronisation setting - Sync type | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47522 |  | 447523 | Sync type | INT16 | X * 1 | X * 1 |  |  | X |  |  |  | X | X
General timer: Settings | 47523 |  | 447524 | Parameters - Breakers - Generator breaker configuration - Synchronisation setting - Sync behavior | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47523 |  | 447524 | Parameters - Breakers - Bus tie breaker configuration - Synchronisation setting - Sync behavior | INT16 | X * 1 | X * 1 |  |  | X
General timer: Settings | 47523 |  | 447524 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Sync behavior | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47524 |  | 447525 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Delta frequency min. | INT16 | X * 100 | X * 0.01 | Hz |  |  |  | X
General timer: Settings | 47524 |  | 447525 | Parameters - Breakers - Tie breaker configuration - Synchronisation setting - Delta frequency min. | INT16 | X * 100 | X * 0.01 | Hz | [6 empty] | X
General timer: Settings | 47525 |  | 447526 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Delta frequency max. | INT16 | X * 100 | X * 0.01 | Hz |  |  |  | X
General timer: Settings | 47525 |  | 447526 | Parameters - Breakers - Tie breaker configuration - Synchronisation setting - Delta frequency max. | INT16 | X * 100 | X * 0.01 | Hz | [6 empty] | X
General timer: Settings | 47526 |  | 447527 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Delta voltage min. | INT16 | X * 10 | X * 0.1 | % |  |  |  | X
General timer: Settings | 47526 |  | 447527 | Parameters - Breakers - Tie breaker configuration - Synchronisation setting - Delta voltage min. | INT16 | X * 10 | X * 0.1 | % | [6 empty] | X
General timer: Settings | 47527 |  | 447528 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Delta voltage max. | INT16 | X * 10 | X * 0.1 | % |  |  |  | X
General timer: Settings | 47527 |  | 447528 | Parameters - Breakers - Tie breaker configuration - Synchronisation setting - Delta voltage max. | INT16 | X * 10 | X * 0.1 | % | [6 empty] | X
General timer: Settings | 47528 |  | 447529 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Breaker close time | INT16 | X * 1000 | X * 0.001 | s |  |  |  | X
General timer: Settings | 47528 |  | 447529 | Parameters - Breakers - Tie breaker configuration - Synchronisation setting - Breaker close time | INT16 | X * 1000 | X * 0.001 | s | [6 empty] | X
General timer: Settings | 47529 |  | 447530 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Phase window | INT16 | X * 10 | X * 0.1 | ° |  |  |  | X
General timer: Settings | 47529 |  | 447530 | Parameters - Breakers - Tie breaker configuration - Synchronisation setting - Phase window | INT16 | X * 10 | X * 0.1 | ° | [6 empty] | X
General timer: Settings | 47530 |  | 447531 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Minimum time in phase window | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
General timer: Settings | 47530 |  | 447531 | Parameters - Breakers - Tie breaker configuration - Synchronisation setting - Minimum time in phase window | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
General timer: Settings | 47531 |  | 447532 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Sync type | INT16 | X * 1 | X * 1 |  |  |  |  | X
General timer: Settings | 47531 |  | 447532 | Sync type | INT16 | X * 1 | X * 1 | [7 empty] | X
General timer: Settings | 47532 |  | 447533 | Parameters - Breakers - Mains breaker configuration - Synchronisation setting - Sync behavior | INT16 | X * 1 | X * 1 |  |  |  |  | X
General timer: Settings | 47532 |  | 447533 | Parameters - Breakers - Tie breaker configuration - Synchronisation setting - Sync behavior | INT16 | X * 1 | X * 1 | [7 empty] | X
General timer: Settings | 47542 |  | 447543 | Parameters - Transducers - Transducer 1 - Synchronisation - Synchronisation setting - Delta frequency min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47543 |  | 447544 | Parameters - Transducers - Transducer 1 - Synchronisation - Synchronisation setting - Delta frequency max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47544 |  | 447545 | Parameters - Transducers - Transducer 1 - Synchronisation - Synchronisation setting - Delta voltage min. | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 47545 |  | 447546 | Parameters - Transducers - Transducer 1 - Synchronisation - Synchronisation setting - Delta voltage max. | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 47546 |  | 447547 | Parameters - Transducers - Transducer 1 - Synchronisation - Synchronisation setting - Breaker close time | INT16 | X * 1000 | X * 0.001 | s | X | X | X | X | X | X | X
General timer: Settings | 47547 |  | 447548 | Parameters - Transducers - Transducer 1 - Synchronisation - Synchronisation setting - Phase window | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47548 |  | 447549 | Parameters - Transducers - Transducer 1 - Synchronisation - Synchronisation setting - Minimum time in phase window | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47549 |  | 447550 | Parameters - Transducers - Transducer 1 - Synchronisation - Synchronisation setting - Sync type | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47550 |  | 447551 | Parameters - Transducers - Transducer 1 - Synchronisation - Synchronisation setting - Sync behavior | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47551 |  | 447552 | Parameters - Transducers - Transducer 2 - Synchronisation - Synchronisation setting - Delta frequency min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47552 |  | 447553 | Parameters - Transducers - Transducer 2 - Synchronisation - Synchronisation setting - Delta frequency max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47553 |  | 447554 | Parameters - Transducers - Transducer 2 - Synchronisation - Synchronisation setting - Delta voltage min. | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 47554 |  | 447555 | Parameters - Transducers - Transducer 2 - Synchronisation - Synchronisation setting - Delta voltage max. | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 47555 |  | 447556 | Parameters - Transducers - Transducer 2 - Synchronisation - Synchronisation setting - Breaker close time | INT16 | X * 1000 | X * 0.001 | s | X | X | X | X | X | X | X
General timer: Settings | 47556 |  | 447557 | Parameters - Transducers - Transducer 2 - Synchronisation - Synchronisation setting - Phase window | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47557 |  | 447558 | Parameters - Transducers - Transducer 2 - Synchronisation - Synchronisation setting - Minimum time in phase window | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47558 |  | 447559 | Parameters - Transducers - Transducer 2 - Synchronisation - Synchronisation setting - Sync type | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47559 |  | 447560 | Parameters - Transducers - Transducer 2 - Synchronisation - Synchronisation setting - Sync behavior | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47560 |  | 447561 | Parameters - Transducers - Transducer 3 - Synchronisation - Synchronisation setting - Delta frequency min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47561 |  | 447562 | Parameters - Transducers - Transducer 3 - Synchronisation - Synchronisation setting - Delta frequency max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47562 |  | 447563 | Parameters - Transducers - Transducer 3 - Synchronisation - Synchronisation setting - Delta voltage min. | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 47563 |  | 447564 | Parameters - Transducers - Transducer 3 - Synchronisation - Synchronisation setting - Delta voltage max. | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 47564 |  | 447565 | Parameters - Transducers - Transducer 3 - Synchronisation - Synchronisation setting - Breaker close time | INT16 | X * 1000 | X * 0.001 | s | X | X | X | X | X | X | X
General timer: Settings | 47565 |  | 447566 | Parameters - Transducers - Transducer 3 - Synchronisation - Synchronisation setting - Phase window | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47566 |  | 447567 | Parameters - Transducers - Transducer 3 - Synchronisation - Synchronisation setting - Minimum time in phase window | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47567 |  | 447568 | Parameters - Transducers - Transducer 3 - Synchronisation - Synchronisation setting - Sync type | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47568 |  | 447569 | Parameters - Transducers - Transducer 3 - Synchronisation - Synchronisation setting - Sync behavior | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47569 |  | 447570 | Parameters - Transducers - Transducer 4 - Synchronisation - Synchronisation setting - Delta frequency min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47570 |  | 447571 | Parameters - Transducers - Transducer 4 - Synchronisation - Synchronisation setting - Delta frequency max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47571 |  | 447572 | Parameters - Transducers - Transducer 4 - Synchronisation - Synchronisation setting - Delta voltage min. | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 47572 |  | 447573 | Parameters - Transducers - Transducer 4 - Synchronisation - Synchronisation setting - Delta voltage max. | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
General timer: Settings | 47573 |  | 447574 | Parameters - Transducers - Transducer 4 - Synchronisation - Synchronisation setting - Breaker close time | INT16 | X * 1000 | X * 0.001 | s | X | X | X | X | X | X | X
General timer: Settings | 47574 |  | 447575 | Parameters - Transducers - Transducer 4 - Synchronisation - Synchronisation setting - Phase window | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47575 |  | 447576 | Parameters - Transducers - Transducer 4 - Synchronisation - Synchronisation setting - Minimum time in phase window | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47576 |  | 447577 | Parameters - Transducers - Transducer 4 - Synchronisation - Synchronisation setting - Sync type | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47577 |  | 447578 | Parameters - Transducers - Transducer 4 - Synchronisation - Synchronisation setting - Sync behavior | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47578 |  | 447579 | Parameters - Local - Nominal settings - Transducer 1 nominal setting - Selection | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47579 |  | 447580 | Parameters - Local - Nominal settings - Transducer 2 nominal setting - Selection | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47580 |  | 447581 | Parameters - Local - Nominal settings - Transducer 3 nominal setting - Selection | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47581 |  | 447582 | Parameters - Local - Nominal settings - Transducer 4 nominal setting - Selection | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47582 |  | 447583 | Source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47583 |  | 447584 | Source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47584 |  | 447585 | Source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47585 |  | 447586 | Source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47586 |  | 447587 | Parameters - Transducers - Transducer 1 - Reference B - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47587 |  | 447588 | Parameters - Transducers - Transducer 1 - Reference B - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47588 |  | 447589 | Parameters - Transducers - Transducer 2 - Reference B - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47589 |  | 447590 | Parameters - Transducers - Transducer 2 - Reference B - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47590 |  | 447591 | Parameters - Transducers - Transducer 3 - Reference B - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47591 |  | 447592 | Parameters - Transducers - Transducer 3 - Reference B - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47592 |  | 447593 | Parameters - Transducers - Transducer 4 - Reference B - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47593 |  | 447594 | Parameters - Transducers - Transducer 4 - Reference B - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47594 |  | 447595 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47595 |  | 447596 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 1 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47596 |  | 447597 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 1 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47597 |  | 447598 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 1 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47598 |  | 447599 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47599 |  | 447600 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47600 |  | 447601 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47601 |  | 447602 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 1 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47602 |  | 447603 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 1 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47603 |  | 447604 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 1 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47604 |  | 447605 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 1 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47605 |  | 447606 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47606 |  | 447607 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 1 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47607 |  | 447608 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 1 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47608 |  | 447609 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 1 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47609 |  | 447610 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47610 |  | 447611 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47611 |  | 447612 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47612 |  | 447613 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 1 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47613 |  | 447614 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 1 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47614 |  | 447615 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 1 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47615 |  | 447616 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 1 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47616 |  | 447617 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47617 |  | 447618 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 1 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47618 |  | 447619 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 1 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47619 |  | 447620 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 1 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47620 |  | 447621 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47621 |  | 447622 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47622 |  | 447623 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47623 |  | 447624 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 1 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47624 |  | 447625 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 1 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47625 |  | 447626 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 1 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47626 |  | 447627 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 1 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47627 |  | 447628 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 1 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47628 |  | 447629 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 1 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47629 |  | 447630 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 1 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47630 |  | 447631 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 1 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47631 |  | 447632 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47632 |  | 447633 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47633 |  | 447634 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47634 |  | 447635 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 1 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47635 |  | 447636 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 1 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47636 |  | 447637 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 1 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47637 |  | 447638 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 1 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47638 |  | 447639 | Parameters - Transducers - Transducer 1 - 4th current input - Nominal settings - Nominal settings 1 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47639 |  | 447640 | Parameters - Transducers - Transducer 2 - 4th current input - Nominal settings - Nominal settings 1 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47640 |  | 447641 | Parameters - Transducers - Transducer 3 - 4th current input - Nominal settings - Nominal settings 1 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47641 |  | 447642 | Parameters - Transducers - Transducer 4 - 4th current input - Nominal settings - Nominal settings 1 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47642 |  | 447643 | Parameters - Transducers - Transducer 1 - Reference B - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47643 |  | 447644 | Parameters - Transducers - Transducer 1 - Reference B - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47644 |  | 447645 | Parameters - Transducers - Transducer 2 - Reference B - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47645 |  | 447646 | Parameters - Transducers - Transducer 2 - Reference B - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47646 |  | 447647 | Parameters - Transducers - Transducer 3 - Reference B - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47647 |  | 447648 | Parameters - Transducers - Transducer 3 - Reference B - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47648 |  | 447649 | Parameters - Transducers - Transducer 4 - Reference B - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47649 |  | 447650 | Parameters - Transducers - Transducer 4 - Reference B - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47650 |  | 447651 | Parameters - Transducers - Transducer 1 - Reference B - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47651 |  | 447652 | Parameters - Transducers - Transducer 1 - Reference B - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47652 |  | 447653 | Parameters - Transducers - Transducer 2 - Reference B - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47653 |  | 447654 | Parameters - Transducers - Transducer 2 - Reference B - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47654 |  | 447655 | Parameters - Transducers - Transducer 3 - Reference B - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47655 |  | 447656 | Parameters - Transducers - Transducer 3 - Reference B - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47656 |  | 447657 | Parameters - Transducers - Transducer 4 - Reference B - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47657 |  | 447658 | Parameters - Transducers - Transducer 4 - Reference B - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47658 |  | 447659 | Parameters - Transducers - Transducer 1 - Reference B - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47659 |  | 447660 | Parameters - Transducers - Transducer 1 - Reference B - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47660 |  | 447661 | Parameters - Transducers - Transducer 2 - Reference B - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47661 |  | 447662 | Parameters - Transducers - Transducer 2 - Reference B - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47662 |  | 447663 | Parameters - Transducers - Transducer 3 - Reference B - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47663 |  | 447664 | Parameters - Transducers - Transducer 3 - Reference B - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47664 |  | 447665 | Parameters - Transducers - Transducer 4 - Reference B - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47665 |  | 447666 | Parameters - Transducers - Transducer 4 - Reference B - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal value source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47666 |  | 447667 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47667 |  | 447668 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 2 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47668 |  | 447669 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 2 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47669 |  | 447670 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 2 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47670 |  | 447671 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47671 |  | 447672 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47672 |  | 447673 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47673 |  | 447674 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 2 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47674 |  | 447675 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 2 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47675 |  | 447676 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 2 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47676 |  | 447677 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 2 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47677 |  | 447678 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47678 |  | 447679 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 2 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47679 |  | 447680 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 2 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47680 |  | 447681 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 2 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47681 |  | 447682 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47682 |  | 447683 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47683 |  | 447684 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47684 |  | 447685 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 2 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47685 |  | 447686 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 2 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47686 |  | 447687 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 2 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47687 |  | 447688 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 2 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47688 |  | 447689 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47689 |  | 447690 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 2 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47690 |  | 447691 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 2 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47691 |  | 447692 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 2 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47692 |  | 447693 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47693 |  | 447694 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47694 |  | 447695 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47695 |  | 447696 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 2 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47696 |  | 447697 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 2 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47697 |  | 447698 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 2 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47698 |  | 447699 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 2 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47699 |  | 447700 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 2 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47700 |  | 447701 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 2 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47701 |  | 447702 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 2 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47702 |  | 447703 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 2 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47703 |  | 447704 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47704 |  | 447705 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47705 |  | 447706 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47706 |  | 447707 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 2 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47707 |  | 447708 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 2 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47708 |  | 447709 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 2 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47709 |  | 447710 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 2 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47710 |  | 447711 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47711 |  | 447712 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 3 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47712 |  | 447713 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 3 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47713 |  | 447714 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 3 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47714 |  | 447715 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47715 |  | 447716 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47716 |  | 447717 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47717 |  | 447718 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 3 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47718 |  | 447719 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 3 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47719 |  | 447720 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 3 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47720 |  | 447721 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 3 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47721 |  | 447722 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47722 |  | 447723 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 3 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47723 |  | 447724 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 3 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47724 |  | 447725 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 3 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47725 |  | 447726 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47726 |  | 447727 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47727 |  | 447728 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47728 |  | 447729 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 3 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47729 |  | 447730 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 3 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47730 |  | 447731 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 3 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47731 |  | 447732 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 3 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47732 |  | 447733 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47733 |  | 447734 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 3 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47734 |  | 447735 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 3 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47735 |  | 447736 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 3 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47736 |  | 447737 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47737 |  | 447738 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47738 |  | 447739 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47739 |  | 447740 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 3 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47740 |  | 447741 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 3 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47741 |  | 447742 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 3 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47742 |  | 447743 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 3 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47743 |  | 447744 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 3 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47744 |  | 447745 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 3 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47745 |  | 447746 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 3 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47746 |  | 447747 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 3 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47747 |  | 447748 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47748 |  | 447749 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47749 |  | 447750 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47750 |  | 447751 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 3 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47751 |  | 447752 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 3 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47752 |  | 447753 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 3 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47753 |  | 447754 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 3 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47754 |  | 447755 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47755 |  | 447756 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 4 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47756 |  | 447757 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 4 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47757 |  | 447758 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 4 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47758 |  | 447759 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47759 |  | 447760 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47760 |  | 447761 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47761 |  | 447762 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 4 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47762 |  | 447763 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 4 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47763 |  | 447764 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 4 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47764 |  | 447765 | Parameters - Transducers - Transducer 1 - Reference A - Nominal settings - Nominal settings 4 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47765 |  | 447766 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47766 |  | 447767 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 4 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47767 |  | 447768 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 4 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47768 |  | 447769 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 4 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47769 |  | 447770 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47770 |  | 447771 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47771 |  | 447772 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47772 |  | 447773 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 4 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47773 |  | 447774 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 4 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47774 |  | 447775 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 4 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47775 |  | 447776 | Parameters - Transducers - Transducer 2 - Reference A - Nominal settings - Nominal settings 4 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47776 |  | 447777 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47777 |  | 447778 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 4 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47778 |  | 447779 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 4 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47779 |  | 447780 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 4 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47780 |  | 447781 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47781 |  | 447782 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47782 |  | 447783 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47783 |  | 447784 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 4 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47784 |  | 447785 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 4 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47785 |  | 447786 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 4 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47786 |  | 447787 | Parameters - Transducers - Transducer 3 - Reference A - Nominal settings - Nominal settings 4 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47787 |  | 447788 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 4 - Voltage (V) - Nominal | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
General timer: Settings | 47788 |  | 447789 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 4 - Frequency (f) - Nominal | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
General timer: Settings | 47789 |  | 447790 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 4 - Current (I) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47790 |  | 447791 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 4 - Power (P) - Nominal | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47791 |  | 447792 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kW | X | X | X | X | X | X | X
General timer: Settings | 47792 |  | 447793 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kvar | X | X | X | X | X | X | X
General timer: Settings | 47793 |  | 447794 | Nominal (calculated) | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47794 |  | 447795 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 4 - Apparent power (S) - Nominal | INT16 | X * 10 | X * 0.1 | kVA | X | X | X | X | X | X | X
General timer: Settings | 47795 |  | 447796 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 4 - Power factor (PF) - Nominal | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
General timer: Settings | 47796 |  | 447797 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 4 - Calculation method - Reactive power (Q) nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47797 |  | 447798 | Parameters - Transducers - Transducer 4 - Reference A - Nominal settings - Nominal settings 4 - Calculation method - P or S nominal | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47798 |  | 447799 | Parameters - Transducers - Transducer 1 - 4th current input - Nominal settings - Nominal settings 2 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47799 |  | 447800 | Parameters - Transducers - Transducer 2 - 4th current input - Nominal settings - Nominal settings 2 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47800 |  | 447801 | Parameters - Transducers - Transducer 3 - 4th current input - Nominal settings - Nominal settings 2 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47801 |  | 447802 | Parameters - Transducers - Transducer 4 - 4th current input - Nominal settings - Nominal settings 2 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47802 |  | 447803 | Parameters - Transducers - Transducer 1 - 4th current input - Nominal settings - Nominal settings 3 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47803 |  | 447804 | Parameters - Transducers - Transducer 2 - 4th current input - Nominal settings - Nominal settings 3 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47804 |  | 447805 | Parameters - Transducers - Transducer 3 - 4th current input - Nominal settings - Nominal settings 3 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47805 |  | 447806 | Parameters - Transducers - Transducer 4 - 4th current input - Nominal settings - Nominal settings 3 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47806 |  | 447807 | Parameters - Transducers - Transducer 1 - 4th current input - Nominal settings - Nominal settings 4 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47807 |  | 447808 | Parameters - Transducers - Transducer 2 - 4th current input - Nominal settings - Nominal settings 4 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47808 |  | 447809 | Parameters - Transducers - Transducer 3 - 4th current input - Nominal settings - Nominal settings 4 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47809 |  | 447810 | Parameters - Transducers - Transducer 4 - 4th current input - Nominal settings - Nominal settings 4 - Current (I4) - Nominal | INT16 | X * 10 | X * 0.1 | A | X | X | X | X | X | X | X
General timer: Settings | 47810 |  | 447811 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy export - Pulse every | INT16 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
General timer: Settings | 47811 |  | 447812 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy export - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47812 |  | 447813 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy export - Pulse every | INT16 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
General timer: Settings | 47813 |  | 447814 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy export - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47814 |  | 447815 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy import - Pulse every | INT16 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
General timer: Settings | 47815 |  | 447816 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy import - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47816 |  | 447817 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy import - Pulse every | INT16 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
General timer: Settings | 47817 |  | 447818 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy import - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47818 |  | 447819 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy difference - Pulse every | INT16 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
General timer: Settings | 47819 |  | 447820 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Active energy difference - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47820 |  | 447821 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy difference - Pulse every | INT16 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
General timer: Settings | 47821 |  | 447822 | Parameters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy difference - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47822 |  | 447823 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy export - Pulse every | INT16 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
General timer: Settings | 47823 |  | 447824 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy export - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47824 |  | 447825 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy export - Pulse every | INT16 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
General timer: Settings | 47825 |  | 447826 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy export - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47826 |  | 447827 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy import - Pulse every | INT16 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
General timer: Settings | 47827 |  | 447828 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy import - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47828 |  | 447829 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy import - Pulse every | INT16 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
General timer: Settings | 47829 |  | 447830 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy import - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47830 |  | 447831 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy difference - Pulse every | INT16 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
General timer: Settings | 47831 |  | 447832 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Active energy difference - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47832 |  | 447833 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy difference - Pulse every | INT16 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
General timer: Settings | 47833 |  | 447834 | Parameters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy difference - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47834 |  | 447835 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy export - Pulse every | INT16 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
General timer: Settings | 47835 |  | 447836 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy export - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47836 |  | 447837 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy export - Pulse every | INT16 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
General timer: Settings | 47837 |  | 447838 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy export - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47838 |  | 447839 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy import - Pulse every | INT16 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
General timer: Settings | 47839 |  | 447840 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy import - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47840 |  | 447841 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy import - Pulse every | INT16 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
General timer: Settings | 47841 |  | 447842 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy import - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47842 |  | 447843 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy difference - Pulse every | INT16 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
General timer: Settings | 47843 |  | 447844 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Active energy difference - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47844 |  | 447845 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy difference - Pulse every | INT16 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
General timer: Settings | 47845 |  | 447846 | Parameters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy difference - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47846 |  | 447847 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy export - Pulse every | INT16 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
General timer: Settings | 47847 |  | 447848 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy export - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47848 |  | 447849 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy export - Pulse every | INT16 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
General timer: Settings | 47849 |  | 447850 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy export - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47850 |  | 447851 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy import - Pulse every | INT16 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
General timer: Settings | 47851 |  | 447852 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy import - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47852 |  | 447853 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy import - Pulse every | INT16 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
General timer: Settings | 47853 |  | 447854 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy import - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47854 |  | 447855 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy difference - Pulse every | INT16 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
General timer: Settings | 47855 |  | 447856 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Active energy difference - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47856 |  | 447857 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy difference - Pulse every | INT16 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
General timer: Settings | 47857 |  | 447858 | Parameters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy difference - Pulse length - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47858 |  | 447859 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Voltage transformer - Primary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47859 |  | 447860 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Voltage transformer - Secondary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47860 |  | 447861 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Voltage transformer - Primary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47861 |  | 447862 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Voltage transformer - Secondary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47862 |  | 447863 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Voltage transformer - Primary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47863 |  | 447864 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Voltage transformer - Secondary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47864 |  | 447865 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Voltage transformer - Primary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47865 |  | 447866 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Voltage transformer - Secondary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47866 |  | 447867 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Voltage transformer - Primary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47867 |  | 447868 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Voltage transformer - Secondary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47868 |  | 447869 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Current transformer - Primary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47869 |  | 447870 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Current transformer - Secondary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47870 |  | 447871 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Voltage transformer - Primary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47871 |  | 447872 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Voltage transformer - Secondary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47872 |  | 447873 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Current transformer - Primary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47873 |  | 447874 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Current transformer - Secondary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47874 |  | 447875 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Voltage transformer - Primary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47875 |  | 447876 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Voltage transformer - Secondary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47876 |  | 447877 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Current transformer - Primary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47877 |  | 447878 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Current transformer - Secondary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47878 |  | 447879 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Voltage transformer - Primary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47879 |  | 447880 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Voltage transformer - Secondary | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
General timer: Settings | 47880 |  | 447881 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Current transformer - Primary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47881 |  | 447882 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Current transformer - Secondary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47882 |  | 447883 | Parameters - Transducers - Transducer 1 - 4th current input - Current transformer (I4) - Primary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47883 |  | 447884 | Parameters - Transducers - Transducer 1 - 4th current input - Current transformer (I4) - Secondary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47884 |  | 447885 | Parameters - Transducers - Transducer 2 - 4th current input - Current transformer (I4) - Primary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47885 |  | 447886 | Parameters - Transducers - Transducer 2 - 4th current input - Current transformer (I4) - Secondary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47886 |  | 447887 | Parameters - Transducers - Transducer 3 - 4th current input - Current transformer (I4) - Primary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47887 |  | 447888 | Parameters - Transducers - Transducer 3 - 4th current input - Current transformer (I4) - Secondary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47888 |  | 447889 | Parameters - Transducers - Transducer 4 - 4th current input - Current transformer (I4) - Primary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47889 |  | 447890 | Parameters - Transducers - Transducer 4 - 4th current input - Current transformer (I4) - Secondary | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
General timer: Settings | 47890 |  | 447891 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Voltage and frequency OK - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47891 |  | 447892 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Voltage and frequency OK - Minimum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47892 |  | 447893 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Voltage and frequency OK - Maximum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47893 |  | 447894 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Voltage and frequency OK - Minimum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47894 |  | 447895 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Voltage and frequency OK - Maximum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47895 |  | 447896 | Maximum voltage balance deviation | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47896 |  | 447897 | Maximum phase deviation | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47897 |  | 447898 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Detection voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47898 |  | 447899 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Blackout detection - Blackout delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47899 |  | 447900 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Voltage and frequency OK - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47900 |  | 447901 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Voltage and frequency OK - Minimum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47901 |  | 447902 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Voltage and frequency OK - Maximum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47902 |  | 447903 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Voltage and frequency OK - Minimum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47903 |  | 447904 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Voltage and frequency OK - Maximum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47904 |  | 447905 | Maximum voltage balance deviation | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47905 |  | 447906 | Maximum phase deviation | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47906 |  | 447907 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Detection voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47907 |  | 447908 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Blackout detection - Blackout delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47908 |  | 447909 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Voltage and frequency OK - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47909 |  | 447910 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Voltage and frequency OK - Minimum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47910 |  | 447911 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Voltage and frequency OK - Maximum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47911 |  | 447912 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Voltage and frequency OK - Minimum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47912 |  | 447913 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Voltage and frequency OK - Maximum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47913 |  | 447914 | Maximum voltage balance deviation | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47914 |  | 447915 | Maximum phase deviation | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47915 |  | 447916 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Detection voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47916 |  | 447917 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Blackout detection - Blackout delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47917 |  | 447918 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Voltage and frequency OK - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47918 |  | 447919 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Voltage and frequency OK - Minimum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47919 |  | 447920 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Voltage and frequency OK - Maximum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47920 |  | 447921 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Voltage and frequency OK - Minimum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47921 |  | 447922 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Voltage and frequency OK - Maximum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47922 |  | 447923 | Maximum voltage balance deviation | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47923 |  | 447924 | Maximum phase deviation | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47924 |  | 447925 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Detection voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47925 |  | 447926 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Blackout detection - Blackout delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47926 |  | 447927 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Voltage and frequency OK - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47927 |  | 447928 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Voltage and frequency OK - Minimum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47928 |  | 447929 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Voltage and frequency OK - Maximum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47929 |  | 447930 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Voltage and frequency OK - Minimum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47930 |  | 447931 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Voltage and frequency OK - Maximum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47931 |  | 447932 | Maximum voltage balance deviation | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47932 |  | 447933 | Maximum phase deviation | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47933 |  | 447934 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Detection voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47934 |  | 447935 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Blackout detection - Blackout delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47935 |  | 447936 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Voltage and frequency OK - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47936 |  | 447937 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Voltage and frequency OK - Minimum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47937 |  | 447938 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Voltage and frequency OK - Maximum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47938 |  | 447939 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Voltage and frequency OK - Minimum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47939 |  | 447940 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Voltage and frequency OK - Maximum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47940 |  | 447941 | Maximum voltage balance deviation | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47941 |  | 447942 | Maximum phase deviation | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47942 |  | 447943 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Detection voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47943 |  | 447944 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Blackout detection - Blackout delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47944 |  | 447945 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Voltage and frequency OK - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47945 |  | 447946 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Voltage and frequency OK - Minimum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47946 |  | 447947 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Voltage and frequency OK - Maximum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47947 |  | 447948 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Voltage and frequency OK - Minimum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47948 |  | 447949 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Voltage and frequency OK - Maximum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47949 |  | 447950 | Maximum voltage balance deviation | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47950 |  | 447951 | Maximum phase deviation | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47951 |  | 447952 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Detection voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47952 |  | 447953 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Blackout detection - Blackout delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47953 |  | 447954 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Voltage and frequency OK - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47954 |  | 447955 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Voltage and frequency OK - Minimum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47955 |  | 447956 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Voltage and frequency OK - Maximum OK voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47956 |  | 447957 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Voltage and frequency OK - Minimum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47957 |  | 447958 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Voltage and frequency OK - Maximum OK frequency | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
General timer: Settings | 47958 |  | 447959 | Maximum voltage balance deviation | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47959 |  | 447960 | Maximum phase deviation | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
General timer: Settings | 47960 |  | 447961 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Detection voltage | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
General timer: Settings | 47961 |  | 447962 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Blackout detection - Blackout delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X | X | X | X | X | X | X
General timer: Settings | 47962 |  | 447963 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase configuration - AC configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47963 |  | 447964 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase direction | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47964 |  | 447965 | AC phase rotation | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47965 |  | 447966 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase configuration - AC configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47966 |  | 447967 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase direction | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47967 |  | 447968 | AC phase rotation | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47968 |  | 447969 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase configuration - AC configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47969 |  | 447970 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase direction | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47970 |  | 447971 | AC phase rotation | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47971 |  | 447972 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase configuration - AC configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47972 |  | 447973 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase direction | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47973 |  | 447974 | AC phase rotation | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47974 |  | 447975 | Source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47975 |  | 447976 | Source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47976 |  | 447977 | Source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47977 |  | 447978 | Source | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47978 |  | 447979 | Parameters - Local - Mode - Command mode - Selected mode | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47979 |  | 447980 | Parameters - Local - Mode - Command mode - Boot mode | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47980 |  | 447981 | Parameters - Breakers - Short-time parallel - Configuration - Maximum overlap time | INT16 | X * 100 | X * 0.01 | s | X |  | X | X | X | X | X
General timer: Settings | 47981 |  | 447982 | Parameters - Breakers - Close before excitation - Configuration - Enable | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
General timer: Settings | 47982 |  | 447983 | Parameters - Regulators - GOV - Regulation set points - Base load | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47983 |  | 447984 | Parameters - Regulators - GOV - Regulation set points - Base load - Set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47984 |  | 447985 | Parameters - Power management rules - Asymmetric load sharing - Start when an asymmetric set point is exceeded - Enable | INT16 | X * 1 | X * 1 |  | X | X | X | X | X
General timer: Settings | 47985 |  | 447986 | Parameters - Power management rules - Asymmetric load sharing - Start when an asymmetric set point is exceeded - Set point | INT16 | X * 1 | X * 1 | % | X | X | X | X | X
General timer: Settings | 47986 |  | 447987 | Parameters - Local power management - Genset test - Settings - Type | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47986 |  | 447987 | Parameters - Power management rules - Mains power - Mains test - Type | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47987 |  | 447988 | Parameters - Local power management - Genset test - Settings - Base load | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 47987 |  | 447988 | Parameters - Power management rules - Mains power - Mains test - Base load | INT16 | X * 1 | X * 1 | % | [5 empty] | X | X
General timer: Settings | 47988 |  | 447989 | Parameters - Local power management - Genset test - Settings - Mode | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47988 |  | 447989 | Parameters - Power management rules - Mains power - Mains test - Mode | INT16 | X * 1 | X * 1 | [6 empty] | X | X
General timer: Settings | 47989 |  | 447990 | Parameters - Local power management - Genset test - Settings - Test time - Configuration | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General timer: Settings | 47989 |  | 447990 | Parameters - Power management rules - Mains power - Mains test - Test time - Configuration | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X
General timer: Settings | 47990 |  | 447991 | Parameters - Power management rules - Mains power - Peak shaving - Stop delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 47991 |  | 447992 | Parameters - Power management rules - Load-dependent start/stop - Start 2 - Enable | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47992 |  | 447993 | Parameters - Power management rules - Load-dependent start/stop - Stop 2 - Enable | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47993 |  | 447994 | Parameters - Power management rules - Power reservation - Reserved power - Enable | INT16 | X * 1 | X * 1 |  | X | X | X | X | X
General timer: Settings | 47994 |  | 447995 | Parameters - Engine - ECU - Controls - Speed control (TSC1 / Custom) - Destination address | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47995 |  | 447996 | Parameters - System - Application selector | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
General timer: Settings | 47996 |  | 447997 | Parameters - Engine - ECU diagnostic - Enable | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47997 |  | 447998 | Parameters - Engine - ECU diagnostic - Use timer | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 47998 |  | 447999 | Parameters - Engine - ECU diagnostic - Time to enable function - Configuration | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
General timer: Settings | 47999 |  | 448000 | Parameters - Engine - ECU diagnostic - Mode | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 48000 |  | 448001 | Parameters - Auxiliary - Pump logic 1 - Pump logic settings - Pump ON delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 48001 |  | 448002 | Parameters - Auxiliary - Pump logic 1 - Fill check slope | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 48002 |  | 448003 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump ON set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 48003 |  | 448004 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump OFF set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 48004 |  | 448005 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump ON delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 48005 |  | 448006 | Parameters - Auxiliary - Pump logic 2 - Pump logic settings - Pump OFF delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 48006 |  | 448007 | Parameters - Auxiliary - Pump logic 2 - Source selection - Pump source select | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 48007 |  | 448008 | Parameters - Auxiliary - Pump logic 2 - Fill check slope | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 48008 |  | 448009 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump ON set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 48009 |  | 448010 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump OFF set point | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
General timer: Settings | 48010 |  | 448011 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump ON delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 48011 |  | 448012 | Parameters - Auxiliary - Pump logic 3 - Pump logic settings - Pump OFF delay - Configuration | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
General timer: Settings | 48012 |  | 448013 | Parameters - Auxiliary - Pump logic 3 - Source selection - Pump source select | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
General timer: Settings | 48013 |  | 448014 | Parameters - Auxiliary - Pump logic 3 - Fill check slope | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
General timer: Settings | 48014 |  | 448015 | Parameters - Grid code - Frequency offset - Frequency offset source | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48015 |  | 448016 | Parameters - Grid code - Frequency offset - Frequency offset enable | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48016 |  | 448017 | Parameters - Grid code - RRCR - RRCR inputs enable | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48017 |  | 448018 | Parameters - Grid code - RRCR - RRCR outputs enable | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48020 |  | 448021 | Parameters - Grid code - Droop curve 1 - Droop curve 1 enable | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48030 |  | 448031 | Parameters - Grid code - Droop curve 1 - Dependency | INT16 | X * 10 | X * 0.1 |  |  |  | X | X
General timer: Settings | 48046 |  | 448047 | Parameters - Grid code - Feedforward - FeedForwardVolt_KFF | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48047 |  | 448048 | Parameters - Grid code - Feedforward - FeedForwardVolt_Ena | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48048 |  | 448049 | Parameters - Grid code - Feedforward - FeedForwardFreq_KFF | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48049 |  | 448050 | Parameters - Grid code - Feedforward - FeedForwardFreq_Ena | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48050 |  | 448051 | Parameters - Regulators - AVR - Regulation set points - Reactive power operation ramp - Enable ramping | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48051 |  | 448052 | Parameters - Regulators - GOV - Regulation set points - Active power ramp configuration - Enable operation ramp 2 | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48052 |  | 448053 | Parameters - Regulators - GOV - Regulation set points - Active power ramp configuration - Enable operation ramp 3 | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48053 |  | 448054 | Parameters - Regulators - GOV - Regulation set points - Active power ramp configuration - Enable operation ramp 4 | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48054 |  | 448055 | Parameters - Regulators - AVR - Regulation set points - Reactive power operation ramp - Time constant | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48055 |  | 448056 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48056 |  | 448057 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48057 |  | 448058 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48058 |  | 448059 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48059 |  | 448060 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48060 |  | 448061 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48061 |  | 448062 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48062 |  | 448063 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48063 |  | 448064 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48064 |  | 448065 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48065 |  | 448066 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48066 |  | 448067 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48067 |  | 448068 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48068 |  | 448069 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48069 |  | 448070 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48070 |  | 448071 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48071 |  | 448072 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48072 |  | 448073 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48073 |  | 448074 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48074 |  | 448075 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48075 |  | 448076 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48076 |  | 448077 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48077 |  | 448078 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48078 |  | 448079 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48079 |  | 448080 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48080 |  | 448081 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48081 |  | 448082 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48082 |  | 448083 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48083 |  | 448084 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48084 |  | 448085 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48085 |  | 448086 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48086 |  | 448087 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48087 |  | 448088 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48088 |  | 448089 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48089 |  | 448090 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48090 |  | 448091 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48091 |  | 448092 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48092 |  | 448093 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48093 |  | 448094 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48094 |  | 448095 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48095 |  | 448096 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48096 |  | 448097 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 2 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48097 |  | 448098 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48098 |  | 448099 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48099 |  | 448100 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48100 |  | 448101 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48101 |  | 448102 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48102 |  | 448103 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48103 |  | 448104 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48104 |  | 448105 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48105 |  | 448106 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48106 |  | 448107 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48107 |  | 448108 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48108 |  | 448109 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48109 |  | 448110 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48110 |  | 448111 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48111 |  | 448112 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48112 |  | 448113 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48113 |  | 448114 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48114 |  | 448115 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48115 |  | 448116 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48116 |  | 448117 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48117 |  | 448118 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48118 |  | 448119 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48119 |  | 448120 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48120 |  | 448121 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48121 |  | 448122 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48122 |  | 448123 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48123 |  | 448124 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48124 |  | 448125 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48125 |  | 448126 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48126 |  | 448127 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48127 |  | 448128 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48128 |  | 448129 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48129 |  | 448130 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48130 |  | 448131 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48131 |  | 448132 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48132 |  | 448133 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48133 |  | 448134 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48134 |  | 448135 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48135 |  | 448136 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48136 |  | 448137 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48137 |  | 448138 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48138 |  | 448139 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 3 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48139 |  | 448140 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48140 |  | 448141 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48141 |  | 448142 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48142 |  | 448143 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48143 |  | 448144 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48144 |  | 448145 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48145 |  | 448146 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48146 |  | 448147 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48147 |  | 448148 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48148 |  | 448149 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48149 |  | 448150 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48150 |  | 448151 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48151 |  | 448152 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48152 |  | 448153 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48153 |  | 448154 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48154 |  | 448155 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48155 |  | 448156 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48156 |  | 448157 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48157 |  | 448158 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48158 |  | 448159 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48159 |  | 448160 | Parameters - Regulators - GOV - Regulation set points - Active power ramp up - Operation ramp up 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48160 |  | 448161 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48161 |  | 448162 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48162 |  | 448163 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48163 |  | 448164 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48164 |  | 448165 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48165 |  | 448166 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48166 |  | 448167 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48167 |  | 448168 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48168 |  | 448169 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48169 |  | 448170 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48170 |  | 448171 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48171 |  | 448172 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48172 |  | 448173 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48173 |  | 448174 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48174 |  | 448175 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48175 |  | 448176 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48176 |  | 448177 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48177 |  | 448178 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48178 |  | 448179 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48179 |  | 448180 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48180 |  | 448181 | Parameters - Regulators - GOV - Regulation set points - Active power ramp down - Operation ramp down 4 | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48188 |  | 448189 | Parameters - Grid code - var(Q) regulation - Configuration - Type selection | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48189 |  | 448190 | Parameters - Grid code - var(Q) regulation - Configuration - Ramp switch timer | INT16 | X * 1 | X * 1 | s |  |  | X | X
General timer: Settings | 48190 |  | 448191 | Parameters - Grid code - var(Q) regulation - Configuration - Limit Q under-excited | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48191 |  | 448192 | Parameters - Grid code - var(Q) regulation - Configuration - Limit Q over-excited | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48192 |  | 448193 | Parameters - Grid code - var(Q) regulation - Variant A: Q(U) U-shift - Voltage deadband | INT16 | X * 100 | X * 0.01 | % |  |  | X | X
General timer: Settings | 48193 |  | 448194 | Parameters - Grid code - var(Q) regulation - Variant A: Q(U) U-shift - Reference voltage at Q=0 | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48194 |  | 448195 | Parameters - Grid code - var(Q) regulation - Variant A: Q(U) U-shift - Maximum voltage at Q max | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48195 |  | 448196 | Parameters - Grid code - var(Q) regulation - Variant A: Q(U) U-shift - Maximum Q during over-voltage | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48196 |  | 448197 | Parameters - Grid code - var(Q) regulation - Variant A: Q(U) U-shift - Minimum Q during under-voltage | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48197 |  | 448198 | Parameters - Grid code - var(Q) regulation - Variant A: Q(U) U-shift - Reference voltage offset value | INT16 | X * 1000 | X * 0.001 |  |  |  | X | X
General timer: Settings | 48198 |  | 448199 | Parameters - Grid code - var(Q) regulation - Variant A: Q(U) U-shift - External control | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48199 |  | 448200 | Parameters - Grid code - var(Q) regulation - Variant C: Q(U) Q-shift - Q/Pnom offset | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48200 |  | 448201 | Parameters - Grid code - var(Q) regulation - Variant C: Q(U) Q-shift - External control | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48201 |  | 448202 | Parameters - Grid code - var(Q) regulation - Variant D: Cos phi fixed - Cos phi set point | INT16 | X * 1000 | X * 0.001 |  |  |  | X | X
General timer: Settings | 48202 |  | 448203 | Parameters - Grid code - var(Q) regulation - Variant D: Cos phi fixed - Cos phi direction | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48203 |  | 448204 | Parameters - Grid code - var(Q) regulation - Variant D: Cos phi fixed - Cos phi offset | INT16 | X * 1000 | X * 0.001 |  |  |  | X | X
General timer: Settings | 48204 |  | 448205 | Parameters - Grid code - var(Q) regulation - Variant D: Cos phi fixed - External control | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48205 |  | 448206 | Parameters - Grid code - var(Q) regulation - Variant E: Q fixed - Q set point | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48206 |  | 448207 | Parameters - Grid code - Mains sync inhibit - Voltage low limit | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48207 |  | 448208 | Parameters - Grid code - Mains sync inhibit - Voltage high limit | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48208 |  | 448209 | Parameters - Grid code - Mains sync inhibit - Frequency low limit | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48209 |  | 448210 | Parameters - Grid code - Mains sync inhibit - Frequency high limit | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48210 |  | 448211 | Parameters - Grid code - Mains sync inhibit - Recovery delay select | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48211 |  | 448212 | Parameters - Grid code - Mains sync inhibit - Recovery delay select time - Configuration | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48212 |  | 448213 | Parameters - Grid code - Mains sync inhibit - Recovery delay 1 | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48213 |  | 448214 | Parameters - Grid code - Mains sync inhibit - Recovery delay 1 time - Configuration | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48214 |  | 448215 | Parameters - Grid code - Mains sync inhibit - Recovery delay 2 | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48215 |  | 448216 | Parameters - Grid code - Mains sync inhibit - Recovery delay 2 time - Configuration | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48216 |  | 448217 | Parameters - Grid code - Droop curve 1 - Calculation method | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48217 |  | 448218 | Parameters - Grid code - Droop curve 1 - Slope calculation method | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48218 |  | 448219 | Parameters - Grid code - Droop curve 1 - Slope low percentage | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48219 |  | 448220 | Parameters - Grid code - Droop curve 1 - Slope high percentage | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48220 |  | 448221 | Parameters - Grid code - Droop curve 1 - Slope low absolute | INT16 | X * 1 | X * 1 | kW |  |  | X | X
General timer: Settings | 48221 |  | 448222 | Parameters - Grid code - Droop curve 1 - Slope high absolute | INT16 | X * 1 | X * 1 | kW |  |  | X | X
General timer: Settings | 48222 |  | 448223 | Parameters - Grid code - Droop curve 1 - Minimum active power | INT16 | X * 1 | X * 1 | kW |  |  | X | X
General timer: Settings | 48223 |  | 448224 | Parameters - Grid code - Droop curve 1 - Maximum active power | INT16 | X * 1 | X * 1 | kW |  |  | X | X
General timer: Settings | 48224 |  | 448225 | Parameters - Grid code - Droop curve 1 - Deadband low | INT16 | X * 100 | X * 0.01 | % |  |  | X | X
General timer: Settings | 48225 |  | 448226 | Parameters - Grid code - Droop curve 1 - Deadband high | INT16 | X * 100 | X * 0.01 | % |  |  | X | X
General timer: Settings | 48226 |  | 448227 | Parameters - Grid code - Droop curve 1 - Hysteresis low | INT16 | X * 100 | X * 0.01 | % |  |  | X | X
General timer: Settings | 48227 |  | 448228 | Parameters - Grid code - Droop curve 1 - Hysteresis high | INT16 | X * 100 | X * 0.01 | % |  |  | X | X
General timer: Settings | 48228 |  | 448229 | Parameters - Grid code - Droop curve 1 - Recovery delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
General timer: Settings | 48229 |  | 448230 | Parameters - Grid code - Droop curve 1 - Ramp 3 activation delay | INT16 | X * 10 | X * 0.1 | s |  |  | X | X
General timer: Settings | 48230 |  | 448231 | Parameters - Grid code - Droop curve 2 - Droop curve 2 enable | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48231 |  | 448232 | Parameters - Grid code - Droop curve 2 - Curve output | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48232 |  | 448233 | Parameters - Grid code - Droop curve 2 - Dependency | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48233 |  | 448234 | Parameters - Grid code - Droop curve 2 - Cos phi slope low | INT16 | X * 1000 | X * 0.001 |  |  |  | X | X
General timer: Settings | 48234 |  | 448235 | Parameters - Grid code - Droop curve 2 - Cos phi slope high | INT16 | X * 1000 | X * 0.001 |  |  |  | X | X
General timer: Settings | 48235 |  | 448236 | Parameters - Grid code - Droop curve 2 - Cos phi minimum | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48236 |  | 448237 | Parameters - Grid code - Droop curve 2 - Cos phi minimum direction | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48237 |  | 448238 | Parameters - Grid code - Droop curve 2 - Cos phi maximum | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48238 |  | 448239 | Parameters - Grid code - Droop curve 2 - Cos phi maximum direction | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48239 |  | 448240 | Parameters - Grid code - Droop curve 2 - Reactive power slope low | INT16 | X * 1 | X * 1 | kvar |  |  | X | X
General timer: Settings | 48240 |  | 448241 | Parameters - Grid code - Droop curve 2 - Reactive power slope high | INT16 | X * 1 | X * 1 | kvar |  |  | X | X
General timer: Settings | 48241 |  | 448242 | Parameters - Grid code - Droop curve 2 - Reactive power minimum | INT16 | X * 1 | X * 1 | kvar |  |  | X | X
General timer: Settings | 48242 |  | 448243 | Parameters - Grid code - Droop curve 2 - Reactive power maximum | INT16 | X * 1 | X * 1 | kvar |  |  | X | X
General timer: Settings | 48243 |  | 448244 | Parameters - Grid code - Droop curve 2 - Deadband low | INT16 | X * 100 | X * 0.01 | % |  |  | X | X
General timer: Settings | 48244 |  | 448245 | Parameters - Grid code - Droop curve 2 - Deadband high | INT16 | X * 100 | X * 0.01 | % |  |  | X | X
General timer: Settings | 48245 |  | 448246 | Parameters - Grid code - Droop curve 2 - Hysteresis low | INT16 | X * 100 | X * 0.01 | % |  |  | X | X
General timer: Settings | 48246 |  | 448247 | Parameters - Grid code - Droop curve 2 - Hysteresis high | INT16 | X * 100 | X * 0.01 | % |  |  | X | X
General timer: Settings | 48247 |  | 448248 | Parameters - Grid code - Capability curve - Config - AVR limiting set point | INT16 | X * 1 | X * 1 | % |  |  | X | X
General timer: Settings | 48248 |  | 448249 | Parameters - Regulators - AVR - General configuration - Limiting type - AVR limiting type | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48249 |  | 448250 | Parameters - Grid code - Capability curve - Config - y-axis select | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48250 |  | 448251 | Parameters - Grid code - Capability curve - Import graph - Capability curve import | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48251 |  | 448252 | Parameters - Grid code - Capability curve - Import graph - Capability curve import | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48252 |  | 448253 | Parameters - Grid code - Capability curve - Import graph - Capability curve import | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48253 |  | 448254 | Parameters - Grid code - Capability curve - Import graph - Capability curve import | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48254 |  | 448255 | Parameters - Grid code - Capability curve - Import graph - Capability curve import | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48255 |  | 448256 | Parameters - Grid code - Capability curve - Import graph - Capability curve import | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48256 |  | 448257 | Parameters - Grid code - Capability curve - Import graph - Capability curve import | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48257 |  | 448258 | Parameters - Grid code - Capability curve - Import graph - Capability curve import | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48258 |  | 448259 | Parameters - Grid code - Capability curve - Import graph - Capability curve import | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48259 |  | 448260 | Parameters - Grid code - Capability curve - Import graph - Capability curve import | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48260 |  | 448261 | Parameters - Grid code - Capability curve - Import graph - Capability curve import | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48261 |  | 448262 | Parameters - Grid code - Capability curve - Import graph - Capability curve import | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48262 |  | 448263 | Parameters - Grid code - Capability curve - Import graph - Capability curve import | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48263 |  | 448264 | Parameters - Grid code - Capability curve - Export graph - Capability curve export | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48264 |  | 448265 | Parameters - Grid code - Capability curve - Export graph - Capability curve export | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48265 |  | 448266 | Parameters - Grid code - Capability curve - Export graph - Capability curve export | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48266 |  | 448267 | Parameters - Grid code - Capability curve - Export graph - Capability curve export | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48267 |  | 448268 | Parameters - Grid code - Capability curve - Export graph - Capability curve export | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48268 |  | 448269 | Parameters - Grid code - Capability curve - Export graph - Capability curve export | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48269 |  | 448270 | Parameters - Grid code - Capability curve - Export graph - Capability curve export | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48270 |  | 448271 | Parameters - Grid code - Capability curve - Export graph - Capability curve export | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48271 |  | 448272 | Parameters - Grid code - Capability curve - Export graph - Capability curve export | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48272 |  | 448273 | Parameters - Grid code - Capability curve - Export graph - Capability curve export | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48273 |  | 448274 | Parameters - Grid code - Capability curve - Export graph - Capability curve export | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48274 |  | 448275 | Parameters - Grid code - Capability curve - Export graph - Capability curve export | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48275 |  | 448276 | Parameters - Grid code - Capability curve - Export graph - Capability curve export | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48276 |  | 448277 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48277 |  | 448278 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48278 |  | 448279 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48279 |  | 448280 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48280 |  | 448281 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48281 |  | 448282 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48282 |  | 448283 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48283 |  | 448284 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48284 |  | 448285 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48285 |  | 448286 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48286 |  | 448287 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48287 |  | 448288 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48288 |  | 448289 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48289 |  | 448290 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48290 |  | 448291 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48291 |  | 448292 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48292 |  | 448293 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48293 |  | 448294 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48294 |  | 448295 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48295 |  | 448296 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
General timer: Settings | 48296 |  | 448297 | Parameters - Grid code - var(Q) regulation - Variant B: Q(P) curve - Q(P) curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48297 |  | 448298 | Parameters - Grid code - var(Q) regulation - Variant C: Q(U) Q-shift - Q(U) Q-shift curve | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48298 |  | 448299 | Parameters - Grid code - var(Q) regulation - Variant C: Q(U) Q-shift - Q(U) Q-shift curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48299 |  | 448300 | Parameters - Grid code - var(Q) regulation - Variant C: Q(U) Q-shift - Q(U) Q-shift curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48300 |  | 448301 | Parameters - Grid code - var(Q) regulation - Variant C: Q(U) Q-shift - Q(U) Q-shift curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48301 |  | 448302 | Parameters - Grid code - var(Q) regulation - Variant C: Q(U) Q-shift - Q(U) Q-shift curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48302 |  | 448303 | Parameters - Grid code - var(Q) regulation - Variant C: Q(U) Q-shift - Q(U) Q-shift curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48303 |  | 448304 | Parameters - Grid code - var(Q) regulation - Variant C: Q(U) Q-shift - Q(U) Q-shift curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48304 |  | 448305 | Parameters - Grid code - var(Q) regulation - Variant C: Q(U) Q-shift - Q(U) Q-shift curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48305 |  | 448306 | Parameters - Grid code - var(Q) regulation - Variant C: Q(U) Q-shift - Q(U) Q-shift curve | INT16 | X * 100 | X * 0.01 |  |  |  | X | X
General timer: Settings | 48306 |  | 448307 | Parameters - Mains - AC setup - Connection point voltage measurement - Source | INT16 | X * 1 | X * 1 |  |  |  | X | X
General timer: Settings | 48307 |  | 448308 | Parameters - Mains - AC setup - Connection point voltage measurement - Nominal | INT16 | X * 10 | X * 0.1 | V |  |  | X | X

## Input register (04)
Input register (04)
Function group | Modbus address | Bit | PLC address | Controller function name | Data type | Output conversion | Input conversion | Unit | LC_GENSET_GB | LC_BUSTIE_BTB | LC_SINGLE_GENSET_GB | LC_SINGLE_GENSET_GB_MB | LC_SINGLE_GENSET_GB_NO_MAINS | LC_MAINS_MB | LC_MAINS_MB_TB
[Controlled equipment] ACM measurements | 1000 |  | 301001 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ L1-N | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1000 |  | 301001 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ L1-N | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1000 |  | 301001 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L1-N | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1001 |  | 301002 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ L2-N | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1001 |  | 301002 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ L2-N | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1001 |  | 301002 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L2-N | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1002 |  | 301003 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ L3-N | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1002 |  | 301003 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ L3-N | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1002 |  | 301003 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L3-N | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1003 |  | 301004 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ N | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1003 |  | 301004 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ N | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1003 |  | 301004 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ N | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1004 |  | 301005 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ L-N min. | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1004 |  | 301005 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ L-N min. | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1004 |  | 301005 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L-N min. | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1005 |  | 301006 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ L-N max. | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1005 |  | 301006 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ L-N max. | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1005 |  | 301006 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L-N max. | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1006 |  | 301007 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ L-N unbalanced | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1006 |  | 301007 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ L-N unbalanced | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1006 |  | 301007 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L-N unbalanced | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1007 |  | 301008 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ L1-L2 | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1007 |  | 301008 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ L1-L2 | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1007 |  | 301008 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L1-L2 | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1008 |  | 301009 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ L2-L3 | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1008 |  | 301009 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ L2-L3 | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1008 |  | 301009 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L2-L3 | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1009 |  | 301010 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ L3-L1 | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1009 |  | 301010 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ L3-L1 | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1009 |  | 301010 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L3-L1 | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1010 |  | 301011 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ L-L min. | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1010 |  | 301011 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ L-L min. | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1010 |  | 301011 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L-L min. | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1011 |  | 301012 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ L-L max. | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1011 |  | 301012 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ L-L max. | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1011 |  | 301012 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L-L max. | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1012 |  | 301013 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ L-L unbalanced | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1012 |  | 301013 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ L-L unbalanced | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1012 |  | 301013 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L-L unbalanced | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1013 |  | 301014 | Functions - Analogue output functions - Generator - Frequency (f) (from voltage) - Generator ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
[Controlled equipment] ACM measurements | 1013 |  | 301014 | Functions - Analogue output functions - Busbar A - Frequency (f) (from voltage) - Busbar A ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Controlled equipment] ACM measurements | 1013 |  | 301014 | Functions - Analogue output functions - Mains - Frequency (f) (from voltage) - Mains ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1014 |  | 301015 | Functions - Analogue output functions - Generator - Frequency (f) (from voltage) - Generator ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
[Controlled equipment] ACM measurements | 1014 |  | 301015 | Functions - Analogue output functions - Busbar A - Frequency (f) (from voltage) - Busbar A ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Controlled equipment] ACM measurements | 1014 |  | 301015 | Functions - Analogue output functions - Mains - Frequency (f) (from voltage) - Mains ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1015 |  | 301016 | Functions - Analogue output functions - Generator - Frequency (f) (from voltage) - Generator ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
[Controlled equipment] ACM measurements | 1015 |  | 301016 | Functions - Analogue output functions - Busbar A - Frequency (f) (from voltage) - Busbar A ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Controlled equipment] ACM measurements | 1015 |  | 301016 | Functions - Analogue output functions - Mains - Frequency (f) (from voltage) - Mains ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1016 |  | 301017 | Functions - Analogue output functions - Generator - Frequency (f) (from voltage) - Generator ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
[Controlled equipment] ACM measurements | 1016 |  | 301017 | Functions - Analogue output functions - Busbar A - Frequency (f) (from voltage) - Busbar A ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Controlled equipment] ACM measurements | 1016 |  | 301017 | Functions - Analogue output functions - Mains - Frequency (f) (from voltage) - Mains ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1017 |  | 301018 | Functions - Analogue output functions - Generator - Frequency (f) (from voltage) - Generator ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
[Controlled equipment] ACM measurements | 1017 |  | 301018 | Functions - Analogue output functions - Busbar A - Frequency (f) (from voltage) - Busbar A ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Controlled equipment] ACM measurements | 1017 |  | 301018 | Functions - Analogue output functions - Mains - Frequency (f) (from voltage) - Mains ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1018 |  | 301019 | Functions - Analogue output functions - Generator - Frequency (f) (from current) - Generator ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
[Controlled equipment] ACM measurements | 1018 |  | 301019 | Functions - Analogue output functions - Busbar A - Frequency (f) (from current) - Busbar A ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Controlled equipment] ACM measurements | 1018 |  | 301019 | Functions - Analogue output functions - Mains - Frequency (f) (from current) - Mains ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1019 |  | 301020 | Functions - Analogue output functions - Generator - Frequency (f) (from current) - Generator ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
[Controlled equipment] ACM measurements | 1019 |  | 301020 | Functions - Analogue output functions - Busbar A - Frequency (f) (from current) - Busbar A ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Controlled equipment] ACM measurements | 1019 |  | 301020 | Functions - Analogue output functions - Mains - Frequency (f) (from current) - Mains ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1020 |  | 301021 | Functions - Analogue output functions - Generator - Phase angle - Generator ¦ Phase angle L1-L2 | INT16 | X * 10 | X * 0.1 | ° | X |  | X | X | X
[Controlled equipment] ACM measurements | 1020 |  | 301021 | Functions - Analogue output functions - Busbar A - Phase angle - Busbar A ¦ Phase angle L1-L2 | INT16 | X * 10 | X * 0.1 | ° |  | X
[Controlled equipment] ACM measurements | 1020 |  | 301021 | Functions - Analogue output functions - Mains - Phase angle - Mains ¦ Phase angle L1-L2 | INT16 | X * 10 | X * 0.1 | ° | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1021 |  | 301022 | Functions - Analogue output functions - Generator - Phase angle - Generator ¦ Phase angle L2-L3 | INT16 | X * 10 | X * 0.1 | ° | X |  | X | X | X
[Controlled equipment] ACM measurements | 1021 |  | 301022 | Functions - Analogue output functions - Busbar A - Phase angle - Busbar A ¦ Phase angle L2-L3 | INT16 | X * 10 | X * 0.1 | ° |  | X
[Controlled equipment] ACM measurements | 1021 |  | 301022 | Functions - Analogue output functions - Mains - Phase angle - Mains ¦ Phase angle L2-L3 | INT16 | X * 10 | X * 0.1 | ° | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1022 |  | 301023 | Functions - Analogue output functions - Generator - Phase angle - Generator ¦ Phase angle L3-L1 | INT16 | X * 10 | X * 0.1 | ° | X |  | X | X | X
[Controlled equipment] ACM measurements | 1022 |  | 301023 | Functions - Analogue output functions - Busbar A - Phase angle - Busbar A ¦ Phase angle L3-L1 | INT16 | X * 10 | X * 0.1 | ° |  | X
[Controlled equipment] ACM measurements | 1022 |  | 301023 | Functions - Analogue output functions - Mains - Phase angle - Mains ¦ Phase angle L3-L1 | INT16 | X * 10 | X * 0.1 | ° | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1023 |  | 301024 | Functions - Analogue output functions - Generator - Phase angle - Generator ¦ A-B phase angle L1 | INT16 | X * 10 | X * 0.1 | ° | X |  | X | X | X
[Controlled equipment] ACM measurements | 1023 |  | 301024 | Functions - Analogue output functions - Busbar A - Phase angle - Busbar A ¦ Phase angle L1 | INT16 | X * 10 | X * 0.1 | ° |  | X
[Controlled equipment] ACM measurements | 1023 |  | 301024 | Functions - Analogue output functions - Mains - Phase angle - Mains ¦ A-B phase angle L1 | INT16 | X * 10 | X * 0.1 | ° | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1024 |  | 301025 | Functions - Analogue output functions - Generator - Phase angle - Generator ¦ A-B phase angle L2 | INT16 | X * 10 | X * 0.1 | ° | X |  | X | X | X
[Controlled equipment] ACM measurements | 1024 |  | 301025 | Functions - Analogue output functions - Busbar A - Phase angle - Busbar A ¦ Phase angle L2 | INT16 | X * 10 | X * 0.1 | ° |  | X
[Controlled equipment] ACM measurements | 1024 |  | 301025 | Functions - Analogue output functions - Mains - Phase angle - Mains ¦ A-B phase angle L2 | INT16 | X * 10 | X * 0.1 | ° | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1025 |  | 301026 | Functions - Analogue output functions - Generator - Phase angle - Generator ¦ A-B phase angle L3 | INT16 | X * 10 | X * 0.1 | ° | X |  | X | X | X
[Controlled equipment] ACM measurements | 1025 |  | 301026 | Functions - Analogue output functions - Busbar A - Phase angle - Busbar A ¦ Phase angle L3 | INT16 | X * 10 | X * 0.1 | ° |  | X
[Controlled equipment] ACM measurements | 1025 |  | 301026 | Functions - Analogue output functions - Mains - Phase angle - Mains ¦ A-B phase angle L3 | INT16 | X * 10 | X * 0.1 | ° | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1026 |  | 301027 | Functions - Analogue output functions - Generator - Current (I) - Generator ¦ L1 | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM measurements | 1026 |  | 301027 | Functions - Analogue output functions - Busbar A - Current (I) - Busbar A ¦ L1 | INT16 | X * 1 | X * 1 | A |  | X
[Controlled equipment] ACM measurements | 1026 |  | 301027 | Functions - Analogue output functions - Mains - Current (I) - Mains ¦ L1 | INT16 | X * 1 | X * 1 | A | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1027 |  | 301028 | Functions - Analogue output functions - Generator - Current (I) - Generator ¦ L2 | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM measurements | 1027 |  | 301028 | Functions - Analogue output functions - Busbar A - Current (I) - Busbar A ¦ L2 | INT16 | X * 1 | X * 1 | A |  | X
[Controlled equipment] ACM measurements | 1027 |  | 301028 | Functions - Analogue output functions - Mains - Current (I) - Mains ¦ L2 | INT16 | X * 1 | X * 1 | A | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1028 |  | 301029 | Functions - Analogue output functions - Generator - Current (I) - Generator ¦ L3 | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM measurements | 1028 |  | 301029 | Functions - Analogue output functions - Busbar A - Current (I) - Busbar A ¦ L3 | INT16 | X * 1 | X * 1 | A |  | X
[Controlled equipment] ACM measurements | 1028 |  | 301029 | Functions - Analogue output functions - Mains - Current (I) - Mains ¦ L3 | INT16 | X * 1 | X * 1 | A | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1029 |  | 301030 | Functions - Analogue output functions - Generator - Current (I) - Generator ¦ N | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM measurements | 1029 |  | 301030 | Functions - Analogue output functions - Busbar A - Current (I) - Busbar A ¦ N | INT16 | X * 1 | X * 1 | A |  | X
[Controlled equipment] ACM measurements | 1029 |  | 301030 | Functions - Analogue output functions - Mains - Current (I) - Mains ¦ N | INT16 | X * 1 | X * 1 | A | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1030 |  | 301031 | Functions - Analogue output functions - Generator - Current (I) - Generator ¦ Min. | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM measurements | 1030 |  | 301031 | Functions - Analogue output functions - Busbar A - Current (I) - Busbar A ¦ Min. | INT16 | X * 1 | X * 1 | A |  | X
[Controlled equipment] ACM measurements | 1030 |  | 301031 | Functions - Analogue output functions - Mains - Current (I) - Mains ¦ Min. | INT16 | X * 1 | X * 1 | A | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1031 |  | 301032 | Functions - Analogue output functions - Generator - Current (I) - Generator ¦ Max. | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM measurements | 1031 |  | 301032 | Functions - Analogue output functions - Busbar A - Current (I) - Busbar A ¦ Max. | INT16 | X * 1 | X * 1 | A |  | X
[Controlled equipment] ACM measurements | 1031 |  | 301032 | Functions - Analogue output functions - Mains - Current (I) - Mains ¦ Max. | INT16 | X * 1 | X * 1 | A | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1032 |  | 301033 | Functions - Analogue output functions - Generator - Current (I) - Generator ¦ Unbalanced nominal | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM measurements | 1032 |  | 301033 | Functions - Analogue output functions - Busbar A - Current (I) - Busbar A ¦ Unbalanced nominal | INT16 | X * 1 | X * 1 | A |  | X
[Controlled equipment] ACM measurements | 1032 |  | 301033 | Functions - Analogue output functions - Mains - Current (I) - Mains ¦ Unbalanced nominal | INT16 | X * 1 | X * 1 | A | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1033 |  | 301034 | Functions - Analogue output functions - Generator - Current (I) - Generator ¦ Unbalanced average | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM measurements | 1033 |  | 301034 | Functions - Analogue output functions - Busbar A - Current (I) - Busbar A ¦ Unbalanced average | INT16 | X * 1 | X * 1 | A |  | X
[Controlled equipment] ACM measurements | 1033 |  | 301034 | Functions - Analogue output functions - Mains - Current (I) - Mains ¦ Unbalanced average | INT16 | X * 1 | X * 1 | A | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1034 |  | 301035 | Functions - Analogue output functions - Generator - Frequency (f) (from current) - Generator ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
[Controlled equipment] ACM measurements | 1034 |  | 301035 | Functions - Analogue output functions - Busbar A - Frequency (f) (from current) - Busbar A ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Controlled equipment] ACM measurements | 1034 |  | 301035 | Functions - Analogue output functions - Mains - Frequency (f) (from current) - Mains ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1035 |  | 301036 | Functions - Analogue output functions - Generator - Frequency (f) (from current) - Generator ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
[Controlled equipment] ACM measurements | 1035 |  | 301036 | Functions - Analogue output functions - Busbar A - Frequency (f) (from current) - Busbar A ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Controlled equipment] ACM measurements | 1035 |  | 301036 | Functions - Analogue output functions - Mains - Frequency (f) (from current) - Mains ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1036 |  | 301037 | Functions - Analogue output functions - Generator - Frequency (f) (from current) - Generator ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
[Controlled equipment] ACM measurements | 1036 |  | 301037 | Functions - Analogue output functions - Busbar A - Frequency (f) (from current) - Busbar A ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Controlled equipment] ACM measurements | 1036 |  | 301037 | Functions - Analogue output functions - Mains - Frequency (f) (from current) - Mains ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1037 |  | 301038 | Functions - Analogue output functions - Generator - Power (P) - Generator ¦ L1 | INT16 | X * 1 | X * 1 | kW | X |  | X | X | X
[Controlled equipment] ACM measurements | 1037 |  | 301038 | Functions - Analogue output functions - Busbar A - Power (P) - Busbar A ¦ L1 | INT16 | X * 1 | X * 1 | kW |  | X
[Controlled equipment] ACM measurements | 1037 |  | 301038 | Functions - Analogue output functions - Mains - Power (P) - Mains ¦ L1 | INT16 | X * 1 | X * 1 | kW | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1038 |  | 301039 | Functions - Analogue output functions - Generator - Power (P) - Generator ¦ L2 | INT16 | X * 1 | X * 1 | kW | X |  | X | X | X
[Controlled equipment] ACM measurements | 1038 |  | 301039 | Functions - Analogue output functions - Busbar A - Power (P) - Busbar A ¦ L2 | INT16 | X * 1 | X * 1 | kW |  | X
[Controlled equipment] ACM measurements | 1038 |  | 301039 | Functions - Analogue output functions - Mains - Power (P) - Mains ¦ L2 | INT16 | X * 1 | X * 1 | kW | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1039 |  | 301040 | Functions - Analogue output functions - Generator - Power (P) - Generator ¦ L3 | INT16 | X * 1 | X * 1 | kW | X |  | X | X | X
[Controlled equipment] ACM measurements | 1039 |  | 301040 | Functions - Analogue output functions - Busbar A - Power (P) - Busbar A ¦ L3 | INT16 | X * 1 | X * 1 | kW |  | X
[Controlled equipment] ACM measurements | 1039 |  | 301040 | Functions - Analogue output functions - Mains - Power (P) - Mains ¦ L3 | INT16 | X * 1 | X * 1 | kW | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1040 |  | 301041 | Functions - Analogue output functions - Generator - Power (P) - Generator ¦ Min. | INT16 | X * 1 | X * 1 | kW | X |  | X | X | X
[Controlled equipment] ACM measurements | 1040 |  | 301041 | Functions - Analogue output functions - Busbar A - Power (P) - Busbar A ¦ Min. | INT16 | X * 1 | X * 1 | kW |  | X
[Controlled equipment] ACM measurements | 1040 |  | 301041 | Functions - Analogue output functions - Mains - Power (P) - Mains ¦ Min. | INT16 | X * 1 | X * 1 | kW | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1041 |  | 301042 | Functions - Analogue output functions - Generator - Power (P) - Generator ¦ Max. | INT16 | X * 1 | X * 1 | kW | X |  | X | X | X
[Controlled equipment] ACM measurements | 1041 |  | 301042 | Functions - Analogue output functions - Busbar A - Power (P) - Busbar A ¦ Max. | INT16 | X * 1 | X * 1 | kW |  | X
[Controlled equipment] ACM measurements | 1041 |  | 301042 | Functions - Analogue output functions - Mains - Power (P) - Mains ¦ Max. | INT16 | X * 1 | X * 1 | kW | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1042 |  | 301043 | Functions - Analogue output functions - Generator - Power (P) - Generator ¦ Total | INT16 | X * 1 | X * 1 | kW | X |  | X | X | X
[Controlled equipment] ACM measurements | 1042 |  | 301043 | Functions - Analogue output functions - Busbar A - Power (P) - Busbar A ¦ Total | INT16 | X * 1 | X * 1 | kW |  | X
[Controlled equipment] ACM measurements | 1042 |  | 301043 | Functions - Analogue output functions - Mains - Power (P) - Mains ¦ Total | INT16 | X * 1 | X * 1 | kW | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1043 |  | 301044 | Functions - Analogue output functions - Generator - Reactive power (Q) - Generator ¦ L1 | INT16 | X * 1 | X * 1 | kvar | X |  | X | X | X
[Controlled equipment] ACM measurements | 1043 |  | 301044 | Functions - Analogue output functions - Busbar A - Reactive power (Q) - Busbar A ¦ L1 | INT16 | X * 1 | X * 1 | kvar |  | X
[Controlled equipment] ACM measurements | 1043 |  | 301044 | Functions - Analogue output functions - Mains - Reactive power (Q) - Mains ¦ L1 | INT16 | X * 1 | X * 1 | kvar | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1044 |  | 301045 | Functions - Analogue output functions - Generator - Reactive power (Q) - Generator ¦ L2 | INT16 | X * 1 | X * 1 | kvar | X |  | X | X | X
[Controlled equipment] ACM measurements | 1044 |  | 301045 | Functions - Analogue output functions - Busbar A - Reactive power (Q) - Busbar A ¦ L2 | INT16 | X * 1 | X * 1 | kvar |  | X
[Controlled equipment] ACM measurements | 1044 |  | 301045 | Functions - Analogue output functions - Mains - Reactive power (Q) - Mains ¦ L2 | INT16 | X * 1 | X * 1 | kvar | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1045 |  | 301046 | Functions - Analogue output functions - Generator - Reactive power (Q) - Generator ¦ L3 | INT16 | X * 1 | X * 1 | kvar | X |  | X | X | X
[Controlled equipment] ACM measurements | 1045 |  | 301046 | Functions - Analogue output functions - Busbar A - Reactive power (Q) - Busbar A ¦ L3 | INT16 | X * 1 | X * 1 | kvar |  | X
[Controlled equipment] ACM measurements | 1045 |  | 301046 | Functions - Analogue output functions - Mains - Reactive power (Q) - Mains ¦ L3 | INT16 | X * 1 | X * 1 | kvar | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1046 |  | 301047 | Functions - Analogue output functions - Generator - Reactive power (Q) - Generator ¦ Min. | INT16 | X * 1 | X * 1 | kvar | X |  | X | X | X
[Controlled equipment] ACM measurements | 1046 |  | 301047 | Functions - Analogue output functions - Busbar A - Reactive power (Q) - Busbar A ¦ Min. | INT16 | X * 1 | X * 1 | kvar |  | X
[Controlled equipment] ACM measurements | 1046 |  | 301047 | Functions - Analogue output functions - Mains - Reactive power (Q) - Mains ¦ Min. | INT16 | X * 1 | X * 1 | kvar | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1047 |  | 301048 | Functions - Analogue output functions - Generator - Reactive power (Q) - Generator ¦ Max. | INT16 | X * 1 | X * 1 | kvar | X |  | X | X | X
[Controlled equipment] ACM measurements | 1047 |  | 301048 | Functions - Analogue output functions - Busbar A - Reactive power (Q) - Busbar A ¦ Max. | INT16 | X * 1 | X * 1 | kvar |  | X
[Controlled equipment] ACM measurements | 1047 |  | 301048 | Functions - Analogue output functions - Mains - Reactive power (Q) - Mains ¦ Max. | INT16 | X * 1 | X * 1 | kvar | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1048 |  | 301049 | Functions - Analogue output functions - Generator - Reactive power (Q) - Generator ¦ Total | INT16 | X * 1 | X * 1 | kvar | X |  | X | X | X
[Controlled equipment] ACM measurements | 1048 |  | 301049 | Functions - Analogue output functions - Busbar A - Reactive power (Q) - Busbar A ¦ Total | INT16 | X * 1 | X * 1 | kvar |  | X
[Controlled equipment] ACM measurements | 1048 |  | 301049 | Functions - Analogue output functions - Mains - Reactive power (Q) - Mains ¦ Total | INT16 | X * 1 | X * 1 | kvar | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1049 |  | 301050 | Functions - Analogue output functions - Generator - Apparent power (S) - Generator ¦ L1 | INT16 | X * 1 | X * 1 | kVA | X |  | X | X | X
[Controlled equipment] ACM measurements | 1049 |  | 301050 | Functions - Analogue output functions - Busbar A - Apparent power (S) - Busbar A ¦ L1 | INT16 | X * 1 | X * 1 | kVA |  | X
[Controlled equipment] ACM measurements | 1049 |  | 301050 | Functions - Analogue output functions - Mains - Apparent power (S) - Mains ¦ L1 | INT16 | X * 1 | X * 1 | kVA | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1050 |  | 301051 | Functions - Analogue output functions - Generator - Apparent power (S) - Generator ¦ L2 | INT16 | X * 1 | X * 1 | kVA | X |  | X | X | X
[Controlled equipment] ACM measurements | 1050 |  | 301051 | Functions - Analogue output functions - Busbar A - Apparent power (S) - Busbar A ¦ L2 | INT16 | X * 1 | X * 1 | kVA |  | X
[Controlled equipment] ACM measurements | 1050 |  | 301051 | Functions - Analogue output functions - Mains - Apparent power (S) - Mains ¦ L2 | INT16 | X * 1 | X * 1 | kVA | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1051 |  | 301052 | Functions - Analogue output functions - Generator - Apparent power (S) - Generator ¦ L3 | INT16 | X * 1 | X * 1 | kVA | X |  | X | X | X
[Controlled equipment] ACM measurements | 1051 |  | 301052 | Functions - Analogue output functions - Busbar A - Apparent power (S) - Busbar A ¦ L3 | INT16 | X * 1 | X * 1 | kVA |  | X
[Controlled equipment] ACM measurements | 1051 |  | 301052 | Functions - Analogue output functions - Mains - Apparent power (S) - Mains ¦ L3 | INT16 | X * 1 | X * 1 | kVA | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1052 |  | 301053 | Functions - Analogue output functions - Generator - Apparent power (S) - Generator ¦ Min. | INT16 | X * 1 | X * 1 | kVA | X |  | X | X | X
[Controlled equipment] ACM measurements | 1052 |  | 301053 | Functions - Analogue output functions - Busbar A - Apparent power (S) - Busbar A ¦ Min. | INT16 | X * 1 | X * 1 | kVA |  | X
[Controlled equipment] ACM measurements | 1052 |  | 301053 | Functions - Analogue output functions - Mains - Apparent power (S) - Mains ¦ Min. | INT16 | X * 1 | X * 1 | kVA | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1053 |  | 301054 | Functions - Analogue output functions - Generator - Apparent power (S) - Generator ¦ Max. | INT16 | X * 1 | X * 1 | kVA | X |  | X | X | X
[Controlled equipment] ACM measurements | 1053 |  | 301054 | Functions - Analogue output functions - Busbar A - Apparent power (S) - Busbar A ¦ Max. | INT16 | X * 1 | X * 1 | kVA |  | X
[Controlled equipment] ACM measurements | 1053 |  | 301054 | Functions - Analogue output functions - Mains - Apparent power (S) - Mains ¦ Max. | INT16 | X * 1 | X * 1 | kVA | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1054 |  | 301055 | Functions - Analogue output functions - Generator - Apparent power (S) - Generator ¦ Total | INT16 | X * 1 | X * 1 | kVA | X |  | X | X | X
[Controlled equipment] ACM measurements | 1054 |  | 301055 | Functions - Analogue output functions - Busbar A - Apparent power (S) - Busbar A ¦ Total | INT16 | X * 1 | X * 1 | kVA |  | X
[Controlled equipment] ACM measurements | 1054 |  | 301055 | Functions - Analogue output functions - Mains - Apparent power (S) - Mains ¦ Total | INT16 | X * 1 | X * 1 | kVA | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1055 |  | 301056 | Functions - Analogue output functions - Generator - Power factor (PF) - Generator ¦ cos phi | INT16 | X * 10000 | X * 0.0001 |  | X |  | X | X | X
[Controlled equipment] ACM measurements | 1055 |  | 301056 | Functions - Analogue output functions - Busbar A - Power factor (PF) - Busbar A ¦ cos phi | INT16 | X * 10000 | X * 0.0001 |  |  | X
[Controlled equipment] ACM measurements | 1055 |  | 301056 | Functions - Analogue output functions - Mains - Power factor (PF) - Mains ¦ cos phi | INT16 | X * 10000 | X * 0.0001 | [6 empty] | X | X
[Controlled equipment] ACM measurements | 1056 |  | 301057 | Functions - Analogue output functions - Generator - Power factor (PF) - Generator ¦ Power factor | INT16 | X * 10000 | X * 0.0001 |  | X |  | X | X | X
[Controlled equipment] ACM measurements | 1056 |  | 301057 | Functions - Analogue output functions - Busbar A - Power factor (PF) - Busbar A ¦ Power factor | INT16 | X * 10000 | X * 0.0001 |  |  | X
[Controlled equipment] ACM measurements | 1056 |  | 301057 | Functions - Analogue output functions - Mains - Power factor (PF) - Mains ¦ Power factor | INT16 | X * 10000 | X * 0.0001 | [6 empty] | X | X
[Controlled equipment] ACM measurements | 1057 |  | 301058 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ Positive sequence | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1057 |  | 301058 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ Positive sequence | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1057 |  | 301058 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ Positive sequence | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1058 |  | 301059 | Functions - Analogue output functions - Generator - Current (I) - Generator ¦ Positive sequence | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM measurements | 1058 |  | 301059 | Functions - Analogue output functions - Busbar A - Current (I) - Busbar A ¦ Positive sequence | INT16 | X * 1 | X * 1 | A |  | X
[Controlled equipment] ACM measurements | 1058 |  | 301059 | Functions - Analogue output functions - Mains - Current (I) - Mains ¦ Positive sequence | INT16 | X * 1 | X * 1 | A | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1059 |  | 301060 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ Negative sequence | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1059 |  | 301060 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ Negative sequence | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1059 |  | 301060 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ Negative sequence | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1060 |  | 301061 | Functions - Analogue output functions - Generator - Current (I) - Generator ¦ Negative sequence | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM measurements | 1060 |  | 301061 | Functions - Analogue output functions - Busbar A - Current (I) - Busbar A ¦ Negative sequence | INT16 | X * 1 | X * 1 | A |  | X
[Controlled equipment] ACM measurements | 1060 |  | 301061 | Functions - Analogue output functions - Mains - Current (I) - Mains ¦ Negative sequence | INT16 | X * 1 | X * 1 | A | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1061 |  | 301062 | Functions - Analogue output functions - Generator - Voltage (V) - Generator ¦ Zero sequence | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
[Controlled equipment] ACM measurements | 1061 |  | 301062 | Functions - Analogue output functions - Busbar A - Voltage (V) - Busbar A ¦ Zero sequence | INT16 | X * 1 | X * 1 | V |  | X
[Controlled equipment] ACM measurements | 1061 |  | 301062 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ Zero sequence | INT16 | X * 1 | X * 1 | V | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1062 |  | 301063 | Functions - Analogue output functions - Generator - Current (I) - Generator ¦ Zero sequence | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM measurements | 1062 |  | 301063 | Functions - Analogue output functions - Busbar A - Current (I) - Busbar A ¦ Zero sequence | INT16 | X * 1 | X * 1 | A |  | X
[Controlled equipment] ACM measurements | 1062 |  | 301063 | Functions - Analogue output functions - Mains - Current (I) - Mains ¦ Zero sequence | INT16 | X * 1 | X * 1 | A | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1063 |  | 301064 | Functions - Analogue output functions - Generator - Power (P) - Generator ¦ Total | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
[Controlled equipment] ACM measurements | 1063 |  | 301064 | Functions - Analogue output functions - Busbar A - Power (P) - Busbar A ¦ Total | INT16 | X * 1 | X * 1 | % |  | X
[Controlled equipment] ACM measurements | 1063 |  | 301064 | Functions - Analogue output functions - Mains - Power (P) - Mains ¦ Total | INT16 | X * 1 | X * 1 | % | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1064 |  | 301065 | Functions - Analogue output functions - Generator - Reactive power (Q) - Generator ¦ Total | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
[Controlled equipment] ACM measurements | 1064 |  | 301065 | Functions - Analogue output functions - Busbar A - Reactive power (Q) - Busbar A ¦ Total | INT16 | X * 1 | X * 1 | % |  | X
[Controlled equipment] ACM measurements | 1064 |  | 301065 | Functions - Analogue output functions - Mains - Reactive power (Q) - Mains ¦ Total | INT16 | X * 1 | X * 1 | % | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1065 |  | 301066 | Functions - Analogue output functions - Generator - Apparent power (S) - Generator ¦ Total | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
[Controlled equipment] ACM measurements | 1065 |  | 301066 | Functions - Analogue output functions - Busbar A - Apparent power (S) - Busbar A ¦ Total | INT16 | X * 1 | X * 1 | % |  | X
[Controlled equipment] ACM measurements | 1065 |  | 301066 | Functions - Analogue output functions - Mains - Apparent power (S) - Mains ¦ Total | INT16 | X * 1 | X * 1 | % | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1066 |  | 301067 | Functions - Analogue output functions - Generator - Power (P) - Generator ¦ Available | INT16 | X * 1 | X * 1 | kW | X |  | X | X | X
[Controlled equipment] ACM measurements | 1066 |  | 301067 | Functions - Analogue output functions - Busbar A - Power (P) - Busbar A ¦ Available | INT16 | X * 1 | X * 1 | kW |  | X
[Controlled equipment] ACM measurements | 1066 |  | 301067 | Functions - Analogue output functions - Mains - Power (P) - Mains ¦ Available | INT16 | X * 1 | X * 1 | kW | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1067 |  | 301068 | Functions - Analogue output functions - Generator - Reactive power (Q) - Generator ¦ Available | INT16 | X * 1 | X * 1 | kvar | X |  | X | X | X
[Controlled equipment] ACM measurements | 1067 |  | 301068 | Functions - Analogue output functions - Busbar A - Reactive power (Q) - Busbar A ¦ Available | INT16 | X * 1 | X * 1 | kvar |  | X
[Controlled equipment] ACM measurements | 1067 |  | 301068 | Functions - Analogue output functions - Mains - Reactive power (Q) - Mains ¦ Available | INT16 | X * 1 | X * 1 | kvar | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1068 |  | 301069 | Functions - Analogue output functions - Generator - Apparent power (S) - Generator ¦ Available | INT16 | X * 1 | X * 1 | kVA | X |  | X | X | X
[Controlled equipment] ACM measurements | 1068 |  | 301069 | Functions - Analogue output functions - Busbar A - Apparent power (S) - Busbar A ¦ Available | INT16 | X * 1 | X * 1 | kVA |  | X
[Controlled equipment] ACM measurements | 1068 |  | 301069 | Functions - Analogue output functions - Mains - Apparent power (S) - Mains ¦ Available | INT16 | X * 1 | X * 1 | kVA | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1069 |  | 301070 | Functions - Analogue output functions - Generator - Power (P) - Generator ¦ Available | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
[Controlled equipment] ACM measurements | 1069 |  | 301070 | Functions - Analogue output functions - Busbar A - Power (P) - Busbar A ¦ Available | INT16 | X * 1 | X * 1 | % |  | X
[Controlled equipment] ACM measurements | 1069 |  | 301070 | Functions - Analogue output functions - Mains - Power (P) - Mains ¦ Available | INT16 | X * 1 | X * 1 | % | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1070 |  | 301071 | Functions - Analogue output functions - Generator - Reactive power (Q) - Generator ¦ Available | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
[Controlled equipment] ACM measurements | 1070 |  | 301071 | Functions - Analogue output functions - Busbar A - Reactive power (Q) - Busbar A ¦ Available | INT16 | X * 1 | X * 1 | % |  | X
[Controlled equipment] ACM measurements | 1070 |  | 301071 | Functions - Analogue output functions - Mains - Reactive power (Q) - Mains ¦ Available | INT16 | X * 1 | X * 1 | % | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1071 |  | 301072 | Functions - Analogue output functions - Generator - Apparent power (S) - Generator ¦ Available | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
[Controlled equipment] ACM measurements | 1071 |  | 301072 | Functions - Analogue output functions - Busbar A - Apparent power (S) - Busbar A ¦ Available | INT16 | X * 1 | X * 1 | % |  | X
[Controlled equipment] ACM measurements | 1071 |  | 301072 | Functions - Analogue output functions - Mains - Apparent power (S) - Mains ¦ Available | INT16 | X * 1 | X * 1 | % | [5 empty] | X | X
[Controlled equipment] ACM measurements | 1072 |  | 301073 | Functions - Analogue output functions - Generator - Frequency (f) (from voltage) - Generator ¦ Avg. | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
[Controlled equipment] ACM measurements | 1072 |  | 301073 | Functions - Analogue output functions - Busbar A - Frequency (f) (from voltage) - Busbar A ¦ Avg. | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Controlled equipment] ACM measurements | 1072 |  | 301073 | Functions - Analogue output functions - Mains - Frequency (f) (from voltage) - Mains ¦ Avg. | INT16 | X * 100 | X * 0.01 | Hz | [5 empty] | X | X
[Busbar] ACM measurements | 1100 |  | 301101 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L1-N | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1100 |  | 301101 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ L1-N | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1100 |  | 301101 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ L1-N | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1101 |  | 301102 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L2-N | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1101 |  | 301102 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ L2-N | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1101 |  | 301102 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ L2-N | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1102 |  | 301103 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L3-N | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1102 |  | 301103 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ L3-N | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1102 |  | 301103 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ L3-N | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1103 |  | 301104 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ N | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1103 |  | 301104 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ N | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1103 |  | 301104 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ N | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1104 |  | 301105 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L-N min. | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1104 |  | 301105 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ L-N min. | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1104 |  | 301105 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ L-N min. | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1105 |  | 301106 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L-N max. | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1105 |  | 301106 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ L-N max. | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1105 |  | 301106 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ L-N max. | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1106 |  | 301107 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L-N unbalanced | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1106 |  | 301107 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ L-N unbalanced | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1106 |  | 301107 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ L-N unbalanced | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1107 |  | 301108 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L1-L2 | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1107 |  | 301108 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ L1-L2 | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1107 |  | 301108 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ L1-L2 | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1108 |  | 301109 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L2-L3 | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1108 |  | 301109 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ L2-L3 | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1108 |  | 301109 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ L2-L3 | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1109 |  | 301110 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L3-L1 | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1109 |  | 301110 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ L3-L1 | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1109 |  | 301110 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ L3-L1 | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1110 |  | 301111 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L-L min. | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1110 |  | 301111 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ L-L min. | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1110 |  | 301111 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ L-L min. | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1111 |  | 301112 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L-L max. | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1111 |  | 301112 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ L-L max. | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1111 |  | 301112 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ L-L max. | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1112 |  | 301113 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ L-L unbalanced | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1112 |  | 301113 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ L-L unbalanced | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1112 |  | 301113 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ L-L unbalanced | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1113 |  | 301114 | Functions - Analogue output functions - Mains - Frequency (f) (from voltage) - Mains ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz |  |  | X | X
[Busbar] ACM measurements | 1113 |  | 301114 | Functions - Analogue output functions - Busbar - Frequency (f) (from voltage) - Busbar ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1113 |  | 301114 | Functions - Analogue output functions - Busbar B - Frequency (f) (from voltage) - Busbar B ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Busbar] ACM measurements | 1114 |  | 301115 | Functions - Analogue output functions - Mains - Frequency (f) (from voltage) - Mains ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz |  |  | X | X
[Busbar] ACM measurements | 1114 |  | 301115 | Functions - Analogue output functions - Busbar - Frequency (f) (from voltage) - Busbar ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1114 |  | 301115 | Functions - Analogue output functions - Busbar B - Frequency (f) (from voltage) - Busbar B ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Busbar] ACM measurements | 1115 |  | 301116 | Functions - Analogue output functions - Mains - Frequency (f) (from voltage) - Mains ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz |  |  | X | X
[Busbar] ACM measurements | 1115 |  | 301116 | Functions - Analogue output functions - Busbar - Frequency (f) (from voltage) - Busbar ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1115 |  | 301116 | Functions - Analogue output functions - Busbar B - Frequency (f) (from voltage) - Busbar B ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Busbar] ACM measurements | 1116 |  | 301117 | Functions - Analogue output functions - Mains - Frequency (f) (from voltage) - Mains ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz |  |  | X | X
[Busbar] ACM measurements | 1116 |  | 301117 | Functions - Analogue output functions - Busbar - Frequency (f) (from voltage) - Busbar ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1116 |  | 301117 | Functions - Analogue output functions - Busbar B - Frequency (f) (from voltage) - Busbar B ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Busbar] ACM measurements | 1117 |  | 301118 | Functions - Analogue output functions - Mains - Frequency (f) (from voltage) - Mains ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz |  |  | X | X
[Busbar] ACM measurements | 1117 |  | 301118 | Functions - Analogue output functions - Busbar - Frequency (f) (from voltage) - Busbar ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1117 |  | 301118 | Functions - Analogue output functions - Busbar B - Frequency (f) (from voltage) - Busbar B ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz |  | X
[Busbar] ACM measurements | 1118 |  | 301119 | Functions - Analogue output functions - Mains - Phase angle - Mains ¦ Phase angle L1-L2 | INT16 | X * 10 | X * 0.1 | ° |  |  | X | X
[Busbar] ACM measurements | 1118 |  | 301119 | Functions - Analogue output functions - Busbar - Phase angle - Busbar ¦ Phase angle L1-L2 | INT16 | X * 10 | X * 0.1 | ° | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1118 |  | 301119 | Functions - Analogue output functions - Busbar B - Phase angle - Busbar B ¦ Phase angle L1-L2 | INT16 | X * 10 | X * 0.1 | ° |  | X
[Busbar] ACM measurements | 1119 |  | 301120 | Functions - Analogue output functions - Mains - Phase angle - Mains ¦ Phase angle L2-L3 | INT16 | X * 10 | X * 0.1 | ° |  |  | X | X
[Busbar] ACM measurements | 1119 |  | 301120 | Functions - Analogue output functions - Busbar - Phase angle - Busbar ¦ Phase angle L2-L3 | INT16 | X * 10 | X * 0.1 | ° | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1119 |  | 301120 | Functions - Analogue output functions - Busbar B - Phase angle - Busbar B ¦ Phase angle L2-L3 | INT16 | X * 10 | X * 0.1 | ° |  | X
[Busbar] ACM measurements | 1120 |  | 301121 | Functions - Analogue output functions - Mains - Phase angle - Mains ¦ Phase angle L3-L1 | INT16 | X * 10 | X * 0.1 | ° |  |  | X | X
[Busbar] ACM measurements | 1120 |  | 301121 | Functions - Analogue output functions - Busbar - Phase angle - Busbar ¦ Phase angle L3-L1 | INT16 | X * 10 | X * 0.1 | ° | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1120 |  | 301121 | Functions - Analogue output functions - Busbar B - Phase angle - Busbar B ¦ Phase angle L3-L1 | INT16 | X * 10 | X * 0.1 | ° |  | X
[Busbar] ACM measurements | 1121 |  | 301122 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ Positive sequence | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1121 |  | 301122 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ Positive sequence | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1121 |  | 301122 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ Positive sequence | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1122 |  | 301123 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ Negative sequence | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1122 |  | 301123 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ Negative sequence | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1122 |  | 301123 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ Negative sequence | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1123 |  | 301124 | Functions - Analogue output functions - Mains - Voltage (V) - Mains ¦ Zero sequence | INT16 | X * 1 | X * 1 | V |  |  | X | X
[Busbar] ACM measurements | 1123 |  | 301124 | Functions - Analogue output functions - Busbar - Voltage (V) - Busbar ¦ Zero sequence | INT16 | X * 1 | X * 1 | V | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1123 |  | 301124 | Functions - Analogue output functions - Busbar B - Voltage (V) - Busbar B ¦ Zero sequence | INT16 | X * 1 | X * 1 | V |  | X
[Busbar] ACM measurements | 1124 |  | 301125 | Functions - Analogue output functions - Mains - Power (P) - Mains ¦ Min. | INT16 | X * 1 | X * 1 | kW |  |  | X | X
[Busbar] ACM measurements | 1124 |  | 301125 | Functions - Analogue output functions - Busbar - Power (P) - Busbar ¦ Min. | INT16 | X * 1 | X * 1 | kW | [6 empty] | X
[Busbar] ACM measurements | 1125 |  | 301126 | Functions - Analogue output functions - Mains - Power (P) - Mains ¦ Max. | INT16 | X * 1 | X * 1 | kW |  |  | X | X
[Busbar] ACM measurements | 1125 |  | 301126 | Functions - Analogue output functions - Busbar - Power (P) - Busbar ¦ Max. | INT16 | X * 1 | X * 1 | kW | [6 empty] | X
[Busbar] ACM measurements | 1126 |  | 301127 | Functions - Analogue output functions - Mains - Power (P) - Mains ¦ Total | INT16 | X * 1 | X * 1 | kW |  |  | X | X
[Busbar] ACM measurements | 1126 |  | 301127 | Functions - Analogue output functions - Busbar - Power (P) - Busbar ¦ Total | INT16 | X * 1 | X * 1 | kW | [6 empty] | X
[Busbar] ACM measurements | 1127 |  | 301128 | Functions - Analogue output functions - Mains - Reactive power (Q) - Mains ¦ Min. | INT16 | X * 1 | X * 1 | kvar |  |  | X | X
[Busbar] ACM measurements | 1127 |  | 301128 | Functions - Analogue output functions - Busbar - Reactive power (Q) - Busbar ¦ Min. | INT16 | X * 1 | X * 1 | kvar | [6 empty] | X
[Busbar] ACM measurements | 1128 |  | 301129 | Functions - Analogue output functions - Mains - Reactive power (Q) - Mains ¦ Max. | INT16 | X * 1 | X * 1 | kvar |  |  | X | X
[Busbar] ACM measurements | 1128 |  | 301129 | Functions - Analogue output functions - Busbar - Reactive power (Q) - Busbar ¦ Max. | INT16 | X * 1 | X * 1 | kvar | [6 empty] | X
[Busbar] ACM measurements | 1129 |  | 301130 | Functions - Analogue output functions - Mains - Reactive power (Q) - Mains ¦ Total | INT16 | X * 1 | X * 1 | kvar |  |  | X | X
[Busbar] ACM measurements | 1129 |  | 301130 | Functions - Analogue output functions - Busbar - Reactive power (Q) - Busbar ¦ Total | INT16 | X * 1 | X * 1 | kvar | [6 empty] | X
[Busbar] ACM measurements | 1130 |  | 301131 | Functions - Analogue output functions - Mains - Apparent power (S) - Mains ¦ Min. | INT16 | X * 1 | X * 1 | kVA |  |  | X | X
[Busbar] ACM measurements | 1130 |  | 301131 | Functions - Analogue output functions - Busbar - Apparent power (S) - Busbar ¦ Min. | INT16 | X * 1 | X * 1 | kVA | [6 empty] | X
[Busbar] ACM measurements | 1131 |  | 301132 | Functions - Analogue output functions - Mains - Apparent power (S) - Mains ¦ Max. | INT16 | X * 1 | X * 1 | kVA |  |  | X | X
[Busbar] ACM measurements | 1131 |  | 301132 | Functions - Analogue output functions - Busbar - Apparent power (S) - Busbar ¦ Max. | INT16 | X * 1 | X * 1 | kVA | [6 empty] | X
[Busbar] ACM measurements | 1132 |  | 301133 | Functions - Analogue output functions - Mains - Apparent power (S) - Mains ¦ Total | INT16 | X * 1 | X * 1 | kVA |  |  | X | X
[Busbar] ACM measurements | 1132 |  | 301133 | Functions - Analogue output functions - Busbar - Apparent power (S) - Busbar ¦ Total | INT16 | X * 1 | X * 1 | kVA | [6 empty] | X
[Busbar] ACM measurements | 1133 |  | 301134 | Functions - Analogue output functions - Mains - Frequency (f) (from voltage) - Mains ¦ Avg. | INT16 | X * 100 | X * 0.01 | Hz |  |  | X | X
[Busbar] ACM measurements | 1133 |  | 301134 | Functions - Analogue output functions - Busbar - Frequency (f) (from voltage) - Busbar ¦ Avg. | INT16 | X * 100 | X * 0.01 | Hz | X |  |  |  | X | X | X
[Busbar] ACM measurements | 1133 |  | 301134 | Functions - Analogue output functions - Busbar B - Frequency (f) (from voltage) - Busbar B ¦ Avg. | INT16 | X * 100 | X * 0.01 | Hz |  | X
4th current ACM measurements | 1150 |  | 301151 | Functions - Analogue output functions - Local - 4th current input - Current (I) - L4 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
4th current ACM measurements | 1151 |  | 301152 | Functions - Analogue output functions - Local - 4th current input - Power (P) - L4 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
4th current ACM measurements | 1152 |  | 301153 | Functions - Analogue output functions - Local - 4th current input - Reactive power (Q) - L4 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
4th current ACM measurements | 1153 |  | 301154 | Functions - Analogue output functions - Local - 4th current input - Apparent power (S) - L4 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
4th current ACM measurements | 1154 |  | 301155 | Functions - Analogue output functions - Local - 4th current input - Frequency (f) - L4 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
4th current ACM measurements | 1155 |  | 301156 | Functions - Analogue output functions - Local - 4th current input - Phase angle - L4 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
4th current ACM measurements | 1156 |  | 301157 | Functions - Analogue output functions - Local - 4th current input - Power factor (PF) - L4 ¦ cos phi | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
4th current ACM measurements | 1157 |  | 301158 | Functions - Analogue output functions - Local - 4th current input - Power factor (PF) - L4 ¦ Power factor | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1200 |  | 301201 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ L1-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1201 |  | 301202 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ L2-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1202 |  | 301203 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ L3-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1203 |  | 301204 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1204 |  | 301205 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ L-N min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1205 |  | 301206 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ L-N max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1206 |  | 301207 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ L-N unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1207 |  | 301208 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ L1-L2 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1208 |  | 301209 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ L2-L3 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1209 |  | 301210 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ L3-L1 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1210 |  | 301211 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ L-L min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1211 |  | 301212 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ L-L max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1212 |  | 301213 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ L-L unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1213 |  | 301214 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Frequency (f) (from voltage) - Reference A ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1214 |  | 301215 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Frequency (f) (from voltage) - Reference A ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1215 |  | 301216 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Frequency (f) (from voltage) - Reference A ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1216 |  | 301217 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Frequency (f) (from voltage) - Reference A ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1217 |  | 301218 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Frequency (f) (from voltage) - Reference A ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1218 |  | 301219 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Frequency (f) (from current) - Reference A ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1219 |  | 301220 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Frequency (f) (from current) - Reference A ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1220 |  | 301221 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Phase angle - Reference A ¦ Phase angle L1-L2 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1221 |  | 301222 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Phase angle - Reference A ¦ Phase angle L2-L3 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1222 |  | 301223 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Phase angle - Reference A ¦ Phase angle L3-L1 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1223 |  | 301224 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Phase angle - Reference A ¦ Phase angle L1 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1224 |  | 301225 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Phase angle - Reference A ¦ Phase angle L2 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1225 |  | 301226 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Phase angle - Reference A ¦ Phase angle L3 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1226 |  | 301227 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Current (I) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1227 |  | 301228 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Current (I) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1228 |  | 301229 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Current (I) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1229 |  | 301230 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Current (I) - Reference A ¦ N | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1230 |  | 301231 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Current (I) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1231 |  | 301232 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Current (I) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1232 |  | 301233 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Current (I) - Reference A ¦ Unbalanced nominal | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1233 |  | 301234 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Current (I) - Reference A ¦ Unbalanced average | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1234 |  | 301235 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Frequency (f) (from current) - Reference A ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1235 |  | 301236 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Frequency (f) (from current) - Reference A ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1236 |  | 301237 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Frequency (f) (from current) - Reference A ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1237 |  | 301238 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Power (P) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1238 |  | 301239 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Power (P) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1239 |  | 301240 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Power (P) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1240 |  | 301241 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Power (P) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1241 |  | 301242 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Power (P) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1242 |  | 301243 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Power (P) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1243 |  | 301244 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Reactive power (Q) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1244 |  | 301245 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Reactive power (Q) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1245 |  | 301246 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Reactive power (Q) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1246 |  | 301247 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Reactive power (Q) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1247 |  | 301248 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Reactive power (Q) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1248 |  | 301249 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Reactive power (Q) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1249 |  | 301250 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Apparent power (S) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1250 |  | 301251 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Apparent power (S) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1251 |  | 301252 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Apparent power (S) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1252 |  | 301253 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Apparent power (S) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1253 |  | 301254 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Apparent power (S) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1254 |  | 301255 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Apparent power (S) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1255 |  | 301256 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Power factor (PF) - Reference A ¦ cos phi | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1256 |  | 301257 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Power factor (PF) - Reference A ¦ Power factor | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1257 |  | 301258 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ Positive sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1258 |  | 301259 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Current (I) - Reference A ¦ Positive sequence | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1259 |  | 301260 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ Negative sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1260 |  | 301261 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Current (I) - Reference A ¦ Negative sequence | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1261 |  | 301262 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Voltage (V) - Reference A ¦ Zero sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1262 |  | 301263 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Current (I) - Reference A ¦ Zero sequence | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1263 |  | 301264 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Power (P) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1264 |  | 301265 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Reactive power (Q) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1265 |  | 301266 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Apparent power (S) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1266 |  | 301267 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Power (P) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1267 |  | 301268 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Reactive power (Q) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1268 |  | 301269 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Apparent power (S) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1269 |  | 301270 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Power (P) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1270 |  | 301271 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Reactive power (Q) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1271 |  | 301272 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Apparent power (S) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1272 |  | 301273 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference A - Frequency (f) (from voltage) - Reference A ¦ Avg. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1300 |  | 301301 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ L1-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1301 |  | 301302 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ L2-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1302 |  | 301303 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ L3-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1303 |  | 301304 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1304 |  | 301305 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ L-N min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1305 |  | 301306 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ L-N max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1306 |  | 301307 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ L-N unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1307 |  | 301308 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ L1-L2 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1308 |  | 301309 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ L2-L3 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1309 |  | 301310 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ L3-L1 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1310 |  | 301311 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ L-L min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1311 |  | 301312 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ L-L max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1312 |  | 301313 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ L-L unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1313 |  | 301314 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Frequency (f) - Reference B ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1314 |  | 301315 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Frequency (f) - Reference B ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1315 |  | 301316 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Frequency (f) - Reference B ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1316 |  | 301317 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Frequency (f) - Reference B ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1317 |  | 301318 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Frequency (f) - Reference B ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1318 |  | 301319 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Phase angle - Reference B ¦ Phase angle L1-L2 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1319 |  | 301320 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Phase angle - Reference B ¦ Phase angle L2-L3 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1320 |  | 301321 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Phase angle - Reference B ¦ Phase angle L3-L1 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1321 |  | 301322 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ Positive sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1322 |  | 301323 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ Negative sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1323 |  | 301324 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Voltage (V) - Reference B ¦ Zero sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1324 |  | 301325 | Functions - Analogue output functions - Transducers - Transducer 1 - Reference B - Frequency (f) - Reference B ¦ Avg. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
4th current ACM measurements | 1350 |  | 301351 | Functions - Analogue output functions - Transducers - Transducer 1 - 4th current input - Current (I) - L4 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
4th current ACM measurements | 1351 |  | 301352 | Functions - Analogue output functions - Transducers - Transducer 1 - 4th current input - Power (P) - L4 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
4th current ACM measurements | 1352 |  | 301353 | Functions - Analogue output functions - Transducers - Transducer 1 - 4th current input - Reactive power (Q) - L4 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
4th current ACM measurements | 1353 |  | 301354 | Functions - Analogue output functions - Transducers - Transducer 1 - 4th current input - Apparent power (S) - L4 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
4th current ACM measurements | 1354 |  | 301355 | Functions - Analogue output functions - Transducers - Transducer 1 - 4th current input - Frequency (f) - L4 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
4th current ACM measurements | 1355 |  | 301356 | Functions - Analogue output functions - Transducers - Transducer 1 - 4th current input - Phase angle - L4 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
4th current ACM measurements | 1356 |  | 301357 | Functions - Analogue output functions - Transducers - Transducer 1 - 4th current input - Power factor (PF) - L4 ¦ cos phi | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
4th current ACM measurements | 1357 |  | 301358 | Functions - Analogue output functions - Transducers - Transducer 1 - 4th current input - Power factor (PF) - L4 ¦ Power factor | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1400 |  | 301401 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ L1-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1401 |  | 301402 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ L2-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1402 |  | 301403 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ L3-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1403 |  | 301404 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1404 |  | 301405 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ L-N min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1405 |  | 301406 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ L-N max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1406 |  | 301407 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ L-N unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1407 |  | 301408 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ L1-L2 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1408 |  | 301409 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ L2-L3 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1409 |  | 301410 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ L3-L1 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1410 |  | 301411 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ L-L min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1411 |  | 301412 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ L-L max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1412 |  | 301413 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ L-L unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1413 |  | 301414 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Frequency (f) (from voltage) - Reference A ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1414 |  | 301415 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Frequency (f) (from voltage) - Reference A ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1415 |  | 301416 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Frequency (f) (from voltage) - Reference A ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1416 |  | 301417 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Frequency (f) (from voltage) - Reference A ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1417 |  | 301418 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Frequency (f) (from voltage) - Reference A ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1418 |  | 301419 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Frequency (f) (from current) - Reference A ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1419 |  | 301420 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Frequency (f) (from current) - Reference A ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1420 |  | 301421 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Phase angle - Reference A ¦ Phase angle L1-L2 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1421 |  | 301422 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Phase angle - Reference A ¦ Phase angle L2-L3 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1422 |  | 301423 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Phase angle - Reference A ¦ Phase angle L3-L1 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1423 |  | 301424 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Phase angle - Reference A ¦ Phase angle L1 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1424 |  | 301425 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Phase angle - Reference A ¦ Phase angle L2 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1425 |  | 301426 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Phase angle - Reference A ¦ Phase angle L3 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1426 |  | 301427 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Current (I) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1427 |  | 301428 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Current (I) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1428 |  | 301429 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Current (I) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1429 |  | 301430 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Current (I) - Reference A ¦ N | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1430 |  | 301431 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Current (I) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1431 |  | 301432 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Current (I) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1432 |  | 301433 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Current (I) - Reference A ¦ Unbalanced nominal | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1433 |  | 301434 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Current (I) - Reference A ¦ Unbalanced average | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1434 |  | 301435 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Frequency (f) (from current) - Reference A ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1435 |  | 301436 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Frequency (f) (from current) - Reference A ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1436 |  | 301437 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Frequency (f) (from current) - Reference A ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1437 |  | 301438 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Power (P) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1438 |  | 301439 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Power (P) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1439 |  | 301440 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Power (P) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1440 |  | 301441 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Power (P) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1441 |  | 301442 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Power (P) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1442 |  | 301443 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Power (P) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1443 |  | 301444 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Reactive power (Q) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1444 |  | 301445 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Reactive power (Q) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1445 |  | 301446 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Reactive power (Q) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1446 |  | 301447 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Reactive power (Q) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1447 |  | 301448 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Reactive power (Q) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1448 |  | 301449 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Reactive power (Q) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1449 |  | 301450 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Apparent power (S) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1450 |  | 301451 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Apparent power (S) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1451 |  | 301452 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Apparent power (S) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1452 |  | 301453 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Apparent power (S) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1453 |  | 301454 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Apparent power (S) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1454 |  | 301455 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Apparent power (S) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1455 |  | 301456 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Power factor (PF) - Reference A ¦ cos phi | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1456 |  | 301457 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Power factor (PF) - Reference A ¦ Power factor | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1457 |  | 301458 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ Positive sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1458 |  | 301459 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Current (I) - Reference A ¦ Positive sequence | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1459 |  | 301460 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ Negative sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1460 |  | 301461 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Current (I) - Reference A ¦ Negative sequence | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1461 |  | 301462 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Voltage (V) - Reference A ¦ Zero sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1462 |  | 301463 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Current (I) - Reference A ¦ Zero sequence | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1463 |  | 301464 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Power (P) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1464 |  | 301465 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Reactive power (Q) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1465 |  | 301466 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Apparent power (S) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1466 |  | 301467 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Power (P) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1467 |  | 301468 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Reactive power (Q) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1468 |  | 301469 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Apparent power (S) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1469 |  | 301470 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Power (P) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1470 |  | 301471 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Reactive power (Q) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1471 |  | 301472 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Apparent power (S) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1472 |  | 301473 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference A - Frequency (f) (from voltage) - Reference A ¦ Avg. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1500 |  | 301501 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ L1-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1501 |  | 301502 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ L2-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1502 |  | 301503 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ L3-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1503 |  | 301504 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1504 |  | 301505 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ L-N min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1505 |  | 301506 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ L-N max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1506 |  | 301507 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ L-N unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1507 |  | 301508 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ L1-L2 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1508 |  | 301509 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ L2-L3 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1509 |  | 301510 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ L3-L1 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1510 |  | 301511 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ L-L min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1511 |  | 301512 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ L-L max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1512 |  | 301513 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ L-L unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1513 |  | 301514 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Frequency (f) - Reference B ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1514 |  | 301515 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Frequency (f) - Reference B ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1515 |  | 301516 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Frequency (f) - Reference B ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1516 |  | 301517 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Frequency (f) - Reference B ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1517 |  | 301518 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Frequency (f) - Reference B ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1518 |  | 301519 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Phase angle - Reference B ¦ Phase angle L1-L2 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1519 |  | 301520 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Phase angle - Reference B ¦ Phase angle L2-L3 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1520 |  | 301521 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Phase angle - Reference B ¦ Phase angle L3-L1 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1521 |  | 301522 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ Positive sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1522 |  | 301523 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ Negative sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1523 |  | 301524 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Voltage (V) - Reference B ¦ Zero sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1524 |  | 301525 | Functions - Analogue output functions - Transducers - Transducer 2 - Reference B - Frequency (f) - Reference B ¦ Avg. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
4th current ACM measurements | 1550 |  | 301551 | Functions - Analogue output functions - Transducers - Transducer 2 - 4th current input - Current (I) - L4 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
4th current ACM measurements | 1551 |  | 301552 | Functions - Analogue output functions - Transducers - Transducer 2 - 4th current input - Power (P) - L4 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
4th current ACM measurements | 1552 |  | 301553 | Functions - Analogue output functions - Transducers - Transducer 2 - 4th current input - Reactive power (Q) - L4 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
4th current ACM measurements | 1553 |  | 301554 | Functions - Analogue output functions - Transducers - Transducer 2 - 4th current input - Apparent power (S) - L4 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
4th current ACM measurements | 1554 |  | 301555 | Functions - Analogue output functions - Transducers - Transducer 2 - 4th current input - Frequency (f) - L4 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
4th current ACM measurements | 1555 |  | 301556 | Functions - Analogue output functions - Transducers - Transducer 2 - 4th current input - Phase angle - L4 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
4th current ACM measurements | 1556 |  | 301557 | Functions - Analogue output functions - Transducers - Transducer 2 - 4th current input - Power factor (PF) - L4 ¦ cos phi | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
4th current ACM measurements | 1557 |  | 301558 | Functions - Analogue output functions - Transducers - Transducer 2 - 4th current input - Power factor (PF) - L4 ¦ Power factor | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1600 |  | 301601 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ L1-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1601 |  | 301602 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ L2-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1602 |  | 301603 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ L3-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1603 |  | 301604 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1604 |  | 301605 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ L-N min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1605 |  | 301606 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ L-N max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1606 |  | 301607 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ L-N unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1607 |  | 301608 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ L1-L2 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1608 |  | 301609 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ L2-L3 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1609 |  | 301610 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ L3-L1 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1610 |  | 301611 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ L-L min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1611 |  | 301612 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ L-L max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1612 |  | 301613 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ L-L unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1613 |  | 301614 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Frequency (f) (from voltage) - Reference A ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1614 |  | 301615 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Frequency (f) (from voltage) - Reference A ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1615 |  | 301616 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Frequency (f) (from voltage) - Reference A ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1616 |  | 301617 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Frequency (f) (from voltage) - Reference A ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1617 |  | 301618 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Frequency (f) (from voltage) - Reference A ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1618 |  | 301619 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Frequency (f) (from current) - Reference A ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1619 |  | 301620 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Frequency (f) (from current) - Reference A ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1620 |  | 301621 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Phase angle - Reference A ¦ Phase angle L1-L2 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1621 |  | 301622 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Phase angle - Reference A ¦ Phase angle L2-L3 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1622 |  | 301623 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Phase angle - Reference A ¦ Phase angle L3-L1 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1623 |  | 301624 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Phase angle - Reference A ¦ Phase angle L1 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1624 |  | 301625 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Phase angle - Reference A ¦ Phase angle L2 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1625 |  | 301626 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Phase angle - Reference A ¦ Phase angle L3 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1626 |  | 301627 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Current (I) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1627 |  | 301628 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Current (I) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1628 |  | 301629 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Current (I) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1629 |  | 301630 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Current (I) - Reference A ¦ N | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1630 |  | 301631 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Current (I) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1631 |  | 301632 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Current (I) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1632 |  | 301633 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Current (I) - Reference A ¦ Unbalanced nominal | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1633 |  | 301634 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Current (I) - Reference A ¦ Unbalanced average | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1634 |  | 301635 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Frequency (f) (from current) - Reference A ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1635 |  | 301636 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Frequency (f) (from current) - Reference A ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1636 |  | 301637 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Frequency (f) (from current) - Reference A ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1637 |  | 301638 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Power (P) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1638 |  | 301639 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Power (P) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1639 |  | 301640 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Power (P) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1640 |  | 301641 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Power (P) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1641 |  | 301642 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Power (P) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1642 |  | 301643 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Power (P) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1643 |  | 301644 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Reactive power (Q) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1644 |  | 301645 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Reactive power (Q) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1645 |  | 301646 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Reactive power (Q) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1646 |  | 301647 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Reactive power (Q) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1647 |  | 301648 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Reactive power (Q) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1648 |  | 301649 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Reactive power (Q) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1649 |  | 301650 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Apparent power (S) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1650 |  | 301651 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Apparent power (S) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1651 |  | 301652 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Apparent power (S) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1652 |  | 301653 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Apparent power (S) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1653 |  | 301654 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Apparent power (S) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1654 |  | 301655 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Apparent power (S) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1655 |  | 301656 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Power factor (PF) - Reference A ¦ cos phi | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1656 |  | 301657 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Power factor (PF) - Reference A ¦ Power factor | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1657 |  | 301658 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ Positive sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1658 |  | 301659 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Current (I) - Reference A ¦ Positive sequence | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1659 |  | 301660 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ Negative sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1660 |  | 301661 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Current (I) - Reference A ¦ Negative sequence | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1661 |  | 301662 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Voltage (V) - Reference A ¦ Zero sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1662 |  | 301663 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Current (I) - Reference A ¦ Zero sequence | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1663 |  | 301664 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Power (P) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1664 |  | 301665 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Reactive power (Q) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1665 |  | 301666 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Apparent power (S) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1666 |  | 301667 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Power (P) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1667 |  | 301668 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Reactive power (Q) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1668 |  | 301669 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Apparent power (S) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1669 |  | 301670 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Power (P) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1670 |  | 301671 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Reactive power (Q) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1671 |  | 301672 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Apparent power (S) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1672 |  | 301673 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference A - Frequency (f) (from voltage) - Reference A ¦ Avg. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1700 |  | 301701 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ L1-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1701 |  | 301702 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ L2-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1702 |  | 301703 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ L3-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1703 |  | 301704 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1704 |  | 301705 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ L-N min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1705 |  | 301706 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ L-N max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1706 |  | 301707 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ L-N unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1707 |  | 301708 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ L1-L2 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1708 |  | 301709 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ L2-L3 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1709 |  | 301710 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ L3-L1 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1710 |  | 301711 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ L-L min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1711 |  | 301712 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ L-L max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1712 |  | 301713 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ L-L unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1713 |  | 301714 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Frequency (f) - Reference B ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1714 |  | 301715 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Frequency (f) - Reference B ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1715 |  | 301716 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Frequency (f) - Reference B ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1716 |  | 301717 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Frequency (f) - Reference B ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1717 |  | 301718 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Frequency (f) - Reference B ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1718 |  | 301719 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Phase angle - Reference B ¦ Phase angle L1-L2 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1719 |  | 301720 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Phase angle - Reference B ¦ Phase angle L2-L3 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1720 |  | 301721 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Phase angle - Reference B ¦ Phase angle L3-L1 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1721 |  | 301722 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ Positive sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1722 |  | 301723 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ Negative sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1723 |  | 301724 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Voltage (V) - Reference B ¦ Zero sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1724 |  | 301725 | Functions - Analogue output functions - Transducers - Transducer 3 - Reference B - Frequency (f) - Reference B ¦ Avg. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
4th current ACM measurements | 1750 |  | 301751 | Functions - Analogue output functions - Transducers - Transducer 3 - 4th current input - Current (I) - L4 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
4th current ACM measurements | 1751 |  | 301752 | Functions - Analogue output functions - Transducers - Transducer 3 - 4th current input - Power (P) - L4 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
4th current ACM measurements | 1752 |  | 301753 | Functions - Analogue output functions - Transducers - Transducer 3 - 4th current input - Reactive power (Q) - L4 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
4th current ACM measurements | 1753 |  | 301754 | Functions - Analogue output functions - Transducers - Transducer 3 - 4th current input - Apparent power (S) - L4 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
4th current ACM measurements | 1754 |  | 301755 | Functions - Analogue output functions - Transducers - Transducer 3 - 4th current input - Frequency (f) - L4 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
4th current ACM measurements | 1755 |  | 301756 | Functions - Analogue output functions - Transducers - Transducer 3 - 4th current input - Phase angle - L4 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
4th current ACM measurements | 1756 |  | 301757 | Functions - Analogue output functions - Transducers - Transducer 3 - 4th current input - Power factor (PF) - L4 ¦ cos phi | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
4th current ACM measurements | 1757 |  | 301758 | Functions - Analogue output functions - Transducers - Transducer 3 - 4th current input - Power factor (PF) - L4 ¦ Power factor | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1800 |  | 301801 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ L1-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1801 |  | 301802 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ L2-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1802 |  | 301803 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ L3-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1803 |  | 301804 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1804 |  | 301805 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ L-N min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1805 |  | 301806 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ L-N max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1806 |  | 301807 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ L-N unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1807 |  | 301808 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ L1-L2 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1808 |  | 301809 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ L2-L3 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1809 |  | 301810 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ L3-L1 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1810 |  | 301811 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ L-L min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1811 |  | 301812 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ L-L max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1812 |  | 301813 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ L-L unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1813 |  | 301814 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Frequency (f) (from voltage) - Reference A ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1814 |  | 301815 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Frequency (f) (from voltage) - Reference A ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1815 |  | 301816 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Frequency (f) (from voltage) - Reference A ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1816 |  | 301817 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Frequency (f) (from voltage) - Reference A ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1817 |  | 301818 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Frequency (f) (from voltage) - Reference A ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1818 |  | 301819 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Frequency (f) (from current) - Reference A ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1819 |  | 301820 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Frequency (f) (from current) - Reference A ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1820 |  | 301821 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Phase angle - Reference A ¦ Phase angle L1-L2 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1821 |  | 301822 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Phase angle - Reference A ¦ Phase angle L2-L3 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1822 |  | 301823 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Phase angle - Reference A ¦ Phase angle L3-L1 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1823 |  | 301824 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Phase angle - Reference A ¦ Phase angle L1 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1824 |  | 301825 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Phase angle - Reference A ¦ Phase angle L2 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1825 |  | 301826 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Phase angle - Reference A ¦ Phase angle L3 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1826 |  | 301827 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Current (I) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1827 |  | 301828 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Current (I) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1828 |  | 301829 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Current (I) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1829 |  | 301830 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Current (I) - Reference A ¦ N | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1830 |  | 301831 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Current (I) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1831 |  | 301832 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Current (I) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1832 |  | 301833 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Current (I) - Reference A ¦ Unbalanced nominal | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1833 |  | 301834 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Current (I) - Reference A ¦ Unbalanced average | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1834 |  | 301835 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Frequency (f) (from current) - Reference A ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1835 |  | 301836 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Frequency (f) (from current) - Reference A ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1836 |  | 301837 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Frequency (f) (from current) - Reference A ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1837 |  | 301838 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Power (P) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1838 |  | 301839 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Power (P) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1839 |  | 301840 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Power (P) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1840 |  | 301841 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Power (P) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1841 |  | 301842 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Power (P) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1842 |  | 301843 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Power (P) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1843 |  | 301844 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Reactive power (Q) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1844 |  | 301845 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Reactive power (Q) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1845 |  | 301846 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Reactive power (Q) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1846 |  | 301847 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Reactive power (Q) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1847 |  | 301848 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Reactive power (Q) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1848 |  | 301849 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Reactive power (Q) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1849 |  | 301850 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Apparent power (S) - Reference A ¦ L1 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1850 |  | 301851 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Apparent power (S) - Reference A ¦ L2 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1851 |  | 301852 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Apparent power (S) - Reference A ¦ L3 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1852 |  | 301853 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Apparent power (S) - Reference A ¦ Min. | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1853 |  | 301854 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Apparent power (S) - Reference A ¦ Max. | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1854 |  | 301855 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Apparent power (S) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1855 |  | 301856 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Power factor (PF) - Reference A ¦ cos phi | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1856 |  | 301857 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Power factor (PF) - Reference A ¦ Power factor | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1857 |  | 301858 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ Positive sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1858 |  | 301859 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Current (I) - Reference A ¦ Positive sequence | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1859 |  | 301860 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ Negative sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1860 |  | 301861 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Current (I) - Reference A ¦ Negative sequence | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1861 |  | 301862 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Voltage (V) - Reference A ¦ Zero sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1862 |  | 301863 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Current (I) - Reference A ¦ Zero sequence | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1863 |  | 301864 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Power (P) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1864 |  | 301865 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Reactive power (Q) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1865 |  | 301866 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Apparent power (S) - Reference A ¦ Total | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1866 |  | 301867 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Power (P) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1867 |  | 301868 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Reactive power (Q) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1868 |  | 301869 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Apparent power (S) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1869 |  | 301870 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Power (P) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1870 |  | 301871 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Reactive power (Q) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1871 |  | 301872 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Apparent power (S) - Reference A ¦ Available | INT16 | X * 1 | X * 1 | % | X | X | X | X | X | X | X
[Controlled equipment] ACM measurements | 1872 |  | 301873 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference A - Frequency (f) (from voltage) - Reference A ¦ Avg. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1900 |  | 301901 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ L1-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1901 |  | 301902 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ L2-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1902 |  | 301903 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ L3-N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1903 |  | 301904 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ N | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1904 |  | 301905 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ L-N min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1905 |  | 301906 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ L-N max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1906 |  | 301907 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ L-N unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1907 |  | 301908 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ L1-L2 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1908 |  | 301909 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ L2-L3 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1909 |  | 301910 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ L3-L1 | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1910 |  | 301911 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ L-L min. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1911 |  | 301912 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ L-L max. | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1912 |  | 301913 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ L-L unbalanced | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1913 |  | 301914 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Frequency (f) - Reference B ¦ L1 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1914 |  | 301915 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Frequency (f) - Reference B ¦ L2 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1915 |  | 301916 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Frequency (f) - Reference B ¦ L3 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1916 |  | 301917 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Frequency (f) - Reference B ¦ Min. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1917 |  | 301918 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Frequency (f) - Reference B ¦ Max. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1918 |  | 301919 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Phase angle - Reference B ¦ Phase angle L1-L2 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1919 |  | 301920 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Phase angle - Reference B ¦ Phase angle L2-L3 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1920 |  | 301921 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Phase angle - Reference B ¦ Phase angle L3-L1 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1921 |  | 301922 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ Positive sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1922 |  | 301923 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ Negative sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1923 |  | 301924 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Voltage (V) - Reference B ¦ Zero sequence | INT16 | X * 1 | X * 1 | V | X | X | X | X | X | X | X
[Busbar] ACM measurements | 1924 |  | 301925 | Functions - Analogue output functions - Transducers - Transducer 4 - Reference B - Frequency (f) - Reference B ¦ Avg. | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
4th current ACM measurements | 1950 |  | 301951 | Functions - Analogue output functions - Transducers - Transducer 4 - 4th current input - Current (I) - L4 | INT16 | X * 1 | X * 1 | A | X | X | X | X | X | X | X
4th current ACM measurements | 1951 |  | 301952 | Functions - Analogue output functions - Transducers - Transducer 4 - 4th current input - Power (P) - L4 | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
4th current ACM measurements | 1952 |  | 301953 | Functions - Analogue output functions - Transducers - Transducer 4 - 4th current input - Reactive power (Q) - L4 | INT16 | X * 1 | X * 1 | kvar | X | X | X | X | X | X | X
4th current ACM measurements | 1953 |  | 301954 | Functions - Analogue output functions - Transducers - Transducer 4 - 4th current input - Apparent power (S) - L4 | INT16 | X * 1 | X * 1 | kVA | X | X | X | X | X | X | X
4th current ACM measurements | 1954 |  | 301955 | Functions - Analogue output functions - Transducers - Transducer 4 - 4th current input - Frequency (f) - L4 | INT16 | X * 100 | X * 0.01 | Hz | X | X | X | X | X | X | X
4th current ACM measurements | 1955 |  | 301956 | Functions - Analogue output functions - Transducers - Transducer 4 - 4th current input - Phase angle - L4 | INT16 | X * 10 | X * 0.1 | ° | X | X | X | X | X | X | X
4th current ACM measurements | 1956 |  | 301957 | Functions - Analogue output functions - Transducers - Transducer 4 - 4th current input - Power factor (PF) - L4 ¦ cos phi | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
4th current ACM measurements | 1957 |  | 301958 | Functions - Analogue output functions - Transducers - Transducer 4 - 4th current input - Power factor (PF) - L4 ¦ Power factor | INT16 | X * 10000 | X * 0.0001 |  | X | X | X | X | X | X | X
[Controlled equipment] ACM3.2 measurements | 2000 |  | 302001 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ L1 (Consumer side) | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2001 |  | 302002 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ L2 (Consumer side) | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2002 |  | 302003 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ L3 (Consumer side) | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2003 |  | 302004 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ Min. (Consumer side) | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2004 |  | 302005 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ Max. (Consumer side) | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2025 |  | 302026 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ L1 (Neutral side) | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2026 |  | 302027 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ L2 (Neutral side) | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2027 |  | 302028 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ L3 (Neutral side) | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2028 |  | 302029 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ Min. (Neutral side) | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2029 |  | 302030 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ Max. (Neutral side) | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2050 |  | 302051 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ L1 differential | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2051 |  | 302052 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ L2 differential | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2052 |  | 302053 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ L3 differential | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2053 |  | 302054 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ Min. differential | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2054 |  | 302055 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ Max. differential | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2055 |  | 302056 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ L1 restraint | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2056 |  | 302057 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ L2 restraint | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2057 |  | 302058 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ L3 restraint | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2058 |  | 302059 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ Min. restraint | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2059 |  | 302060 | Functions - Analogue output functions - Generator - Current (I) - ACM3.2 - Generator ¦ Max. restraint | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
[Controlled equipment] ACM3.2 measurements | 2060 |  | 302061 | Functions - Analogue output functions - Generator - Frequency (f) - ACM3.2 - Generator ¦ Frequency | INT16 | X * 100 | X * 0.01 | Hz | X |  | X | X | X
CAN bus measurements | 6000 |  | 306001 | Functions - Analogue output functions - Engine - ECU - Speed - Engine speed | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
CAN bus measurements | 6001 |  | 306002 | Functions - Analogue output functions - Engine - ECU - Coolant - Engine coolant temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6002 |  | 306003 | Functions - Analogue output functions - Engine - ECU - Lube oil - Engine oil pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6003 |  | 306004 | Engine requested speed | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
CAN bus measurements | 6004 |  | 306005 | Functions - Analogue output functions - Engine - ECU - Information - Number of actual faults | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6005 |  | 306006 | Functions - Analogue output functions - Engine - ECU - Lube oil - Engine oil temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6006 |  | 306007 | Functions - Analogue output functions - Engine - ECU - Fuel - Fuel temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6007 |  | 306008 | Functions - Analogue output functions - Engine - ECU - Intake - Boost pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6008 |  | 306009 | Functions - Analogue output functions - Engine - ECU - Intake - Air inlet temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6009 |  | 306010 | Functions - Analogue output functions - Engine - ECU - Coolant - Coolant level | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6010 |  | 306011 | Functions - Analogue output functions - Engine - ECU - Fuel - Fuel rate | INT16 | X * 1 | X * 1 | L/h | X |  | X | X | X
CAN bus measurements | 6011 |  | 306012 | Functions - Analogue output functions - Engine - ECU - Intake - Engine intake manifold 1 temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6012 |  | 306013 | Functions - Analogue output functions - Engine - ECU - Engine load - Drivers demand engine percent torque | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6013 |  | 306014 | Functions - Analogue output functions - Engine - ECU - Engine load - Actual engine - percent torque | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6014 |  | 306015 | Functions - Analogue output functions - Engine - ECU - Speed - Accelerator pedal position | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6015 |  | 306016 | Functions - Analogue output functions - Engine - ECU - Engine load - Percent load at current speed | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6016 |  | 306017 | Functions - Analogue output functions - Engine - ECU - Intake - Air inlet pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6017 |  | 306018 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust gas temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6018 |  | 306019 | Functions - Analogue output functions - Engine - ECU - Engine counters - Engine hours | INT16 | X * 1 | X * 1 | h | X |  | X | X | X
CAN bus measurements | 6019 |  | 306020 | Functions - Analogue output functions - Engine - ECU - Lube oil - Engine oil filter differential pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6020 |  | 306021 | Functions - Analogue output functions - Engine - ECU - Information - Battery potential voltage switched | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
CAN bus measurements | 6021 |  | 306022 | Functions - Analogue output functions - Engine - ECU - Fuel - Fuel delivery pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6022 |  | 306023 | Functions - Analogue output functions - Engine - ECU - Lube oil - Engine oil level | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6023 |  | 306024 | Functions - Analogue output functions - Engine - ECU - Information - Crankcase pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6024 |  | 306025 | Functions - Analogue output functions - Engine - ECU - Coolant - Coolant pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6025 |  | 306026 | Functions - Analogue output functions - Engine - ECU - Fuel - Water in fuel indicator | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6026 |  | 306027 | Functions - Analogue output functions - Engine - ECU - Turbo charger - Turbo oil temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6027 |  | 306028 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Particulate trap inlet pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6028 |  | 306029 | Functions - Analogue output functions - Engine - ECU - Intake - Air filter differential pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6029 |  | 306030 | Functions - Analogue output functions - Engine - ECU - Coolant - Coolant filter differential pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6030 |  | 306031 | Functions - Analogue output functions - Engine - ECU - Air ambient - Atmospheric pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6031 |  | 306032 | Functions - Analogue output functions - Engine - ECU - Air ambient - Ambient air temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6032 |  | 306033 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust temperature right | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6033 |  | 306034 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust temperature left | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6034 |  | 306035 | Functions - Analogue output functions - Engine - ECU - Intake - Engine intercooler temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6035 |  | 306036 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine trip fuel | INT16 | X * 1 | X * 1 | L | X |  | X | X | X
CAN bus measurements | 6036 |  | 306037 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine total fuel used | INT16 | X * 1 | X * 1 | L | X |  | X | X | X
CAN bus measurements | 6037 |  | 306038 | Functions - Analogue output functions - Engine - ECU - Fuel - Trip fuel gaseous | INT16 | X * 1 | X * 1 | kg | X |  | X | X | X
CAN bus measurements | 6038 |  | 306039 | Functions - Analogue output functions - Engine - ECU - Fuel - Total fuel used gaseous | INT16 | X * 1 | X * 1 | kg | X |  | X | X | X
CAN bus measurements | 6039 |  | 306040 | Functions - Analogue output functions - Engine - ECU - Fuel - Mean trip fuel consumption | INT16 | X * 1 | X * 1 | L/h | X |  | X | X | X
CAN bus measurements | 6040 |  | 306041 | Functions - Analogue output functions - Engine - ECU - Engine load - Nominal power | INT16 | X * 1 | X * 1 | kW | X |  | X | X | X
CAN bus measurements | 6041 |  | 306042 | Functions - Analogue output functions - Engine - ECU - Intake - Engine intake manifold 1 absolute pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6042 |  | 306043 | Functions - Analogue output functions - Engine - ECU - DPF - Diesel particulate filter lamp command | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6043 |  | 306044 | Functions - Analogue output functions - Engine - ECU - DPF - Diesel particulate filter active regeneration inhibited | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6044 |  | 306045 | Functions - Analogue output functions - Engine - ECU - DPF - Diesel particulate filter active regeneration status | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6045 |  | 306046 | Functions - Analogue output functions - Engine - ECU - DPF - Diesel particulate filter regeneration status | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6046 |  | 306047 | Functions - Analogue output functions - Engine - ECU - Information - Exhaust system high temperature lamp command | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6047 |  | 306048 | Functions - Analogue output functions - Engine - ECU - Intake - Air filter differential pressure 2 | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6048 |  | 306049 | Functions - Analogue output functions - Engine - ECU - Fuel - Fuel supply pump inlet pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6049 |  | 306050 | Functions - Analogue output functions - Engine - ECU - Fuel - Fuel filter (suction side) differential pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6050 |  | 306051 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine fuel filter differential pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6051 |  | 306052 | Functions - Analogue output functions - Engine - ECU - Information - Engine ECU temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6052 |  | 306053 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 01 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6053 |  | 306054 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 02 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6054 |  | 306055 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 03 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6055 |  | 306056 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 04 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6056 |  | 306057 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 05 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6057 |  | 306058 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 06 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6058 |  | 306059 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 07 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6059 |  | 306060 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 08 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6060 |  | 306061 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 09 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6061 |  | 306062 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 10 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6062 |  | 306063 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 11 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6063 |  | 306064 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 12 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6064 |  | 306065 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 13 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6065 |  | 306066 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 14 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6066 |  | 306067 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 15 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6067 |  | 306068 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 16 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6068 |  | 306069 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 17 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6069 |  | 306070 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 18 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6070 |  | 306071 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 19 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6071 |  | 306072 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Exhaust port temperature 20 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6072 |  | 306073 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine filtered fuel delivery pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6073 |  | 306074 | Functions - Analogue output functions - Engine - ECU - Coolant - Engine coolant temperature 2 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6074 |  | 306075 | Functions - Analogue output functions - Engine - ECU - Coolant - Engine coolant temperature 3 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6075 |  | 306076 | Functions - Analogue output functions - Engine - ECU - Coolant - Engine coolant pump outlet temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6076 |  | 306077 | Functions - Analogue output functions - Engine - ECU - Coolant - Engine auxiliary coolant temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6077 |  | 306078 | Functions - Analogue output functions - Engine - ECU - Turbo charger - Engine turbocharger 1 turbine intake temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6078 |  | 306079 | Functions - Analogue output functions - Engine - ECU - Turbo charger - Engine turbocharger 2 turbine intake temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6079 |  | 306080 | Functions - Analogue output functions - Engine - ECU - Coolant - Engine auxiliary coolant pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6080 |  | 306081 | Functions - Analogue output functions - Engine - ECU - Information - Ambient conditions 2 specific humidity | INT16 | X * 1 | X * 1 | g/kg | X |  | X | X | X
CAN bus measurements | 6081 |  | 306082 | Functions - Analogue output functions - Engine - ECU - Turbo charger - Engine turbocharger 2 speed | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
CAN bus measurements | 6082 |  | 306083 | Functions - Analogue output functions - Engine - ECU - Turbo charger - Engine turbocharger 3 speed | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
CAN bus measurements | 6083 |  | 306084 | Functions - Analogue output functions - Engine - ECU - Engine counters - Trip engine running time | INT16 | X * 1 | X * 1 | h | X |  | X | X | X
CAN bus measurements | 6084 |  | 306085 | Functions - Analogue output functions - Engine - ECU - Engine counters - Trip idle time | INT16 | X * 1 | X * 1 | h | X |  | X | X | X
CAN bus measurements | 6085 |  | 306086 | Functions - Analogue output functions - Engine - ECU - Turbo charger - Engine turbocharger 1 speed | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
CAN bus measurements | 6086 |  | 306087 | Functions - Analogue output functions - Engine - ECU - Engine load - Nominal friction - percent torque | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6087 |  | 306088 | Functions - Analogue output functions - Engine - ECU - Information - Engines desired operating speed | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
CAN bus measurements | 6088 |  | 306089 | Functions - Analogue output functions - Engine - ECU - Intake - Engine intake manifold 2 temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6089 |  | 306090 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 diesel exhaust fluid tank level | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6090 |  | 306091 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 diesel exhaust fluid tank temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6091 |  | 306092 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 intake NOx | INT16 | X * 1 | X * 1 | ppm | X |  | X | X | X
CAN bus measurements | 6092 |  | 306093 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 outlet NOx | INT16 | X * 1 | X * 1 | ppm | X |  | X | X | X
CAN bus measurements | 6093 |  | 306094 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 DEF actual dosing quantity | INT16 | X * 1 | X * 1 | g/h | X |  | X | X | X
CAN bus measurements | 6094 |  | 306095 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 DEF doser absolute pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6095 |  | 306096 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 SCR dosing air assist valve | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6096 |  | 306097 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 DEF dosing requested quantity | INT16 | X * 1 | X * 1 | g/h | X |  | X | X | X
CAN bus measurements | 6097 |  | 306098 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 SCR catalyst intake gas temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6098 |  | 306099 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 SCR catalyst outlet gas temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6099 |  | 306100 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 2 intake NOx | INT16 | X * 1 | X * 1 | ppm | X |  | X | X | X
CAN bus measurements | 6100 |  | 306101 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 2 outlet NOx | INT16 | X * 1 | X * 1 | ppm | X |  | X | X | X
CAN bus measurements | 6101 |  | 306102 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 2 DEF actual dosing quantity | INT16 | X * 1 | X * 1 | g/h | X |  | X | X | X
CAN bus measurements | 6102 |  | 306103 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 2 DEF dosing absolute pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6103 |  | 306104 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 2 SCR dosing air assist valve | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6104 |  | 306105 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 2 DEF dosing requested quantity | INT16 | X * 1 | X * 1 | g/h | X |  | X | X | X
CAN bus measurements | 6105 |  | 306106 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 2 SCR catalyst intake gas temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6106 |  | 306107 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 2 SCR catalyst outlet gas temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6107 |  | 306108 | Functions - Analogue output functions - Engine - ECU - Lube oil - Engine oil-filter outlet pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6108 |  | 306109 | Functions - Analogue output functions - Engine - ECU - Information - Engine operating state | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6109 |  | 306110 | Functions - Analogue output functions - Engine - ECU - Information - Source address of controlling device | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6110 |  | 306111 | Functions - Analogue output functions - Engine - ECU - Speed - Engine rated speed | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
CAN bus measurements | 6111 |  | 306112 | Functions - Analogue output functions - Engine - ECU - Speed - Engine speed at idle point 1 | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
CAN bus measurements | 6112 |  | 306113 | Functions - Analogue output functions - Engine - ECU - Information - ECU identification information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6113 |  | 306114 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment SCR operator inducement severity | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6114 |  | 306115 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment SCR operator inducement active | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6115 |  | 306116 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 DPF outlet gas temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6116 |  | 306117 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 DPF time to next active regeneration | INT16 | X * 1 | X * 1 | h | X |  | X | X | X
CAN bus measurements | 6117 |  | 306118 | Functions - Analogue output functions - Engine - ECU - Intake - Engine charge air cooler 1 outlet temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6118 |  | 306119 | Functions - Analogue output functions - Engine - ECU - DPF - Diesel particulate filter 1 soot load percent | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6119 |  | 306120 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 DEF average consumption | INT16 | X * 1 | X * 1 | L/h | X |  | X | X | X
CAN bus measurements | 6120 |  | 306121 | Functions - Analogue output functions - Engine - ECU - Information - Engine operating derate request | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6121 |  | 306122 | Functions - Analogue output functions - Engine - ECU - Information - SW identification | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6122 |  | 306123 | Functions - Analogue output functions - Engine - ECU - Engine load - Engine demand - percent torque | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6123 |  | 306124 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 intake percent oxygen 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6124 |  | 306125 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 outlet percent oxygen 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6125 |  | 306126 | Functions - Analogue output functions - Engine - ECU - Information - Engine throttle actuator 1 control command | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6126 |  | 306127 | Functions - Analogue output functions - Engine - ECU - Information - Long-term fuel trim | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6127 |  | 306128 | Functions - Analogue output functions - Engine - ECU - Information - Short-term fuel trim | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6128 |  | 306129 | Functions - Analogue output functions - Engine - ECU - Exhaust gas - Engine exhaust gas oxygen sensor closed loop operation | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6129 |  | 306130 | Functions - Analogue output functions - Engine - ECU - Information - Engine desired ignition timing no 1 | INT16 | X * 1 | X * 1 | ° | X |  | X | X | X
CAN bus measurements | 6130 |  | 306131 | Functions - Analogue output functions - Engine - ECU - Information - Engine actual ignition timing | INT16 | X * 1 | X * 1 | ° | X |  | X | X | X
CAN bus measurements | 6131 |  | 306132 | Functions - Analogue output functions - Engine - ECU - Information - Engine amber warning lamp command | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6132 |  | 306133 | Functions - Analogue output functions - Engine - ECU - Information - Engine red stop lamp command | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6133 |  | 306134 | Accelerator pedal position | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6134 |  | 306135 | Functions - Analogue output functions - Engine - ECU - Information - Engine Starter Mode | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6135 |  | 306136 | Functions - Analogue output functions - Engine - ECU - Engine load - Actual Maximum Available Engine - Percent Torque | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6136 |  | 306137 | Functions - Analogue output functions - Engine - ECU - Coolant - Engine Coolant Pre-heated State | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6137 |  | 306138 | Functions - Analogue output functions - Engine - ECU - Intake - Engine Intake Manifold 3 Temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6138 |  | 306139 | Functions - Analogue output functions - Engine - ECU - Intake - Engine Intake Manifold 4 Temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6139 |  | 306140 | Functions - Analogue output functions - Engine - ECU - Lube oil - Engine Oil Filter Intake Pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6140 |  | 306141 | Functions - Analogue output functions - Engine - ECU - Turbo charger - Engine Turbocharger 2 Boost Pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6141 |  | 306142 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine Fuel 1 Injector Metering Rail 1 Pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6142 |  | 306143 | Functions - Analogue output functions - Engine - ECU - Information - Battery Potential / Power Input 1 | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
CAN bus measurements | 6143 |  | 306144 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 Exhaust Temperature 1 | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6144 |  | 306145 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 Exhaust Gas Mass Flow Rate | INT16 | X * 1 | X * 1 | kg/h | X |  | X | X | X
CAN bus measurements | 6145 |  | 306146 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 Diesel Particulate Filter Differential Pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6146 |  | 306147 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 Diesel Oxidation Catalyst Intake Temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6147 |  | 306148 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 Diesel Particulate Filter Intake Temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6148 |  | 306149 | Functions - Analogue output functions - Engine - ECU - DPF - Diesel Particulate Filter Active Regeneration Inhibited Due to Out of Neutral | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6149 |  | 306150 | Functions - Analogue output functions - Engine - ECU - DPF - Diesel Particulate Filter Active Regeneration Inhibited Due to Parking Brake Not Set | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6150 |  | 306151 | Functions - Analogue output functions - Engine - ECU - DPF - Operator Inducement Time to Torque Derate Level 1 | INT16 | X * 1 | X * 1 | min | X |  | X | X | X
CAN bus measurements | 6151 |  | 306152 | Functions - Analogue output functions - Engine - ECU - DPF - Operator Inducement Time to Torque Derate Level 2 | INT16 | X * 1 | X * 1 | min | X |  | X | X | X
CAN bus measurements | 6152 |  | 306153 | Functions - Analogue output functions - Engine - ECU - Information - Transmission Neutral Switch | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6153 |  | 306154 | Functions - Analogue output functions - Engine - ECU - Information - Alternator 1 Status | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6154 |  | 306155 | Functions - Analogue output functions - Engine - ECU - Lube oil - Engine Oil Viscosity | INT16 | X * 1 | X * 1 | cp | X |  | X | X | X
CAN bus measurements | 6155 |  | 306156 | Functions - Analogue output functions - Engine - ECU - Lube oil - Engine Oil Density | INT16 | X * 1 | X * 1 | g/cc | X |  | X | X | X
CAN bus measurements | 6156 |  | 306157 | Functions - Analogue output functions - Engine - ECU - Lube oil - Engine Oil Relative Dielectricity (High Resolution) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6157 |  | 306158 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine Fuel Dynamic Viscosity | INT16 | X * 1 | X * 1 | cp | X |  | X | X | X
CAN bus measurements | 6158 |  | 306159 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine Fuel Density | INT16 | X * 1 | X * 1 | g/cc | X |  | X | X | X
CAN bus measurements | 6159 |  | 306160 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine Fuel Dielectricity (High Resolution) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6160 |  | 306161 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine Fuel 1 Temperature 1 (High Resolution) | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
CAN bus measurements | 6161 |  | 306162 | Functions - Analogue output functions - Engine - ECU - Lube oil - Engine Oil Filter Differential Pressure (Extended Range) | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6162 |  | 306163 | Functions - Analogue output functions - Engine - ECU - Intake - Engine Air Filter 3 Differential Pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6163 |  | 306164 | Functions - Analogue output functions - Engine - ECU - Intake - Engine Air Filter 4 Differential Pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6164 |  | 306165 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine Throttle Valve 1 Position 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6165 |  | 306166 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine Fuel Valve 1 Intake Absolute Pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6166 |  | 306167 | Functions - Analogue output functions - Engine - ECU - Turbo charger - Engine Turbocharger 1 Boost Pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6167 |  | 306168 | Functions - Analogue output functions - Engine - ECU - Information - Engine Cylinder 1 Ignition Timing | INT16 | X * 1 | X * 1 | ° | X |  | X | X | X
CAN bus measurements | 6168 |  | 306169 | Functions - Analogue output functions - Engine - ECU - Intake - Engine Intake Air Mass Flow Rate | INT16 | X * 1 | X * 1 | kg/h | X |  | X | X | X
CAN bus measurements | 6169 |  | 306170 | Functions - Analogue output functions - Engine - ECU - DPF - Aftertreatment 1 Diesel Particulate Filter Ash Load Percent | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6170 |  | 306171 | Functions - Analogue output functions - Engine - ECU - Information - Engine Fan 1 Estimated Percent Speed | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6171 |  | 306172 | Functions - Analogue output functions - Engine - ECU - Information - Battery Charger 1 Output Voltage | INT16 | X * 1 | X * 1 | V | X |  | X | X | X
CAN bus measurements | 6172 |  | 306173 | Functions - Analogue output functions - Engine - ECU - Information - Battery Charger 1 Output Current | INT16 | X * 1 | X * 1 | A | X |  | X | X | X
CAN bus measurements | 6173 |  | 306174 | Red lamp from ECU1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6174 |  | 306175 | Amber lamp from ECU1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6175 |  | 306176 | Protect lamp from ECU1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6176 |  | 306177 | Malfunction lamp from ECU1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6177 |  | 306178 | Red lamp from ECU2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6178 |  | 306179 | Amber lamp from ECU2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6179 |  | 306180 | Protect lamp from ECU2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6180 |  | 306181 | Malfunction lamp from ECU2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6183 |  | 306184 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine Fuel Leakage 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6184 |  | 306185 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine Fuel Leakage 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6185 |  | 306186 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine Fuel Rate | INT16 | X * 1 | X * 1 | L/h | X |  | X | X | X
CAN bus measurements | 6186 |  | 306187 | Functions - Analogue output functions - Engine - ECU - Information - Accelerator Pedal 1 Low Idle Switch | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6187 |  | 306188 | Functions - Analogue output functions - Engine - ECU - Information - Accelerator Pedal Position 2 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6188 |  | 306189 | Functions - Analogue output functions - Engine - ECU - Fuel - Fuel Level 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6189 |  | 306190 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine Fuel Valve 1 Outlet Absolute Pressure | INT16 | X * 1 | X * 1 | bar | X |  | X | X | X
CAN bus measurements | 6190 |  | 306191 | Functions - Analogue output functions - Engine - ECU - Fuel - Engine Fuel Valve 1 Position | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
CAN bus measurements | 6500 |  | 306501 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 1 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6502 |  | 306503 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6503 |  | 306504 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6504 |  | 306505 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 2 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6506 |  | 306507 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6507 |  | 306508 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6508 |  | 306509 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 3 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6510 |  | 306511 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 3 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6511 |  | 306512 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 3 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6512 |  | 306513 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 4 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6514 |  | 306515 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 4 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6515 |  | 306516 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 4 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6516 |  | 306517 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 5 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6518 |  | 306519 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 5 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6519 |  | 306520 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 5 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6520 |  | 306521 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 6 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6522 |  | 306523 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 6 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6523 |  | 306524 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 6 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6524 |  | 306525 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 7 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6526 |  | 306527 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 7 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6527 |  | 306528 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 7 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6528 |  | 306529 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 8 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6530 |  | 306531 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 8 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6531 |  | 306532 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 8 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6532 |  | 306533 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 9 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6534 |  | 306535 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 9 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6535 |  | 306536 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 9 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6536 |  | 306537 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 10 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6538 |  | 306539 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 10 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6539 |  | 306540 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 10 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6540 |  | 306541 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 11 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6542 |  | 306543 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 11 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6543 |  | 306544 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 11 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6544 |  | 306545 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 12 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6546 |  | 306547 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 12 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6547 |  | 306548 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 12 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6548 |  | 306549 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 13 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6550 |  | 306551 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 13 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6551 |  | 306552 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 13 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6552 |  | 306553 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 14 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6554 |  | 306555 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 14 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6555 |  | 306556 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 14 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6556 |  | 306557 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 15 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6558 |  | 306559 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 15 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6559 |  | 306560 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 15 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6560 |  | 306561 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 16 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6562 |  | 306563 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 16 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6563 |  | 306564 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 16 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6564 |  | 306565 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 17 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6566 |  | 306567 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 17 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6567 |  | 306568 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 17 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6568 |  | 306569 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 18 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6570 |  | 306571 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 18 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6571 |  | 306572 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 18 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6572 |  | 306573 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 19 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6574 |  | 306575 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 19 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6575 |  | 306576 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 19 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6576 |  | 306577 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 20 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6578 |  | 306579 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 20 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6579 |  | 306580 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 20 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6580 |  | 306581 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 21 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6582 |  | 306583 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 21 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6583 |  | 306584 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 21 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6584 |  | 306585 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 22 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6586 |  | 306587 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 22 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6587 |  | 306588 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 22 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6588 |  | 306589 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 23 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6590 |  | 306591 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 23 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6591 |  | 306592 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 23 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6592 |  | 306593 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 24 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6594 |  | 306595 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 24 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6595 |  | 306596 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 24 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6596 |  | 306597 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 SPN 25 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6598 |  | 306599 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 FMI 25 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6599 |  | 306600 | Functions - Analogue output functions - Engine - Diagnostic - Active alarms - J1939 DM1 OC 25 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6600 |  | 306601 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 1 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6602 |  | 306603 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6603 |  | 306604 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6604 |  | 306605 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 2 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6606 |  | 306607 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6607 |  | 306608 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6608 |  | 306609 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 3 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6610 |  | 306611 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 3 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6611 |  | 306612 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 3 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6612 |  | 306613 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 4 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6614 |  | 306615 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 4 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6615 |  | 306616 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 4 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6616 |  | 306617 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 5 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6618 |  | 306619 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 5 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6619 |  | 306620 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 5 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6620 |  | 306621 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 6 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6622 |  | 306623 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 6 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6623 |  | 306624 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 6 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6624 |  | 306625 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 7 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6626 |  | 306627 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 7 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6627 |  | 306628 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 7 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6628 |  | 306629 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 8 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6630 |  | 306631 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 8 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6631 |  | 306632 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 8 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6632 |  | 306633 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 9 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6634 |  | 306635 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 9 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6635 |  | 306636 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 9 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6636 |  | 306637 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 10 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6638 |  | 306639 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 10 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6639 |  | 306640 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 10 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6640 |  | 306641 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 11 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6642 |  | 306643 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 11 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6643 |  | 306644 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 11 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6644 |  | 306645 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 12 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6646 |  | 306647 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 12 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6647 |  | 306648 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 12 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6648 |  | 306649 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 13 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6650 |  | 306651 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 13 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6651 |  | 306652 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 13 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6652 |  | 306653 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 14 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6654 |  | 306655 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 14 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6655 |  | 306656 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 14 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6656 |  | 306657 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 15 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6658 |  | 306659 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 15 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6659 |  | 306660 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 15 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6660 |  | 306661 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 16 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6662 |  | 306663 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 16 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6663 |  | 306664 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 16 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6664 |  | 306665 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 17 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6666 |  | 306667 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 17 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6667 |  | 306668 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 17 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6668 |  | 306669 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 18 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6670 |  | 306671 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 18 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6671 |  | 306672 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 18 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6672 |  | 306673 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 19 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6674 |  | 306675 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 19 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6675 |  | 306676 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 19 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6676 |  | 306677 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 20 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6678 |  | 306679 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 20 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6679 |  | 306680 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 20 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6680 |  | 306681 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 21 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6682 |  | 306683 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 21 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6683 |  | 306684 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 21 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6684 |  | 306685 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 22 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6686 |  | 306687 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 22 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6687 |  | 306688 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 22 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6688 |  | 306689 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 23 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6690 |  | 306691 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 23 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6691 |  | 306692 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 23 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6692 |  | 306693 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 24 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6694 |  | 306695 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 24 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6695 |  | 306696 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 24 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6696 |  | 306697 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 25 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6698 |  | 306699 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 25 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6699 |  | 306700 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 25 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6700 |  | 306701 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 26 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6702 |  | 306703 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 26 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6703 |  | 306704 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 26 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6704 |  | 306705 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 27 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6706 |  | 306707 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 27 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6707 |  | 306708 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 27 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6708 |  | 306709 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 28 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6710 |  | 306711 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 28 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6711 |  | 306712 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 28 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6712 |  | 306713 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 29 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6714 |  | 306715 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 29 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6715 |  | 306716 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 29 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6716 |  | 306717 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 30 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6718 |  | 306719 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 30 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6719 |  | 306720 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 30 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6720 |  | 306721 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 31 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6722 |  | 306723 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 31 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6723 |  | 306724 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 31 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6724 |  | 306725 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 32 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6726 |  | 306727 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 32 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6727 |  | 306728 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 32 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6728 |  | 306729 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 33 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6730 |  | 306731 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 33 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6731 |  | 306732 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 33 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6732 |  | 306733 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 34 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6734 |  | 306735 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 34 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6735 |  | 306736 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 34 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6736 |  | 306737 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 35 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6738 |  | 306739 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 35 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6739 |  | 306740 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 35 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6740 |  | 306741 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 36 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6742 |  | 306743 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 36 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6743 |  | 306744 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 36 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6744 |  | 306745 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 37 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6746 |  | 306747 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 37 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6747 |  | 306748 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 37 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6748 |  | 306749 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 38 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6750 |  | 306751 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 38 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6751 |  | 306752 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 38 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6752 |  | 306753 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 39 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6754 |  | 306755 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 39 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6755 |  | 306756 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 39 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6756 |  | 306757 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 40 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6758 |  | 306759 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 40 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6759 |  | 306760 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 40 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6760 |  | 306761 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 41 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6762 |  | 306763 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 41 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6763 |  | 306764 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 41 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6764 |  | 306765 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 42 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6766 |  | 306767 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 42 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6767 |  | 306768 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 42 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6768 |  | 306769 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 43 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6770 |  | 306771 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 43 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6771 |  | 306772 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 43 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6772 |  | 306773 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 44 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6774 |  | 306775 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 44 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6775 |  | 306776 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 44 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6776 |  | 306777 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 45 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6778 |  | 306779 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 45 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6779 |  | 306780 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 45 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6780 |  | 306781 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 46 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6782 |  | 306783 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 46 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6783 |  | 306784 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 46 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6784 |  | 306785 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 47 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6786 |  | 306787 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 47 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6787 |  | 306788 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 47 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6788 |  | 306789 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 48 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6790 |  | 306791 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 48 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6791 |  | 306792 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 48 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6792 |  | 306793 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 49 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6794 |  | 306795 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 49 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6795 |  | 306796 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 49 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6796 |  | 306797 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 50 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6798 |  | 306799 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 50 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6799 |  | 306800 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 50 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6800 |  | 306801 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 51 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6802 |  | 306803 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 51 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6803 |  | 306804 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 51 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6804 |  | 306805 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 52 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6806 |  | 306807 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 52 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6807 |  | 306808 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 52 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6808 |  | 306809 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 53 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6810 |  | 306811 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 53 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6811 |  | 306812 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 53 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6812 |  | 306813 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 54 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6814 |  | 306815 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 54 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6815 |  | 306816 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 54 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6816 |  | 306817 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 55 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6818 |  | 306819 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 55 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6819 |  | 306820 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 55 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6820 |  | 306821 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 56 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6822 |  | 306823 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 56 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6823 |  | 306824 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 56 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6824 |  | 306825 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 57 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6826 |  | 306827 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 57 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6827 |  | 306828 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 57 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6828 |  | 306829 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 58 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6830 |  | 306831 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 58 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6831 |  | 306832 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 58 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6832 |  | 306833 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 59 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6834 |  | 306835 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 59 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6835 |  | 306836 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 59 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6836 |  | 306837 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 60 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6838 |  | 306839 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 60 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6839 |  | 306840 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 60 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6840 |  | 306841 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 61 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6842 |  | 306843 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 61 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6843 |  | 306844 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 61 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6844 |  | 306845 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 62 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6846 |  | 306847 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 62 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6847 |  | 306848 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 62 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6848 |  | 306849 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 63 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6850 |  | 306851 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 63 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6851 |  | 306852 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 63 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6852 |  | 306853 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 64 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6854 |  | 306855 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 64 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6855 |  | 306856 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 64 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6856 |  | 306857 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 65 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6858 |  | 306859 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 65 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6859 |  | 306860 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 65 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6860 |  | 306861 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 66 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6862 |  | 306863 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 66 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6863 |  | 306864 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 66 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6864 |  | 306865 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 67 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6866 |  | 306867 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 67 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6867 |  | 306868 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 67 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6868 |  | 306869 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 68 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6870 |  | 306871 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 68 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6871 |  | 306872 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 68 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6872 |  | 306873 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 69 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6874 |  | 306875 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 69 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6875 |  | 306876 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 69 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6876 |  | 306877 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 70 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6878 |  | 306879 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 70 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6879 |  | 306880 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 70 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6880 |  | 306881 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 71 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6882 |  | 306883 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 71 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6883 |  | 306884 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 71 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6884 |  | 306885 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 72 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6886 |  | 306887 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 72 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6887 |  | 306888 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 72 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6888 |  | 306889 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 73 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6890 |  | 306891 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 73 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6891 |  | 306892 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 73 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6892 |  | 306893 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 74 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6894 |  | 306895 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 74 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6895 |  | 306896 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 74 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6896 |  | 306897 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 75 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6898 |  | 306899 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 75 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6899 |  | 306900 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 75 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6900 |  | 306901 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 76 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6902 |  | 306903 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 76 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6903 |  | 306904 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 76 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6904 |  | 306905 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 77 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6906 |  | 306907 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 77 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6907 |  | 306908 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 77 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6908 |  | 306909 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 78 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6910 |  | 306911 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 78 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6911 |  | 306912 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 78 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6912 |  | 306913 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 79 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6914 |  | 306915 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 79 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6915 |  | 306916 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 79 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6916 |  | 306917 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 80 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6918 |  | 306919 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 80 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6919 |  | 306920 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 80 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6920 |  | 306921 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 81 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6922 |  | 306923 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 81 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6923 |  | 306924 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 81 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6924 |  | 306925 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 82 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6926 |  | 306927 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 82 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6927 |  | 306928 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 82 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6928 |  | 306929 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 83 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6930 |  | 306931 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 83 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6931 |  | 306932 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 83 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6932 |  | 306933 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 84 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6934 |  | 306935 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 84 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6935 |  | 306936 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 84 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6936 |  | 306937 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 85 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6938 |  | 306939 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 85 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6939 |  | 306940 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 85 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6940 |  | 306941 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 86 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6942 |  | 306943 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 86 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6943 |  | 306944 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 86 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6944 |  | 306945 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 87 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6946 |  | 306947 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 87 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6947 |  | 306948 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 87 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6948 |  | 306949 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 88 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6950 |  | 306951 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 88 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6951 |  | 306952 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 88 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6952 |  | 306953 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 89 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6954 |  | 306955 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 89 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6955 |  | 306956 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 89 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6956 |  | 306957 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 90 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6958 |  | 306959 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 90 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6959 |  | 306960 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 90 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6960 |  | 306961 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 91 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6962 |  | 306963 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 91 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6963 |  | 306964 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 91 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6964 |  | 306965 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 92 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6966 |  | 306967 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 92 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6967 |  | 306968 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 92 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6968 |  | 306969 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 93 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6970 |  | 306971 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 93 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6971 |  | 306972 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 93 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6972 |  | 306973 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 94 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6974 |  | 306975 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 94 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6975 |  | 306976 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 94 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6976 |  | 306977 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 95 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6978 |  | 306979 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 95 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6979 |  | 306980 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 95 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6980 |  | 306981 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 96 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6982 |  | 306983 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 96 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6983 |  | 306984 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 96 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6984 |  | 306985 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 97 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6986 |  | 306987 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 97 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6987 |  | 306988 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 97 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6988 |  | 306989 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 98 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6990 |  | 306991 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 98 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6991 |  | 306992 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 98 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6992 |  | 306993 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 99 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6994 |  | 306995 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 99 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6995 |  | 306996 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 99 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6996 |  | 306997 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 SPN 100 | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6998 |  | 306999 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 FMI 100 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
CAN bus measurements | 6999 |  | 307000 | Functions - Analogue output functions - Engine - Diagnostic - Historical alarms - J1939 DM2 OC 100 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Status value | 8000 |  | 308001 | Engine state | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Status value | 8001 |  | 308002 | Functions - Analogue output functions - Engine - Measurements - Lube oil - Engine oil pressure | INT16 | X * 10 | X * 0.1 | bar | X |  | X | X | X
Status value | 8002 |  | 308003 | Functions - Analogue output functions - Engine - Measurements - Lube oil - Engine oil temperature | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
Status value | 8003 |  | 308004 | Functions - Analogue output functions - Engine - Measurements - Coolant - Engine coolant water | INT16 | X * 1 | X * 1 | °C | X |  | X | X | X
Status value | 8004 |  | 308005 | Functions - Analogue output functions - Engine - Measurements - Coolant - Engine coolant level | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Status value | 8005 |  | 308006 | Functions - Analogue output functions - Engine - Measurements - Speed - Engine speed | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
Status value | 8006 |  | 308007 | Functions - Analogue output functions - Engine - Measurements - Speed - Analogue input - Engine MPU | INT16 | X * 1 | X * 1 | RPM | X |  | X | X | X
Status value | 8019 |  | 308020 | GB state | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Status value | 8019 |  | 308020 | BTB state | INT16 | X * 1 | X * 1 |  |  | X
Status value | 8019 |  | 308020 | MB state | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Status value | 8020 |  | 308021 | MB state | INT16 | X * 1 | X * 1 |  |  |  |  | X
Status value | 8020 |  | 308021 | TB state | INT16 | X * 1 | X * 1 | [7 empty] | X
Status value | 8021 |  | 308022 | Emergency busbar status GB side | INT16 | X * 1 | X * 1 |  |  |  |  | X
Status value | 8022 |  | 308023 | MB virtual busbar status | INT16 | X * 1 | X * 1 |  |  |  |  | X |  |  | X
Status value | 8023 |  | 308024 | Sync. status | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8024 |  | 308025 | Sync. status | INT16 | X * 1 | X * 1 |  |  |  |  | X |  |  | X
Status value | 8025 |  | 308026 | Functions - Analogue output functions - Local - Nominal settings - Controller nominal setting - Nominal setting selected | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8026 |  | 308027 | Mains ¦ State | INT16 | X * 1 | X * 1 |  |  |  | X | X
Status value | 8026 |  | 308027 | Busbar ¦ State | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Status value | 8026 |  | 308027 | Busbar B ¦ State | INT16 | X * 1 | X * 1 |  |  | X
Status value | 8027 |  | 308028 | Generator ¦ State | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Status value | 8027 |  | 308028 | Busbar A ¦ State | INT16 | X * 1 | X * 1 |  |  | X
Status value | 8027 |  | 308028 | Mains ¦ State | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Status value | 8028 |  | 308029 | Current control | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8030 |  | 308031 | Number of alarms | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8031 |  | 308032 | Number of unacknowledged alarms | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8032 |  | 308033 | Number of acknowledged alarms | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8033 |  | 308034 | UTC year | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8034 |  | 308035 | UTC month | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8035 |  | 308036 | UTC day | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8036 |  | 308037 | UTC hour | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8037 |  | 308038 | UTC minute | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8038 |  | 308039 | UTC second | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8039 |  | 308040 | Local time year | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8040 |  | 308041 | Local time month | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8041 |  | 308042 | Local time day | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8042 |  | 308043 | Local time hour | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8043 |  | 308044 | Local time minute | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8044 |  | 308045 | Local time second | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8045 |  | 308046 | Functions - Analogue output functions - Regulators - AVR - AVR output | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
Status value | 8046 |  | 308047 | Functions - Analogue output functions - Regulators - GOV - GOV output | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
Status value | 8049 |  | 308050 | Regulator status - AVR regulator percentage | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
Status value | 8050 |  | 308051 | Regulator status - GOV regulator percentage | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
Status value | 8051 |  | 308052 | Functions - Analogue output functions - Hardware - CPU - Load - Currently | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8052 |  | 308053 | Functions - Analogue output functions - Hardware - CPU - Load - Average over 10 seconds | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8053 |  | 308054 | Functions - Analogue output functions - Hardware - CPU - Load - Average over 1 minute | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8054 |  | 308055 | Functions - Analogue output functions - Hardware - CPU - Load - Average over 10 minutes | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8055 |  | 308056 | Functions - Analogue output functions - Hardware - Power supply - PSM3.1 1 - PSM3.1 1 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Status value | 8056 |  | 308057 | Functions - Analogue output functions - Hardware - Power supply - PSM3.2 1 - PSM3.2 1 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Status value | 8057 |  | 308058 | Functions - Analogue output functions - Hardware - Power supply - PSM3.2 2 - PSM3.2 2 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Status value | 8058 |  | 308059 | Functions - Analogue output functions - Hardware - Power supply - PSM3.2 3 - PSM3.2 3 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Status value | 8059 |  | 308060 | Functions - Analogue output functions - Hardware - Power supply - EIM3.1 1 - EIM3.1 1 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Status value | 8060 |  | 308061 | Functions - Analogue output functions - Hardware - Power supply - EIM3.1 2 - EIM3.1 2 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Status value | 8061 |  | 308062 | Functions - Analogue output functions - Hardware - Power supply - EIM3.1 3 - EIM3.1 3 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Status value | 8062 |  | 308063 | EIM3.1 4 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Status value | 8063 |  | 308064 | EIM3.1 5 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Status value | 8065 |  | 308066 | Functions - Analogue output functions - Hardware - Power supply - GAM3.2 1 - GAM3.2 1 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Status value | 8066 |  | 308067 | Functions - Analogue output functions - Hardware - Power supply - GAM3.2 2 - GAM3.2 2 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Status value | 8067 |  | 308068 | Functions - Analogue output functions - Hardware - Power supply - GAM3.2 3 - GAM3.2 3 supply voltage | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Status value | 8072 |  | 308073 | Controller ID | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8094 |  | 308095 | Application version major | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8095 |  | 308096 | Application version minor | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8096 |  | 308097 | Application version micro | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8097 |  | 308098 | Application version bugfix | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8112 |  | 308113 | Emergency busbar status TB side | INT16 | X * 1 | X * 1 | [7 empty] | X
Status value | 8113 |  | 308114 | Current PMS mode | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8114 |  | 308115 | Functions - Analogue output functions - Regulators - AVR - Cos phi reference | INT16 | X * 100 | X * 0.01 |  | X |  | X | X | X
Status value | 8114 |  | 308115 | Cos phi reference | INT16 | X * 100 | X * 0.01 |  |  | X |  |  |  | X | X
Status value | 8115 |  | 308116 | Functions - Analogue output functions - System power management - Monitoring - Plant - Section ¦ PMS P avail. | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
Status value | 8116 |  | 308117 | Functions - Analogue output functions - System power management - Monitoring - Plant - Section ¦ PMS P used | INT16 | X * 1 | X * 1 | kW | X | X | X | X | X | X | X
Status value | 8117 |  | 308118 | Priority in section | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Status value | 8118 |  | 308119 | Functions - Analogue output functions - Local - Nominal settings - Transducer 1 nominal setting - Nominal setting selected | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8119 |  | 308120 | Functions - Analogue output functions - Local - Nominal settings - Transducer 2 nominal setting - Nominal setting selected | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8120 |  | 308121 | Functions - Analogue output functions - Local - Nominal settings - Transducer 3 nominal setting - Nominal setting selected | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8121 |  | 308122 | Functions - Analogue output functions - Local - Nominal settings - Transducer 4 nominal setting - Nominal setting selected | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8122 |  | 308123 | Busbar B ¦ State | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8123 |  | 308124 | Busbar B ¦ State | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8124 |  | 308125 | Busbar B ¦ State | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8125 |  | 308126 | Busbar B ¦ State | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8126 |  | 308127 | Busbar A ¦ State | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8127 |  | 308128 | Busbar A ¦ State | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8128 |  | 308129 | Busbar A ¦ State | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8129 |  | 308130 | Busbar A ¦ State | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Status value | 8134 |  | 308135 | Functions - Analogue output functions - Engine - Measurements - Fuel - Engine fuel level | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Status value | 8135 |  | 308136 | Functions - Analogue output functions - Engine - Measurements - Lube oil - Engine oil level | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
Status value | 8136 |  | 308137 | Functions - Analogue output functions - Hardware - CPU - Core 1 - Currently | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8137 |  | 308138 | Functions - Analogue output functions - Hardware - CPU - Core 1 - Average over 10 seconds | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8138 |  | 308139 | Functions - Analogue output functions - Hardware - CPU - Core 1 - Average over 1 minute | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8139 |  | 308140 | Functions - Analogue output functions - Hardware - CPU - Core 1 - Average over 10 minutes | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8140 |  | 308141 | Functions - Analogue output functions - Hardware - CPU - Core 2 - Currently | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8141 |  | 308142 | Functions - Analogue output functions - Hardware - CPU - Core 2 - Average over 10 seconds | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8142 |  | 308143 | Functions - Analogue output functions - Hardware - CPU - Core 2 - Average over 1 minute | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8143 |  | 308144 | Functions - Analogue output functions - Hardware - CPU - Core 2 - Average over 10 minutes | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8144 |  | 308145 | Functions - Analogue output functions - Hardware - CPU - Core 3 - Currently | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8145 |  | 308146 | Functions - Analogue output functions - Hardware - CPU - Core 3 - Average over 10 seconds | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8146 |  | 308147 | Functions - Analogue output functions - Hardware - CPU - Core 3 - Average over 1 minute | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8147 |  | 308148 | Functions - Analogue output functions - Hardware - CPU - Core 3 - Average over 10 minutes | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8148 |  | 308149 | Functions - Analogue output functions - Hardware - CPU - Core 4 - Currently | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8149 |  | 308150 | Functions - Analogue output functions - Hardware - CPU - Core 4 - Average over 10 seconds | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8150 |  | 308151 | Functions - Analogue output functions - Hardware - CPU - Core 4 - Average over 1 minute | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8151 |  | 308152 | Functions - Analogue output functions - Hardware - CPU - Core 4 - Average over 10 minutes | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Status value | 8155 |  | 308156 | Functions - Analogue output functions - Regulators - GOV - Active operation ramp | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Status value | 8156 |  | 308157 | Functions - Analogue input functions - Regulators - GOV - Request operation ramp | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Status value | 8157 |  | 308158 | Power reference selection | INT16 | X * 1 | X * 1 |  |  |  | X | X
Status value | 8158 |  | 308159 | Excitation selection | INT16 | X * 1 | X * 1 |  |  |  | X | X
Status value | 8159 |  | 308160 | Reactive power reference selection | INT16 | X * 1 | X * 1 |  |  |  | X | X
Status value | 8160 |  | 308161 | Functions - Analogue input functions - Grid code - var(Q) regulation - Ramp switch timer | INT16 | X * 1 | X * 1 | s |  |  | X | X
Status value | 8161 |  | 308162 | Synchronisation progress | INT16 | X * 100 | X * 0.01 | % | X | X | X | X | X | X | X
Compensation: Interger | 12100 |  | 312101 | Functions - Analogue input functions - Thermocouple cold junction - Compensation 1 | INT16 | X * 1 | X * 1 | °C | X | X | X | X | X | X | X
Compensation: Interger | 12101 |  | 312102 | Functions - Analogue input functions - Thermocouple cold junction - Compensation 2 | INT16 | X * 1 | X * 1 | °C | X | X | X | X | X | X | X
Compensation: Interger | 12102 |  | 312103 | Functions - Analogue input functions - Thermocouple cold junction - Compensation 3 | INT16 | X * 1 | X * 1 | °C | X | X | X | X | X | X | X
Compensation: Interger | 12103 |  | 312104 | Functions - Analogue input functions - Thermocouple cold junction - Compensation 4 | INT16 | X * 1 | X * 1 | °C | X | X | X | X | X | X | X
Compensation: Interger | 12104 |  | 312105 | Functions - Analogue input functions - Thermocouple cold junction - Compensation 5 | INT16 | X * 1 | X * 1 | °C | X | X | X | X | X | X | X
Compensation: Interger | 12105 |  | 312106 | Functions - Analogue input functions - Thermocouple cold junction - Compensation 6 | INT16 | X * 1 | X * 1 | °C | X | X | X | X | X | X | X
Compensation: Interger | 12106 |  | 312107 | Functions - Analogue input functions - Thermocouple cold junction - Compensation 7 | INT16 | X * 1 | X * 1 | °C | X | X | X | X | X | X | X
Compensation: Interger | 12107 |  | 312108 | Functions - Analogue input functions - Thermocouple cold junction - Compensation 8 | INT16 | X * 1 | X * 1 | °C | X | X | X | X | X | X | X
Custom logic: analogue output | 12200 |  | 312201 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12201 |  | 312202 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12202 |  | 312203 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12203 |  | 312204 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12204 |  | 312205 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12205 |  | 312206 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12206 |  | 312207 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12207 |  | 312208 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12208 |  | 312209 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12209 |  | 312210 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12210 |  | 312211 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12211 |  | 312212 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12212 |  | 312213 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12213 |  | 312214 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12214 |  | 312215 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12215 |  | 312216 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12216 |  | 312217 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12217 |  | 312218 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12218 |  | 312219 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Custom logic: analogue output | 12219 |  | 312220 | Functions - Analogue output functions - Local - CustomLogic - Outputs - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
GOV regulator status | 13802 |  | 313803 | Regulator status - Active GOV regulation mode | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
GOV regulator status | 13804 |  | 313805 | Regulator status - GOV set point | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
GOV regulator status | 13806 |  | 313807 | Regulator status - GOV measured value | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
AVR regulator status | 13852 |  | 313853 | Regulator status - Active AVR regulation mode | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
AVR regulator status | 13854 |  | 313855 | Regulator status - AVR set point | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
AVR regulator status | 13856 |  | 313857 | Regulator status - AVR measured value | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Controller status text | 13900 |  | 313901 | Texts - Controller status text | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Popup text | 13950 |  | 313951 | Texts - Pop-up text line 1 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Popup text | 13952 |  | 313953 | Texts - Pop-up text line 2 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Popup text | 13954 |  | 313955 | Texts - Pop-up text line 3 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Popup text | 13956 |  | 313957 | Texts - Pop-up text line 4 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Breaker priority: Value | 14001 |  | 314002 | Priority of breaker 1 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14002 |  | 314003 | Priority of breaker 2 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14003 |  | 314004 | Priority of breaker 3 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14004 |  | 314005 | Priority of breaker 4 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14005 |  | 314006 | Priority of breaker 5 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14006 |  | 314007 | Priority of breaker 6 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14007 |  | 314008 | Priority of breaker 7 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14008 |  | 314009 | Priority of breaker 8 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14009 |  | 314010 | Priority of breaker 9 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14010 |  | 314011 | Priority of breaker 10 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14011 |  | 314012 | Priority of breaker 11 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14012 |  | 314013 | Priority of breaker 12 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14013 |  | 314014 | Priority of breaker 13 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14014 |  | 314015 | Priority of breaker 14 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14015 |  | 314016 | Priority of breaker 15 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14016 |  | 314017 | Priority of breaker 16 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14017 |  | 314018 | Priority of breaker 17 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14018 |  | 314019 | Priority of breaker 18 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14019 |  | 314020 | Priority of breaker 19 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14020 |  | 314021 | Priority of breaker 20 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14021 |  | 314022 | Priority of breaker 21 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14022 |  | 314023 | Priority of breaker 22 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14023 |  | 314024 | Priority of breaker 23 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14024 |  | 314025 | Priority of breaker 24 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14025 |  | 314026 | Priority of breaker 25 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14026 |  | 314027 | Priority of breaker 26 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14027 |  | 314028 | Priority of breaker 27 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14028 |  | 314029 | Priority of breaker 28 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14029 |  | 314030 | Priority of breaker 29 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14030 |  | 314031 | Priority of breaker 30 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14031 |  | 314032 | Priority of breaker 31 | INT16 | X * 1 | X * 1 |  | X
Breaker priority: Value | 14032 |  | 314033 | Priority of breaker 32 | INT16 | X * 1 | X * 1 |  | X
Codesys analogue outputs | 16000 |  | 316001 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16001 |  | 316002 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16002 |  | 316003 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16003 |  | 316004 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16004 |  | 316005 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16005 |  | 316006 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16006 |  | 316007 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16007 |  | 316008 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16008 |  | 316009 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16009 |  | 316010 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16010 |  | 316011 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16011 |  | 316012 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16012 |  | 316013 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16013 |  | 316014 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16014 |  | 316015 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16015 |  | 316016 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16016 |  | 316017 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16017 |  | 316018 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16018 |  | 316019 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16019 |  | 316020 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16020 |  | 316021 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16021 |  | 316022 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16022 |  | 316023 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16023 |  | 316024 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16024 |  | 316025 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16025 |  | 316026 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16026 |  | 316027 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16027 |  | 316028 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16028 |  | 316029 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16029 |  | 316030 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16030 |  | 316031 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16031 |  | 316032 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16032 |  | 316033 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16033 |  | 316034 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16034 |  | 316035 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16035 |  | 316036 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16036 |  | 316037 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16037 |  | 316038 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16038 |  | 316039 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16039 |  | 316040 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16040 |  | 316041 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16041 |  | 316042 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16042 |  | 316043 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16043 |  | 316044 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16044 |  | 316045 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16045 |  | 316046 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16046 |  | 316047 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16047 |  | 316048 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16048 |  | 316049 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16049 |  | 316050 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16050 |  | 316051 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16051 |  | 316052 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16052 |  | 316053 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16053 |  | 316054 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16054 |  | 316055 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16055 |  | 316056 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16056 |  | 316057 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16057 |  | 316058 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16058 |  | 316059 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16059 |  | 316060 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16060 |  | 316061 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16061 |  | 316062 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16062 |  | 316063 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16063 |  | 316064 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16064 |  | 316065 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16065 |  | 316066 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16066 |  | 316067 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16067 |  | 316068 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16068 |  | 316069 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16069 |  | 316070 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16070 |  | 316071 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16071 |  | 316072 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16072 |  | 316073 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16073 |  | 316074 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16074 |  | 316075 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16075 |  | 316076 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16076 |  | 316077 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16077 |  | 316078 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16078 |  | 316079 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16079 |  | 316080 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16080 |  | 316081 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16081 |  | 316082 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16082 |  | 316083 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16083 |  | 316084 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16084 |  | 316085 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16085 |  | 316086 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16086 |  | 316087 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16087 |  | 316088 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16088 |  | 316089 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16089 |  | 316090 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16090 |  | 316091 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16091 |  | 316092 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16092 |  | 316093 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16093 |  | 316094 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16094 |  | 316095 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16095 |  | 316096 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16096 |  | 316097 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16097 |  | 316098 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16098 |  | 316099 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Codesys analogue outputs | 16099 |  | 316100 | Functions - Analogue output functions - Local - CODESYS - Custom analogue output | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18000 |  | 318001 | Counters - Engine - Start attempts - Total | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Counter | 18006 |  | 318007 | Counters - Engine - Operation time - Total running hours | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18008 |  | 318009 | Counters - Engine - Operation time - Total running minutes | INT32 | X * 1 | X * 1 | min | X |  | X | X | X
Counter | 18010 |  | 318011 | Counters - Engine - Operation time - Running hours since reset 1 | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18012 |  | 318013 | Counters - Engine - Operation time - Running minutes since reset 1 | INT32 | X * 1 | X * 1 | min | X |  | X | X | X
Counter | 18014 |  | 318015 | Counters - Engine - Operation time - Running hours since reset 2 | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18016 |  | 318017 | Counters - Engine - Operation time - Running minutes since reset 2 | INT32 | X * 1 | X * 1 | min | X |  | X | X | X
Counter | 18018 |  | 318019 | Counters - Engine - Operation time - Running hours since reset 3 | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18020 |  | 318021 | Counters - Engine - Operation time - Running minutes since reset 3 | INT32 | X * 1 | X * 1 | min | X |  | X | X | X
Counter | 18022 |  | 318023 | Counters - Engine - Operation time - Running hours since reset 4 | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18024 |  | 318025 | Counters - Engine - Operation time - Running minutes since reset 4 | INT32 | X * 1 | X * 1 | min | X |  | X | X | X
Counter | 18050 |  | 318051 | Counters - Breakers - Generator breaker - Close operations | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Counter | 18050 |  | 318051 | Counters - Breakers - Bus tie breaker - Close operations | INT32 | X * 1 | X * 1 |  |  | X
Counter | 18050 |  | 318051 | Counters - Breakers - Mains breaker - Close operations | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Counter | 18052 |  | 318053 | Counters - Breakers - Generator breaker - Trips | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Counter | 18052 |  | 318053 | Counters - Breakers - Bus tie breaker - Trips | INT32 | X * 1 | X * 1 |  |  | X
Counter | 18052 |  | 318053 | Counters - Breakers - Mains breaker - Trips | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Counter | 18054 |  | 318055 | Counters - Breakers - Generator breaker - Close operations since reset | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Counter | 18054 |  | 318055 | Counters - Breakers - Bus tie breaker - Close operations since reset | INT32 | X * 1 | X * 1 |  |  | X
Counter | 18054 |  | 318055 | Counters - Breakers - Mains breaker - Close operations since reset | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Counter | 18056 |  | 318057 | Counters - Breakers - Generator breaker - Failed operations | INT32 | X * 1 | X * 1 |  | X |  | X | X | X
Counter | 18056 |  | 318057 | Counters - Breakers - Bus tie breaker - Failed operations | INT32 | X * 1 | X * 1 |  |  | X
Counter | 18056 |  | 318057 | Counters - Breakers - Mains breaker - Failed operations | INT32 | X * 1 | X * 1 | [6 empty] | X | X
Counter | 18058 |  | 318059 | Counters - Breakers - Mains breaker - Close operations | INT32 | X * 1 | X * 1 |  |  |  |  | X
Counter | 18058 |  | 318059 | Counters - Breakers - Tie breaker - Close operations | INT32 | X * 1 | X * 1 | [7 empty] | X
Counter | 18060 |  | 318061 | Counters - Breakers - Mains breaker - Trips | INT32 | X * 1 | X * 1 |  |  |  |  | X
Counter | 18060 |  | 318061 | Counters - Breakers - Tie breaker - Trips | INT32 | X * 1 | X * 1 | [7 empty] | X
Counter | 18062 |  | 318063 | Counters - Breakers - Mains breaker - Close operations since reset | INT32 | X * 1 | X * 1 |  |  |  |  | X
Counter | 18062 |  | 318063 | Counters - Breakers - Tie breaker - Close operations since reset | INT32 | X * 1 | X * 1 | [7 empty] | X
Counter | 18064 |  | 318065 | Counters - Breakers - Mains breaker - Failed operations | INT32 | X * 1 | X * 1 |  |  |  |  | X
Counter | 18064 |  | 318065 | Counters - Breakers - Tie breaker - Failed operations | INT32 | X * 1 | X * 1 | [7 empty] | X
Counter | 18066 |  | 318067 | Counters - Generator - Production counters - Active energy export | INT32 | X * 1 | X * 1 | kWh | X |  | X | X | X
Counter | 18066 |  | 318067 | Counters - Busbar A - Production counters - Active energy export | INT32 | X * 1 | X * 1 | kWh |  | X
Counter | 18066 |  | 318067 | Counters - Mains - Production counters - Active energy export | INT32 | X * 1 | X * 1 | kWh | [5 empty] | X | X
Counter | 18068 |  | 318069 | Counters - Generator - Production counters - Reactive energy export | INT32 | X * 1 | X * 1 | kvarh | X |  | X | X | X
Counter | 18068 |  | 318069 | Counters - Busbar A - Production counters - Reactive energy export | INT32 | X * 1 | X * 1 | kvarh |  | X
Counter | 18068 |  | 318069 | Counters - Mains - Production counters - Reactive energy export | INT32 | X * 1 | X * 1 | kvarh | [5 empty] | X | X
Counter | 18070 |  | 318071 | Counters - Busbar A - Production counters - Active energy import | INT32 | X * 1 | X * 1 | kWh |  | X
Counter | 18070 |  | 318071 | Counters - Mains - Production counters - Active energy import | INT32 | X * 1 | X * 1 | kWh | [5 empty] | X | X
Counter | 18072 |  | 318073 | Counters - Busbar A - Production counters - Reactive energy import | INT32 | X * 1 | X * 1 | kvarh |  | X
Counter | 18072 |  | 318073 | Counters - Mains - Production counters - Reactive energy import | INT32 | X * 1 | X * 1 | kvarh | [5 empty] | X | X
Counter | 18074 |  | 318075 | Counters - Busbar A - Production counters - Active energy difference | INT32 | X * 1 | X * 1 | kWh |  | X
Counter | 18074 |  | 318075 | Counters - Mains - Production counters - Active energy difference | INT32 | X * 1 | X * 1 | kWh | [5 empty] | X | X
Counter | 18076 |  | 318077 | Counters - Busbar A - Production counters - Reactive energy difference | INT32 | X * 1 | X * 1 | kvarh |  | X
Counter | 18076 |  | 318077 | Counters - Mains - Production counters - Reactive energy difference | INT32 | X * 1 | X * 1 | kvarh | [5 empty] | X | X
Counter | 18086 |  | 318087 | Counters - Custom counters - Custom counter 0 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18088 |  | 318089 | Counters - Custom counters - Custom counter 1 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18090 |  | 318091 | Counters - Custom counters - Custom counter 2 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18092 |  | 318093 | Counters - Custom counters - Custom counter 3 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18094 |  | 318095 | Counters - Custom counters - Custom counter 4 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18096 |  | 318097 | Counters - Custom counters - Custom counter 5 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18098 |  | 318099 | Counters - Custom counters - Custom counter 6 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18100 |  | 318101 | Counters - Custom counters - Custom counter 7 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18102 |  | 318103 | Counters - Custom counters - Custom counter 8 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18104 |  | 318105 | Counters - Custom counters - Custom counter 9 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18106 |  | 318107 | Counters - Custom counters - Custom counter 10 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18108 |  | 318109 | Counters - Custom counters - Custom counter 11 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18110 |  | 318111 | Counters - Custom counters - Custom counter 12 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18112 |  | 318113 | Counters - Custom counters - Custom counter 13 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18114 |  | 318115 | Counters - Custom counters - Custom counter 14 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18116 |  | 318117 | Counters - Custom counters - Custom counter 15 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18118 |  | 318119 | Counters - Custom counters - Custom counter 16 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18120 |  | 318121 | Counters - Custom counters - Custom counter 17 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18122 |  | 318123 | Counters - Custom counters - Custom counter 18 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18124 |  | 318125 | Counters - Custom counters - Custom counter 19 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18126 |  | 318127 | Counters - Custom counters - Custom counter 20 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18128 |  | 318129 | Counters - Custom counters - Custom counter 21 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18130 |  | 318131 | Counters - Custom counters - Custom counter 22 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18132 |  | 318133 | Counters - Custom counters - Custom counter 23 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18134 |  | 318135 | Counters - Custom counters - Custom counter 24 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18136 |  | 318137 | Counters - Custom counters - Custom counter 25 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18138 |  | 318139 | Counters - Custom counters - Custom counter 26 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18140 |  | 318141 | Counters - Custom counters - Custom counter 27 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18142 |  | 318143 | Counters - Custom counters - Custom counter 28 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18144 |  | 318145 | Counters - Custom counters - Custom counter 29 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18146 |  | 318147 | Counters - Custom counters - Custom counter 30 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18148 |  | 318149 | Counters - Custom counters - Custom counter 31 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18150 |  | 318151 | Counters - Custom counters - Custom counter 32 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18152 |  | 318153 | Counters - Custom counters - Custom counter 33 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18154 |  | 318155 | Counters - Custom counters - Custom counter 34 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18156 |  | 318157 | Counters - Custom counters - Custom counter 35 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18158 |  | 318159 | Counters - Custom counters - Custom counter 36 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18160 |  | 318161 | Counters - Custom counters - Custom counter 37 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18162 |  | 318163 | Counters - Custom counters - Custom counter 38 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18164 |  | 318165 | Counters - Custom counters - Custom counter 39 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18166 |  | 318167 | Counters - Custom counters - Custom counter 40 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18168 |  | 318169 | Counters - Custom counters - Custom counter 41 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18170 |  | 318171 | Counters - Custom counters - Custom counter 42 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18172 |  | 318173 | Counters - Custom counters - Custom counter 43 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18174 |  | 318175 | Counters - Custom counters - Custom counter 44 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18176 |  | 318177 | Counters - Custom counters - Custom counter 45 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18178 |  | 318179 | Counters - Custom counters - Custom counter 46 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18180 |  | 318181 | Counters - Custom counters - Custom counter 47 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18182 |  | 318183 | Counters - Custom counters - Custom counter 48 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18184 |  | 318185 | Counters - Custom counters - Custom counter 49 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18186 |  | 318187 | Counters - Custom counters - Custom counter 50 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18188 |  | 318189 | Counters - Custom counters - Custom counter 51 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18190 |  | 318191 | Counters - Custom counters - Custom counter 52 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18192 |  | 318193 | Counters - Custom counters - Custom counter 53 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18194 |  | 318195 | Counters - Custom counters - Custom counter 54 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18196 |  | 318197 | Counters - Custom counters - Custom counter 55 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18198 |  | 318199 | Counters - Custom counters - Custom counter 56 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18200 |  | 318201 | Counters - Custom counters - Custom counter 57 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18202 |  | 318203 | Counters - Custom counters - Custom counter 58 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18204 |  | 318205 | Counters - Custom counters - Custom counter 59 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18206 |  | 318207 | Counters - Custom counters - Custom counter 60 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18208 |  | 318209 | Counters - Custom counters - Custom counter 61 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18210 |  | 318211 | Counters - Custom counters - Custom counter 62 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18212 |  | 318213 | Counters - Custom counters - Custom counter 63 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18214 |  | 318215 | Counters - Custom counters - Custom counter 64 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18216 |  | 318217 | Counters - Custom counters - Custom counter 65 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18218 |  | 318219 | Counters - Custom counters - Custom counter 66 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18220 |  | 318221 | Counters - Custom counters - Custom counter 67 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18222 |  | 318223 | Counters - Custom counters - Custom counter 68 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18224 |  | 318225 | Counters - Custom counters - Custom counter 69 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18226 |  | 318227 | Counters - Custom counters - Custom counter 70 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18228 |  | 318229 | Counters - Custom counters - Custom counter 71 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18230 |  | 318231 | Counters - Custom counters - Custom counter 72 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18232 |  | 318233 | Counters - Custom counters - Custom counter 73 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18234 |  | 318235 | Counters - Custom counters - Custom counter 74 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18236 |  | 318237 | Counters - Custom counters - Custom counter 75 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18238 |  | 318239 | Counters - Custom counters - Custom counter 76 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18240 |  | 318241 | Counters - Custom counters - Custom counter 77 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18242 |  | 318243 | Counters - Custom counters - Custom counter 78 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18244 |  | 318245 | Counters - Custom counters - Custom counter 79 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18246 |  | 318247 | Counters - Custom counters - Custom counter 80 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18248 |  | 318249 | Counters - Custom counters - Custom counter 81 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18250 |  | 318251 | Counters - Custom counters - Custom counter 82 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18252 |  | 318253 | Counters - Custom counters - Custom counter 83 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18254 |  | 318255 | Counters - Custom counters - Custom counter 84 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18256 |  | 318257 | Counters - Custom counters - Custom counter 85 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18258 |  | 318259 | Counters - Custom counters - Custom counter 86 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18260 |  | 318261 | Counters - Custom counters - Custom counter 87 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18262 |  | 318263 | Counters - Custom counters - Custom counter 88 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18264 |  | 318265 | Counters - Custom counters - Custom counter 89 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18266 |  | 318267 | Counters - Custom counters - Custom counter 90 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18268 |  | 318269 | Counters - Custom counters - Custom counter 91 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18270 |  | 318271 | Counters - Custom counters - Custom counter 92 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18272 |  | 318273 | Counters - Custom counters - Custom counter 93 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18274 |  | 318275 | Counters - Custom counters - Custom counter 94 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18276 |  | 318277 | Counters - Custom counters - Custom counter 95 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18278 |  | 318279 | Counters - Custom counters - Custom counter 96 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18280 |  | 318281 | Counters - Custom counters - Custom counter 97 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18282 |  | 318283 | Counters - Custom counters - Custom counter 98 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18284 |  | 318285 | Counters - Custom counters - Custom counter 99 | INT32 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Counter | 18286 |  | 318287 | Counters - Engine - Operation time - Running hours load profiled | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18288 |  | 318289 | Counters - Engine - Operation time - Running days since reset 1 | INT32 | X * 1 | X * 1 | d | X |  | X | X | X
Counter | 18290 |  | 318291 | Counters - Engine - Operation time - Running days since reset 2 | INT32 | X * 1 | X * 1 | d | X |  | X | X | X
Counter | 18292 |  | 318293 | Counters - Engine - Operation time - Running days since reset 3 | INT32 | X * 1 | X * 1 | d | X |  | X | X | X
Counter | 18294 |  | 318295 | Counters - Engine - Operation time - Running days since reset 4 | INT32 | X * 1 | X * 1 | d | X |  | X | X | X
Counter | 18296 |  | 318297 | Counters - Engine - Operation time - Running hours relative | INT32 | X * 1 | X * 1 | h | X |  | X | X | X
Counter | 18298 |  | 318299 | Counters - Engine - Operation time - Automatic priority swap hours | INT32 | X * 1 | X * 1 | h | X | X | X | X | X | X | X
Counter | 18300 |  | 318301 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Active energy export (transducer 1) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18302 |  | 318303 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy export (transducer 1) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18304 |  | 318305 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Active energy import (transducer 1) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18306 |  | 318307 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy import (transducer 1) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18308 |  | 318309 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Active energy difference (transducer 1) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18310 |  | 318311 | Counters - Transducers - Transducer 1 - Reference A - Production counters - Reactive energy difference (transducer 1) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18312 |  | 318313 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Active energy export (transducer 2) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18314 |  | 318315 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy export (transducer 2) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18316 |  | 318317 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Active energy import (transducer 2) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18318 |  | 318319 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy import (transducer 2) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18320 |  | 318321 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Active energy difference (transducer 2) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18322 |  | 318323 | Counters - Transducers - Transducer 2 - Reference A - Production counters - Reactive energy difference (transducer 2) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18324 |  | 318325 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Active energy export (transducer 3) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18326 |  | 318327 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy export (transducer 3) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18328 |  | 318329 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Active energy import (transducer 3) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18330 |  | 318331 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy import (transducer 3) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18332 |  | 318333 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Active energy difference (transducer 3) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18334 |  | 318335 | Counters - Transducers - Transducer 3 - Reference A - Production counters - Reactive energy difference (transducer 3) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18336 |  | 318337 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Active energy export (transducer 4) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18338 |  | 318339 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy export (transducer 4) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18340 |  | 318341 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Active energy import (transducer 4) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18342 |  | 318343 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy import (transducer 4) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Counter | 18344 |  | 318345 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Active energy difference (transducer 4) | INT32 | X * 1 | X * 1 | kWh | X | X | X | X | X | X | X
Counter | 18346 |  | 318347 | Counters - Transducers - Transducer 4 - Reference A - Production counters - Reactive energy difference (transducer 4) | INT32 | X * 1 | X * 1 | kvarh | X | X | X | X | X | X | X
Alarm status: Operating value | 20000 |  | 320001 | Application initialisation error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20001 |  | 320002 | Application configuration changed. The controller rack must be powered off and on for the changes to take effect. | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20002 |  | 320003 | Preliminary software | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20003 |  | 320004 | Parameters - Engine - Stop sequence - Stop failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20004 |  | 320005 | Parameters - Engine - Start sequence - Start failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20005 |  | 320006 | Parameters - Engine - Start sequence - Crank failure - Information | INT16 | X * 10 | X * 0.1 | RPM | X |  | X | X | X
Alarm status: Operating value | 20006 |  | 320007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20007 |  | 320008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20008 |  | 320009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20009 |  | 320010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20010 |  | 320011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Magnetic pickup wire break alarm | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20011 |  | 320012 | Parameters - Engine - Stop sequence - Externally stopped - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20013 |  | 320014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information | INT16 | X * 10 | X * 0.1 | bar | X |  | X | X | X
Alarm status: Operating value | 20014 |  | 320015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information | INT16 | X * 10 | X * 0.1 | bar | X |  | X | X | X
Alarm status: Operating value | 20015 |  | 320016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm status: Operating value | 20016 |  | 320017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm status: Operating value | 20017 |  | 320018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm status: Operating value | 20018 |  | 320019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm status: Operating value | 20019 |  | 320020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information | INT16 | X * 10 | X * 0.1 | °C | X |  | X | X | X
Alarm status: Operating value | 20020 |  | 320021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20021 |  | 320022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20022 |  | 320023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20027 |  | 320028 | Parameters - Engine - Running detection - Primary running feedback failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20041 |  | 320042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - GB closing failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20041 |  | 320042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - BTB closing failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20041 |  | 320042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - MB closing failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20042 |  | 320043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - GB opening failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20042 |  | 320043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - BTB opening failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20042 |  | 320043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - MB opening failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20043 |  | 320044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - GB position failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20043 |  | 320044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - BTB position failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20043 |  | 320044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - MB position failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20044 |  | 320045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - GB configuration failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20044 |  | 320045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - BTB configuration failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20044 |  | 320045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - MB configuration failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20045 |  | 320046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - GB synchronisation failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20045 |  | 320046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - BTB synchronisation failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20045 |  | 320046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - MB synchronisation failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20046 |  | 320047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - GB de-load failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20046 |  | 320047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - BTB de-load failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20046 |  | 320047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - MB de-load failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20047 |  | 320048 | Parameters - Breakers - Generator breaker monitoring - Tripped (external) - Information - GB tripped (external) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20047 |  | 320048 | Parameters - Breakers - Bus tie breaker monitoring - Tripped (external) - Information - BTB tripped (external) | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20047 |  | 320048 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - MB tripped (external) | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20048 |  | 320049 | Parameters - Breakers - Generator breaker monitoring - Short circuit - Information - GB short circuit | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20048 |  | 320049 | Parameters - Breakers - Bus tie breaker monitoring - Short circuit - Information - BTB short circuit | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20048 |  | 320049 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - MB short circuit | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20049 |  | 320050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - MB closing failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20049 |  | 320050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - TB closing failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20050 |  | 320051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - MB opening failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20050 |  | 320051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - TB opening failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20051 |  | 320052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - MB position failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20051 |  | 320052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - TB position failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20052 |  | 320053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - MB configuration failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20052 |  | 320053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - TB configuration failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20053 |  | 320054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - MB synchronisation failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20053 |  | 320054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - TB synchronisation failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20054 |  | 320055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - MB de-load failure | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20054 |  | 320055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - TB de-load failure | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20055 |  | 320056 | Parameters - Breakers - Mains breaker monitoring - Tripped (external) - Information - MB tripped (external) | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20055 |  | 320056 | Parameters - Breakers - Tie breaker monitoring - Tripped (external) - Information - TB tripped (external) | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20056 |  | 320057 | Parameters - Breakers - Mains breaker monitoring - Short circuit - Information - MB short circuit | INT16 | X * 1 | X * 1 |  |  |  |  | X
Alarm status: Operating value | 20056 |  | 320057 | Parameters - Breakers - Tie breaker monitoring - Short circuit - Information - TB short circuit | INT16 | X * 1 | X * 1 | [7 empty] | X
Alarm status: Operating value | 20060 |  | 320061 | Parameters - Mains - AC setup - Phase sequence error - Information - Mains phase sequence error | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Operating value | 20060 |  | 320061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Busbar phase sequence error | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Operating value | 20060 |  | 320061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Busbar B phase sequence error | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20061 |  | 320062 | Parameters - Generator - AC setup - Phase sequence error - Information - Generator phase sequence error | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20061 |  | 320062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Busbar A phase sequence error | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20061 |  | 320062 | Parameters - Mains - AC setup - Phase sequence error - Information - Mains phase sequence error | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20062 |  | 320063 | Parameters - Generator - AC setup - Voltage or frequency not OK - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20103 |  | 320104 | Parameters - Mains - Additional protections - ROCOF (df/dt) - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Operating value | 20103 |  | 320104 | Parameters - Busbar - Additional protections - ROCOF (df/dt) - Information | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X | X
Alarm status: Operating value | 20103 |  | 320104 | Parameters - Busbar B - Additional protections - ROCOF (df/dt) - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20104 |  | 320105 | Parameters - Mains - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 | ° |  |  | X | X
Alarm status: Operating value | 20104 |  | 320105 | Parameters - Busbar - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 | ° | X |  |  |  | X | X | X
Alarm status: Operating value | 20104 |  | 320105 | Parameters - Busbar B - Additional protections - Vector shift - Information | INT16 | X * 1 | X * 1 | ° |  | X
Alarm status: Operating value | 20105 |  | 320106 | Parameters - Generator - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20105 |  | 320106 | Parameters - Busbar A - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20105 |  | 320106 | Parameters - Mains - Current protections - Inverse time over-current - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20106 |  | 320107 | Parameters - Local - 4th current input - Earth inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20107 |  | 320108 | Parameters - Local - 4th current input - Neutral inverse time over-current - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20108 |  | 320109 | Parameters - Generator - Additional protections - V< and Q< 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20108 |  | 320109 | Parameters - Busbar A - Additional protections - V< and Q< 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20108 |  | 320109 | Parameters - Mains - Additional protections - V< and Q< 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20109 |  | 320110 | Parameters - Generator - Additional protections - V< and Q< 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20109 |  | 320110 | Parameters - Busbar A - Additional protections - V< and Q< 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20109 |  | 320110 | Parameters - Mains - Additional protections - V< and Q< 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20110 |  | 320111 | Parameters - Generator - Additional protections - Average over-voltage 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20110 |  | 320111 | Parameters - Busbar A - Additional protections - Average over-voltage 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20110 |  | 320111 | Parameters - Mains - Additional protections - Average over-voltage 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20111 |  | 320112 | Parameters - Generator - Additional protections - Average over-voltage 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20111 |  | 320112 | Parameters - Busbar A - Additional protections - Average over-voltage 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20111 |  | 320112 | Parameters - Mains - Additional protections - Average over-voltage 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20115 |  | 320116 | Protection set point out of range | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20116 |  | 320117 | Parameters - Generator - Current protections - Stabilised differential current - Information - Stabilised differential | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20117 |  | 320118 | Parameters - Generator - Current protections - High set differential current - Information - High set differential | INT16 | X * 1 | X * 1 | % | X |  | X | X | X
Alarm status: Operating value | 20118 |  | 320119 | Protection set point out of range (differential current) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20119 |  | 320120 | Parameters - Local - Mode - Not under remote control - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20121 |  | 320122 | Parameters - Local - Monitoring - System not OK - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20122 |  | 320123 | Configuration update delayed | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20123 |  | 320124 | Critical process error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20124 |  | 320125 | Restore error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20125 |  | 320126 | SD-card format error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20126 |  | 320127 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for the changes to take effect. | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20127 |  | 320128 | Fieldbus configuration exceeded maximum I/O configuration | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20128 |  | 320129 | Parameters - Custom alarm - Custom alarm 0 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20129 |  | 320130 | Parameters - Custom alarm - Custom alarm 1 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20130 |  | 320131 | Parameters - Custom alarm - Custom alarm 2 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20131 |  | 320132 | Parameters - Custom alarm - Custom alarm 3 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20132 |  | 320133 | Parameters - Custom alarm - Custom alarm 4 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20133 |  | 320134 | Parameters - Custom alarm - Custom alarm 5 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20134 |  | 320135 | Parameters - Custom alarm - Custom alarm 6 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20135 |  | 320136 | Parameters - Custom alarm - Custom alarm 7 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20136 |  | 320137 | Parameters - Custom alarm - Custom alarm 8 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20137 |  | 320138 | Parameters - Custom alarm - Custom alarm 9 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20138 |  | 320139 | Parameters - Custom alarm - Custom alarm 10 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20139 |  | 320140 | Parameters - Custom alarm - Custom alarm 11 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20140 |  | 320141 | Parameters - Custom alarm - Custom alarm 12 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20141 |  | 320142 | Parameters - Custom alarm - Custom alarm 13 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20142 |  | 320143 | Parameters - Custom alarm - Custom alarm 14 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20143 |  | 320144 | Parameters - Custom alarm - Custom alarm 15 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20144 |  | 320145 | Parameters - Custom alarm - Custom alarm 16 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20145 |  | 320146 | Parameters - Custom alarm - Custom alarm 17 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20146 |  | 320147 | Parameters - Custom alarm - Custom alarm 18 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20147 |  | 320148 | Parameters - Custom alarm - Custom alarm 19 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20148 |  | 320149 | Parameters - Custom alarm - Custom alarm 20 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20149 |  | 320150 | Parameters - Custom alarm - Custom alarm 21 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20150 |  | 320151 | Parameters - Custom alarm - Custom alarm 22 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20151 |  | 320152 | Parameters - Custom alarm - Custom alarm 23 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20152 |  | 320153 | Parameters - Custom alarm - Custom alarm 24 - Information - | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20153 |  | 320154 | Parameters - Regulators - GOV - Monitoring - Regulation error - Information - GOV regulation error | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20154 |  | 320155 | Parameters - Regulators - AVR - Monitoring - Regulation error - Information - AVR regulation error | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20163 |  | 320164 | Required hardware card(s) not found | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20164 |  | 320165 | Software mismatch on hardware module(s) | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20165 |  | 320166 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Mains L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Operating value | 20165 |  | 320166 | Parameters - Busbar - AC setup - Multiple phase wire break - Information - Busbar L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Operating value | 20165 |  | 320166 | Parameters - Busbar B - AC setup - Multiple phase wire break - Information - Busbar B L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20166 |  | 320167 | Parameters - Generator - AC setup - Multiple phase wire break - Information - Generator L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Operating value | 20166 |  | 320167 | Parameters - Busbar A - AC setup - Multiple phase wire break - Information - Busbar A L1-L2-L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20166 |  | 320167 | Parameters - Mains - AC setup - Multiple phase wire break - Information - Mains L1-L2-L3 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Operating value | 20167 |  | 320168 | Parameters - Mains - AC setup - L1 wire break - Information - Mains L1 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Operating value | 20167 |  | 320168 | Parameters - Busbar - AC setup - L1 wire break - Information - Busbar L1 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Operating value | 20167 |  | 320168 | Parameters - Busbar B - AC setup - L1 wire break - Information - Busbar B L1 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20168 |  | 320169 | Parameters - Mains - AC setup - L2 wire break - Information - Mains L2 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Operating value | 20168 |  | 320169 | Parameters - Busbar - AC setup - L2 wire break - Information - Busbar L2 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Operating value | 20168 |  | 320169 | Parameters - Busbar B - AC setup - L2 wire break - Information - Busbar B L2 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20169 |  | 320170 | Parameters - Mains - AC setup - L3 wire break - Information - Mains L3 wire break | INT16 | X * 1 | X * 1 |  |  |  | X
Alarm status: Operating value | 20169 |  | 320170 | Parameters - Busbar - AC setup - L3 wire break - Information - Busbar L3 wire break | INT16 | X * 1 | X * 1 |  | X |  |  |  | X | X
Alarm status: Operating value | 20169 |  | 320170 | Parameters - Busbar B - AC setup - L3 wire break - Information - Busbar B L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20170 |  | 320171 | Parameters - Generator - AC setup - L1 wire break - Information - Generator L1 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Operating value | 20170 |  | 320171 | Parameters - Busbar A - AC setup - L1 wire break - Information - Busbar A L1 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20170 |  | 320171 | Parameters - Mains - AC setup - L1 wire break - Information - Mains L1 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Operating value | 20171 |  | 320172 | Parameters - Generator - AC setup - L2 wire break - Information - Generator L2 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Operating value | 20171 |  | 320172 | Parameters - Busbar A - AC setup - L2 wire break - Information - Busbar A L2 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20171 |  | 320172 | Parameters - Mains - AC setup - L2 wire break - Information - Mains L2 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Operating value | 20172 |  | 320173 | Parameters - Generator - AC setup - L3 wire break - Information - Generator L3 wire break | INT16 | X * 1 | X * 1 |  | X |  | X |  | X
Alarm status: Operating value | 20172 |  | 320173 | Parameters - Busbar A - AC setup - L3 wire break - Information - Busbar A L3 wire break | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20172 |  | 320173 | Parameters - Mains - AC setup - L3 wire break - Information - Mains L3 wire break | INT16 | X * 1 | X * 1 | [6 empty] | X
Alarm status: Operating value | 20178 |  | 320179 | Parameters - Mains - AC setup - Supervision alarm - Information - Mains supervision alarm | INT16 | X * 1 | X * 1 |  |  |  | X | X |  | X | X
Alarm status: Operating value | 20179 |  | 320180 | Parameters - Engine - Emergency stop - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20179 |  | 320180 | Parameters - Busbar A - Emergency stop - Information | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20179 |  | 320180 | Parameters - Mains - Emergency stop - Information | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20180 |  | 320181 | Clock battery failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20181 |  | 320182 | Controller temperature too high | INT16 | X * 1 | X * 1 | °C | X | X | X | X | X | X | X
Alarm status: Operating value | 20182 |  | 320183 | Parameters - Hardware - PSM3.1 1 - High voltage alarm - Information - PSM3.1 1 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20183 |  | 320184 | Parameters - Hardware - PSM3.1 1 - Low voltage alarm - Information - PSM3.1 1 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20184 |  | 320185 | Parameters - Hardware - PSM3.2 1 - High voltage alarm - Information - PSM3.2 1 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20185 |  | 320186 | Parameters - Hardware - PSM3.2 1 - Low voltage alarm - Information - PSM3.2 1 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20186 |  | 320187 | Parameters - Hardware - PSM3.2 2 - High voltage alarm - Information - PSM3.2 2 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20187 |  | 320188 | Parameters - Hardware - PSM3.2 2 - Low voltage alarm - Information - PSM3.2 2 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20188 |  | 320189 | Parameters - Hardware - PSM3.2 3 - High voltage alarm - Information - PSM3.2 3 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20189 |  | 320190 | Parameters - Hardware - PSM3.2 3 - Low voltage alarm - Information - PSM3.2 3 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20190 |  | 320191 | Parameters - Hardware - EIM3.1 1 - High voltage alarm - Information - EIM3.1 1 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20191 |  | 320192 | Parameters - Hardware - EIM3.1 1 - Low voltage alarm - Information - EIM3.1 1 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20192 |  | 320193 | Parameters - Hardware - EIM3.1 2 - High voltage alarm - Information - EIM3.1 2 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20193 |  | 320194 | Parameters - Hardware - EIM3.1 2 - Low voltage alarm - Information - EIM3.1 2 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20194 |  | 320195 | Parameters - Hardware - EIM3.1 3 - High voltage alarm - Information - EIM3.1 3 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20195 |  | 320196 | Parameters - Hardware - EIM3.1 3 - Low voltage alarm - Information - EIM3.1 3 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20196 |  | 320197 | EIM3.1 4 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20197 |  | 320198 | EIM3.1 4 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20198 |  | 320199 | EIM3.1 5 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20199 |  | 320200 | EIM3.1 5 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20200 |  | 320201 | Parameters - Hardware - EIM3.1 1 - Relay 4 supervision - Information - EIM3.1 1 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20201 |  | 320202 | Parameters - Hardware - EIM3.1 2 - Relay 4 supervision - Information - EIM3.1 2 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20202 |  | 320203 | Parameters - Hardware - EIM3.1 3 - Relay 4 supervision - Information - EIM3.1 3 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20203 |  | 320204 | EIM3.1 4 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20204 |  | 320205 | EIM3.1 5 relay 4 wire break | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20205 |  | 320206 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20206 |  | 320207 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20207 |  | 320208 | AC protections not running (differential current) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20208 |  | 320209 | AC data is missing (differential current) | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20209 |  | 320210 | Parameters - Hardware - GAM3.2 1 - High voltage alarm - Information - GAM3.2 1 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20210 |  | 320211 | Parameters - Hardware - GAM3.2 1 - Low voltage alarm - Information - GAM3.2 1 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20211 |  | 320212 | Parameters - Hardware - GAM3.2 2 - High voltage alarm - Information - GAM3.2 2 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20212 |  | 320213 | Parameters - Hardware - GAM3.2 2 - Low voltage alarm - Information - GAM3.2 2 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20213 |  | 320214 | Parameters - Hardware - GAM3.2 3 - High voltage alarm - Information - GAM3.2 3 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20214 |  | 320215 | Parameters - Hardware - GAM3.2 3 - Low voltage alarm - Information - GAM3.2 3 supply voltage low or missing | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20215 |  | 320216 | Parameters - Hardware - PSM3.2 4 - High voltage alarm - Information - PSM3.2 4 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20216 |  | 320217 | Parameters - Hardware - PSM3.2 4 - Low voltage alarm - Information - PSM3.2 4 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20217 |  | 320218 | Parameters - Hardware - PSM3.2 5 - High voltage alarm - Information - PSM3.2 5 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20218 |  | 320219 | Parameters - Hardware - PSM3.2 5 - Low voltage alarm - Information - PSM3.2 5 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20219 |  | 320220 | Parameters - Hardware - PSM3.2 6 - High voltage alarm - Information - PSM3.2 6 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20220 |  | 320221 | Parameters - Hardware - PSM3.2 6 - Low voltage alarm - Information - PSM3.2 6 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20221 |  | 320222 | Parameters - Hardware - PSM3.2 7 - High voltage alarm - Information - PSM3.2 7 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20222 |  | 320223 | Parameters - Hardware - PSM3.2 7 - Low voltage alarm - Information - PSM3.2 7 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20223 |  | 320224 | Parameters - Hardware - PSM3.2 8 - High voltage alarm - Information - PSM3.2 8 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20224 |  | 320225 | Parameters - Hardware - PSM3.2 8 - Low voltage alarm - Information - PSM3.2 8 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20225 |  | 320226 | Parameters - Hardware - PSM3.2 9 - High voltage alarm - Information - PSM3.2 9 supply voltage high | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20226 |  | 320227 | Parameters - Hardware - PSM3.2 9 - Low voltage alarm - Information - PSM3.2 9 supply voltage low | INT16 | X * 10 | X * 0.1 | V | X | X | X | X | X | X | X
Alarm status: Operating value | 20228 |  | 320229 | Parameters - System - Monitoring - Duplicate controller ID - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20229 |  | 320230 | Parameters - System - Monitoring - Missing all controllers - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20231 |  | 320232 | Controller ID not configured | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20236 |  | 320237 | Parameters - Communication - DEIF network - DEIF network redundancy broken - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20237 |  | 320238 | Blackout detection mismatch | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20240 |  | 320241 | Parameters - Communication - NTP - NTP server 1 not connected - Information - NTP server 1 could not connect | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20241 |  | 320242 | Parameters - Communication - NTP - NTP server 1 no response - Information - NTP server 1 is not responding | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20242 |  | 320243 | Parameters - Communication - NTP - NTP server 2 not connected - Information - NTP server 2 could not connect | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20243 |  | 320244 | Parameters - Communication - NTP - NTP server 2 no response - Information - NTP server 2 is not responding | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20244 |  | 320245 | Parameters - Communication - NTP - No NTP server time synchronisation - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20245 |  | 320246 | Parameters - Communication - NTP - No NTP server(s) connected - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20246 |  | 320247 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-A bus off - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20247 |  | 320248 | Parameters - Communication - Fieldbus - CAN bus - Bus off - CAN-B bus off - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20296 |  | 320297 | Controller not part of system | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20297 |  | 320298 | Different single-line configurations | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20298 |  | 320299 | Single-line missing/none active | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20299 |  | 320300 | Parameters - Communication - Modbus - Modbus communication timeout - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20300 |  | 320301 | Parameters - CODESYS - Monitoring - I/O config conflict - Information - CODESYS configuration conflict | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20301 |  | 320302 | Parameters - CODESYS - Monitoring - Application not OK - Information - CODESYS application not OK | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20302 |  | 320303 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20303 |  | 320304 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20304 |  | 320305 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20305 |  | 320306 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20306 |  | 320307 | Parameters - Communication - Fieldbus - CAN bus - ECU - ECU Communication failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20307 |  | 320308 | Parameters - Engine - ECU - Diagnostic alarms - ECU Red stop lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20308 |  | 320309 | Parameters - Engine - ECU - Diagnostic alarms - ECU Amber warning lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20309 |  | 320310 | Parameters - Engine - ECU - Diagnostic alarms - ECU Protect lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20310 |  | 320311 | Parameters - Engine - ECU - Diagnostic alarms - ECU Malfunction indicator lamp (ECU2) - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20311 |  | 320312 | Parameters - Communication - Fieldbus - Fieldbus conflict - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20312 |  | 320313 | Parameters - Communication - Fieldbus - Fieldbus connection missing - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20315 |  | 320316 | Parameters - Local - CustomLogic - Configuration invalid - Information - CustomLogic configuration invalid | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20316 |  | 320317 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Communication error - Information - Digital AVR communication error | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20317 |  | 320318 | Parameters - Generator - Digital AVR - Alarms - Over-voltage - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20318 |  | 320319 | Parameters - Generator - Digital AVR - Alarms - Under-voltage - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20319 |  | 320320 | Parameters - Generator - Digital AVR - Alarms - Over-frequency - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20320 |  | 320321 | Parameters - Generator - Digital AVR - Alarms - Under-frequency - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20321 |  | 320322 | Parameters - Generator - Digital AVR - Alarms - Open diode - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20322 |  | 320323 | Parameters - Generator - Digital AVR - Alarms - Shorted diode - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20323 |  | 320324 | Parameters - Generator - Digital AVR - Alarms - Reverse kW - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20324 |  | 320325 | Parameters - Generator - Digital AVR - Alarms - Reverse kvar - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20325 |  | 320326 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20326 |  | 320327 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20327 |  | 320328 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20328 |  | 320329 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20329 |  | 320330 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20330 |  | 320331 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20331 |  | 320332 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20332 |  | 320333 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20333 |  | 320334 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 alarm - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20334 |  | 320335 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20335 |  | 320336 | Parameters - Generator - Digital AVR - Alarms - PTC 1 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20336 |  | 320337 | Parameters - Generator - Digital AVR - Alarms - PTC 2 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20337 |  | 320338 | Parameters - Generator - Digital AVR - Alarms - PTC 3 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20338 |  | 320339 | Parameters - Generator - Digital AVR - Alarms - PTC 4 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20339 |  | 320340 | Parameters - Generator - Digital AVR - Alarms - PTC 5 fault - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20340 |  | 320341 | Parameters - Generator - Digital AVR - Alarms - Sensing lost - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20341 |  | 320342 | Parameters - Generator - Digital AVR - Alarms - Unbalanced voltage - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20342 |  | 320343 | Parameters - Generator - Digital AVR - Alarms - Unbalanced current - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20343 |  | 320344 | Parameters - Generator - Digital AVR - Alarms - Short circuit - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20344 |  | 320345 | Parameters - Generator - Digital AVR - Alarms - IGBT overheat - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20345 |  | 320346 | Parameters - Generator - Digital AVR - Alarms - Motor start - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20346 |  | 320347 | Parameters - Generator - Digital AVR - Alarms - PWR bridge overload - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20347 |  | 320348 | Parameters - Generator - Digital AVR - Alarms - Power supply - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20348 |  | 320349 | Parameters - Generator - Digital AVR - Alarms - CAN supply - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20349 |  | 320350 | Parameters - Generator - Digital AVR - Alarms - Pt100 1 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20350 |  | 320351 | Parameters - Generator - Digital AVR - Alarms - Pt100 2 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20351 |  | 320352 | Parameters - Generator - Digital AVR - Alarms - Pt100 3 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20352 |  | 320353 | Parameters - Generator - Digital AVR - Alarms - Pt100 4 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20353 |  | 320354 | Parameters - Generator - Digital AVR - Alarms - Pt100 5 open short fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20354 |  | 320355 | Parameters - Generator - Digital AVR - Alarms - AIN 1 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20355 |  | 320356 | Parameters - Generator - Digital AVR - Alarms - AIN 2 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20356 |  | 320357 | Parameters - Generator - Digital AVR - Alarms - AIN 3 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20357 |  | 320358 | Parameters - Generator - Digital AVR - Alarms - AIN 4 wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20358 |  | 320359 | Parameters - Generator - Digital AVR - Alarms - AOUT 1 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20359 |  | 320360 | Parameters - Generator - Digital AVR - Alarms - AOUT 2 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20360 |  | 320361 | Parameters - Generator - Digital AVR - Alarms - AOUT 3 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20361 |  | 320362 | Parameters - Generator - Digital AVR - Alarms - AOUT 4 overload wire break fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20362 |  | 320363 | Parameters - Generator - Digital AVR - Alarms - DOUT overload fault status - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20363 |  | 320364 | DAVR unsupported AC configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20364 |  | 320365 | Parameters - Communication - Fieldbus - CAN bus - Digital AVR - Illegal configuration - Information - Illegal DAVR configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20365 |  | 320366 | Parameters - Generator - Voltage protections - Under-voltage 1 - Information - Generator under-voltage 1 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20365 |  | 320366 | Parameters - Busbar A - Voltage protections - Under-voltage 1 - Information - Busbar A under-voltage 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20365 |  | 320366 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Mains under-voltage 1 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20366 |  | 320367 | Parameters - Generator - Voltage protections - Under-voltage 2 - Information - Generator under-voltage 2 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20366 |  | 320367 | Parameters - Busbar A - Voltage protections - Under-voltage 2 - Information - Busbar A under-voltage 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20366 |  | 320367 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Mains under-voltage 2 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20367 |  | 320368 | Parameters - Generator - Voltage protections - Under-voltage 3 - Information - Generator under-voltage 3 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20367 |  | 320368 | Parameters - Busbar A - Voltage protections - Under-voltage 3 - Information - Busbar A under-voltage 3 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20367 |  | 320368 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Mains under-voltage 3 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20368 |  | 320369 | Parameters - Generator - Voltage protections - Over-voltage 1 - Information - Generator over-voltage 1 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20368 |  | 320369 | Parameters - Busbar A - Voltage protections - Over-voltage 1 - Information - Busbar A over-voltage 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20368 |  | 320369 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Mains over-voltage 1 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20369 |  | 320370 | Parameters - Generator - Voltage protections - Over-voltage 2 - Information - Generator over-voltage 2 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20369 |  | 320370 | Parameters - Busbar A - Voltage protections - Over-voltage 2 - Information - Busbar A over-voltage 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20369 |  | 320370 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Mains over-voltage 2 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20370 |  | 320371 | Parameters - Generator - Voltage protections - Voltage unbalance - Information - Generator voltage unbalance | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20370 |  | 320371 | Parameters - Busbar A - Voltage protections - Voltage unbalance - Information - Busbar A voltage unbalance | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20370 |  | 320371 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Mains voltage unbalance | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20371 |  | 320372 | Parameters - Generator - Voltage protections - Negative sequence voltage - Information - Generator negative sequence voltage | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20371 |  | 320372 | Parameters - Busbar A - Voltage protections - Negative sequence voltage - Information - Busbar A negative sequence voltage | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20371 |  | 320372 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Mains negative sequence voltage | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20372 |  | 320373 | Parameters - Generator - Voltage protections - Zero sequence voltage - Information - Generator zero sequence voltage | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20372 |  | 320373 | Parameters - Busbar A - Voltage protections - Zero sequence voltage - Information - Busbar A zero sequence voltage | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20372 |  | 320373 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Mains zero sequence voltage | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20373 |  | 320374 | Parameters - Generator - Voltage protections - Positive sequence under-voltage - Information - Generator positive sequence under-voltage | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20373 |  | 320374 | Parameters - Busbar A - Voltage protections - Positive sequence under-voltage - Information - Busbar A positive sequence under-voltage | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20373 |  | 320374 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Mains positive sequence under-voltage | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20374 |  | 320375 | Parameters - Generator - Current protections - Over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20374 |  | 320375 | Parameters - Busbar A - Current protections - Over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20374 |  | 320375 | Parameters - Mains - Current protections - Over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20375 |  | 320376 | Parameters - Generator - Current protections - Over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20375 |  | 320376 | Parameters - Busbar A - Current protections - Over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20375 |  | 320376 | Parameters - Mains - Current protections - Over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20376 |  | 320377 | Parameters - Generator - Current protections - Over-current 3 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20376 |  | 320377 | Parameters - Busbar A - Current protections - Over-current 3 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20376 |  | 320377 | Parameters - Mains - Current protections - Over-current 3 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20377 |  | 320378 | Parameters - Generator - Current protections - Over-current 4 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20377 |  | 320378 | Parameters - Busbar A - Current protections - Over-current 4 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20377 |  | 320378 | Parameters - Mains - Current protections - Over-current 4 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20378 |  | 320379 | Parameters - Generator - Current protections - Fast over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20378 |  | 320379 | Parameters - Busbar A - Current protections - Fast over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20378 |  | 320379 | Parameters - Mains - Current protections - Fast over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20379 |  | 320380 | Parameters - Generator - Current protections - Fast over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20379 |  | 320380 | Parameters - Busbar A - Current protections - Fast over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20379 |  | 320380 | Parameters - Mains - Current protections - Fast over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20380 |  | 320381 | Parameters - Generator - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20380 |  | 320381 | Parameters - Busbar A - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20380 |  | 320381 | Parameters - Mains - Current protections - Current unbalance (average calc.) - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20381 |  | 320382 | Parameters - Generator - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20381 |  | 320382 | Parameters - Busbar A - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20381 |  | 320382 | Parameters - Mains - Current protections - Current unbalance (nominal calc.) - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20382 |  | 320383 | Parameters - Generator - Current protections - Directional over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20382 |  | 320383 | Parameters - Busbar A - Current protections - Directional over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20382 |  | 320383 | Parameters - Mains - Current protections - Directional over-current 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20383 |  | 320384 | Parameters - Generator - Current protections - Directional over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20383 |  | 320384 | Parameters - Busbar A - Current protections - Directional over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20383 |  | 320384 | Parameters - Mains - Current protections - Directional over-current 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20384 |  | 320385 | Parameters - Busbar A - Current protections - Directional over-current 3 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20385 |  | 320386 | Parameters - Busbar A - Current protections - Directional over-current 4 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20386 |  | 320387 | Parameters - Generator - Current protections - Negative sequence current - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20386 |  | 320387 | Parameters - Busbar A - Current protections - Negative sequence current - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20386 |  | 320387 | Parameters - Mains - Current protections - Negative sequence current - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20387 |  | 320388 | Parameters - Generator - Current protections - Zero sequence current - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20387 |  | 320388 | Parameters - Busbar A - Current protections - Zero sequence current - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20387 |  | 320388 | Parameters - Mains - Current protections - Zero sequence current - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20388 |  | 320389 | Parameters - Generator - Frequency protections - Over-frequency 1 - Information - Generator over-frequency 1 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20388 |  | 320389 | Parameters - Busbar A - Frequency protections - Over-frequency 1 - Information - Busbar A over-frequency 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20388 |  | 320389 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Mains over-frequency 1 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20389 |  | 320390 | Parameters - Generator - Frequency protections - Over-frequency 2 - Information - Generator over-frequency 2 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20389 |  | 320390 | Parameters - Busbar A - Frequency protections - Over-frequency 2 - Information - Busbar A over-frequency 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20389 |  | 320390 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Mains over-frequency 2 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20390 |  | 320391 | Parameters - Generator - Frequency protections - Over-frequency 3 - Information - Generator over-frequency 3 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20390 |  | 320391 | Parameters - Busbar A - Frequency protections - Over-frequency 3 - Information - Busbar A over-frequency 3 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20390 |  | 320391 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Mains over-frequency 3 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20391 |  | 320392 | Parameters - Generator - Frequency protections - Under-frequency 1 - Information - Generator under-frequency 1 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20391 |  | 320392 | Parameters - Busbar A - Frequency protections - Under-frequency 1 - Information - Busbar A under-frequency 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20391 |  | 320392 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Mains under-frequency 1 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20392 |  | 320393 | Parameters - Generator - Frequency protections - Under-frequency 2 - Information - Generator under-frequency 2 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20392 |  | 320393 | Parameters - Busbar A - Frequency protections - Under-frequency 2 - Information - Busbar A under-frequency 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20392 |  | 320393 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Mains under-frequency 2 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20393 |  | 320394 | Parameters - Generator - Frequency protections - Under-frequency 3 - Information - Generator under-frequency 3 | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20393 |  | 320394 | Parameters - Busbar A - Frequency protections - Under-frequency 3 - Information - Busbar A under-frequency 3 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20393 |  | 320394 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Mains under-frequency 3 | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20394 |  | 320395 | Parameters - Generator - Power protections - Overload 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20394 |  | 320395 | Parameters - Busbar A - Power protections - Power export 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20394 |  | 320395 | Parameters - Mains - Power protections - Overload 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20395 |  | 320396 | Parameters - Generator - Power protections - Overload 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20395 |  | 320396 | Parameters - Busbar A - Power protections - Power export 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20395 |  | 320396 | Parameters - Mains - Power protections - Overload 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20396 |  | 320397 | Parameters - Generator - Power protections - Overload 3 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20396 |  | 320397 | Parameters - Busbar A - Power protections - Power export 3 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20396 |  | 320397 | Parameters - Mains - Power protections - Overload 3 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20397 |  | 320398 | Parameters - Generator - Power protections - Overload 4 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20397 |  | 320398 | Parameters - Busbar A - Power protections - Power export 4 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20397 |  | 320398 | Parameters - Mains - Power protections - Overload 4 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20398 |  | 320399 | Parameters - Generator - Power protections - Overload 5 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20398 |  | 320399 | Parameters - Busbar A - Power protections - Power export 5 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20398 |  | 320399 | Parameters - Mains - Power protections - Overload 5 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20399 |  | 320400 | Parameters - Generator - Power protections - Reverse power 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20399 |  | 320400 | Parameters - Busbar A - Power protections - Power import 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20399 |  | 320400 | Parameters - Mains - Power protections - Reverse power 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20400 |  | 320401 | Parameters - Generator - Power protections - Reverse power 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20400 |  | 320401 | Parameters - Busbar A - Power protections - Power import 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20400 |  | 320401 | Parameters - Mains - Power protections - Reverse power 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20401 |  | 320402 | Parameters - Generator - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20401 |  | 320402 | Parameters - Busbar A - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20401 |  | 320402 | Parameters - Mains - Reactive power protections - Reactive power export 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20402 |  | 320403 | Parameters - Generator - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20402 |  | 320403 | Parameters - Busbar A - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20402 |  | 320403 | Parameters - Mains - Reactive power protections - Reactive power export 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20403 |  | 320404 | Parameters - Generator - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20403 |  | 320404 | Parameters - Busbar A - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20403 |  | 320404 | Parameters - Mains - Reactive power protections - Reactive power import 1 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20404 |  | 320405 | Parameters - Generator - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 10 | X * 0.1 | % | X |  | X | X | X
Alarm status: Operating value | 20404 |  | 320405 | Parameters - Busbar A - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20404 |  | 320405 | Parameters - Mains - Reactive power protections - Reactive power import 2 - Information | INT16 | X * 10 | X * 0.1 | % | [5 empty] | X | X
Alarm status: Operating value | 20405 |  | 320406 | Parameters - Mains - Voltage protections - Over-voltage 1 - Information - Mains over-voltage 1 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20405 |  | 320406 | Parameters - Busbar - Voltage protections - Over-voltage 1 - Information - Busbar over-voltage 1 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20405 |  | 320406 | Parameters - Busbar B - Voltage protections - Over-voltage 1 - Information - Busbar B over-voltage 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20406 |  | 320407 | Parameters - Mains - Voltage protections - Over-voltage 2 - Information - Mains over-voltage 2 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20406 |  | 320407 | Parameters - Busbar - Voltage protections - Over-voltage 2 - Information - Busbar over-voltage 2 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20406 |  | 320407 | Parameters - Busbar B - Voltage protections - Over-voltage 2 - Information - Busbar B over-voltage 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20407 |  | 320408 | Parameters - Mains - Voltage protections - Over-voltage 3 - Information - Mains over-voltage 3 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20407 |  | 320408 | Parameters - Busbar - Voltage protections - Over-voltage 3 - Information - Busbar over-voltage 3 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20407 |  | 320408 | Parameters - Busbar B - Voltage protections - Over-voltage 3 - Information - Busbar B over-voltage 3 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20408 |  | 320409 | Parameters - Mains - Voltage protections - Under-voltage 1 - Information - Mains under-voltage 1 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20408 |  | 320409 | Parameters - Busbar - Voltage protections - Under-voltage 1 - Information - Busbar under-voltage 1 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20408 |  | 320409 | Parameters - Busbar B - Voltage protections - Under-voltage 1 - Information - Busbar B under-voltage 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20409 |  | 320410 | Parameters - Mains - Voltage protections - Under-voltage 2 - Information - Mains under-voltage 2 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20409 |  | 320410 | Parameters - Busbar - Voltage protections - Under-voltage 2 - Information - Busbar under-voltage 2 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20409 |  | 320410 | Parameters - Busbar B - Voltage protections - Under-voltage 2 - Information - Busbar B under-voltage 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20410 |  | 320411 | Parameters - Mains - Voltage protections - Under-voltage 3 - Information - Mains under-voltage 3 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20410 |  | 320411 | Parameters - Busbar - Voltage protections - Under-voltage 3 - Information - Busbar under-voltage 3 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20410 |  | 320411 | Parameters - Busbar B - Voltage protections - Under-voltage 3 - Information - Busbar B under-voltage 3 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20411 |  | 320412 | Parameters - Mains - Voltage protections - Under-voltage 4 - Information - Mains under-voltage 4 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20411 |  | 320412 | Parameters - Busbar - Voltage protections - Under-voltage 4 - Information - Busbar under-voltage 4 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20411 |  | 320412 | Parameters - Busbar B - Voltage protections - Under-voltage 4 - Information - Busbar B under-voltage 4 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20412 |  | 320413 | Parameters - Mains - Voltage protections - Voltage unbalance - Information - Mains voltage unbalance | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20412 |  | 320413 | Parameters - Busbar - Voltage protections - Voltage unbalance - Information - Busbar voltage unbalance | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20412 |  | 320413 | Parameters - Busbar B - Voltage protections - Voltage unbalance - Information - Busbar B voltage unbalance | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20413 |  | 320414 | Parameters - Mains - Frequency protections - Over-frequency 1 - Information - Mains over-frequency 1 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20413 |  | 320414 | Parameters - Busbar - Frequency protections - Over-frequency 1 - Information - Busbar over-frequency 1 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20413 |  | 320414 | Parameters - Busbar B - Frequency protections - Over-frequency 1 - Information - Busbar B over-frequency 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20414 |  | 320415 | Parameters - Mains - Frequency protections - Over-frequency 2 - Information - Mains over-frequency 2 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20414 |  | 320415 | Parameters - Busbar - Frequency protections - Over-frequency 2 - Information - Busbar over-frequency 2 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20414 |  | 320415 | Parameters - Busbar B - Frequency protections - Over-frequency 2 - Information - Busbar B over-frequency 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20415 |  | 320416 | Parameters - Mains - Frequency protections - Over-frequency 3 - Information - Mains over-frequency 3 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20415 |  | 320416 | Parameters - Busbar - Frequency protections - Over-frequency 3 - Information - Busbar over-frequency 3 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20415 |  | 320416 | Parameters - Busbar B - Frequency protections - Over-frequency 3 - Information - Busbar B over-frequency 3 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20416 |  | 320417 | Parameters - Mains - Frequency protections - Under-frequency 1 - Information - Mains under-frequency 1 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20416 |  | 320417 | Parameters - Busbar - Frequency protections - Under-frequency 1 - Information - Busbar under-frequency 1 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20416 |  | 320417 | Parameters - Busbar B - Frequency protections - Under-frequency 1 - Information - Busbar B under-frequency 1 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20417 |  | 320418 | Parameters - Mains - Frequency protections - Under-frequency 2 - Information - Mains under-frequency 2 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20417 |  | 320418 | Parameters - Busbar - Frequency protections - Under-frequency 2 - Information - Busbar under-frequency 2 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20417 |  | 320418 | Parameters - Busbar B - Frequency protections - Under-frequency 2 - Information - Busbar B under-frequency 2 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20418 |  | 320419 | Parameters - Mains - Frequency protections - Under-frequency 3 - Information - Mains under-frequency 3 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20418 |  | 320419 | Parameters - Busbar - Frequency protections - Under-frequency 3 - Information - Busbar under-frequency 3 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20418 |  | 320419 | Parameters - Busbar B - Frequency protections - Under-frequency 3 - Information - Busbar B under-frequency 3 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20419 |  | 320420 | Parameters - Mains - Frequency protections - Under-frequency 4 - Information - Mains under-frequency 4 | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20419 |  | 320420 | Parameters - Busbar - Frequency protections - Under-frequency 4 - Information - Busbar under-frequency 4 | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20419 |  | 320420 | Parameters - Busbar B - Frequency protections - Under-frequency 4 - Information - Busbar B under-frequency 4 | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20420 |  | 320421 | Parameters - Mains - Voltage protections - Negative sequence voltage - Information - Busbar negative sequence voltage | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20420 |  | 320421 | Parameters - Busbar - Voltage protections - Negative sequence voltage - Information - Busbar negative sequence voltage | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20420 |  | 320421 | Parameters - Busbar B - Voltage protections - Negative sequence voltage - Information - Busbar B negative sequence voltage | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20421 |  | 320422 | Parameters - Mains - Voltage protections - Zero sequence voltage - Information - Busbar zero sequence voltage | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20421 |  | 320422 | Parameters - Busbar - Voltage protections - Zero sequence voltage - Information - Busbar zero sequence voltage | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20421 |  | 320422 | Parameters - Busbar B - Voltage protections - Zero sequence voltage - Information - Busbar B zero sequence voltage | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20422 |  | 320423 | Parameters - Mains - Voltage protections - Positive sequence under-voltage - Information - Busbar positive sequence under-voltage | INT16 | X * 10 | X * 0.1 | % |  |  | X | X
Alarm status: Operating value | 20422 |  | 320423 | Parameters - Busbar - Voltage protections - Positive sequence under-voltage - Information - Busbar positive sequence under-voltage | INT16 | X * 10 | X * 0.1 | % | X |  |  |  | X | X | X
Alarm status: Operating value | 20422 |  | 320423 | Parameters - Busbar B - Voltage protections - Positive sequence under-voltage - Information - Busbar B positive sequence under-voltage | INT16 | X * 10 | X * 0.1 | % |  | X
Alarm status: Operating value | 20467 |  | 320468 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 1 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20468 |  | 320469 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 2 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20469 |  | 320470 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 3 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20470 |  | 320471 | Parameters - Engine - Maintenance - Service timer - Information - Service timer 4 | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20471 |  | 320472 | External MB open failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20472 |  | 320473 | Parameters - Power management rules - Ground relay - Ground relay general failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20473 |  | 320474 | Parameters - Power management rules - Ground relay - Ground relay open failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20474 |  | 320475 | Parameters - Power management rules - Ground relay - Ground relay close failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20475 |  | 320476 | Parameters - Power management rules - Ground relay - Ground relay position failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20476 |  | 320477 | Parameters - Breakers - Close before excitation - CBE rerun failure - Information | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20477 |  | 320478 | Parameters - Breakers - Close before excitation - CBE failure - Information - Close before excitation failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20478 |  | 320479 | Load too high | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20479 |  | 320480 | ID to run configuration failure | INT16 | X * 1 | X * 1 | [6 empty] | X | X
Alarm status: Operating value | 20481 |  | 320482 | Parameters - System - Monitoring - Missing any genset controller - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20482 |  | 320483 | Parameters - System - Monitoring - Missing any mains controller - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20483 |  | 320484 | Parameters - System - Monitoring - Missing any bustie controller - Information - Missing any bus tie controller | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20484 |  | 320485 | Can ID not available | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20485 |  | 320486 | Duplicated CAN IDs | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20486 |  | 320487 | Parameters - Local power management - Alarms - Busbar blocked - Information - Busbar blocked due to position failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X | X | X
Alarm status: Operating value | 20487 |  | 320488 | Parameters - Local power management - Alarms - Busbar blocked - Busbar B - Information - Busbar A blocked due to position failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20488 |  | 320489 | Parameters - Local power management - Alarms - Busbar blocked - Busbar A - Information - Busbar B blocked due to position failure | INT16 | X * 1 | X * 1 |  |  | X
Alarm status: Operating value | 20489 |  | 320490 | Parameters - System - Monitoring - BTB 33 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20490 |  | 320491 | Parameters - System - Monitoring - BTB 34 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20491 |  | 320492 | Parameters - System - Monitoring - BTB 35 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20492 |  | 320493 | Parameters - System - Monitoring - BTB 36 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20493 |  | 320494 | Parameters - System - Monitoring - BTB 37 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20494 |  | 320495 | Parameters - System - Monitoring - BTB 38 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20495 |  | 320496 | Parameters - System - Monitoring - BTB 39 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20496 |  | 320497 | Parameters - System - Monitoring - BTB 40 position failure - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20497 |  | 320498 | Primary CAN missing ID 1 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20498 |  | 320499 | Primary CAN missing ID 2 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20499 |  | 320500 | Primary CAN missing ID 3 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20500 |  | 320501 | Primary CAN missing ID 4 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20501 |  | 320502 | Primary CAN missing ID 5 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20502 |  | 320503 | Primary CAN missing ID 6 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20503 |  | 320504 | Primary CAN missing ID 7 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20504 |  | 320505 | Primary CAN missing ID 8 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20505 |  | 320506 | Primary CAN missing ID 9 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20506 |  | 320507 | Primary CAN missing ID 10 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20507 |  | 320508 | Primary CAN missing ID 11 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20508 |  | 320509 | Primary CAN missing ID 12 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20509 |  | 320510 | Primary CAN missing ID 13 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20510 |  | 320511 | Primary CAN missing ID 14 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20511 |  | 320512 | Primary CAN missing ID 15 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20512 |  | 320513 | Primary CAN missing ID 16 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20513 |  | 320514 | Primary CAN missing ID 17 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20514 |  | 320515 | Primary CAN missing ID 18 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20515 |  | 320516 | Primary CAN missing ID 19 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20516 |  | 320517 | Primary CAN missing ID 20 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20517 |  | 320518 | Primary CAN missing ID 21 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20518 |  | 320519 | Primary CAN missing ID 22 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20519 |  | 320520 | Primary CAN missing ID 23 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20520 |  | 320521 | Primary CAN missing ID 24 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20521 |  | 320522 | Primary CAN missing ID 25 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20522 |  | 320523 | Primary CAN missing ID 26 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20523 |  | 320524 | Primary CAN missing ID 27 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20524 |  | 320525 | Primary CAN missing ID 28 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20525 |  | 320526 | Primary CAN missing ID 29 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20526 |  | 320527 | Primary CAN missing ID 30 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20527 |  | 320528 | Primary CAN missing ID 31 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20528 |  | 320529 | Primary CAN missing ID 32 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20529 |  | 320530 | Primary CAN missing ID 33 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20530 |  | 320531 | Primary CAN missing ID 34 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20531 |  | 320532 | Primary CAN missing ID 35 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20532 |  | 320533 | Primary CAN missing ID 36 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20533 |  | 320534 | Primary CAN missing ID 37 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20534 |  | 320535 | Primary CAN missing ID 38 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20535 |  | 320536 | Primary CAN missing ID 39 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20536 |  | 320537 | Primary CAN missing ID 40 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20537 |  | 320538 | Secondary CAN missing ID 1 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20538 |  | 320539 | Secondary CAN missing ID 2 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20539 |  | 320540 | Secondary CAN missing ID 3 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20540 |  | 320541 | Secondary CAN missing ID 4 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20541 |  | 320542 | Secondary CAN missing ID 5 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20542 |  | 320543 | Secondary CAN missing ID 6 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20543 |  | 320544 | Secondary CAN missing ID 7 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20544 |  | 320545 | Secondary CAN missing ID 8 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20545 |  | 320546 | Secondary CAN missing ID 9 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20546 |  | 320547 | Secondary CAN missing ID 10 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20547 |  | 320548 | Secondary CAN missing ID 11 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20548 |  | 320549 | Secondary CAN missing ID 12 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20549 |  | 320550 | Secondary CAN missing ID 13 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20550 |  | 320551 | Secondary CAN missing ID 14 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20551 |  | 320552 | Secondary CAN missing ID 15 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20552 |  | 320553 | Secondary CAN missing ID 16 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20553 |  | 320554 | Secondary CAN missing ID 17 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20554 |  | 320555 | Secondary CAN missing ID 18 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20555 |  | 320556 | Secondary CAN missing ID 19 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20556 |  | 320557 | Secondary CAN missing ID 20 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20557 |  | 320558 | Secondary CAN missing ID 21 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20558 |  | 320559 | Secondary CAN missing ID 22 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20559 |  | 320560 | Secondary CAN missing ID 23 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20560 |  | 320561 | Secondary CAN missing ID 24 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20561 |  | 320562 | Secondary CAN missing ID 25 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20562 |  | 320563 | Secondary CAN missing ID 26 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20563 |  | 320564 | Secondary CAN missing ID 27 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20564 |  | 320565 | Secondary CAN missing ID 28 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20565 |  | 320566 | Secondary CAN missing ID 29 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20566 |  | 320567 | Secondary CAN missing ID 30 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20567 |  | 320568 | Secondary CAN missing ID 31 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20568 |  | 320569 | Secondary CAN missing ID 32 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20569 |  | 320570 | Secondary CAN missing ID 33 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20570 |  | 320571 | Secondary CAN missing ID 34 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20571 |  | 320572 | Secondary CAN missing ID 35 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20572 |  | 320573 | Secondary CAN missing ID 36 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20573 |  | 320574 | Secondary CAN missing ID 37 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20574 |  | 320575 | Secondary CAN missing ID 38 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20575 |  | 320576 | Secondary CAN missing ID 39 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20576 |  | 320577 | Secondary CAN missing ID 40 | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20577 |  | 320578 | Priority error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20578 |  | 320579 | Parameters - Non-essential load trip - Trip 1 - Over-current - Information - NEL 1 over-current | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20579 |  | 320580 | Parameters - Non-essential load trip - Trip 1 - Under-frequency - Information - NEL 1 under-frequency | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20580 |  | 320581 | Parameters - Non-essential load trip - Trip 1 - Overload 1 - Information - NEL 1 overload 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20581 |  | 320582 | Parameters - Non-essential load trip - Trip 1 - Overload 2 - Information - NEL 1 overload 2 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20582 |  | 320583 | Parameters - Non-essential load trip - Trip 1 - Reactive overload - Information - NEL 1 reactive overload | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20583 |  | 320584 | Parameters - Non-essential load trip - Trip 2 - Over-current - Information - NEL 2 over-current | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20584 |  | 320585 | Parameters - Non-essential load trip - Trip 2 - Under-frequency - Information - NEL 2 under-frequency | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20585 |  | 320586 | Parameters - Non-essential load trip - Trip 2 - Overload 1 - Information - NEL 2 overload 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20586 |  | 320587 | Parameters - Non-essential load trip - Trip 2 - Overload 2 - Information - NEL 2 overload 2 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20587 |  | 320588 | Parameters - Non-essential load trip - Trip 2 - Reactive overload - Information - NEL 2 reactive overload | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20588 |  | 320589 | Parameters - Non-essential load trip - Trip 3 - Over-current - Information - NEL 3 over-current | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20589 |  | 320590 | Parameters - Non-essential load trip - Trip 3 - Under-frequency - Information - NEL 3 under-frequency | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20590 |  | 320591 | Parameters - Non-essential load trip - Trip 3 - Overload 1 - Information - NEL 3 overload 1 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20591 |  | 320592 | Parameters - Non-essential load trip - Trip 3 - Overload 2 - Information - NEL 3 overload 2 | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20592 |  | 320593 | Parameters - Non-essential load trip - Trip 3 - Reactive overload - Information - NEL 3 reactive overload | INT16 | X * 1 | X * 1 | % | X |  | X | X | X | X | X
Alarm status: Operating value | 20593 |  | 320594 | Parameters - System - Monitoring - Single-line hazard - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20594 |  | 320595 | ID not present | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20595 |  | 320596 | Unsupported application | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20596 |  | 320597 | Application internal CAN protocol conflict | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20597 |  | 320598 | Parameters - Power management rules - Short circuit - Short-circuit limitation - Information - Section P> | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20598 |  | 320599 | Dry mode: Voltage level unexpected | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20599 |  | 320600 | Invalid DAVR configuration | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20600 |  | 320601 | Parameters - Communication - DEIF network - DEIF network fork detected - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20602 |  | 320603 | Parameters - Communication - DEIF network - DEIF network has only one connection - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20604 |  | 320605 | Parameters - Breakers - Generator breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | ° | X |  | X | X | X
Alarm status: Operating value | 20604 |  | 320605 | Parameters - Breakers - Bus tie breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | ° |  | X
Alarm status: Operating value | 20604 |  | 320605 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | ° | [5 empty] | X | X
Alarm status: Operating value | 20605 |  | 320606 | Parameters - Breakers - Mains breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | ° |  |  |  | X
Alarm status: Operating value | 20605 |  | 320606 | Parameters - Breakers - Tie breaker monitoring - Vector mismatch - Information - Breaker vector mismatch | INT16 | X * 1 | X * 1 | ° | [6 empty] | X
Alarm status: Operating value | 20607 |  | 320608 | Parameters - Transducers - Transducer 1 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
Alarm status: Operating value | 20608 |  | 320609 | Parameters - Transducers - Transducer 2 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
Alarm status: Operating value | 20609 |  | 320610 | Parameters - Transducers - Transducer 3 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
Alarm status: Operating value | 20610 |  | 320611 | Parameters - Transducers - Transducer 4 - Monitoring - Vector mismatch - Information | INT16 | X * 1 | X * 1 | ° | X | X | X | X | X | X | X
Alarm status: Operating value | 20611 |  | 320612 | Parameters - Transducers - Transducer 1 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20612 |  | 320613 | Parameters - Transducers - Transducer 2 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20613 |  | 320614 | Parameters - Transducers - Transducer 3 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20614 |  | 320615 | Parameters - Transducers - Transducer 4 - Reference B - AC setup - Phase sequence error - Information - Reference B phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20615 |  | 320616 | Parameters - Transducers - Transducer 1 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20616 |  | 320617 | Parameters - Transducers - Transducer 2 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20617 |  | 320618 | Parameters - Transducers - Transducer 3 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20618 |  | 320619 | Parameters - Transducers - Transducer 4 - Reference A - AC setup - Phase sequence error - Information - Reference A phase sequence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20619 |  | 320620 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20620 |  | 320621 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20621 |  | 320622 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20622 |  | 320623 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20623 |  | 320624 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20624 |  | 320625 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20625 |  | 320626 | AC protections not running | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20626 |  | 320627 | AC data is missing | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20627 |  | 320628 | Live voltage detected | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20628 |  | 320629 | Internal issue detected. A restart is required soon! | INT16 | X * 10 | X * 0.1 | % | X | X | X | X | X | X | X
Alarm status: Operating value | 20629 |  | 320630 | Parameters - System - Monitoring - Missing controllers - Information | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20630 |  | 320631 | Card issue detected | INT16 | X * 10 | X * 0.1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20631 |  | 320632 | Card configuration failed | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20632 |  | 320633 | Unknown traffic on DEIF network | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20633 |  | 320634 | Parameters - Auxiliary - Pump logic 1 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20634 |  | 320635 | Parameters - Auxiliary - Pump logic 2 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20635 |  | 320636 | Parameters - Auxiliary - Pump logic 3 - Fill alarm - Information - Fill failure | INT16 | X * 1 | X * 1 |  | X |  | X | X | X
Alarm status: Operating value | 20636 |  | 320637 | Local IO service error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20637 |  | 320638 | App logging failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20638 |  | 320639 | Event logging failure | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20639 |  | 320640 | Licence error | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20640 |  | 320641 | Brightness is dimmed according to temperature | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 20641 |  | 320642 | Parameters - Grid code - Mains sync inhibit - Information | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Operating value | 20642 |  | 320643 | Parameters - Grid code - Capability curve - Import protection - Information - Power import capability curve protection | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Operating value | 20643 |  | 320644 | Parameters - Grid code - Capability curve - Export protection - Information - Power export capability curve protection | INT16 | X * 1 | X * 1 |  |  |  | X | X
Alarm status: Operating value | 20644 |  | 320645 | Hardware is not compatible based on module versions | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21500 |  | 321501 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21501 |  | 321502 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21502 |  | 321503 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21503 |  | 321504 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21504 |  | 321505 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21505 |  | 321506 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21506 |  | 321507 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21507 |  | 321508 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21508 |  | 321509 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21509 |  | 321510 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21510 |  | 321511 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21511 |  | 321512 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21512 |  | 321513 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21513 |  | 321514 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21514 |  | 321515 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21515 |  | 321516 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21516 |  | 321517 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21517 |  | 321518 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21518 |  | 321519 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21519 |  | 321520 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21520 |  | 321521 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21521 |  | 321522 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21522 |  | 321523 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21523 |  | 321524 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21524 |  | 321525 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21525 |  | 321526 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21526 |  | 321527 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21527 |  | 321528 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21528 |  | 321529 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21529 |  | 321530 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21530 |  | 321531 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21531 |  | 321532 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21532 |  | 321533 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21533 |  | 321534 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21534 |  | 321535 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21535 |  | 321536 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21536 |  | 321537 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21537 |  | 321538 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21538 |  | 321539 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21539 |  | 321540 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21540 |  | 321541 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21541 |  | 321542 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21542 |  | 321543 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21543 |  | 321544 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21544 |  | 321545 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21545 |  | 321546 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21546 |  | 321547 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21547 |  | 321548 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21548 |  | 321549 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21549 |  | 321550 | Digital custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21600 |  | 321601 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21601 |  | 321602 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21602 |  | 321603 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21603 |  | 321604 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21604 |  | 321605 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21605 |  | 321606 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21606 |  | 321607 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21607 |  | 321608 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21608 |  | 321609 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21609 |  | 321610 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21610 |  | 321611 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21611 |  | 321612 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21612 |  | 321613 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21613 |  | 321614 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21614 |  | 321615 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21615 |  | 321616 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21616 |  | 321617 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21617 |  | 321618 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21618 |  | 321619 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21619 |  | 321620 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21620 |  | 321621 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21621 |  | 321622 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21622 |  | 321623 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21623 |  | 321624 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21624 |  | 321625 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21625 |  | 321626 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21626 |  | 321627 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21627 |  | 321628 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21628 |  | 321629 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21629 |  | 321630 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21630 |  | 321631 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21631 |  | 321632 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21632 |  | 321633 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21633 |  | 321634 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21634 |  | 321635 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21635 |  | 321636 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21636 |  | 321637 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21637 |  | 321638 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21638 |  | 321639 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21639 |  | 321640 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21640 |  | 321641 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21641 |  | 321642 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21642 |  | 321643 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21643 |  | 321644 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21644 |  | 321645 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21645 |  | 321646 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21646 |  | 321647 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21647 |  | 321648 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21648 |  | 321649 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21649 |  | 321650 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21650 |  | 321651 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21651 |  | 321652 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21652 |  | 321653 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21653 |  | 321654 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21654 |  | 321655 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21655 |  | 321656 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21656 |  | 321657 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21657 |  | 321658 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21658 |  | 321659 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21659 |  | 321660 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21660 |  | 321661 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21661 |  | 321662 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21662 |  | 321663 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21663 |  | 321664 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21664 |  | 321665 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21665 |  | 321666 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21666 |  | 321667 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21667 |  | 321668 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21668 |  | 321669 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21669 |  | 321670 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21670 |  | 321671 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21671 |  | 321672 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21672 |  | 321673 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21673 |  | 321674 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21674 |  | 321675 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21675 |  | 321676 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21676 |  | 321677 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21677 |  | 321678 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21678 |  | 321679 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21679 |  | 321680 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21680 |  | 321681 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21681 |  | 321682 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21682 |  | 321683 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21683 |  | 321684 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21684 |  | 321685 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21685 |  | 321686 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21686 |  | 321687 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21687 |  | 321688 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21688 |  | 321689 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21689 |  | 321690 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21690 |  | 321691 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21691 |  | 321692 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21692 |  | 321693 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21693 |  | 321694 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21694 |  | 321695 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21695 |  | 321696 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21696 |  | 321697 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21697 |  | 321698 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21698 |  | 321699 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21699 |  | 321700 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21700 |  | 321701 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21701 |  | 321702 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21702 |  | 321703 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21703 |  | 321704 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21704 |  | 321705 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21705 |  | 321706 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21706 |  | 321707 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21707 |  | 321708 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21708 |  | 321709 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21709 |  | 321710 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21710 |  | 321711 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21711 |  | 321712 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21712 |  | 321713 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21713 |  | 321714 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21714 |  | 321715 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21715 |  | 321716 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21716 |  | 321717 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21717 |  | 321718 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21718 |  | 321719 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21719 |  | 321720 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21720 |  | 321721 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21721 |  | 321722 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21722 |  | 321723 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21723 |  | 321724 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21724 |  | 321725 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21725 |  | 321726 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21726 |  | 321727 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21727 |  | 321728 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21728 |  | 321729 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21729 |  | 321730 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21730 |  | 321731 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21731 |  | 321732 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21732 |  | 321733 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21733 |  | 321734 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21734 |  | 321735 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21735 |  | 321736 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21736 |  | 321737 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21737 |  | 321738 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21738 |  | 321739 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21739 |  | 321740 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21740 |  | 321741 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21741 |  | 321742 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21742 |  | 321743 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21743 |  | 321744 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21744 |  | 321745 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21745 |  | 321746 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21746 |  | 321747 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21747 |  | 321748 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21748 |  | 321749 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21749 |  | 321750 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21750 |  | 321751 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21751 |  | 321752 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21752 |  | 321753 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21753 |  | 321754 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21754 |  | 321755 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21755 |  | 321756 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21756 |  | 321757 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21757 |  | 321758 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21758 |  | 321759 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21759 |  | 321760 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21760 |  | 321761 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21761 |  | 321762 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21762 |  | 321763 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21763 |  | 321764 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21764 |  | 321765 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21765 |  | 321766 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21766 |  | 321767 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21767 |  | 321768 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21768 |  | 321769 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21769 |  | 321770 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21770 |  | 321771 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21771 |  | 321772 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21772 |  | 321773 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21773 |  | 321774 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21774 |  | 321775 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21775 |  | 321776 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21776 |  | 321777 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21777 |  | 321778 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21778 |  | 321779 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21779 |  | 321780 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21780 |  | 321781 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21781 |  | 321782 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21782 |  | 321783 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21783 |  | 321784 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21784 |  | 321785 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21785 |  | 321786 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21786 |  | 321787 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21787 |  | 321788 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21788 |  | 321789 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21789 |  | 321790 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21790 |  | 321791 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21791 |  | 321792 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21792 |  | 321793 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21793 |  | 321794 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21794 |  | 321795 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21795 |  | 321796 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21796 |  | 321797 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21797 |  | 321798 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21798 |  | 321799 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Operating value | 21799 |  | 321800 | Analogue custom alarm | INT16 | X * 1 | X * 1 |  | X | X | X | X | X | X | X
Alarm status: Delay timer elapsed time | 22003 |  | 322004 | Parameters - Engine - Stop sequence - Stop failure - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22005 |  | 322006 | Parameters - Engine - Start sequence - Crank failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22006 |  | 322007 | Parameters - Engine - Protections - Speed - Overspeed 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22007 |  | 322008 | Parameters - Engine - Protections - Speed - Overspeed 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22008 |  | 322009 | Parameters - Engine - Protections - Speed - Under-speed 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22009 |  | 322010 | Parameters - Engine - Protections - Speed - Under-speed 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22010 |  | 322011 | Parameters - Engine - Running detection - Magnetic pickup wire break - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22013 |  | 322014 | Parameters - Engine - Protections - Pressure - Oil pressure 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22014 |  | 322015 | Parameters - Engine - Protections - Pressure - Oil pressure 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22015 |  | 322016 | Parameters - Engine - Protections - Temperature - Oil temperature 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22016 |  | 322017 | Parameters - Engine - Protections - Temperature - Oil temperature 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22017 |  | 322018 | Parameters - Engine - Protections - Temperature - Coolant temperature 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22018 |  | 322019 | Parameters - Engine - Protections - Temperature - Coolant temperature 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22019 |  | 322020 | Parameters - Engine - Protections - Temperature - Coolant temperature 3 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22020 |  | 322021 | Parameters - Engine - Protections - Level - Coolant level 1 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22021 |  | 322022 | Parameters - Engine - Protections - Level - Coolant level 2 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22022 |  | 322023 | Parameters - Engine - Protections - Level - Coolant level 3 - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22027 |  | 322028 | Parameters - Engine - Running detection - Primary running feedback failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22041 |  | 322042 | Parameters - Breakers - Generator breaker monitoring - Closing failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22041 |  | 322042 | Parameters - Breakers - Bus tie breaker monitoring - Closing failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22041 |  | 322042 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22042 |  | 322043 | Parameters - Breakers - Generator breaker monitoring - Opening failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22042 |  | 322043 | Parameters - Breakers - Bus tie breaker monitoring - Opening failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22042 |  | 322043 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22043 |  | 322044 | Parameters - Breakers - Generator breaker monitoring - Position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22043 |  | 322044 | Parameters - Breakers - Bus tie breaker monitoring - Position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22043 |  | 322044 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22044 |  | 322045 | Parameters - Breakers - Generator breaker monitoring - Configuration failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22044 |  | 322045 | Parameters - Breakers - Bus tie breaker monitoring - Configuration failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22044 |  | 322045 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22045 |  | 322046 | Parameters - Breakers - Generator breaker monitoring - Synchronisation failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22045 |  | 322046 | Parameters - Breakers - Bus tie breaker monitoring - Synchronisation failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22045 |  | 322046 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22046 |  | 322047 | Parameters - Breakers - Generator breaker monitoring - De-load failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22046 |  | 322047 | Parameters - Breakers - Bus tie breaker monitoring - De-load failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  | X
Alarm status: Delay timer elapsed time | 22046 |  | 322047 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [5 empty] | X | X
Alarm status: Delay timer elapsed time | 22049 |  | 322050 | Parameters - Breakers - Mains breaker monitoring - Closing failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer elapsed time | 22049 |  | 322050 | Parameters - Breakers - Tie breaker monitoring - Closing failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer elapsed time | 22050 |  | 322051 | Parameters - Breakers - Mains breaker monitoring - Opening failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer elapsed time | 22050 |  | 322051 | Parameters - Breakers - Tie breaker monitoring - Opening failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer elapsed time | 22051 |  | 322052 | Parameters - Breakers - Mains breaker monitoring - Position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer elapsed time | 22051 |  | 322052 | Parameters - Breakers - Tie breaker monitoring - Position failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer elapsed time | 22052 |  | 322053 | Parameters - Breakers - Mains breaker monitoring - Configuration failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer elapsed time | 22052 |  | 322053 | Parameters - Breakers - Tie breaker monitoring - Configuration failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer elapsed time | 22053 |  | 322054 | Parameters - Breakers - Mains breaker monitoring - Synchronisation failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer elapsed time | 22053 |  | 322054 | Parameters - Breakers - Tie breaker configuration - Synchronisation failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer elapsed time | 22054 |  | 322055 | Parameters - Breakers - Mains breaker monitoring - De-load failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s |  |  |  | X
Alarm status: Delay timer elapsed time | 22054 |  | 322055 | Parameters - Breakers - Tie breaker monitoring - De-load failure - Information - Delay | INT16 | X * 10 | X * 0.1 | s | [6 empty] | X
Alarm status: Delay timer elapsed time | 22060 |  | 322061 | Parameters - Mains - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s |  |  | X | X
Alarm status: Delay timer elapsed time | 22060 |  | 322061 | Parameters - Busbar - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  |  |  | X | X | X
Alarm status: Delay timer elapsed time | 22060 |  | 322061 | Parameters - Busbar B - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22061 |  | 322062 | Parameters - Generator - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | X |  | X | X | X
Alarm status: Delay timer elapsed time | 22061 |  | 322062 | Parameters - Busbar A - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s |  | X
Alarm status: Delay timer elapsed time | 22061 |  | 322062 | Parameters - Mains - AC setup - Phase sequence error - Information - Delay | INT16 | X * 1 | X * 1 | s | [5 empty] | X | X